## Revision
PLS-CADD Weather Case and Load Criteria Generator
Rev | Date | Details
4 | 2016-10-21 | Added capability for multiple height ranges - included Structure Groups
| 2016-10-21 | Revised Load case selection tabs to identify if the weather case "exists" (selected for input)
| 2016-10-21 | Added Instructions to Tab "Control"
| 2016-10-21 | Added "Revision" tab
| 2016-10-22 | Structure Groups: Added Groups to cater for Failure containment to be resisted by strain structures only Load Case: Structure group lookup formula revised for failure containment cases (as above)
5 | 2016-10-22 | Issued for internal review
6 | 2016-12-01 | Weather Cases: C&M Snow & Ice loading cases: Required column - formula revised to look at radial thickness only
| 2016-12-01 | Weather Cases: Case MOT - revised Label to include temperature
| 2016-12-01 | Weather Cases: Added capability for input of 4 different conductor s and 4 different earthwires | Red = Items to do
| 2016-12-01 | Weather Cases: Modified 12.01 height bands for ice and snow to be only in multiples of 100m
| 2016-12-01 | Structure Groups: Modified
| 2016-12-01 | Conductors: Added OPGW 70mm2 Hitachi; Added OPGW 174mm2 data; added 120mm2 Hitachi
| 2016-12-01 | Moved Instructions to New Tab; added hyperlinks between tabs
| 2016-12-01 | Modified allocation of Failure Containment load cases to structure group "Stop" requiring manual input in the staking table. This enables both Vulnerability (all structures designated 'Stop') and Security analysis (only designated structures) | Consider adding different levels of "stop", e.g. Stop = all specified FC StopL2, all conductor long with 2 cond bkn torsion StopT1, One conductor torsion, etc.
| 2016-12-05 | Modified Strength factor for Concrete poles so that only one value is specified (others need to be zero)
7 | 2016-12-11 | General update following internal feedback
- | 2017-01-17 | Additional update and revision following comments from M. Wilson
A | 2017-02-01 | FIRST ISSUE for external feedback & application
B1 | 2017-02-04 | Load Criteria - Modified weather cases for HWD and RSL Load criteria to include Wind Region and Height (as applicable)
B1 | 2017-02-04 | Weather Cases - Revised Case Selection columns with value "0" to "-" to be consistent and facilitate dropdown selection
B1 | 2017-02-04 | Staking Table - corrected Comments columns for wind on spans and structures to Columns 4 and 7 respectively ( as per ADEGL.02.06)
B1 | 2017-02-06 | PLS-CADD Folders: Added Hyperlinks to other spreadsheet tabs
B1 | 2017-02-15 | Control - Added "revision" to the Spreadsheet and Criteria Filenames
B2 | 2017-02-21 | Weather Cases: Added EDD load case to differentiate between EDW (Loading based on ED temp) and EDD (clearances based on coincident temp) Made EDD, HWD and MWD weather cases dependent on operating temperature (MOT with coincident wind) for each conductor type.
B2 | 2017-02-21 | Cables: Changed Column A to display either 1 or "-" (rather than 0). Corrected Cell A39 to check A38. Ditto for A40 through A53.
B2 | 2017-02-21 | Load Criteria: Wind direction column U. "MAX" changed to "Max".
B2 | 2017-02-21 | Load Criteria: Double & Single circuit torsional snow / Ice cases. Added sets with ahead / back spans at 70% (those not split 70%:40%)
B2 | 2017-02-21 | Load Criteria: Cells AY233 through AY264 and AY288 through AY319, corrected ‘Ahead’ and ‘Back’ (were transposed).
B3 | 2017-02-22 | Weather Cases: Modified Labels for TP.DL 12.02 Weather Cases to indicate the conductor operating temperature rather than the calculated wire temperature (to simplify lookup selection)
B | 2017-02-23 | ISSUED for external feedback & Project application
C1 | 2107-03-14 | Ref: Generic wind speeds rounded to nearest 1m/s
C1 | 2017-03-28 | Structure Groups: Added Note that the Max Height is to be rounded up to the nearest 100m
C1 | 2017-03-28 | Ref: Everyday temp Lookup table values corrected; Cell M54 = 10; Cell O54 = 5
C2 | 2017-03-29 | Control: Modified conditional formatting for Cell D24 to highlight "orange" when Ice Zone N1 selected for South Island
C2 | 2017-04-03 | Ref: Corrected the lookup altitude values for Ice and snow thicknesses
C2 | 2017-04-04 | Instructions: Corrected "Generic wind pressures are presented in cells Z4 and AC4." Corrected Wind Speeds on Structures - Comment 7 Corrected Wind Speeds on Spans - Comment 4
C2 | 2017-04-04 | Staking Table - modified Max and Min elevations to give the rounded up and rounded down values to nearest 100m
C | 2017-04-04 | ISSUED for external feedback & Project application
D1 | 2017-04-05 | Weather Cases: Introduced cases for structural deflection for Pole serviceability limits: NOTE WILL REQUIRE REVISION TO TP.DL 12.01. HWD (Structural) 3yr RP with ted MWD (structural) 50yr RP with tmw
D1 | 2017-04-05 | Load Criteria: Modified HWD and MWD load cases to identify the correct weather case and to extend to all conductor types
D1 | 2017-04-05 | Control: Deleted hidden values in Cells I10 - I12 (previously employed for test purposes); not critical
D1 | 2017-04-05 | Structure Groups; Weather Cases, etc. Row 1: Revised Lookup for Title Site Name-Section to remove the duplicate term "Section"
D1 | 2017-04-05 | Control: Added input data entry to identify whether the type of pole structure (if applicable). These are required for the generic serviceability load criteria (deflection, crack limit). Load Criteria: Added note that the serviceability load cases for poles (SP, CP) are only required for generic design - they are not required for PLS-CADD models (the poles are designed to meet certain limits that are a function of the selected extreme load; if they survive the extreme load then they are deemed to survive the serviceability loading).
D2 | 2017-04-09 | Instructions: Added clarification for scope of spreadsheet: "The spreadsheet assumes there will be only Towers and or poles within a CADD model. It does not differentiate between different pole types. The designer should recognise that Standard poles (wood, concrete, steel) are handled differently to towers and (special) steel poles in terms of ability to withstand RSL loading. Structures that are required to withstand RSL shall be designated "STOP" structures in the staking table under "Manual Structure Group Membership" Note 5.01: "Load Case Applicable"? Added clarification that the selected cases are applicable to PLS-CADD models only. For generic design of new standard structures the designer is required to make allowance for TP Standard poles cracking and deflection limits
D | 2017-04-09 | ISSUED for external feedback & Project application
E1 | 2017-04-11 | Control: Introduced revision to "Pole" type definitions dependent on pole cracking or deflection limits as specified in their supply specifications (see new note 2.5 in tab Instructions)
E1 | 2017-04-11 | Instructions: Added new note 2.5 to define the applicable supply standard for pole types
E1 | 2017-04-11 | Weather Cases: Added cases for High Wind Deflection (Structural) & Maximum Wind deflection (Structural); Modified formula in column "Weather case reqd" to look for pole type rather than conductor (these cases only required for generic serviceability checks for standard steel and wood poles)
E1 | 2017-04-11 | Load Criteria: Column A, "Load Case Applicable?" cells A69 to A140 corrected to =IF(Control!$D$4="Y","-",1)
E1 | 2017-04-11 | Load Criteria: Made "Strength factor for concrete pole" 1 for all Load Criteria; ditto wood poles
E1 | 2017-04-11 | Load Criteria: Separated Replacement Criteria Load cases from Serviceability load cases (deflection & cracking); Made Replacement criteria cases applicable to all structure types. Reorganised the Serviceability cases to make presentation more logical (separated Replacement cases)
E1 | 2017-04-11 | Load Criteria: Serviceability cases Changed Crack Factor to EDW = 0.4; HWD=0.65, MWD =0. Removed values from all cases except nominated Pole Serviceability Load Criteria; All others set to Zero (not checked)
E1 | 2017-04-11 | Load Criteria: Changed all "Strength Factor Concrete Poles Zero Tension" values to "0" (not checked)
E2 | 2017-04-12 | Load Criteria: RSL Ice Torsion Column AY rows 343 to 374 (Weather Case "RI"); Formulae changed to =IF($N343="","",$N343&":1:"&IF($L343="A","Ahead","Back")) [ the "Ahead" and "Back" were transposed]
E2 | 2017-04-12 | Load Criteria: Revised the formulae in the PLS command columns for Differential TI, EI and ES Torsional load cases to correctly identify the "Affected" set-span for the 40% thickness; introduced columns P:T to identify Set-spans "Not affected" (70% thickness)
E2 | 2017-04-12 | Instructions: Renumbered instructions from 4 onwards due to duplicate numbering
E2 | 2017-04-12 | Instructions: Note 7 Load Criteria - added comments for the input columns for Phase-Set AFFECTED and NOT AFFECTED
E2 | 2017-04-13 | Instructions: Modified Note 7.10 to require Project / Asset Spreadsheet revision control should employ the Tab "Revision"
E2 | 2017-04-13 | Instructions: Key to Cell Shading: Added definitions for Purple and Red cells
E2 | 2017-04-13 | Control: Added space to permit addition of designers comments
E2 | 2017-04-13 | All Tabs: Revised Filter tabs to limit columns to those required for application All Tabs: Formatted to permit printing (if required to accompany DCD, etc.)
E2 | 2017-04-17 | Revised Spreadsheet Filename to PLS-CADD WC & LC Generator Master
E3 | 2017-04-20 | Load Criteria: Load cases RW Longitudinal (Rows 211 & 212) have not been repeated for NA- Winds. 2 new rows inserted at 213 for NA- Winds Ditto for RS and RI Longitudinal Load cases
E3 | 2017-04-20 | Weather Cases: Security conditions, RW, RS and RI. a) Revised Case Descriptions to refer to input "SECURITY Level (for RSL loading)" in Control Tab (Control!$D$25) which identifies the wind pressure at the time of breakage (i.e. 1 = 100Pa; 2 = 200Pa, etc.) b) Changed RW and RS to be height dependent cases (Column G) and replaced return period with "Security Level"
E3 | 2017-04-20 | Load Criteria: All Security Conditions RW, RS and RI. Changed Return period to refer to selected Security Level
E3 | 2017-04-20 | Instructions: Added new note 5.5 and Expanded Note 7.11 to explain that Vulnerability Analysis relating to Security Cases will require the Weather Cases and Load Criteria to be repeated for each selected security level to be included in the analysis
E4 | 2017-04-20 | Load Criteria: Type of Analysis (Column D) Changed FC/VUL to FC only to permit case selection for different Security levels
E4 | 2017-04-24 | Instructions: Modified Note 2.2 to clarify the default situation is for a single height “group” for all analyses. The decision to proceed with more than 1 height group will be dependent on showing identified overloads can be mitigated by this method
E | 2017-04-24 | ISSUED for Project application
F1 | 2017-06-05 | All Tabs (for printing as project records): Added cell that identifies the spreadsheet filename and revision from which the WC and LC were generated
F1 | 2017-07-22 | Weather Cases: Changed "Wire Gust Response Factor" to "1" for all load cases (not TPNZ 2008) as PLS-CADD does not properly apply TSRF and SRF for all design checks. Site specific wind speeds now required to cater for the effects of site-specific SRF (to be obtained from Transpower)
F1 | 2017-07-22 | Control: For Generic Load Cases added input for "average Span length" and included Span Reduction Factor on derived wind speeds
F | 2017-07-23 | ISSUED for Project application
G1 | 2017-08-04 | Load Criteria: Inserted new column (AS) for "Strength Factor Hardware"
G1 | 2017-08-22 | Load Criteria - Added explanation Comments to Select columns "Structure Type" and "Type of Analysis"
G1 | 2017-08-22 | Control: Added Conditional formatting to cells E37 & E38 for Site Specific (hidden)
G | 2017-11-29 | ISSUED for Project application
H1 | 2018-04-13 | Control: Deleted Input Cell (row) C21 to remove reference to Central Plateau and references to 25km from coast (should be 5km throughout); The requirement for ted & tmw is not dependant on distance to coast; Tab: Ref corrected lookup to match
H1 | 2018-04-13 | Load Criteria: Linked note for Max wind angle interval to Control Tab for "Vulnerability" = Y; Revised note Instructions: Added example where the default interval can be accessed
H1 | 2018-04-13 | Instructions: Added new Note 7.12 addressing the required wind direction interval for weather cases with wind dirn "MAX"
H1 | 2018-04-13 | Load Criteria: Concrete Pole serviceability strength factors modified as follows (only one check permitted for 1 load case): EDW for 1st Crack = 0 (not checked); zero tension 0.4 HWD 1st Crack = 0.65; zero tension 0.0 (not checked)
H1 | 2018-06-17 | Control: Added pop up note to "Failure Containment (FC) on all structures ?" to identify that if "No" is selected then those structures designated "STOP" structures need to be entered in the Staking table
H1 | 2018-10-30 | Structure Groups: When "FC applied to all structures" is entered as "Yes" in tab:Control - remove "STOP" groups to avoid confusion
H1 | 2018-10-30 | Instructions: Revised Note 7.05 to clarify how FC cases are to be applied and handled
H1 | 2018-10-30 | Control: For criteria file add the selected Return Period in the Filename
H1 | 2018-10-30 | Control: Added Revision control for Project specific versions of the master spreadsheet
H1 | 2019-02-04 | Staking Table: Deleted 1 column data "Row Number"
H1 | 2019-07-24 | Load Criteria: Added differential wind cases for CM1, CM2 and CM3; added note that all CM load cases are Generic and subject to project specific modification
H1 | 2019-07-24 | Load Criteria: Added Differential snow & ice cases for CM2 & CM3 (note these are identical, i.e. CM2S = CM3S, etc.)
H1 | 2019-07-24 | Weather Cases: added CM2S & CM2I for extended periods with possibility of snow and ice
H1 | 2019-08-20 | Weather Cases: Added FTD (Falling Tree Deflection) wind case for TP.DL 12.02 clearance checks
H1 | 2019-09-05 | Ref: Modified density formula in cell U120 to give zero for ice thickness of zero Added notes throughout the Tab that no data is to be modified
H1 | 2019-09-19 | Weather Cases: Wire Gust Response Factor. Added formula to give factor 1.2 for ice / snow cases with wind
H1 | 2019-09-19 | Instructions: Updated notes (at end of instructions) for Terrain Category. This requirement is now deleted as is not applicable for "site specific winds". Deleted requirement for Ice drag factor in Loading code TPNZ
H | 2019-09-30 | ISSUED for Project application
H-M1 | 2020-04-02 | Added Weather Cases EDS_xx (tedd), and now all snow / ice weather cases up to and including the zones relevant to maximum altitude specified in the control tab are shown in "Weather Cases All" Tab. Structure loads are untouched. Weather cases relevant to those required for UCA risk assessment have been updated. It is noted the following are cases vary with height and remain untouched by this revision RS, RI, CM, MTS, RC, CA, RCS, RCI.
PENDING
Load Criteria: Consider adding columns / tabs for specific PLS-CADD run types, e.g. Blowout reports, etc.
Weather Cases: Consider additional cases for earthwires when used for external clearance checks (different conductor temperatures)
Instructions: Add check list for all the PLS-CADD reports and checks that need to be tidied up to refer to the new load case names
H-M2 | 2021-03-04 | Ammended torsional snow/ice cases so that correct 40/70% is applied to strain structures.
H-M3 | 2021-04-15 | Ammended cell U120 on ref tab. Was incorrectly not applying densities for north island ice zones. Affected RSL and CM based ice cases for N0 and N1.
H-M4 | 2021-08-16 | Added corresponding weather cases to Load Criteria for cases (CM2S, CM2I, CM3S & CM3I) which did not have opposing NA+ / NA- pair. Change to original weather case table to negate weather cases (MOT, EDD, HWD & MWD) for conductors 2, 3 & 4 where no conductor is specified.

## Instructions
PLS-CADD Weather Case and Load Criteria Generator
INSTRUCTIONS | This spreadsheet provides the default weather case and loading criteria input for PLS-CADD Line models for evaluation of a typical transmission line and its components in accordance with the principles of TP.DL 12.01 Loading Code. For lines containing any special structures (quad circuit, tee-offs, etc.) additional cases may be required which shall be developed employing the same principles and submitted for approval and inclusion into this Master Generator. The spreadsheet contains tabs standardising data labelling and input for: - PLS Folder identification - Cable Tension Criteria (up to 4 conductors and earthwire types may be accommodated) - Structure Groups required for the Loading - Weather Case and - Structure Load Criteria - Designation of RSL capable (Stop) structures
| The weather and loads cases generated by this spreadsheet permits differentiation between the following variables along the line for: a) AS/NZS 1170.2 Wind Regions (PRESENT VERSION DOES NOT CATER FOR TWO WIND ZONES FOR A SINGLE LINE SECTION) b) Different height zones for ice and snow loading c) Different conductors and their ruling conditions | Wind Zone requires definition of limiting station in Structure Groups
The spreadsheet assumes there will be only Towers and or poles within a CADD model. It does not differentiate between different pole types. The designer should recognise that Standard poles (wood, concrete, steel) are handled differently to towers and (special) steel poles in terms of ability to withstand RSL loading. Structures that are required to withstand RSL shall be designated "STOP" structures in the staking table under "Manual Structure Group Membership"
Key to Cell shading
Cells requiring user data input. (some cells provide guidance by comments and or default drop down lists that restrict the allowable input)
Cells containing formulae *do not overwrite*. Note, some formulae in Weather & Load Case tabs are not suitable for copying through the sheet. Additional cases should be input at the appropriate sheet row for correct labelling and data.
Cells containing default input data in the "inclusion" sense (may be modified to suit actual requirements; these dictate the case name, etc.)
Cells containing default input data in the "exclusion" sense (may be modified to suit actual requirements; these dictate the case name, etc.)
Cells with data to be transferred to PLS-CADD (all contain formulae / data - same as above); Also used as a warning of possible data error in Control Tab
Data Error, or Data required
Tabs Within this spreadsheet
INSTRUCTIONS | (This tab) Provides instructions and guidelines for the use of this design tool
STAKING TABLE | The PLS-CADD structure data; Provides ability to extract the ground elevation data and input generic and site specific reference wind speeds. Also used to define which structures are to be designated "Stop" structures to which residual static loading is to be applied.
CONTROL INPUT | Master data for the spreadsheet; Defines conductors and earthwires and their operating conditions together with details of the site locations, heights, wind regions, etc.
STRUCTURE GROUPS | Provide the master structure groups and their naming for the PLS-CADD Model Requires definition of the ground level height bands to be applied along the line route
WEATHER CASES | Provides the Master Weather cases to be applied to the Line Model; Cases are selected depending on the type of analysis, i.e. vulnerability analysis and or final reliability /security design. Also provides the default weather cases for Safety (C&M) and Serviceability loading. The weather cases are dependant on the selected wind regions and height bands along the line route and will require multiple usage if more than one region / band is selected
CABLES | Facilitates the data entry necessary for the "Criteria / Cable Tensions"; requires Cable filenames to be entered in Tab "Control".
LOAD CRITERIA | Provides the Master Loading Criteria to be applied to the Line Model employing standard case naming; Permits selection as required for vulnerability analysis and or final reliability /security design. Also provides the default weather cases for Safety (C&M) and Serviceability loading. The weather cases are dependant on the selected wind regions and height bands
PLS-CADD | "Tools" for auto-naming file directory data entry into PLS-CADD.
Hidden Tabs | "Ref" Provides the reference lookup data obtained from AS/NZS 1170.2 and TP.DL 12.01
"Conductor-Properties" The default lookup data for Transpower standard conductors, earthwires and OPGW
PROCEDURE
Preliminaries
1 | Determine the number of line PLS-CADD Models required:
1.1 | The optimum solution is for the complete line to be contained within one PLS-CADD Model. To assist the following criteria shall be employed for determining whether or not a line shall be split:
1.2 | The length and complexity of the line. Some lines are too long and result in PLS-CADD models of a size that restricts its functionality and or usability. In these cases the line shall be split. Typically models shall be restricted to approximately 200 structures (discuss with Transpower)
1.3 | The global terrain category (TC). Typically the model shall adopt a Global TC that best represents the sites / span specific TC value as derived in accordance with ADEGL.02.11. If there are significant differences along the line or cost benefits for adopting different TC along the line, consideration shall be given to splitting the line route.
1.4 | The AS/NZS 1170.2 Wind Regions traversed. If the line crosses the boundary between "W" and "A6/A7" then weather cases will be required for both regions and the structure groups will need to be restricted to a station along the line. | This feature has not yet been automated (contact Transpower if required)
1.5 | Ground elevations: Determine the ranges of ground elevations traversed and whether or not more than one height group is required. Copy the PLS-CADD Staking table to tab "Staking Table". This provides the maximum and minimum ground elevations along the line route. Typically all models shall adopt a single height derived from the maximum ground line elevation (this is the default for vulnerability analyses). A single height band shall be adopted initially for reliability analyses. However, for some lines, adopting a single height can result in some structures being subject to ice loads and temperatures that are more critical than that required by TP.DL 12.01 with resulting structure overloads. If deemed appropriate multiple height bands may be utilised to better represent the conditions along the line route. This decision will be based on cost-benefit analyses. Tab "Structure Groups" permits these height bands to be pre-selected (after an engineering analysis of the line route). The default interval is derived based on three equal splits between zero and the maximum height (from the staking table). The bands may be manually adjusted.
1.6 | NOTE: PLS-CADD limits the number of weather cases to 100. The default number of TP.DL 12.01 weather cases required for each wind region / height band is dependent on the analysis type; for Vulnerability analysis 40 cases are required for the base condition plus another 30 for another wind region and 34 for each height band. Consequently only one height band is recommended for Vulnerability analysis. For Reliability analysis 37 cases are required for the base condition (this includes all default serviceability and safety cases) plus another 5 for another wind region and 27 for each height band. Therefore, with two wind regions the maximum number of height bands will be 2; for one wind region the max number of height bands will be 3. The number of Structure Load Criteria is limited to 1000. The default number of load cases is approx. 300 plus another 90 for another wind region. An additional 170 cases are required for each height band / wind region. Therefore the maximum number of height bands will be approx. 2 for lines with 2 wind regions and 4 for lines with one wind region (the actual number will be dependent on the line configuration and structure complexity). With the above program limits the maximum number of height bands will be taken as 3 irrespective of the number of wind regions.
1.7 | The number of conductor and or earthwire types along the line - this only defines the weather cases and cable tension criteria necessary for VDC and the weather criteria for MOT. This also populates the Tab "Cables" which provides the required input for PLS-CADD Criteria \ Cables (tension limits)
2 | Tab "Control"
2.1 | Enter the relevant data for the line section for which the Weather cases and Load Criteria are required
2.2 | Ground elevations: Determine the maximum ground elevations traversed. Copy the PLS-CADD Staking table to tab "Staking Table". This provides the maximum and minimum ground elevations along the line route. Determine and whether or not more than one height "group" is required. The default is for a single height group for all analyses. The decision to proceed with more than 1 height group will be dependent on identifying whether overloads can be mitigated by this method. For some lines, adopting a single height group can result in structures being subject to ice loads and temperatures that are more critical than that required by TP.DL 12.01 with resulting structure overloads. If deemed appropriate multiple height groups may be utilised to better represent the conditions along the line route. Tab "Structure Groups" permits these height bands to be pre-selected (after an engineering analysis of the line route). The default interval is derived based on three equal splits between zero and the maximum height (from the staking table). The bands may be manually adjusted.
2.3 | The number of conductor and or earthwire types along the line - this only defines the weather cases and cable tension criteria necessary for VDC and the weather criteria for MOT. This also populates the Tab "Cables" which provides the required input for PLS-CADD Criteria \ Cables (tension limits)
2.4 | Whether or not the model is to be analysed for Vulnerability or for predetermined reliability & security levels. For Vulnerability analyses only one zone (the most extreme) need be considered for the complete line unless the line is found to be overly sensitive. NOTE: Vulnerability Load Criteria are provided to permit Vulnerability analyses in accordance with the principles of TP.DL 12.01 Section 6.4 Reliability Analyses, with the objective to determining the risk of failure vs the cost of achieving the target reliability
2.5 | Identify which Serviceability limits are required, i.e. whether or not deflection or cracking limits are applicable. Note for a mixture of pole types it may be necessary to introduce different Load Criteria to cater for the different limits as PLS only considers whether or not a structure is modelled as a POLE or a TOWER. The following default conditions are assumed: a) "WP" identifies Standard Wood poles supplied to TP.PL 01.11 (no deflection or cracking limits) b) "SP" identifies a Standard prestressed reinforced concrete pole supplied to TP.PL 01.15 (with cracking and deflection limits) or a Standard steel pole supplied to TP.PL 01.20 with deflection limits to TP.PL 01.15 (same as concrete); these poles are typically to employed at 110kV and below. c) "XP" identifies a Steel Pole supplied to TP.PL 01.20 (with deflection limits). These poles are typically employed for 220kV but are also employed for special poles.
3 | Tab "Structure Groups": Default ground elevation ranges
This tab establishes the default Structure Groups to be adopted for the model. There are two default structure groups; "All" and "PLS-Pole" The other groups are dependent on the selected number of height bands for the line. The spreadsheet defaults to the maximum ground level determined from the Staking Table (rounded up to the next 100m). Enter how many height bands are required, 1,2 or 3 If the height bands are required to be fine-tuned to better reflect the line profile enter the required values in the green shaded cells. The Yellow cells are for any special structure groups required Remove blank rows and copy to PLS-CADD
4 | Tab "Control"
Enter:
The Line / Model site identification
Details of the conductors and earthwires applicable to the line model (permits up to 4 conductors and 45 earthwires)
Enter the applicable line route location data relating to the selected line section
For Generic Loading additional data is required for default terrain category and average heights of structures and conductors
Print tab to record the Selection
5 | Tab "Weather Cases"
This tab provides all the default weather cases applicable to the site location data entered in tab "Control". No additional input is required
in columns "Case selection" select the following:
5.1 | "Weather case reqd [Select 1]" This identifies whether the Weather case is: a) Required, or b) Loaded (e.g. an Ice load case with zero ice thickness is deselected) Select only those Weather cases with "1"
5.2 | "Wind Region Dependent [Select A or W]": This column identifies whether the Weather Case is wind region dependent. If the line traverses more than one wind region select those cases with "A" or "W" (the region is set in Tab "Control" under "Wind Zone"). For each wind region repeat the weather case selection
5.3 | "Height Dependent Case [Select H]": This identifies those weather cases that are height dependent. The selected height band is set in Tab "Control" under "Max GROUND LEVEL Altitude along line section". For each height band repeat the weather case selection
5.4 | For each combination of Wind region and Height Band repeat step 4.1, 4.2 and 4.3 Copy / add Weather Case data to PLS-CADD
5.5 | For Vulnerability analyses that require different SECURITY levels to be included in the analysis the RW, RS and RI Weather Criteria and Load Criteria have to be repeated and input into CADD for each SECURITY level. Recommend inset new rows for each selected Security Level
6 | Tab "Cables"
This tab provides the data to be copied into PLS-CADD Criteria / Cables
Employ the drop down list to select a) Applicable Cables cases. b) Repeat for the height dependent conditions (selecting the appropriate conductor / earthwire as applicable) Note the cable *.wir filename must exactly correspond to that given in Tab Control and be filed in the correct default directory (see Tab "pls-cadd folders" for default directory naming)
7 | Tab "Load Criteria"
No user input is required for default structure types. However, for special or non-standard structures the load cases may be modified by use of the "Control columns - Input". These provide the default variables for TP.DL 12.01 Load case naming.
For example, for Failure containment RSL loading cases the set numbers may be revised to suit special set naming as maybe required.
The usage and Key nomenclature employed are presented as comments in Cell A2 (Key nomenclature) and Cell H2 (usage notes)
For non-standard (default) load criteria employ columns I to V to modify the load criteria as applicable; these also affect the Load Criteria label etc.
In column "SELECTION CRITERIA (Filter to suit)" select those load criteria require based on the following selection criteria:
7.01 | "Load Case Applicable"? This identifies applicable default load cases, i.e. checks to see if the weather case is selected and loaded (select criteria with 1 only); if the weather case is not loaded Note: These load criteria are applicable to PLS-CADD models only; They are not applicable for generic design of new standard structures, for example: Standard Poles (steel and concrete) are required to meet deflection limits (TP.DL 12.01 Clause 7.7.2); these load cases are provided in rows 406 to 428; The default is that these cases are excluded. Double circuit Steel Towers (and steel poles) are required to be designed for single circuit erected - these are not covered by the present spreadsheet and the load cases will have to be developed by the designer.
7.02 | "Structure Type"; Some load cases are specific to structure type; select as applicable, i.e. ALL = Any structure type TWR = Lattice tower only SP = Steel Poles CP = Concrete poles
7.03 | "Structure Configuration": Some cases are dependent on the number of circuits carried by the structure. The spreadsheet caters for one (SC) or two circuits (DC). Some cases are common to both (SC/DC). For structures with more than 2 circuits special loads cases will need to be generated.
7.04 | "Type of Analysis": To minimise the number of load criteria required select either those necessary for: Vulnerability (VUL) analysis or Reliability analysis (RP). In addition it is possible to further select for Failure Containment (FC) Serviceability (SER)
7.05 | "Number of Broken wires / Phases": Under the "FC" load criteria there are a number of options that are applicable to the structure types. Typically structure families were designed for the same number of broken earthwires and or conductors. Notwithstanding the Transpower default is to adopt the broken conditions as specified in TP.DL 12.01 clause 6.2.3. After determining the required level of Security loading cases employ the dropdown list to select the appropriate load criteria employing: ALL = Full longitudinal cascade 1, 2 = 1 or two phases / earthwire broken at the same time
7.06 | "Earthwires": If the line has, anywhere along its length, one earthwire (EW7) or two earthwires (EW& & EW8) select as applicable.
7.07 | "Wind Region Dependent" Identifies those load criteria that are dependent on weather cases that are wind region dependent. Select as appropriate (input under "Wind Region" in Tab "Control")
7.08 | "Height Dependent"? Identifies those load criteria that are dependent on weather cases that are height dependent. Select as appropriate (input under "Max GROUND LEVEL Altitude along line section" in Tab "Control").
7.09 | For the selected load criteria in 5.1 to 5.8 copy / paste Load criteria data to PLS-CADD Repeat steps 5.7 and 5.8 for applicable wind and height bands
7.1 | Save PLS-CADD Criteria File employing the filename given in Tab "Control" Note the Asset Specific spreadsheet is also to be saved with the Line Model EMPLOY THE TAB "REVISION" FOR PROJECT / ASSET SPREADSHEET REVISION CONTROL - EMPLOY NUMBERS RATHER THAN LETTERS
7.11 | Repeat for each type of Analysis; Note For Vulnerability Analyses that require more than one security level to be analysed the Load Criteria for Security Criteria RW, RS and RI have to be repeated for each selected Security Level
7.12 | For Vulnerability analyses the user is required to manually adjust the wind interval for weather cases that employ a wind Direction "MAX". PLS-CADD defaults to a 1° interval which result is very long run times. 10° or 15° provides acceptable results.
8 | Tab "Staking Table"
This tab permits the data from existing CADD models to be extracted, analysed to develop "Structure Groups". The wind speeds to be adopted for the analysis are also to be entered in the staking table (irrespective whether Generic or WAsP site specific). Generic wind pressures are presented in Cells Z4 and AC4.
The preferred default is for the following Comment fields: to be selected under "Criteria \ Code Specific Wind and Terrain Parameters \ Span Specific Wind & Ice Adjustments"
Wind Speeds on Structures - Comment 7
Wind Speeds on Spans - Comment 4
9 | Tab " pls-cadd folders"
This Tab provides a simplified method by which the folders of an existing PLS-CADD line model can be modified to follow the default CAD folders as required by Transpower standards.
REFERENCES | TP.DL 12.01 Issue 4 Transmission Line Loading Code
Concrete Pole crack limits TP.DL 12.01 Table 13
Concrete Poles deflection limits TP.PL 01.15 Clause 2.1.2.5
Steel Pole deflection limits TP.PL 02.20 Table 3
NOTES:
Drag Factors | All Load cases assume the applicable structure wind-on-structure wind drag factor is input within the applicable structure model i.e. for TOWER models (Section) or POLE models (Pole Properties). If stick models are employed the PLS-CADD output will not address wind-on-structure effects. These will have to be "added" together with the applicable Drag factor (see TP.DL 12.01 Clause 7.4.3 and 7.4.4)
Live Line Working | Live Line Working Load Criteria are required to be based on the applicable MOT load case together with the required point loads to be applied to the conductor. These need to be applied on a project / procedure specific basis by manual input (Sections\Cables & Concentrated Load Files\Create New Concentrated Load File)
Terrain Category | This is not applicable as TP adopt Loading Code of "None" or "Apply Span specific wind / ice" only. |  | Rev H
CRF and Safety Factors | None of the load cases have been allocated capacity reduction factors; this is to ensure the user clearly recognises they are always dealing with actual (ultimate) loads and actual (ultimate) capacities. In all cases the user shall be responsible to ensure the required CRF is available for the loading condition (see TP.DL 12.01 Tables 2 and 3). Special attention is required for Construction & Maintenance cases to ensure a maximum CRF of 0.5 is achieved.
C&M Loading | For lines that traverse between Wind Regions W and A6/A7 it will be necessary to include additional weather and load cases. These are selected by adopting the wind region drop down selection (1). To ensure the load cases are applied correctly the Structure Groups will have to be modified to identify the applicable line section range
ALS Sag Matching | Some existing PLS Models have weather cases entered for the ALS sag matching purposes. These weather cases are not required and may be deleted. The "as-surveyed" temperatures are available in the Section Table in the Sag Temp column. The weather cases are only required for display purposes. The Sag Temperatures column can be copied to the "Display Weather Case" column as the weather case may be simply described as the wire temperature.
Rev H

## Structure Groups
INSTRUCTIONS |  | CONTROL | WEATHER CASES | LOAD CRITERIA | STAKING TABLE
PLS-CADD STRUCTURE GROUPS |  |  |  | GIP_Standard T1-T3 Rev A | PLS-CADD WC & LC Generator Master Rev H.xlsx
These are the structure groups to be included; Grey indicates the CADD default group "All";
| 800 | Max height (from Staking Table); ROUND UP to nearest 100m |  | the others are line specific but may be included as defaults
| 1 | Enter number of height intervals (max 3)
IF REQUIRED THE HEIGHT BANDS MAY BE ADJUSTED MANUALLY |  |  |  | Filter to remove blank rows and copy orange columns to PLS-CADD
Height Bands |  | PLS-CADD INPUT [CRITERIA \ STRUCTURE LOADS (METHODS 3, 4)… \ STRUCTURE GROUPS ]
Min | Max | Group Name | Group Description | Rule For Group Membership | PURPOSE
| - | All | Built in group that all structures belong to | Automatic: all structures | Default - Automatic - all structures
| DEFAULT | PLS-POLE | PLS-POLE created structure | Automatic: PLS-POLE created | TP for pole serviceability cases
600 | 800 | GL Max 800m | GL not more than 800m | Automatic: str. base elevation inside 600.00 to 800.00 (m) | For elevation dependent load cases | Note - data entry based on elevation input
Note - data entry based on elevation input
Note - data entry based on elevation input
| DEFAULT | Stop | Designated Stop Structure | Manually assigned by user | For Failure containiment cases restricted to "stop" structures
600 | 800 | Stop GL Max 800m | Stop with GL up to 800m | Automatic: str. base elevation inside 600.00 to 800.00 (m) and inside all following groups 'Stop' | For height dependent FC cases restricted to stop structures | Note - data entry based on elevation input
Note - data entry based on elevation input
Note - data entry based on elevation input
Line specific - as required
Line specific - as required
Line specific - as required
Line specific - as required
Line specific - as required
Line specific - as required
Line specific - as required
Note on B4: Refer to Staking table for max elevation

## Weather Cases
INSTRUCTIONS |  | STAKING TABLE |  | CONTROL INPUT |  |  | STRUCTURE GROUPS |  |  | LOAD CRITERIA |  |  | PLS-CADD
PLS-CADD WEATHER CASES |  |  | GIP_Standard T1-T3 Rev A
[7 empty] | FOLLOWING WEATHER CASES APPLICABLE TO SITES WITH GROUND ELEVATIONS < | 800 | m | FOR DEFAULT TP.DL 12.01 ANALYSES
PLS-CADD WC & LC Generator Master Rev H.xlsx |  |  |  | 1) Select Weather Case "1" (checks to see if the case is "loaded") - These also include the default weather cases for Safety, Serviceability, etc.
2) Cases with "1" are those that are Lines with more than one wind region. Select "W" (=Wind) after resetting previous columns
3) "Repeat" Cases for Lines with more than one height range. Select "H" (=Height) after resetting previous columns
CONTROL COLUMNS |  |  |  | CASE SELECTION |  |  | PLS-CADD DATA INPUT [Criteria \ Weather ]
WEATHER CASE | Weather Case ID | Weather Case Return Period (Years) | Coincident Wind Return Period (years) | Weather case reqd [Select 1] | Wind Region [Select A, W] | Height Dependent Case [Select H] | Description | Air Density Factor (Q) (kg/m^3) (Pa/(m/s)^2) | Wind Velocity (m/s) | Wind Pressure (Pa) | Wire Ice Thickness (cm) | Wire Ice Density (N/m^3) | Wire Ice Load (N/m) | Wire Temp. (deg C) | Ambient Temp. (deg C) | Weather Load Factor | NESC Constant (N/m) | Wire Wind Height Adjust Model | Wire Gust Response Factor | Notes
RELIABILITY CONDITIONS |  |  |  | - | - | -
Maximum Wind conditions | MW | 1000 | 1000 | - | A | H | MW1000_A8 | 0.6 | 1 | 0.6 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw | Applicable to Normal & Differential loading
Maximum Wind conditions | MW | 500 | 500 | - | A | H | MW0500_A8 | 0.6 | 0.978 | 0.57389 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw
Maximum Wind conditions | MW | 400 | 400 | - | A | H | MW0400_A8 | 0.6 | 0.967 | 0.56105 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw
Maximum Wind conditions | MW | 300 | 300 | 1 | A | H | MW0300_A8 | 0.6 | 0.953 | 0.54493 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw
Maximum Wind conditions | MW | 250 | 250 | - | A | H | MW0250_A8 | 0.6 | 0.943 | 0.53355 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw
Maximum Wind conditions | MW | 200 | 200 | - | A | H | MW0200_A8 | 0.6 | 0.932 | 0.52117 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw
Maximum Wind conditions | MW | 150 | 150 | - | A | H | MW0150_A8 | 0.6 | 0.916 | 0.50343 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw
Maximum Wind conditions | MW | 100 | 100 | - | A | H | MW0100_A8 | 0.6 | 0.894 | 0.47954 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw | Applicable to Normal & Differential loading
Maximum Wind conditions | MW | 75 | 75 | - | A | H | MW0075_A8 | 0.6 | 0.878 | 0.46253 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw
Maximum Wind conditions | MW | 50 | 50 | - | A | H | MW0050_A8 | 0.6 | 0.854 | 0.43759 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw
Maximum Wind conditions | MW | 25 | 25 | - | A | H | MW0025_A8 | 0.6 | 0.811 | 0.39463 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw
Maximum Wind conditions | MW | 15 | 15 | - | A | H | MW0015_A8 | 0.6 | 0.777 | 0.36224 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw | 10 year no replacement
Maximum Wind conditions | MW | 10 | 10 | - | A | H | MW0010_A8 | 0.6 | 0.749 | 0.3366 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw | 6 year prioritise
Maximum Wind conditions | MW | 4 | 4 | - | A | H | MW0004_A8 | 0.6 | 0.681 | 0.27826 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw | Orange Tag
Maximum Wind conditions | MW | 2 | 2 | - | A | H | MW0002_A8 | 0.6 | 0.625 | 0.23438 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw | Red Tag
Minimum Temperature with wind | MT | 1000 | 1000 | - | A | H | MT1000_A8 | 0.6 | 0.6 | 0.216 | 0 | 0 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmin
Minimum Temperature with wind | MT | 500 | 500 | - | A | H | MT0500_A8 | 0.6 | 0.587 | 0.20674 | 0 | 0 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmin
Minimum Temperature with wind | MT | 400 | 400 | - | A | H | MT0400_A8 | 0.6 | 0.58 | 0.20184 | 0 | 0 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmin
Minimum Temperature with wind | MT | 300 | 300 | 1 | A | H | MT0300_A8 | 0.6 | 0.572 | 0.19631 | 0 | 0 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmin
Minimum Temperature with wind | MT | 250 | 250 | - | A | H | MT0250_A8 | 0.6 | 0.566 | 0.19221 | 0 | 0 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmin
Minimum Temperature with wind | MT | 200 | 200 | - | A | H | MT0200_A8 | 0.6 | 0.559 | 0.18749 | 0 | 0 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmin
Minimum Temperature with wind | MT | 150 | 150 | - | A | H | MT0150_A8 | 0.6 | 0.55 | 0.1815 | 0 | 0 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmin
Minimum Temperature with wind | MT | 100 | 100 | - | A | H | MT0100_A8 | 0.6 | 0.536 | 0.17238 | 0 | 0 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmin
Minimum Temperature with wind | MT | 75 | 75 | - | A | H | MT0075_A8 | 0.6 | 0.527 | 0.16664 | 0 | 0 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmin
Minimum Temperature with wind | MT | 50 | 50 | - | A | H | MT0050_A8 | 0.6 | 0.512 | 0.15729 | 0 | 0 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmin
Minimum Temperature with wind | MT | 25 | 25 | - | A | H | MT0025_A8 | 0.6 | 0.486 | 0.14172 | 0 | 0 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmin
Minimum Temperature with wind | MT | 15 | 15 | - | A | H | MT0015_A8 | 0.6 | 0.466 | 0.13029 | 0 | 0 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmin | Equivalent to 10 year no replacement
Minimum Temperature with wind | MT | 10 | 10 | - | A | H | MT0010_A8 | 0.6 | 0.449 | 0.12096 | 0 | 0 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmin | Equivalent to 6 year prioritise
Minimum Temperature with wind | MT | 4 | 4 | - | A | H | MT0004_A8 | 0.6 | 0.408 | 0.099878 | 0 | 0 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmin | Equivalent to Orange Tag
Minimum Temperature with wind | MT | 2 | 2 | - | A | H | MT0002_A8 | 0.6 | 0.375 | 0.084375 | 0 | 0 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmin | Equivalent to Red Tag
Extreme Snow | ES | 50 | - | 1 | - | H | ES0050_8 | 0.6 | 5.7735 | 20 | 3 | 3900 | 0 | -5 |  | 1 |  | None | 1.2 | tsnow | Applicable to Normal & Differential loading
Thin Ice with wind | TI | 50 | 1 | 1 | A | H | TI0050_A8 | 0.6 | 0.565 | 0.19153 | 0.8 | 6850 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1.2 | tice | Applicable to Normal & Differential loading
Extreme (thick) ice | EI | 50 | - | 1 | - | H | EI0050_8 | 0.6 | 5.7735 | 20 | 5.5 | 3550 | 0 | -14 |  | 1 |  | None | 1.2 | tice
SECURITY CONDITIONS | - | Security Level |  | - | - | - | [6 empty] | 0
Cascade & RSL Wind | RW | 1 | - | 1 | - | H | RW0001_8 | 0.6 | 12.9099 | 100 | 0 | 0 | 0 | 5 |  | 1 |  | None | 1 | ted | Applicable to Cascade and Torsional loading
Cascade & RSL Snow | RS | 1 | - | 1 | - | H | RS0001_8 | 0.6 | 0 | 0 | 1 | 3900 | 0 | -5 |  | 1 |  | None | 1.2 | tsnow | Applicable to Cascade and Torsional loading
Cascade & RSL Thick Ice | RI | 1 | - | 1 | - | H | RI0001_8 | 0.6 | 0 | 0 | 1.8 | 6850 | 0 | -14 |  | 1 |  | None | 1.2 | tice | Applicable to Cascade and Torsional loading
SAFETY LOADING |  |  |  | - | - | - | [6 empty] | 0
Default C&M | CM1 | - | - | 1 | - | - | CM1 | 0.6 | 12.9099 | 100 | 0 | 0 | 0 | 5 |  | 1 |  | None | 1 | tcm
Extended C&M Works (Summer) | CM2 | - | 1 | 1 | A | - | CM2_A | 0.6 | 0.565 | 0.19153 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tcm |  | Rev H
Extended C&M Works (with snow) | CM2S | - | - | 1 | - | H | CM2S_8 | 0.6 | 5.7735 | 20 | 1 | 3900 | 0 | -5 |  | 1 |  | None | 1.2 | tsnow | New - to cover non-summer months; if required | Rev H
Extended C&M Works (with Ice) | CM2I | - | - | 1 | - | H | CM2I_8 | 0.6 | 5.7735 | 20 | 1.8 | 6850 | 0 | -14 |  | 1 |  | None | 1.2 | tice | New - to cover non-summer months; if required | Rev H
Delayed Strengthening (Summer) | CM3 | - | 4 | 1 | A | H | CM3_A8 | 0.6 | 0.681 | 0.27826 | 0 | 0 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmin
Delayed Strengthening (Snow) | CM3S | - | - | 1 | - | H | CM3S_8 | 0.6 | 5.7735 | 20 | 1 | 3900 | 0 | -5 |  | 1 |  | None | 1.2 | tsnow | New - to cover non-summer months | Rev H
Delayed Strengthening (Ice) | CM3I | - | - | 1 | - | H | CM3I_8 | 0.6 | 5.7735 | 20 | 1.8 | 6850 | 0 | -14 |  | 1 |  | None | 1.2 | tice | New - to cover non-summer months | Rev H
SERVICEABILITY CONDITIONS |  | %CBL or temp |  | - | - | -
Vibration Damage Control | VDC | - | - | 1 | - | - | VDC | 0.6 | 7.0711 | 30 | 0 | 0 | 0 | 5 |  | 1 |  | None | 1
Everyday still air | EDS | - | - | 1 | - | - | EDS | 0.6 | 0 | 0 | 0 | 0 | 0 | 5 |  | 1 |  | None | 1 | ted
Everyday Wind (Structural) | EDW | - | - | 1 | - | - | EDW | 0.6 | 12.9099 | 100 | 0 | 0 | 0 | 5 |  | 1 |  | None | 1 | ted
Falling Tree Deflection TP.SS 02.18 | FTD | - | - | 1 | - | - | FTD | 0.6 | 18.2574 | 200 | 0 | 0 | 0 | 42 |  | 1 |  | None | 1 | tedd | New | Rev H
Maximum Operating Temperature Condr 1 | MOT | 120 | - | 1 | - | - | MOT_120 | 0.6 | 0 | 0 | 0 | 0 | 0 | 120 |  | 1 |  | None | 1 | tmax
Maximum Operating Temperature Condr 2 | MOT | 90 | - | - | - | - | - | 0.6 | 0 | 0 | 0 | 0 | 0 | 90 |  | 1 |  | None | 1 | tmax
Maximum Operating Temperature Condr 3 | MOT | 120 | - | - | - | - | - | 0.6 | 0 | 0 | 0 | 0 | 0 | 120 |  | 1 |  | None | 1 | tmax
Maximum Operating Temperature Condr 4 | MOT | 0 | - | - | - | - | - | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 |  | None | 1 | tmax
Everyday wind deflection Condr 1 | EDD | 120 | - | 1 | - | - | EDD_120 | 0.6 | 12.9099 | 100 | 0 | 0 | 0 | 42 |  | 1 |  | None | 1 | tedd
Everyday wind deflection Condr 2 | EDD | 90 | - | - | - | - | - | 0.6 | 12.9099 | 100 | 0 | 0 | 0 | 39 |  | 1 |  | None | 1 | tedd
Everyday wind deflection Condr 3 | EDD | 120 | - | - | - | - | - | 0.6 | 12.9099 | 100 | 0 | 0 | 0 | 42 |  | 1 |  | None | 1 | tedd
Everyday wind deflection Condr 4 | EDD | 0 | - | - | - | - | - | 0.6 | 12.9099 | 100 | 0 | 0 | 0 | 0 |  | 1 |  | None | 1 | tedd
High Wind Deflection (Structural) | HWD |  | 3 | - | A | - | HWD_A | 0.6 | 0.658 | 0.25978 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | ted
High Wind Deflection Condr 1 | HWD | 120 | 3 | 1 | A | - | HWD_A120 | 0.6 | 0.658 | 0.25978 | 0 | 0 | 0 | 37 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | thwd
High Wind Deflection Condr 2 | HWD | 90 | 3 | - | A | - | - | 0.6 | 0.658 | 0.25978 | 0 | 0 | 0 | 35 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | thwd
High Wind Deflection Condr 3 | HWD | 120 | 3 | - | A | - | - | 0.6 | 0.658 | 0.25978 | 0 | 0 | 0 | 37 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | thwd
High Wind Deflection Condr 4 | HWD | 0 | 3 | - | A | - | - | 0.6 | 0.658 | 0.25978 | 0 | 0 | 0 | 0 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | thwd
Maximum Wind deflection (Structural) | MWD |  | 50 | - | A | H | MWD_A8 | 0.6 | 0.854 | 0.43759 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw
Maximum Wind deflection Condr 1 | MWD | 120 | 50 | 1 | A | - | MWD_A120 | 0.6 | 0.854 | 0.43759 | 0 | 0 | 0 | 35 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmwd
Maximum Wind deflection Condr 2 | MWD | 90 | 50 | - | A | - | - | 0.6 | 0.854 | 0.43759 | 0 | 0 | 0 | 34 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmwd
Maximum Wind deflection Condr 3 | MWD | 120 | 50 | - | A | - | - | 0.6 | 0.854 | 0.43759 | 0 | 0 | 0 | 35 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmwd
Maximum Wind deflection Condr 4 | MWD | 0 | 50 | - | A | - | - | 0.6 | 0.854 | 0.43759 | 0 | 0 | 0 | 0 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmwd
Snow Deflection – Still air | SDS | - | - | 1 | - | H | SDS_8 | 0.6 | 0 | 0 | 3 | 3900 | 0 | -5 |  | 1 |  | None | 1.2 | tsnow
Snow Deflection – Wind 50%Pdes | SDD | - | - | 1 | - | H | SDD_8 | 0.6 | 4.0825 | 10 | 3 | 3900 | 0 | -5 |  | 1 |  | None | 1.2 | tsnow
Snow Deflection – No snow | SDO | - | - | 1 | - | - | SDO | 0.6 | 0 | 0 | 0 | 0 | 0 | -5 |  | 1 |  | None | 1 | tsnow
Thin Ice – Still air | TIS | - | - | 1 | - | H | TIS_8 | 0.6 | 0 | 0 | 0.8 | 6850 | 0 | -14 |  | 1 |  | None | 1.2 | tice
Thin Ice Deflection – 50%Pdes | TID | - | - | 1 | A | H | TID_A8 | 0.6 | 0.39952 | 0.095767 | 0.8 | 6850 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1.2 | tice
Thin (and thick) Ice – No Ice | TIO | - | - | 1 | - | - | TIO | 0.6 | 0 | 0 | 0 | 0 | 0 | -14 |  | 1 |  | None | 1 | tice
Extreme (thick) Ice – Still Air | EIS | - | - | 1 | - | H | EIS_8 | 0.6 | 0 | 0 | 5.5 | 3550 | 0 | -14 |  | 1 |  | None | 1.2 | tice
Extreme (thick) Ice Deflection – 50%Pdes | EID | - | - | 1 | - | H | EID_8 | 0.6 | 4.0825 | 10 | 5.5 | 3550 | 0 | -14 |  | 1 |  | None | 1.2 | tice
Minimum Temp Still air | MTS | - | - | 1 | - | H | MTS_8 | 0.6 | 0 | 0 | 0 | 0 | 0 | -14 |  | 1 |  | None | 1 | tmin
Support replace criteria 10 year for wind | RCW | 15 | 15 | 1 | A | H | RCW_A8 | 0.6 | 0.777 | 0.36224 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw
CA criteria wind 6 year | CA6 | 10 | 10 | 1 | A | H | CA6_A8 | 0.6 | 0.749 | 0.3366 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw
CA criteria Wind Orange Tag | CA1 | 4 | 4 | 1 | A | H | CA1_A8 | 0.6 | 0.681 | 0.27826 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw
CA criteria Wind Red Tag | CA0 | 2 | 2 | 1 | A | H | CA0_A8 | 0.6 | 0.625 | 0.23438 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw
Support Replacement criteria snow | RCS |  | - | 1 | - | H | RCS_8 | 0.6 | 0 | 0 | 1 | 3900 | 0 | -5 |  | 1 |  | None | 1.2 | tsnow
Support Replacement criteria ice | RCI |  | - | 1 | - | H | RCI_8 | 0.6 | 0 | 0 | 1.8 | 6850 | 0 | -14 |  | 1 |  | None | 1.2 | tice
Gantry 2500yr RP | MW | 2500 | 2500 | 1 | A | H | MW2500_A8 | 0.6 | 1.049 | 0.66024 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1
Seismic / Earthquake | EQ | 500 | - | - | - | - | EQ_8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 5 |  | 1 |  | None | 1 | ted
Note on E8: ONLY SELECT THOSE CASES WITH "1"
Note on F8: Select only if Line crosses over the wind Region Boundary between W and A6/A7
Note on G8: Required for lines with more than one height boundary layer
Note on H8: Refer to TP. 12.01 Section 8

## Cables
GIP_Standard T1-T3 Rev A | [6 empty] | PLS-CADD WC & LC Generator Master Rev H.xlsx
Criteria / Cable Tensions
|  |  |  | Cable *.wir file must be saved in directory | GIP_Standard_T1-T3\PLS\Cables
This tab does not require any input - mereley select the appropriate rows and copy to PLS-CADD
FIRST Case Applicable ? [Select 1] | SECOND Height Dependent? | Weather Case | Cable Condition | % of Ultimate | Maximum Tension (N) | Maximum Catenary (m) | Applicable Cable (blank=all cables)
1 |  | VDC | Creep FE | 22% |  |  | chukar_nz_acsr_ac_greased_04092013_l_downlead 6 degree creep.wir
- |  | VDC | Creep FE | 22% |  |  | chukar_nz_acsr_ac_greased_04092013_l.wir
- |  | VDC | Creep FE | 23% |  |  | zebra_acsr_gz_greased_pre1977_l.wir
- |  | VDC | Creep FE | 0% |  |  | 0
- |  | VDC | Creep FE | 22% |  |  | 7_3-05_scac_greased_l.wir
- |  | VDC | Creep FE | 0% |  |  | 0
- |  | VDC | Creep FE | 0% |  |  | 0
- |  | VDC | Creep FE | 0% |  |  | 0
1 | YES | MW0300_A8 | Creep FE | 70% |  |  | chukar_nz_acsr_ac_greased_04092013_l_downlead 6 degree creep.wir
- | YES | MW0300_A8 | Creep FE | 70% |  |  | chukar_nz_acsr_ac_greased_04092013_l.wir
- | YES | MW0300_A8 | Creep FE | 70% |  |  | zebra_acsr_gz_greased_pre1977_l.wir
- | YES | MW0300_A8 | Creep FE | 0% |  |  | 0
- | YES | MW0300_A8 | Creep FE | 70% |  |  | 7_3-05_scac_greased_l.wir
- | YES | MW0300_A8 | Creep FE | 0% |  |  | 0
- | YES | MW0300_A8 | Creep FE | 0% |  |  | 0
- | YES | MW0300_A8 | Creep FE | 0% |  |  | 0
1 | YES | MT0300_A8 | Creep FE | 70% |  |  | chukar_nz_acsr_ac_greased_04092013_l_downlead 6 degree creep.wir
- | YES | MT0300_A8 | Creep FE | 70% |  |  | chukar_nz_acsr_ac_greased_04092013_l.wir
- | YES | MT0300_A8 | Creep FE | 70% |  |  | zebra_acsr_gz_greased_pre1977_l.wir
- | YES | MT0300_A8 | Creep FE | 0% |  |  | 0
- | YES | MT0300_A8 | Creep FE | 70% |  |  | 7_3-05_scac_greased_l.wir
- | YES | MT0300_A8 | Creep FE | 0% |  |  | 0
- | YES | MT0300_A8 | Creep FE | 0% |  |  | 0
- | YES | MT0300_A8 | Creep FE | 0% |  |  | 0
1 | YES | ES0050_8 | Creep FE | 70% |  |  | chukar_nz_acsr_ac_greased_04092013_l_downlead 6 degree creep.wir
- | YES | ES0050_8 | Creep FE | 70% |  |  | chukar_nz_acsr_ac_greased_04092013_l.wir
- | YES | ES0050_8 | Creep FE | 70% |  |  | zebra_acsr_gz_greased_pre1977_l.wir
- | YES | ES0050_8 | Creep FE | 0% |  |  | 0
- | YES | ES0050_8 | Creep FE | 70% |  |  | 7_3-05_scac_greased_l.wir
- | YES | ES0050_8 | Creep FE | 0% |  |  | 0
- | YES | ES0050_8 | Creep FE | 0% |  |  | 0
- | YES | ES0050_8 | Creep FE | 0% |  |  | 0
1 | YES | TI0050_A8 | Creep FE | 70% |  |  | chukar_nz_acsr_ac_greased_04092013_l_downlead 6 degree creep.wir
- | YES | TI0050_A8 | Creep FE | 70% |  |  | chukar_nz_acsr_ac_greased_04092013_l.wir
- | YES | TI0050_A8 | Creep FE | 70% |  |  | zebra_acsr_gz_greased_pre1977_l.wir
- | YES | TI0050_A8 | Creep FE | 0% |  |  | 0
- | YES | TI0050_A8 | Creep FE | 70% |  |  | 7_3-05_scac_greased_l.wir
- | YES | TI0050_A8 | Creep FE | 0% |  |  | 0
- | YES | TI0050_A8 | Creep FE | 0% |  |  | 0
- | YES | TI0050_A8 | Creep FE | 0% |  |  | 0
1 | YES | EI0050_8 | Creep FE | 70% |  |  | chukar_nz_acsr_ac_greased_04092013_l_downlead 6 degree creep.wir
- | YES | EI0050_8 | Creep FE | 70% |  |  | chukar_nz_acsr_ac_greased_04092013_l.wir
- | YES | EI0050_8 | Creep FE | 70% |  |  | zebra_acsr_gz_greased_pre1977_l.wir
- | YES | EI0050_8 | Creep FE | 0% |  |  | 0
- | YES | EI0050_8 | Creep FE | 70% |  |  | 7_3-05_scac_greased_l.wir
- | YES | EI0050_8 | Creep FE | 0% |  |  | 0
- | YES | EI0050_8 | Creep FE | 0% |  |  | 0
- | YES | EI0050_8 | Creep FE | 0% |  |  | 0

## Load Criteria
PLS-CADD STRUCTURE LOAD CRITERIA | [21 empty] | GIP_Standard T1-T3 Rev A | [15 empty] | PLS-CADD WC & LC Generator Master Rev H.xlsx
KEY FOR SELECTION CRITERIA | [6 empty] | NOTES | [14 empty] | PLS-CADD STRUCTURE LOAD CRITERIA | [7 empty] | INSTRUCTIONS |  |  | STRUCTURE GROUPS | [11 empty] | Failure Containment on all structures? |  | N | [Data input]
PLS-CADD WC & LC Generator Master Rev H.xlsx | [7 empty] | The control columns adopt TP.DL 12.01 Weather & Load Case naming procedure | [21 empty] | STAKING TABLE |  |  | WEATHER CASES
MAX GROUND ALTITUDE FOR SELECTED LINE SECTION | [29 empty] | CONTROL INPUT |  |  | PLS-CADD | [47 empty] | Note Input truncated (COLUMNS NOT REQUIRED FOR DEFAULT LOAD CRITERIA)
| 800 | 8 | < Do not delete |  |  |  |  | These are the default definitions for the loading cases
SELECTION CRITERIA (Filter to suit) | [7 empty] | CONTROL COLUMNS - INPUT | [13 empty] | PLS-CADD INPUT - COPY AND PASTE TO [CRITERIA \ STRUCTURE LOADS (METHODS 3, 4…)] | [85 empty] | Not Used by generator
Load Case Applicable? | Structure Type | Structure Configuration | Type of Analysis | Number of Broken wires / Phases | Earthwires | Wind Region Dependent | Height Dependent? | Controlling Weather Case | Return Period | Code 1 | Code 2 | Sets Affected #1 | Sets Affected #2 | Sets Affected #3 | Set NOT AFFECTED #1 | Set NOT AFFECTED #2 | Set NOT AFFECTED #3 | Set NOT AFFECTED #4 | Set NOT AFFECTED #5 | Wind Dirn | Wind Angle | Description | Weather case | Cable condition | Wind Direction | Bisector Wind Dir (deg) | Wire Vert. Load Factor | Wire and Struct. Wind Load Factor | Wire Tension Load Factor | Struct. Weight Load Factor | Struct. Wind Area Factor | Struct. Wind Load Model | Struct. Ice Thickness (cm) | Struct. Ice Density (N/m^3) | Strength Factor Steel Poles Tubular- Arms Towers | Strength Factor Wood Poles | Strength Factor Concrete Poles Ultimate | Strength Factor Concrete Poles First Crack | Strength Factor Concrete Poles Zero Tension | Strength Factor Guys | Strength Factor Non- Tubular Arms | Strength Factor Braces | Strength Factor Insulators | Strength Factor Hardware | Strength Factor Foundation | Strength Factor Climbing | Structure Groups On Which To Apply | Pole Tip Deflection Check (PLS-POLE only) | Pole Tip Deflect. Limit % or (m) | Adjust Cable Loads | #1 Wire(s) Set Phase Span | #1 Command | #1 Value (%) (# subcond.) (N) (deg) | #2 Wire(s) Set Phase Span | #2 Command | #2 Value (%) (# subcond.) (N) (deg) | #3 Wire(s) Set Phase Span | #3 Command | #3 Value (%) (# subcond.) (N) (deg) | #4 Wire(s) Set Phase Span | #4 Command | #4 Value (%) (# subcond.) (N) (deg) | #5 Wire(s) Set Phase Span | #5 Command | #5 Value (%) (# subcond.) (N) (deg) | #6 Wire(s) Set Phase Span | #6 Command | #6 Value (%) (# subcond.) (N) (deg) | #7 Wire(s) Set Phase Span | #7 Command | #7 Value (%) (# subcond.) (N) (deg) | #8 Wire(s) Set Phase Span | #8 Command | #8 Value (%) (# subcond.) (N) (deg) | #9 Wire(s) Set Phase Span | #9 Command | #9 Value (%) (# subcond.) (N) (deg) | #10 Wire(s) Set Phase Span | #10 Command | #10 Value (%) (# subcond.) (N) (deg) | #11 Wire(s) Set Phase Span | #11 Command | #11 Value (%) (# subcond.) (N) (deg) | #12 Wire(s) Set Phase Span | #12 Command | #12 Value (%) (# subcond.) (N) (deg) | #13 Wire(s) Set Phase Span | #13 Command | #13 Value (%) (# subcond.) (N) (deg) | #14 Wire(s) Set Phase Span | #14 Command | #14 Value (%) (# subcond.) (N) (deg) | #15 Wire(s) Set Phase Span | #15 Command | #15 Value (%) (# subcond.) (N) (deg) | #16 Wire(s) Set Phase Span | #16 Command | #16 Value (%) (# subcond.) (N) (deg) | #17 Wire(s) Set Phase Span | #17 Command | #17 Value (%) (# subcond.) (N) (deg) | #18 Wire(s) Set Phase Span | #18 Command | #18 Value (%) (# subcond.) (N) (deg) | #19 Wire(s) Set Phase Span | #19 Command | #19 Value (%) (# subcond.) (N) (deg) | #20 Wire(s) Set Phase Span | #20 Command | #20 Value (%) (# subcond.) (N) (deg)
- | - | - | - | - | - | - | - | EXTREME WIND "MAX" REPORTS THE LOAD CASE WITH THE MAXIMUM USAGE ONLY (REFER PLS-TOWER MANUAL Page 166)
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 1000 | E | [9 empty] | Max |  | MW1000_A8+E Max | MW1000_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | No
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 500 | E | [9 empty] | Max |  | MW0500_A8+E Max | MW0500_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | No
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 400 | E | [9 empty] | Max |  | MW0400_A8+E Max | MW0400_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | No
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 300 | E | [9 empty] | Max |  | MW0300_A8+E Max | MW0300_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | No
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 250 | E | [9 empty] | Max |  | MW0250_A8+E Max | MW0250_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | No
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 200 | E | [9 empty] | Max |  | MW0200_A8+E Max | MW0200_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | No
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 150 | E | [9 empty] | Max |  | MW0150_A8+E Max | MW0150_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | No
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 100 | E | [9 empty] | Max |  | MW0100_A8+E Max | MW0100_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | No
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 75 | E | [9 empty] | Max |  | MW0075_A8+E Max | MW0075_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | No
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 50 | E | [9 empty] | Max |  | MW0050_A8+E Max | MW0050_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | No
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 25 | E | [9 empty] | Max |  | MW0025_A8+E Max | MW0025_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | No
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 15 | E | [9 empty] | Max |  | MW0015_A8+E Max | MW0015_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | No
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 10 | E | [9 empty] | Max |  | MW0010_A8+E Max | MW0010_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | No
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 4 | E | [9 empty] | Max |  | MW0004_A8+E Max | MW0004_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | No
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 2 | E | [9 empty] | Max |  | MW0002_A8+E Max | MW0002_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | No
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 1000 | D | A | [8 empty] | Max |  | MW1000_A8+DA Max | MW1000_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 500 | D | A | [8 empty] | Max |  | MW0500_A8+DA Max | MW0500_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 400 | D | A | [8 empty] | Max |  | MW0400_A8+DA Max | MW0400_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 300 | D | A | [8 empty] | Max |  | MW0300_A8+DA Max | MW0300_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 250 | D | A | [8 empty] | Max |  | MW0250_A8+DA Max | MW0250_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 200 | D | A | [8 empty] | Max |  | MW0200_A8+DA Max | MW0200_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 150 | D | A | [8 empty] | Max |  | MW0150_A8+DA Max | MW0150_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 100 | D | A | [8 empty] | Max |  | MW0100_A8+DA Max | MW0100_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 75 | D | A | [8 empty] | Max |  | MW0075_A8+DA Max | MW0075_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 50 | D | A | [8 empty] | Max |  | MW0050_A8+DA Max | MW0050_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 25 | D | A | [8 empty] | Max |  | MW0025_A8+DA Max | MW0025_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 15 | D | A | [8 empty] | Max |  | MW0015_A8+DA Max | MW0015_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 10 | D | A | [8 empty] | Max |  | MW0010_A8+DA Max | MW0010_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 4 | D | A | [8 empty] | Max |  | MW0004_A8+DA Max | MW0004_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 2 | D | A | [8 empty] | Max |  | MW0002_A8+DA Max | MW0002_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 1000 | D | B | [8 empty] | Max |  | MW1000_A8+DB Max | MW1000_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 500 | D | B | [8 empty] | Max |  | MW0500_A8+DB Max | MW0500_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 400 | D | B | [8 empty] | Max |  | MW0400_A8+DB Max | MW0400_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 300 | D | B | [8 empty] | Max |  | MW0300_A8+DB Max | MW0300_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 250 | D | B | [8 empty] | Max |  | MW0250_A8+DB Max | MW0250_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 200 | D | B | [8 empty] | Max |  | MW0200_A8+DB Max | MW0200_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 150 | D | B | [8 empty] | Max |  | MW0150_A8+DB Max | MW0150_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 100 | D | B | [8 empty] | Max |  | MW0100_A8+DB Max | MW0100_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 75 | D | B | [8 empty] | Max |  | MW0075_A8+DB Max | MW0075_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 50 | D | B | [8 empty] | Max |  | MW0050_A8+DB Max | MW0050_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 25 | D | B | [8 empty] | Max |  | MW0025_A8+DB Max | MW0025_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 15 | D | B | [8 empty] | Max |  | MW0015_A8+DB Max | MW0015_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 10 | D | B | [8 empty] | Max |  | MW0010_A8+DB Max | MW0010_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 4 | D | B | [8 empty] | Max |  | MW0004_A8+DB Max | MW0004_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
- | ALL | DC/SC | VUL | - | - | YES | YES | MW | 2 | D | B | [8 empty] | Max |  | MW0002_A8+DB Max | MW0002_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
- | ALL | DC/SC | VUL | - | - | YES | YES | MT | 1000 | E | [9 empty] | Max |  | MT1000_A8+E Max | MT1000_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | No
- | ALL | DC/SC | VUL | - | - | YES | YES | MT | 500 | E | [9 empty] | Max |  | MT0500_A8+E Max | MT0500_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | No
- | ALL | DC/SC | VUL | - | - | YES | YES | MT | 400 | E | [9 empty] | Max |  | MT0400_A8+E Max | MT0400_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | No
- | ALL | DC/SC | VUL | - | - | YES | YES | MT | 300 | E | [9 empty] | Max |  | MT0300_A8+E Max | MT0300_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | No
- | ALL | DC/SC | VUL | - | - | YES | YES | MT | 250 | E | [9 empty] | Max |  | MT0250_A8+E Max | MT0250_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | No
- | ALL | DC/SC | VUL | - | - | YES | YES | MT | 200 | E | [9 empty] | Max |  | MT0200_A8+E Max | MT0200_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | No
- | ALL | DC/SC | VUL | - | - | YES | YES | MT | 150 | E | [9 empty] | Max |  | MT0150_A8+E Max | MT0150_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | No
- | ALL | DC/SC | VUL | - | - | YES | YES | MT | 100 | E | [9 empty] | Max |  | MT0100_A8+E Max | MT0100_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | No
- | ALL | DC/SC | VUL | - | - | YES | YES | MT | 75 | E | [9 empty] | Max |  | MT0075_A8+E Max | MT0075_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | No
- | ALL | DC/SC | VUL | - | - | YES | YES | MT | 50 | E | [9 empty] | Max |  | MT0050_A8+E Max | MT0050_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | No
- | ALL | DC/SC | VUL | - | - | YES | YES | MT | 25 | E | [9 empty] | Max |  | MT0025_A8+E Max | MT0025_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | No
- | ALL | DC/SC | VUL | - | - | YES | YES | MT | 15 | E | [9 empty] | Max |  | MT0015_A8+E Max | MT0015_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | No
- | ALL | DC/SC | VUL | - | - | YES | YES | MT | 10 | E | [9 empty] | Max |  | MT0010_A8+E Max | MT0010_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | No
- | ALL | DC/SC | VUL | - | - | YES | YES | MT | 4 | E | [9 empty] | Max |  | MT0004_A8+E Max | MT0004_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | No
- | ALL | DC/SC | VUL | - | - | YES | YES | MT | 2 | E | [9 empty] | Max |  | MT0002_A8+E Max | MT0002_A8 | Creep FE | Max |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | E | [9 empty] | BI+ | 90 | MW0300_A8+E BI++90 | MW0300_A8 | Creep FE | BI+ | 90 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | E | [9 empty] | BI+ | 45 | MW0300_A8+E BI++45 | MW0300_A8 | Creep FE | BI+ | 45 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | E | [9 empty] | BI+ | 30 | MW0300_A8+E BI++30 | MW0300_A8 | Creep FE | BI+ | 30 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | E | [9 empty] | BI+ | 15 | MW0300_A8+E BI++15 | MW0300_A8 | Creep FE | BI+ | 15 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | E | [9 empty] | BI+ | 0 | MW0300_A8+E BI++00 | MW0300_A8 | Creep FE | BI+ | 0 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | E | [9 empty] | BI+ | -15 | MW0300_A8+E BI+-15 | MW0300_A8 | Creep FE | BI+ | -15 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | E | [9 empty] | BI+ | -30 | MW0300_A8+E BI+-30 | MW0300_A8 | Creep FE | BI+ | -30 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | E | [9 empty] | BI+ | -45 | MW0300_A8+E BI+-45 | MW0300_A8 | Creep FE | BI+ | -45 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | E | [9 empty] | BI+ | -90 | MW0300_A8+E BI+-90 | MW0300_A8 | Creep FE | BI+ | -90 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | E | [9 empty] | BI- | 90 | MW0300_A8+E BI-+90 | MW0300_A8 | Creep FE | BI- | 90 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | E | [9 empty] | BI- | 45 | MW0300_A8+E BI-+45 | MW0300_A8 | Creep FE | BI- | 45 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | E | [9 empty] | BI- | 30 | MW0300_A8+E BI-+30 | MW0300_A8 | Creep FE | BI- | 30 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | E | [9 empty] | BI- | 15 | MW0300_A8+E BI-+15 | MW0300_A8 | Creep FE | BI- | 15 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | E | [9 empty] | BI- | 0 | MW0300_A8+E BI-+00 | MW0300_A8 | Creep FE | BI- | 0 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | E | [9 empty] | BI- | -15 | MW0300_A8+E BI--15 | MW0300_A8 | Creep FE | BI- | -15 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | E | [9 empty] | BI- | -30 | MW0300_A8+E BI--30 | MW0300_A8 | Creep FE | BI- | -30 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | E | [9 empty] | BI- | -45 | MW0300_A8+E BI--45 | MW0300_A8 | Creep FE | BI- | -45 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | E | [9 empty] | BI- | -90 | MW0300_A8+E BI--90 | MW0300_A8 | Creep FE | BI- | -90 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | A | [8 empty] | BI+ | 90 | MW0300_A8+DA BI++90 | MW0300_A8 | Creep FE | BI+ | 90 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | A | [8 empty] | BI+ | 45 | MW0300_A8+DA BI++45 | MW0300_A8 | Creep FE | BI+ | 45 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | A | [8 empty] | BI+ | 30 | MW0300_A8+DA BI++30 | MW0300_A8 | Creep FE | BI+ | 30 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | A | [8 empty] | BI+ | 15 | MW0300_A8+DA BI++15 | MW0300_A8 | Creep FE | BI+ | 15 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | A | [8 empty] | BI+ | 0 | MW0300_A8+DA BI++00 | MW0300_A8 | Creep FE | BI+ | 0 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | A | [8 empty] | BI+ | -15 | MW0300_A8+DA BI+-15 | MW0300_A8 | Creep FE | BI+ | -15 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | A | [8 empty] | BI+ | -30 | MW0300_A8+DA BI+-30 | MW0300_A8 | Creep FE | BI+ | -30 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | A | [8 empty] | BI+ | -45 | MW0300_A8+DA BI+-45 | MW0300_A8 | Creep FE | BI+ | -45 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | A | [8 empty] | BI+ | -90 | MW0300_A8+DA BI+-90 | MW0300_A8 | Creep FE | BI+ | -90 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | A | [8 empty] | BI- | 90 | MW0300_A8+DA BI-+90 | MW0300_A8 | Creep FE | BI- | 90 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | A | [8 empty] | BI- | 45 | MW0300_A8+DA BI-+45 | MW0300_A8 | Creep FE | BI- | 45 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | A | [8 empty] | BI- | 30 | MW0300_A8+DA BI-+30 | MW0300_A8 | Creep FE | BI- | 30 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | A | [8 empty] | BI- | 15 | MW0300_A8+DA BI-+15 | MW0300_A8 | Creep FE | BI- | 15 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | A | [8 empty] | BI- | 0 | MW0300_A8+DA BI-+00 | MW0300_A8 | Creep FE | BI- | 0 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | A | [8 empty] | BI- | -15 | MW0300_A8+DA BI--15 | MW0300_A8 | Creep FE | BI- | -15 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | A | [8 empty] | BI- | -30 | MW0300_A8+DA BI--30 | MW0300_A8 | Creep FE | BI- | -30 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | A | [8 empty] | BI- | -45 | MW0300_A8+DA BI--45 | MW0300_A8 | Creep FE | BI- | -45 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | A | [8 empty] | BI- | -90 | MW0300_A8+DA BI--90 | MW0300_A8 | Creep FE | BI- | -90 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | B | [8 empty] | BI+ | 90 | MW0300_A8+DB BI++90 | MW0300_A8 | Creep FE | BI+ | 90 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | B | [8 empty] | BI+ | 45 | MW0300_A8+DB BI++45 | MW0300_A8 | Creep FE | BI+ | 45 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | B | [8 empty] | BI+ | 30 | MW0300_A8+DB BI++30 | MW0300_A8 | Creep FE | BI+ | 30 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | B | [8 empty] | BI+ | 15 | MW0300_A8+DB BI++15 | MW0300_A8 | Creep FE | BI+ | 15 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | B | [8 empty] | BI+ | 0 | MW0300_A8+DB BI++00 | MW0300_A8 | Creep FE | BI+ | 0 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | B | [8 empty] | BI+ | -15 | MW0300_A8+DB BI+-15 | MW0300_A8 | Creep FE | BI+ | -15 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | B | [8 empty] | BI+ | -30 | MW0300_A8+DB BI+-30 | MW0300_A8 | Creep FE | BI+ | -30 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | B | [8 empty] | BI+ | -45 | MW0300_A8+DB BI+-45 | MW0300_A8 | Creep FE | BI+ | -45 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | B | [8 empty] | BI+ | -90 | MW0300_A8+DB BI+-90 | MW0300_A8 | Creep FE | BI+ | -90 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | B | [8 empty] | BI- | 90 | MW0300_A8+DB BI-+90 | MW0300_A8 | Creep FE | BI- | 90 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | B | [8 empty] | BI- | 45 | MW0300_A8+DB BI-+45 | MW0300_A8 | Creep FE | BI- | 45 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | B | [8 empty] | BI- | 30 | MW0300_A8+DB BI-+30 | MW0300_A8 | Creep FE | BI- | 30 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | B | [8 empty] | BI- | 15 | MW0300_A8+DB BI-+15 | MW0300_A8 | Creep FE | BI- | 15 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | B | [8 empty] | BI- | 0 | MW0300_A8+DB BI-+00 | MW0300_A8 | Creep FE | BI- | 0 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | B | [8 empty] | BI- | -15 | MW0300_A8+DB BI--15 | MW0300_A8 | Creep FE | BI- | -15 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | B | [8 empty] | BI- | -30 | MW0300_A8+DB BI--30 | MW0300_A8 | Creep FE | BI- | -30 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | B | [8 empty] | BI- | -45 | MW0300_A8+DB BI--45 | MW0300_A8 | Creep FE | BI- | -45 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 300 | D | B | [8 empty] | BI- | -90 | MW0300_A8+DB BI--90 | MW0300_A8 | Creep FE | BI- | -90 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 2500 | E | [9 empty] | BI+ | 90 | MW2500_A8+E BI++90 | MW2500_A8 | Creep FE | BI+ | 90 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 2500 | E | [9 empty] | BI+ | 45 | MW2500_A8+E BI++45 | MW2500_A8 | Creep FE | BI+ | 45 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 2500 | E | [9 empty] | BI+ | 30 | MW2500_A8+E BI++30 | MW2500_A8 | Creep FE | BI+ | 30 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 2500 | E | [9 empty] | BI+ | 15 | MW2500_A8+E BI++15 | MW2500_A8 | Creep FE | BI+ | 15 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 2500 | E | [9 empty] | BI+ | 0 | MW2500_A8+E BI++00 | MW2500_A8 | Creep FE | BI+ | 0 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 2500 | E | [9 empty] | BI+ | -15 | MW2500_A8+E BI+-15 | MW2500_A8 | Creep FE | BI+ | -15 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 2500 | E | [9 empty] | BI+ | -30 | MW2500_A8+E BI+-30 | MW2500_A8 | Creep FE | BI+ | -30 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 2500 | E | [9 empty] | BI+ | -45 | MW2500_A8+E BI+-45 | MW2500_A8 | Creep FE | BI+ | -45 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MW | 2500 | E | [9 empty] | BI+ | -90 | MW2500_A8+E BI+-90 | MW2500_A8 | Creep FE | BI+ | -90 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MT | 300 | E | [9 empty] | BI+ | 90 | MT0300_A8+E BI++90 | MT0300_A8 | Creep FE | BI+ | 90 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MT | 300 | E | [9 empty] | BI+ | 45 | MT0300_A8+E BI++45 | MT0300_A8 | Creep FE | BI+ | 45 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MT | 300 | E | [9 empty] | BI+ | 30 | MT0300_A8+E BI++30 | MT0300_A8 | Creep FE | BI+ | 30 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MT | 300 | E | [9 empty] | BI+ | 15 | MT0300_A8+E BI++15 | MT0300_A8 | Creep FE | BI+ | 15 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MT | 300 | E | [9 empty] | BI+ | 0 | MT0300_A8+E BI++00 | MT0300_A8 | Creep FE | BI+ | 0 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MT | 300 | E | [9 empty] | BI+ | -15 | MT0300_A8+E BI+-15 | MT0300_A8 | Creep FE | BI+ | -15 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MT | 300 | E | [9 empty] | BI+ | -30 | MT0300_A8+E BI+-30 | MT0300_A8 | Creep FE | BI+ | -30 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MT | 300 | E | [9 empty] | BI+ | -45 | MT0300_A8+E BI+-45 | MT0300_A8 | Creep FE | BI+ | -45 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MT | 300 | E | [9 empty] | BI+ | -90 | MT0300_A8+E BI+-90 | MT0300_A8 | Creep FE | BI+ | -90 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MT | 300 | E | [9 empty] | BI- | 90 | MT0300_A8+E BI-+90 | MT0300_A8 | Creep FE | BI- | 90 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MT | 300 | E | [9 empty] | BI- | 45 | MT0300_A8+E BI-+45 | MT0300_A8 | Creep FE | BI- | 45 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MT | 300 | E | [9 empty] | BI- | 30 | MT0300_A8+E BI-+30 | MT0300_A8 | Creep FE | BI- | 30 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MT | 300 | E | [9 empty] | BI- | 15 | MT0300_A8+E BI-+15 | MT0300_A8 | Creep FE | BI- | 15 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MT | 300 | E | [9 empty] | BI- | 0 | MT0300_A8+E BI-+00 | MT0300_A8 | Creep FE | BI- | 0 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MT | 300 | E | [9 empty] | BI- | -15 | MT0300_A8+E BI--15 | MT0300_A8 | Creep FE | BI- | -15 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MT | 300 | E | [9 empty] | BI- | -30 | MT0300_A8+E BI--30 | MT0300_A8 | Creep FE | BI- | -30 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MT | 300 | E | [9 empty] | BI- | -45 | MT0300_A8+E BI--45 | MT0300_A8 | Creep FE | BI- | -45 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP | - | - | YES | YES | MT | 300 | E | [9 empty] | BI- | -90 | MT0300_A8+E BI--90 | MT0300_A8 | Creep FE | BI- | -90 | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
- | - | - | - | - | - | - | - | SNOW LOADING
1 | ALL | DC/SC | RP,VUL | - | - | - | YES | ES | 50 | E | [9 empty] | NA+ |  | ES0050_8+E NA+ | ES0050_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP,VUL | - | - | - | YES | ES | 50 | L | A | [8 empty] | NA+ |  | ES0050_8+LA NA+ | ES0050_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Ice | 40 | Back Spans | % Wire Ice | 70
1 | ALL | DC/SC | RP,VUL | - | - | - | YES | ES | 50 | L | B | [8 empty] | NA+ |  | ES0050_8+LB NA+ | ES0050_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Ice | 40 | Ahead Spans | % Wire Ice | 70
1 | ALL | SC | RP,VUL | - | - | - | YES | ES | 50 | T | A | 1 | 2 |  | 3 | 7 | 8 |  |  | NA+ |  | ES0050_8+TA12 NA+ | ES0050_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | 1:1:Ahead | % Wire Ice | 40 | 11:1:Ahead | % Wire Ice | 40 | 1:1:Back | % Wire Ice | 70 | 2:1:Ahead | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 40 | 2:1:Back | % Wire Ice | 70 | [9 empty] | 3:1:Back+Ahead | % Wire Ice | 70 | 13:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | SC | RP,VUL | - | - | - | YES | ES | 50 | T | B | 1 | 2 |  | 3 | 7 | 8 |  |  | NA+ |  | ES0050_8+TB12 NA+ | ES0050_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | 1:1:Back | % Wire Ice | 40 | 11:1:Ahead | % Wire Ice | 70 | 1:1:Ahead | % Wire Ice | 70 | 2:1:Back | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 70 | 2:1:Ahead | % Wire Ice | 70 | [9 empty] | 3:1:Back+Ahead | % Wire Ice | 70 | 13:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | SC | RP,VUL | - | - | - | YES | ES | 50 | T | A | 2 | 3 |  | 1 | 7 | 8 |  |  | NA+ |  | ES0050_8+TA23 NA+ | ES0050_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | 2:1:Ahead | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 40 | 2:1:Back | % Wire Ice | 70 | 3:1:Ahead | % Wire Ice | 40 | 13:1:Ahead | % Wire Ice | 40 | 3:1:Back | % Wire Ice | 70 | [9 empty] | 1:1:Back+Ahead | % Wire Ice | 70 | 11:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | SC | RP,VUL | - | - | - | YES | ES | 50 | T | B | 2 | 3 |  | 1 | 7 | 8 |  |  | NA+ |  | ES0050_8+TB23 NA+ | ES0050_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | 2:1:Back | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 70 | 2:1:Ahead | % Wire Ice | 70 | 3:1:Back | % Wire Ice | 40 | 13:1:Ahead | % Wire Ice | 70 | 3:1:Ahead | % Wire Ice | 70 | [9 empty] | 1:1:Back+Ahead | % Wire Ice | 70 | 11:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | DC | RP,VUL | - | - | - | YES | ES | 50 | T | A | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | NA+ |  | ES0050_8+TA123 NA+ | ES0050_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | 1:1:Ahead | % Wire Ice | 40 | 11:1:Ahead | % Wire Ice | 40 | 1:1:Back | % Wire Ice | 70 | 2:1:Ahead | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 40 | 2:1:Back | % Wire Ice | 70 | 3:1:Ahead | % Wire Ice | 40 | 13:1:Ahead | % Wire Ice | 40 | 3:1:Back | % Wire Ice | 70 | 4:1:Back+Ahead | % Wire Ice | 70 | 14:1:Ahead | % Wire Ice | 70 | 5:1:Back+Ahead | % Wire Ice | 70 | 15:1:Ahead | % Wire Ice | 70 | 6:1:Back+Ahead | % Wire Ice | 70 | 16:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | DC | RP,VUL | - | - | - | YES | ES | 50 | T | B | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | NA+ |  | ES0050_8+TB123 NA+ | ES0050_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | 1:1:Back | % Wire Ice | 40 | 11:1:Ahead | % Wire Ice | 70 | 1:1:Ahead | % Wire Ice | 70 | 2:1:Back | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 70 | 2:1:Ahead | % Wire Ice | 70 | 3:1:Back | % Wire Ice | 40 | 13:1:Ahead | % Wire Ice | 70 | 3:1:Ahead | % Wire Ice | 70 | 4:1:Back+Ahead | % Wire Ice | 70 | 14:1:Ahead | % Wire Ice | 70 | 5:1:Back+Ahead | % Wire Ice | 70 | 15:1:Ahead | % Wire Ice | 70 | 6:1:Back+Ahead | % Wire Ice | 70 | 16:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | DC | RP,VUL | - | - | - | YES | ES | 50 | T | A | 4 | 5 | 6 | 1 | 2 | 3 | 7 | 8 | NA+ |  | ES0050_8+TA456 NA+ | ES0050_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | 4:1:Ahead | % Wire Ice | 40 | 14:1:Ahead | % Wire Ice | 40 | 4:1:Back | % Wire Ice | 70 | 5:1:Ahead | % Wire Ice | 40 | 15:1:Ahead | % Wire Ice | 40 | 5:1:Back | % Wire Ice | 70 | 6:1:Ahead | % Wire Ice | 40 | 16:1:Ahead | % Wire Ice | 40 | 6:1:Back | % Wire Ice | 70 | 1:1:Back+Ahead | % Wire Ice | 70 | 11:1:Ahead | % Wire Ice | 70 | 2:1:Back+Ahead | % Wire Ice | 70 | 12:1:Ahead | % Wire Ice | 70 | 3:1:Back+Ahead | % Wire Ice | 70 | 13:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | DC | RP,VUL | - | - | - | YES | ES | 50 | T | B | 4 | 5 | 6 | 1 | 2 | 3 | 7 | 8 | NA+ |  | ES0050_8+TB456 NA+ | ES0050_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | 4:1:Back | % Wire Ice | 40 | 14:1:Ahead | % Wire Ice | 70 | 4:1:Ahead | % Wire Ice | 70 | 5:1:Back | % Wire Ice | 40 | 15:1:Ahead | % Wire Ice | 70 | 5:1:Ahead | % Wire Ice | 70 | 6:1:Back | % Wire Ice | 40 | 16:1:Ahead | % Wire Ice | 70 | 6:1:Ahead | % Wire Ice | 70 | 1:1:Back+Ahead | % Wire Ice | 70 | 11:1:Ahead | % Wire Ice | 70 | 2:1:Back+Ahead | % Wire Ice | 70 | 12:1:Ahead | % Wire Ice | 70 | 3:1:Back+Ahead | % Wire Ice | 70 | 13:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | DC/SC | RP,VUL | - | - | - | YES | ES | 50 | E | [9 empty] | NA- |  | ES0050_8+E NA- | ES0050_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP,VUL | - | - | - | YES | ES | 50 | L | A | [8 empty] | NA- |  | ES0050_8+LA NA- | ES0050_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Ice | 40 | Back Spans | % Wire Ice | 70
1 | ALL | DC/SC | RP,VUL | - | - | - | YES | ES | 50 | L | B | [8 empty] | NA- |  | ES0050_8+LB NA- | ES0050_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Ice | 40 | Ahead Spans | % Wire Ice | 70
1 | ALL | SC | RP,VUL | - | - | - | YES | ES | 50 | T | A | 1 | 2 |  | 3 | 7 | 8 |  |  | NA- |  | ES0050_8+TA12 NA- | ES0050_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | 1:1:Ahead | % Wire Ice | 40 | 11:1:Ahead | % Wire Ice | 40 | 1:1:Back | % Wire Ice | 70 | 2:1:Ahead | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 40 | 2:1:Back | % Wire Ice | 70 | [9 empty] | 3:1:Back+Ahead | % Wire Ice | 70 | 13:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | SC | RP,VUL | - | - | - | YES | ES | 50 | T | B | 1 | 2 |  | 3 | 7 | 8 |  |  | NA- |  | ES0050_8+TB12 NA- | ES0050_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | 1:1:Back | % Wire Ice | 40 | 11:1:Ahead | % Wire Ice | 70 | 1:1:Ahead | % Wire Ice | 70 | 2:1:Back | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 70 | 2:1:Ahead | % Wire Ice | 70 | [9 empty] | 3:1:Back+Ahead | % Wire Ice | 70 | 13:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | SC | RP,VUL | - | - | - | YES | ES | 50 | T | A | 2 | 3 |  | 1 | 7 | 8 |  |  | NA- |  | ES0050_8+TA23 NA- | ES0050_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | 2:1:Ahead | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 40 | 2:1:Back | % Wire Ice | 70 | 3:1:Ahead | % Wire Ice | 40 | 13:1:Ahead | % Wire Ice | 40 | 3:1:Back | % Wire Ice | 70 | [9 empty] | 1:1:Back+Ahead | % Wire Ice | 70 | 11:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | SC | RP,VUL | - | - | - | YES | ES | 50 | T | B | 2 | 3 |  | 1 | 7 | 8 |  |  | NA- |  | ES0050_8+TB23 NA- | ES0050_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | 2:1:Back | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 70 | 2:1:Ahead | % Wire Ice | 70 | 3:1:Back | % Wire Ice | 40 | 13:1:Ahead | % Wire Ice | 70 | 3:1:Ahead | % Wire Ice | 70 | [9 empty] | 1:1:Back+Ahead | % Wire Ice | 70 | 11:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | DC | RP,VUL | - | - | - | YES | ES | 50 | T | A | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | NA- |  | ES0050_8+TA123 NA- | ES0050_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | 1:1:Ahead | % Wire Ice | 40 | 11:1:Ahead | % Wire Ice | 40 | 1:1:Back | % Wire Ice | 70 | 2:1:Ahead | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 40 | 2:1:Back | % Wire Ice | 70 | 3:1:Ahead | % Wire Ice | 40 | 13:1:Ahead | % Wire Ice | 40 | 3:1:Back | % Wire Ice | 70 | 4:1:Back+Ahead | % Wire Ice | 70 | 14:1:Ahead | % Wire Ice | 70 | 5:1:Back+Ahead | % Wire Ice | 70 | 15:1:Ahead | % Wire Ice | 70 | 6:1:Back+Ahead | % Wire Ice | 70 | 16:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | DC | RP,VUL | - | - | - | YES | ES | 50 | T | B | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | NA- |  | ES0050_8+TB123 NA- | ES0050_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | 1:1:Back | % Wire Ice | 40 | 11:1:Ahead | % Wire Ice | 70 | 1:1:Ahead | % Wire Ice | 70 | 2:1:Back | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 70 | 2:1:Ahead | % Wire Ice | 70 | 3:1:Back | % Wire Ice | 40 | 13:1:Ahead | % Wire Ice | 70 | 3:1:Ahead | % Wire Ice | 70 | 4:1:Back+Ahead | % Wire Ice | 70 | 14:1:Ahead | % Wire Ice | 70 | 5:1:Back+Ahead | % Wire Ice | 70 | 15:1:Ahead | % Wire Ice | 70 | 6:1:Back+Ahead | % Wire Ice | 70 | 16:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | DC | RP,VUL | - | - | - | YES | ES | 50 | T | A | 4 | 5 | 6 | 1 | 2 | 3 | 7 | 8 | NA- |  | ES0050_8+TA456 NA- | ES0050_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | 4:1:Ahead | % Wire Ice | 40 | 14:1:Ahead | % Wire Ice | 40 | 4:1:Back | % Wire Ice | 70 | 5:1:Ahead | % Wire Ice | 40 | 15:1:Ahead | % Wire Ice | 40 | 5:1:Back | % Wire Ice | 70 | 6:1:Ahead | % Wire Ice | 40 | 16:1:Ahead | % Wire Ice | 40 | 6:1:Back | % Wire Ice | 70 | 1:1:Back+Ahead | % Wire Ice | 70 | 11:1:Ahead | % Wire Ice | 70 | 2:1:Back+Ahead | % Wire Ice | 70 | 12:1:Ahead | % Wire Ice | 70 | 3:1:Back+Ahead | % Wire Ice | 70 | 13:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | DC | RP,VUL | - | - | - | YES | ES | 50 | T | B | 4 | 5 | 6 | 1 | 2 | 3 | 7 | 8 | NA- |  | ES0050_8+TB456 NA- | ES0050_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | 4:1:Back | % Wire Ice | 40 | 14:1:Ahead | % Wire Ice | 70 | 4:1:Ahead | % Wire Ice | 70 | 5:1:Back | % Wire Ice | 40 | 15:1:Ahead | % Wire Ice | 70 | 5:1:Ahead | % Wire Ice | 70 | 6:1:Back | % Wire Ice | 40 | 16:1:Ahead | % Wire Ice | 70 | 6:1:Ahead | % Wire Ice | 70 | 1:1:Back+Ahead | % Wire Ice | 70 | 11:1:Ahead | % Wire Ice | 70 | 2:1:Back+Ahead | % Wire Ice | 70 | 12:1:Ahead | % Wire Ice | 70 | 3:1:Back+Ahead | % Wire Ice | 70 | 13:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
- | - | - | - | - | - | - | - | THIN ICE WITH COINCIDENT WIND LOADING
1 | ALL | DC/SC | RP,VUL | - | - | YES | YES | TI | 50 | E | [9 empty] | NA+ |  | TI0050_A8+E NA+ | TI0050_A8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP,VUL | - | - | YES | YES | TI | 50 | L | A | [8 empty] | NA+ |  | TI0050_A8+LA NA+ | TI0050_A8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Ice | 40 | Back Spans | % Wire Ice | 70
1 | ALL | DC/SC | RP,VUL | - | - | YES | YES | TI | 50 | L | B | [8 empty] | NA+ |  | TI0050_A8+LB NA+ | TI0050_A8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Ice | 40 | Ahead Spans | % Wire Ice | 70
1 | ALL | SC | RP,VUL | - | - | YES | YES | TI | 50 | T | A | 1 | 2 |  | 3 | 7 | 8 |  |  | NA+ |  | TI0050_A8+TA12 NA+ | TI0050_A8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | 1:1:Ahead | % Wire Ice | 40 | 11:1:Ahead | % Wire Ice | 40 | 1:1:Back | % Wire Ice | 70 | 2:1:Ahead | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 40 | 2:1:Back | % Wire Ice | 70 | [9 empty] | 3:1:Back+Ahead | % Wire Ice | 70 | 13:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | SC | RP,VUL | - | - | YES | YES | TI | 50 | T | B | 1 | 2 |  | 3 | 7 | 8 |  |  | NA+ |  | TI0050_A8+TB12 NA+ | TI0050_A8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | 1:1:Back | % Wire Ice | 40 | 11:1:Ahead | % Wire Ice | 70 | 1:1:Ahead | % Wire Ice | 70 | 2:1:Back | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 70 | 2:1:Ahead | % Wire Ice | 70 | [9 empty] | 3:1:Back+Ahead | % Wire Ice | 70 | 13:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | SC | RP,VUL | - | - | YES | YES | TI | 50 | T | A | 2 | 3 |  | 1 | 7 | 8 |  |  | NA+ |  | TI0050_A8+TA23 NA+ | TI0050_A8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | 2:1:Ahead | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 40 | 2:1:Back | % Wire Ice | 70 | 3:1:Ahead | % Wire Ice | 40 | 13:1:Ahead | % Wire Ice | 40 | 3:1:Back | % Wire Ice | 70 | [9 empty] | 1:1:Back+Ahead | % Wire Ice | 70 | 11:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | SC | RP,VUL | - | - | YES | YES | TI | 50 | T | B | 2 | 3 |  | 1 | 7 | 8 |  |  | NA+ |  | TI0050_A8+TB23 NA+ | TI0050_A8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | 2:1:Back | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 70 | 2:1:Ahead | % Wire Ice | 70 | 3:1:Back | % Wire Ice | 40 | 13:1:Ahead | % Wire Ice | 70 | 3:1:Ahead | % Wire Ice | 70 | [9 empty] | 1:1:Back+Ahead | % Wire Ice | 70 | 11:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | DC | RP,VUL | - | - | YES | YES | TI | 50 | T | A | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | NA+ |  | TI0050_A8+TA123 NA+ | TI0050_A8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | 1:1:Ahead | % Wire Ice | 40 | 11:1:Ahead | % Wire Ice | 40 | 1:1:Back | % Wire Ice | 70 | 2:1:Ahead | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 40 | 2:1:Back | % Wire Ice | 70 | 3:1:Ahead | % Wire Ice | 40 | 13:1:Ahead | % Wire Ice | 40 | 3:1:Back | % Wire Ice | 70 | 4:1:Back+Ahead | % Wire Ice | 70 | 14:1:Ahead | % Wire Ice | 70 | 5:1:Back+Ahead | % Wire Ice | 70 | 15:1:Ahead | % Wire Ice | 70 | 6:1:Back+Ahead | % Wire Ice | 70 | 16:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | DC | RP,VUL | - | - | YES | YES | TI | 50 | T | B | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | NA+ |  | TI0050_A8+TB123 NA+ | TI0050_A8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | 1:1:Back | % Wire Ice | 40 | 11:1:Ahead | % Wire Ice | 70 | 1:1:Ahead | % Wire Ice | 70 | 2:1:Back | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 70 | 2:1:Ahead | % Wire Ice | 70 | 3:1:Back | % Wire Ice | 40 | 13:1:Ahead | % Wire Ice | 70 | 3:1:Ahead | % Wire Ice | 70 | 4:1:Back+Ahead | % Wire Ice | 70 | 14:1:Ahead | % Wire Ice | 70 | 5:1:Back+Ahead | % Wire Ice | 70 | 15:1:Ahead | % Wire Ice | 70 | 6:1:Back+Ahead | % Wire Ice | 70 | 16:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | DC | RP,VUL | - | - | YES | YES | TI | 50 | T | A | 4 | 5 | 6 | 1 | 2 | 3 | 7 | 8 | NA+ |  | TI0050_A8+TA456 NA+ | TI0050_A8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | 4:1:Ahead | % Wire Ice | 40 | 14:1:Ahead | % Wire Ice | 40 | 4:1:Back | % Wire Ice | 70 | 5:1:Ahead | % Wire Ice | 40 | 15:1:Ahead | % Wire Ice | 40 | 5:1:Back | % Wire Ice | 70 | 6:1:Ahead | % Wire Ice | 40 | 16:1:Ahead | % Wire Ice | 40 | 6:1:Back | % Wire Ice | 70 | 1:1:Back+Ahead | % Wire Ice | 70 | 11:1:Ahead | % Wire Ice | 70 | 2:1:Back+Ahead | % Wire Ice | 70 | 12:1:Ahead | % Wire Ice | 70 | 3:1:Back+Ahead | % Wire Ice | 70 | 13:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | DC | RP,VUL | - | - | YES | YES | TI | 50 | T | B | 4 | 5 | 6 | 1 | 2 | 3 | 7 | 8 | NA+ |  | TI0050_A8+TB456 NA+ | TI0050_A8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | 4:1:Back | % Wire Ice | 40 | 14:1:Ahead | % Wire Ice | 70 | 4:1:Ahead | % Wire Ice | 70 | 5:1:Back | % Wire Ice | 40 | 15:1:Ahead | % Wire Ice | 70 | 5:1:Ahead | % Wire Ice | 70 | 6:1:Back | % Wire Ice | 40 | 16:1:Ahead | % Wire Ice | 70 | 6:1:Ahead | % Wire Ice | 70 | 1:1:Back+Ahead | % Wire Ice | 70 | 11:1:Ahead | % Wire Ice | 70 | 2:1:Back+Ahead | % Wire Ice | 70 | 12:1:Ahead | % Wire Ice | 70 | 3:1:Back+Ahead | % Wire Ice | 70 | 13:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | DC/SC | RP,VUL | - | - | YES | YES | TI | 50 | E | [9 empty] | NA- |  | TI0050_A8+E NA- | TI0050_A8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP,VUL | - | - | YES | YES | TI | 50 | L | A | [8 empty] | NA- |  | TI0050_A8+LA NA- | TI0050_A8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Ice | 40 | Back Spans | % Wire Ice | 70
1 | ALL | DC/SC | RP,VUL | - | - | YES | YES | TI | 50 | L | B | [8 empty] | NA- |  | TI0050_A8+LB NA- | TI0050_A8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Ice | 40 | Ahead Spans | % Wire Ice | 70
1 | ALL | SC | RP,VUL | - | - | YES | YES | TI | 50 | T | A | 1 | 2 |  | 3 | 7 | 8 |  |  | NA- |  | TI0050_A8+TA12 NA- | TI0050_A8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | 1:1:Ahead | % Wire Ice | 40 | 11:1:Ahead | % Wire Ice | 40 | 1:1:Back | % Wire Ice | 70 | 2:1:Ahead | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 40 | 2:1:Back | % Wire Ice | 70 | [9 empty] | 3:1:Back+Ahead | % Wire Ice | 70 | 13:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | SC | RP,VUL | - | - | YES | YES | TI | 50 | T | B | 1 | 2 |  | 3 | 7 | 8 |  |  | NA- |  | TI0050_A8+TB12 NA- | TI0050_A8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | 1:1:Back | % Wire Ice | 40 | 11:1:Ahead | % Wire Ice | 70 | 1:1:Ahead | % Wire Ice | 70 | 2:1:Back | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 70 | 2:1:Ahead | % Wire Ice | 70 | [9 empty] | 3:1:Back+Ahead | % Wire Ice | 70 | 13:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | SC | RP,VUL | - | - | YES | YES | TI | 50 | T | A | 2 | 3 |  | 1 | 7 | 8 |  |  | NA- |  | TI0050_A8+TA23 NA- | TI0050_A8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | 2:1:Ahead | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 40 | 2:1:Back | % Wire Ice | 70 | 3:1:Ahead | % Wire Ice | 40 | 13:1:Ahead | % Wire Ice | 40 | 3:1:Back | % Wire Ice | 70 | [9 empty] | 1:1:Back+Ahead | % Wire Ice | 70 | 11:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | SC | RP,VUL | - | - | YES | YES | TI | 50 | T | B | 2 | 3 |  | 1 | 7 | 8 |  |  | NA- |  | TI0050_A8+TB23 NA- | TI0050_A8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | 2:1:Back | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 70 | 2:1:Ahead | % Wire Ice | 70 | 3:1:Back | % Wire Ice | 40 | 13:1:Ahead | % Wire Ice | 70 | 3:1:Ahead | % Wire Ice | 70 | [9 empty] | 1:1:Back+Ahead | % Wire Ice | 70 | 11:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | DC | RP,VUL | - | - | YES | YES | TI | 50 | T | A | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | NA- |  | TI0050_A8+TA123 NA- | TI0050_A8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | 1:1:Ahead | % Wire Ice | 40 | 11:1:Ahead | % Wire Ice | 40 | 1:1:Back | % Wire Ice | 70 | 2:1:Ahead | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 40 | 2:1:Back | % Wire Ice | 70 | 3:1:Ahead | % Wire Ice | 40 | 13:1:Ahead | % Wire Ice | 40 | 3:1:Back | % Wire Ice | 70 | 4:1:Back+Ahead | % Wire Ice | 70 | 14:1:Ahead | % Wire Ice | 70 | 5:1:Back+Ahead | % Wire Ice | 70 | 15:1:Ahead | % Wire Ice | 70 | 6:1:Back+Ahead | % Wire Ice | 70 | 16:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | DC | RP,VUL | - | - | YES | YES | TI | 50 | T | B | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | NA- |  | TI0050_A8+TB123 NA- | TI0050_A8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | 1:1:Back | % Wire Ice | 40 | 11:1:Ahead | % Wire Ice | 70 | 1:1:Ahead | % Wire Ice | 70 | 2:1:Back | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 70 | 2:1:Ahead | % Wire Ice | 70 | 3:1:Back | % Wire Ice | 40 | 13:1:Ahead | % Wire Ice | 70 | 3:1:Ahead | % Wire Ice | 70 | 4:1:Back+Ahead | % Wire Ice | 70 | 14:1:Ahead | % Wire Ice | 70 | 5:1:Back+Ahead | % Wire Ice | 70 | 15:1:Ahead | % Wire Ice | 70 | 6:1:Back+Ahead | % Wire Ice | 70 | 16:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | DC | RP,VUL | - | - | YES | YES | TI | 50 | T | A | 4 | 5 | 6 | 1 | 2 | 3 | 7 | 8 | NA- |  | TI0050_A8+TA456 NA- | TI0050_A8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | 4:1:Ahead | % Wire Ice | 40 | 14:1:Ahead | % Wire Ice | 40 | 4:1:Back | % Wire Ice | 70 | 5:1:Ahead | % Wire Ice | 40 | 15:1:Ahead | % Wire Ice | 40 | 5:1:Back | % Wire Ice | 70 | 6:1:Ahead | % Wire Ice | 40 | 16:1:Ahead | % Wire Ice | 40 | 6:1:Back | % Wire Ice | 70 | 1:1:Back+Ahead | % Wire Ice | 70 | 11:1:Ahead | % Wire Ice | 70 | 2:1:Back+Ahead | % Wire Ice | 70 | 12:1:Ahead | % Wire Ice | 70 | 3:1:Back+Ahead | % Wire Ice | 70 | 13:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | DC | RP,VUL | - | - | YES | YES | TI | 50 | T | B | 4 | 5 | 6 | 1 | 2 | 3 | 7 | 8 | NA- |  | TI0050_A8+TB456 NA- | TI0050_A8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | 4:1:Back | % Wire Ice | 40 | 14:1:Ahead | % Wire Ice | 70 | 4:1:Ahead | % Wire Ice | 70 | 5:1:Back | % Wire Ice | 40 | 15:1:Ahead | % Wire Ice | 70 | 5:1:Ahead | % Wire Ice | 70 | 6:1:Back | % Wire Ice | 40 | 16:1:Ahead | % Wire Ice | 70 | 6:1:Ahead | % Wire Ice | 70 | 1:1:Back+Ahead | % Wire Ice | 70 | 11:1:Ahead | % Wire Ice | 70 | 2:1:Back+Ahead | % Wire Ice | 70 | 12:1:Ahead | % Wire Ice | 70 | 3:1:Back+Ahead | % Wire Ice | 70 | 13:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
- | - | - | - | - | - | - | - | EXTREME (THICK) ICE LOADING
1 | ALL | DC/SC | RP,VUL | - | - | - | YES | EI | 50 | E | [9 empty] | NA+ |  | EI0050_8+E NA+ | EI0050_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP,VUL | - | - | - | YES | EI | 50 | L | A | [8 empty] | NA+ |  | EI0050_8+LA NA+ | EI0050_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Ice | 40 | Back Spans | % Wire Ice | 70
1 | ALL | DC/SC | RP,VUL | - | - | - | YES | EI | 50 | L | B | [8 empty] | NA+ |  | EI0050_8+LB NA+ | EI0050_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Ice | 40 | Ahead Spans | % Wire Ice | 70
1 | ALL | SC | RP,VUL | - | - | - | YES | EI | 50 | T | A | 1 | 2 |  | 3 | 7 | 8 |  |  | NA+ |  | EI0050_8+TA12 NA+ | EI0050_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | 1:1:Ahead | % Wire Ice | 40 | 11:1:Ahead | % Wire Ice | 40 | 1:1:Back | % Wire Ice | 70 | 2:1:Ahead | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 40 | 2:1:Back | % Wire Ice | 70 | [9 empty] | 3:1:Back+Ahead | % Wire Ice | 70 | 13:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | SC | RP,VUL | - | - | - | YES | EI | 50 | T | B | 1 | 2 |  | 3 | 7 | 8 |  |  | NA+ |  | EI0050_8+TB12 NA+ | EI0050_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | 1:1:Back | % Wire Ice | 40 | 11:1:Ahead | % Wire Ice | 70 | 1:1:Ahead | % Wire Ice | 70 | 2:1:Back | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 70 | 2:1:Ahead | % Wire Ice | 70 | [9 empty] | 3:1:Back+Ahead | % Wire Ice | 70 | 13:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | SC | RP,VUL | - | - | - | YES | EI | 50 | T | A | 2 | 3 |  | 1 | 7 | 8 |  |  | NA+ |  | EI0050_8+TA23 NA+ | EI0050_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | 2:1:Ahead | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 40 | 2:1:Back | % Wire Ice | 70 | 3:1:Ahead | % Wire Ice | 40 | 13:1:Ahead | % Wire Ice | 40 | 3:1:Back | % Wire Ice | 70 | [9 empty] | 1:1:Back+Ahead | % Wire Ice | 70 | 11:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | SC | RP,VUL | - | - | - | YES | EI | 50 | T | B | 2 | 3 |  | 1 | 7 | 8 |  |  | NA+ |  | EI0050_8+TB23 NA+ | EI0050_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | 2:1:Back | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 70 | 2:1:Ahead | % Wire Ice | 70 | 3:1:Back | % Wire Ice | 40 | 13:1:Ahead | % Wire Ice | 70 | 3:1:Ahead | % Wire Ice | 70 | [9 empty] | 1:1:Back+Ahead | % Wire Ice | 70 | 11:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | DC | RP,VUL | - | - | - | YES | EI | 50 | T | A | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | NA+ |  | EI0050_8+TA123 NA+ | EI0050_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | 1:1:Ahead | % Wire Ice | 40 | 11:1:Ahead | % Wire Ice | 40 | 1:1:Back | % Wire Ice | 70 | 2:1:Ahead | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 40 | 2:1:Back | % Wire Ice | 70 | 3:1:Ahead | % Wire Ice | 40 | 13:1:Ahead | % Wire Ice | 40 | 3:1:Back | % Wire Ice | 70 | 4:1:Back+Ahead | % Wire Ice | 70 | 14:1:Ahead | % Wire Ice | 70 | 5:1:Back+Ahead | % Wire Ice | 70 | 15:1:Ahead | % Wire Ice | 70 | 6:1:Back+Ahead | % Wire Ice | 70 | 16:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | DC | RP,VUL | - | - | - | YES | EI | 50 | T | B | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | NA+ |  | EI0050_8+TB123 NA+ | EI0050_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | 1:1:Back | % Wire Ice | 40 | 11:1:Ahead | % Wire Ice | 70 | 1:1:Ahead | % Wire Ice | 70 | 2:1:Back | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 70 | 2:1:Ahead | % Wire Ice | 70 | 3:1:Back | % Wire Ice | 40 | 13:1:Ahead | % Wire Ice | 70 | 3:1:Ahead | % Wire Ice | 70 | 4:1:Back+Ahead | % Wire Ice | 70 | 14:1:Ahead | % Wire Ice | 70 | 5:1:Back+Ahead | % Wire Ice | 70 | 15:1:Ahead | % Wire Ice | 70 | 6:1:Back+Ahead | % Wire Ice | 70 | 16:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | DC | RP,VUL | - | - | - | YES | EI | 50 | T | A | 4 | 5 | 6 | 1 | 2 | 3 | 7 | 8 | NA+ |  | EI0050_8+TA456 NA+ | EI0050_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | 4:1:Ahead | % Wire Ice | 40 | 14:1:Ahead | % Wire Ice | 40 | 4:1:Back | % Wire Ice | 70 | 5:1:Ahead | % Wire Ice | 40 | 15:1:Ahead | % Wire Ice | 40 | 5:1:Back | % Wire Ice | 70 | 6:1:Ahead | % Wire Ice | 40 | 16:1:Ahead | % Wire Ice | 40 | 6:1:Back | % Wire Ice | 70 | 1:1:Back+Ahead | % Wire Ice | 70 | 11:1:Ahead | % Wire Ice | 70 | 2:1:Back+Ahead | % Wire Ice | 70 | 12:1:Ahead | % Wire Ice | 70 | 3:1:Back+Ahead | % Wire Ice | 70 | 13:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | DC | RP,VUL | - | - | - | YES | EI | 50 | T | B | 4 | 5 | 6 | 1 | 2 | 3 | 7 | 8 | NA+ |  | EI0050_8+TB456 NA+ | EI0050_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | 4:1:Back | % Wire Ice | 40 | 14:1:Ahead | % Wire Ice | 70 | 4:1:Ahead | % Wire Ice | 70 | 5:1:Back | % Wire Ice | 40 | 15:1:Ahead | % Wire Ice | 70 | 5:1:Ahead | % Wire Ice | 70 | 6:1:Back | % Wire Ice | 40 | 16:1:Ahead | % Wire Ice | 70 | 6:1:Ahead | % Wire Ice | 70 | 1:1:Back+Ahead | % Wire Ice | 70 | 11:1:Ahead | % Wire Ice | 70 | 2:1:Back+Ahead | % Wire Ice | 70 | 12:1:Ahead | % Wire Ice | 70 | 3:1:Back+Ahead | % Wire Ice | 70 | 13:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | DC/SC | RP,VUL | - | - | - | YES | EI | 50 | E | [9 empty] | NA- |  | EI0050_8+E NA- | EI0050_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | RP,VUL | - | - | - | YES | EI | 50 | L | A | [8 empty] | NA- |  | EI0050_8+LA NA- | EI0050_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Ice | 40 | Back Spans | % Wire Ice | 70
1 | ALL | DC/SC | RP,VUL | - | - | - | YES | EI | 50 | L | B | [8 empty] | NA- |  | EI0050_8+LB NA- | EI0050_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Ice | 40 | Ahead Spans | % Wire Ice | 70
1 | ALL | SC | RP,VUL | - | - | - | YES | EI | 50 | T | A | 1 | 2 |  | 3 | 7 | 8 |  |  | NA- |  | EI0050_8+TA12 NA- | EI0050_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | 1:1:Ahead | % Wire Ice | 40 | 11:1:Ahead | % Wire Ice | 40 | 1:1:Back | % Wire Ice | 70 | 2:1:Ahead | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 40 | 2:1:Back | % Wire Ice | 70 | [9 empty] | 3:1:Back+Ahead | % Wire Ice | 70 | 13:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | SC | RP,VUL | - | - | - | YES | EI | 50 | T | B | 1 | 2 |  | 3 | 7 | 8 |  |  | NA- |  | EI0050_8+TB12 NA- | EI0050_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | 1:1:Back | % Wire Ice | 40 | 11:1:Ahead | % Wire Ice | 70 | 1:1:Ahead | % Wire Ice | 70 | 2:1:Back | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 70 | 2:1:Ahead | % Wire Ice | 70 | [9 empty] | 3:1:Back+Ahead | % Wire Ice | 70 | 13:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | SC | RP,VUL | - | - | - | YES | EI | 50 | T | A | 2 | 3 |  | 1 | 7 | 8 |  |  | NA- |  | EI0050_8+TA23 NA- | EI0050_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | 2:1:Ahead | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 40 | 2:1:Back | % Wire Ice | 70 | 3:1:Ahead | % Wire Ice | 40 | 13:1:Ahead | % Wire Ice | 40 | 3:1:Back | % Wire Ice | 70 | [9 empty] | 1:1:Back+Ahead | % Wire Ice | 70 | 11:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | SC | RP,VUL | - | - | - | YES | EI | 50 | T | B | 2 | 3 |  | 1 | 7 | 8 |  |  | NA- |  | EI0050_8+TB23 NA- | EI0050_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'GL Max 800m' | No Limit |  | Yes | 2:1:Back | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 70 | 2:1:Ahead | % Wire Ice | 70 | 3:1:Back | % Wire Ice | 40 | 13:1:Ahead | % Wire Ice | 70 | 3:1:Ahead | % Wire Ice | 70 | [9 empty] | 1:1:Back+Ahead | % Wire Ice | 70 | 11:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | DC | RP,VUL | - | - | - | YES | EI | 50 | T | A | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | NA- |  | EI0050_8+TA123 NA- | EI0050_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | 1:1:Ahead | % Wire Ice | 40 | 11:1:Ahead | % Wire Ice | 40 | 1:1:Back | % Wire Ice | 70 | 2:1:Ahead | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 40 | 2:1:Back | % Wire Ice | 70 | 3:1:Ahead | % Wire Ice | 40 | 13:1:Ahead | % Wire Ice | 40 | 3:1:Back | % Wire Ice | 70 | 4:1:Back+Ahead | % Wire Ice | 70 | 14:1:Ahead | % Wire Ice | 70 | 5:1:Back+Ahead | % Wire Ice | 70 | 15:1:Ahead | % Wire Ice | 70 | 6:1:Back+Ahead | % Wire Ice | 70 | 16:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | DC | RP,VUL | - | - | - | YES | EI | 50 | T | B | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | NA- |  | EI0050_8+TB123 NA- | EI0050_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | 1:1:Back | % Wire Ice | 40 | 11:1:Ahead | % Wire Ice | 70 | 1:1:Ahead | % Wire Ice | 70 | 2:1:Back | % Wire Ice | 40 | 12:1:Ahead | % Wire Ice | 70 | 2:1:Ahead | % Wire Ice | 70 | 3:1:Back | % Wire Ice | 40 | 13:1:Ahead | % Wire Ice | 70 | 3:1:Ahead | % Wire Ice | 70 | 4:1:Back+Ahead | % Wire Ice | 70 | 14:1:Ahead | % Wire Ice | 70 | 5:1:Back+Ahead | % Wire Ice | 70 | 15:1:Ahead | % Wire Ice | 70 | 6:1:Back+Ahead | % Wire Ice | 70 | 16:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | DC | RP,VUL | - | - | - | YES | EI | 50 | T | A | 4 | 5 | 6 | 1 | 2 | 3 | 7 | 8 | NA- |  | EI0050_8+TA456 NA- | EI0050_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | 4:1:Ahead | % Wire Ice | 40 | 14:1:Ahead | % Wire Ice | 40 | 4:1:Back | % Wire Ice | 70 | 5:1:Ahead | % Wire Ice | 40 | 15:1:Ahead | % Wire Ice | 40 | 5:1:Back | % Wire Ice | 70 | 6:1:Ahead | % Wire Ice | 40 | 16:1:Ahead | % Wire Ice | 40 | 6:1:Back | % Wire Ice | 70 | 1:1:Back+Ahead | % Wire Ice | 70 | 11:1:Ahead | % Wire Ice | 70 | 2:1:Back+Ahead | % Wire Ice | 70 | 12:1:Ahead | % Wire Ice | 70 | 3:1:Back+Ahead | % Wire Ice | 70 | 13:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
1 | ALL | DC | RP,VUL | - | - | - | YES | EI | 50 | T | B | 4 | 5 | 6 | 1 | 2 | 3 | 7 | 8 | NA- |  | EI0050_8+TB456 NA- | EI0050_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | 4:1:Back | % Wire Ice | 40 | 14:1:Ahead | % Wire Ice | 70 | 4:1:Ahead | % Wire Ice | 70 | 5:1:Back | % Wire Ice | 40 | 15:1:Ahead | % Wire Ice | 70 | 5:1:Ahead | % Wire Ice | 70 | 6:1:Back | % Wire Ice | 40 | 16:1:Ahead | % Wire Ice | 70 | 6:1:Ahead | % Wire Ice | 70 | 1:1:Back+Ahead | % Wire Ice | 70 | 11:1:Ahead | % Wire Ice | 70 | 2:1:Back+Ahead | % Wire Ice | 70 | 12:1:Ahead | % Wire Ice | 70 | 3:1:Back+Ahead | % Wire Ice | 70 | 13:1:Ahead | % Wire Ice | 70 | 7:1:Back+Ahead | % Wire Ice | 70 | 17:1:Ahead | % Wire Ice | 70 | 8:1:Back+Ahead | % Wire Ice | 70 | 18:1:Ahead | % Wire Ice | 70
- | - | - | - | - | - | - | - | SECURITY LOADING - FAILURE CONTAINMENT - WIND | [41 empty] | Note - all phases / earthwires default to complete breakage - employ # sub-conductors = 4
1 | ALL | DC/SC | FC | ALL | - | - | - | RW | 1 | L | A | [8 empty] | NA+ |  | RW0001_8+LA NA+ | RW0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | Ahead Spans | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | ALL | - | - | - | RW | 1 | L | B | [8 empty] | NA+ |  | RW0001_8+LB NA+ | RW0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | Back Spans | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | ALL | - | - | - | RW | 1 | L | A | [8 empty] | NA- |  | RW0001_8+LA NA- | RW0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | Ahead Spans | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | ALL | - | - | - | RW | 1 | L | B | [8 empty] | NA- |  | RW0001_8+LB NA- | RW0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | Back Spans | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RW | 1 | T | A | 1 | [7 empty] | NA+ |  | RW0001_8+TA1 NA+ | RW0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 1:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 11:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RW | 1 | T | B | 1 | [7 empty] | NA+ |  | RW0001_8+TB1 NA+ | RW0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 1:1:Back | Broken Wire (# Broken Subconductors) | 4 | 11:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RW | 1 | T | A | 2 | [7 empty] | NA+ |  | RW0001_8+TA2 NA+ | RW0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 2:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 12:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RW | 1 | T | B | 2 | [7 empty] | NA+ |  | RW0001_8+TB2 NA+ | RW0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 2:1:Back | Broken Wire (# Broken Subconductors) | 4 | 12:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RW | 1 | T | A | 3 | [7 empty] | NA+ |  | RW0001_8+TA3 NA+ | RW0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 3:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 13:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RW | 1 | T | B | 3 | [7 empty] | NA+ |  | RW0001_8+TB3 NA+ | RW0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 3:1:Back | Broken Wire (# Broken Subconductors) | 4 | 13:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RW | 1 | T | A | 4 | [7 empty] | NA+ |  | RW0001_8+TA4 NA+ | RW0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 4:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 14:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RW | 1 | T | B | 4 | [7 empty] | NA+ |  | RW0001_8+TB4 NA+ | RW0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 4:1:Back | Broken Wire (# Broken Subconductors) | 4 | 14:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RW | 1 | T | A | 5 | [7 empty] | NA+ |  | RW0001_8+TA5 NA+ | RW0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 5:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 15:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RW | 1 | T | B | 5 | [7 empty] | NA+ |  | RW0001_8+TB5 NA+ | RW0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 5:1:Back | Broken Wire (# Broken Subconductors) | 4 | 15:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RW | 1 | T | A | 6 | [7 empty] | NA+ |  | RW0001_8+TA6 NA+ | RW0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 6:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 16:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RW | 1 | T | B | 6 | [7 empty] | NA+ |  | RW0001_8+TB6 NA+ | RW0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 6:1:Back | Broken Wire (# Broken Subconductors) | 4 | 16:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | EW7 | - | - | RW | 1 | T | A | 7 | [7 empty] | NA+ |  | RW0001_8+TA7 NA+ | RW0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 7:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 17:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | EW7 | - | - | RW | 1 | T | B | 7 | [7 empty] | NA+ |  | RW0001_8+TB7 NA+ | RW0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 7:1:Back | Broken Wire (# Broken Subconductors) | 4 | 17:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | EW8 | - | - | RW | 1 | T | A | 8 | [7 empty] | NA+ |  | RW0001_8+TA8 NA+ | RW0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 8:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 18:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | EW8 | - | - | RW | 1 | T | B | 8 | [7 empty] | NA+ |  | RW0001_8+TB8 NA+ | RW0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 8:1:Back | Broken Wire (# Broken Subconductors) | 4 | 18:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RW | 1 | T | A | 1 | [7 empty] | NA- |  | RW0001_8+TA1 NA- | RW0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 1:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 11:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RW | 1 | T | B | 1 | [7 empty] | NA- |  | RW0001_8+TB1 NA- | RW0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 1:1:Back | Broken Wire (# Broken Subconductors) | 4 | 11:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RW | 1 | T | A | 2 | [7 empty] | NA- |  | RW0001_8+TA2 NA- | RW0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 2:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 12:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RW | 1 | T | B | 2 | [7 empty] | NA- |  | RW0001_8+TB2 NA- | RW0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 2:1:Back | Broken Wire (# Broken Subconductors) | 4 | 12:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RW | 1 | T | A | 3 | [7 empty] | NA- |  | RW0001_8+TA3 NA- | RW0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 3:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 13:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RW | 1 | T | B | 3 | [7 empty] | NA- |  | RW0001_8+TB3 NA- | RW0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 3:1:Back | Broken Wire (# Broken Subconductors) | 4 | 13:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RW | 1 | T | A | 4 | [7 empty] | NA- |  | RW0001_8+TA4 NA- | RW0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 4:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 14:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RW | 1 | T | B | 4 | [7 empty] | NA- |  | RW0001_8+TB4 NA- | RW0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 4:1:Back | Broken Wire (# Broken Subconductors) | 4 | 14:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RW | 1 | T | A | 5 | [7 empty] | NA- |  | RW0001_8+TA5 NA- | RW0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 5:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 15:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RW | 1 | T | B | 5 | [7 empty] | NA- |  | RW0001_8+TB5 NA- | RW0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 5:1:Back | Broken Wire (# Broken Subconductors) | 4 | 15:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RW | 1 | T | A | 6 | [7 empty] | NA- |  | RW0001_8+TA6 NA- | RW0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 6:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 16:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RW | 1 | T | B | 6 | [7 empty] | NA- |  | RW0001_8+TB6 NA- | RW0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 6:1:Back | Broken Wire (# Broken Subconductors) | 4 | 16:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | EW7 | - | - | RW | 1 | T | A | 7 | [7 empty] | NA- |  | RW0001_8+TA7 NA- | RW0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 7:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 17:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | EW7 | - | - | RW | 1 | T | B | 7 | [7 empty] | NA- |  | RW0001_8+TB7 NA- | RW0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 7:1:Back | Broken Wire (# Broken Subconductors) | 4 | 17:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | EW8 | - | - | RW | 1 | T | A | 8 | [7 empty] | NA- |  | RW0001_8+TA8 NA- | RW0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 8:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 18:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | EW8 | - | - | RW | 1 | T | B | 8 | [7 empty] | NA- |  | RW0001_8+TB8 NA- | RW0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 8:1:Back | Broken Wire (# Broken Subconductors) | 4 | 18:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RW | 1 | T | A | 1 | 2 | [6 empty] | NA+ |  | RW0001_8+TA12 NA+ | RW0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 1:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 11:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 2:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 12:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RW | 1 | T | A | 2 | 3 | [6 empty] | NA+ |  | RW0001_8+TA23 NA+ | RW0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 2:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 12:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 3:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 13:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RW | 1 | T | A | 1 | 3 | [6 empty] | NA+ |  | RW0001_8+TA13 NA+ | RW0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 1:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 11:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 3:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 13:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | EW7 | - | - | RW | 1 | T | A | 3 | 7 | [6 empty] | NA+ |  | RW0001_8+TA37 NA+ | RW0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 3:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 13:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 7:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 17:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RW | 1 | T | A | 4 | 5 | [6 empty] | NA+ |  | RW0001_8+TA45 NA+ | RW0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 4:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 14:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 5:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 15:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RW | 1 | T | A | 4 | 6 | [6 empty] | NA+ |  | RW0001_8+TA46 NA+ | RW0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 4:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 14:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 6:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 16:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RW | 1 | T | A | 5 | 6 | [6 empty] | NA+ |  | RW0001_8+TA56 NA+ | RW0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 5:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 15:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 6:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 16:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | EW8 | - | - | RW | 1 | T | A | 6 | 8 | [6 empty] | NA+ |  | RW0001_8+TA68 NA+ | RW0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 6:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 16:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 8:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 18:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RW | 1 | T | B | 1 | 2 | [6 empty] | NA+ |  | RW0001_8+TB12 NA+ | RW0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 1:1:Back | Broken Wire (# Broken Subconductors) | 4 | 11:1:Back | Broken Wire (# Broken Subconductors) | 4 | 2:1:Back | Broken Wire (# Broken Subconductors) | 4 | 12:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RW | 1 | T | B | 2 | 3 | [6 empty] | NA+ |  | RW0001_8+TB23 NA+ | RW0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 2:1:Back | Broken Wire (# Broken Subconductors) | 4 | 12:1:Back | Broken Wire (# Broken Subconductors) | 4 | 3:1:Back | Broken Wire (# Broken Subconductors) | 4 | 13:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RW | 1 | T | B | 1 | 3 | [6 empty] | NA+ |  | RW0001_8+TB13 NA+ | RW0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 1:1:Back | Broken Wire (# Broken Subconductors) | 4 | 11:1:Back | Broken Wire (# Broken Subconductors) | 4 | 3:1:Back | Broken Wire (# Broken Subconductors) | 4 | 13:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | EW7 | - | - | RW | 1 | T | B | 3 | 7 | [6 empty] | NA+ |  | RW0001_8+TB37 NA+ | RW0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 3:1:Back | Broken Wire (# Broken Subconductors) | 4 | 13:1:Back | Broken Wire (# Broken Subconductors) | 4 | 7:1:Back | Broken Wire (# Broken Subconductors) | 4 | 17:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RW | 1 | T | B | 4 | 5 | [6 empty] | NA+ |  | RW0001_8+TB45 NA+ | RW0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 4:1:Back | Broken Wire (# Broken Subconductors) | 4 | 14:1:Back | Broken Wire (# Broken Subconductors) | 4 | 5:1:Back | Broken Wire (# Broken Subconductors) | 4 | 15:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RW | 1 | T | B | 4 | 6 | [6 empty] | NA+ |  | RW0001_8+TB46 NA+ | RW0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 4:1:Back | Broken Wire (# Broken Subconductors) | 4 | 14:1:Back | Broken Wire (# Broken Subconductors) | 4 | 6:1:Back | Broken Wire (# Broken Subconductors) | 4 | 16:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RW | 1 | T | B | 5 | 6 | [6 empty] | NA+ |  | RW0001_8+TB56 NA+ | RW0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 5:1:Back | Broken Wire (# Broken Subconductors) | 4 | 15:1:Back | Broken Wire (# Broken Subconductors) | 4 | 6:1:Back | Broken Wire (# Broken Subconductors) | 4 | 16:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | EW8 | - | - | RW | 1 | T | B | 6 | 8 | [6 empty] | NA+ |  | RW0001_8+TB68 NA+ | RW0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 6:1:Back | Broken Wire (# Broken Subconductors) | 4 | 16:1:Back | Broken Wire (# Broken Subconductors) | 4 | 8:1:Back | Broken Wire (# Broken Subconductors) | 4 | 18:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RW | 1 | T | A | 1 | 2 | [6 empty] | NA- |  | RW0001_8+TA12 NA- | RW0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 1:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 11:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 2:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 12:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RW | 1 | T | A | 2 | 3 | [6 empty] | NA- |  | RW0001_8+TA23 NA- | RW0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 2:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 12:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 3:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 13:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RW | 1 | T | A | 1 | 3 | [6 empty] | NA- |  | RW0001_8+TA13 NA- | RW0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 1:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 11:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 3:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 13:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | EW7 | - | - | RW | 1 | T | A | 3 | 7 | [6 empty] | NA- |  | RW0001_8+TA37 NA- | RW0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 3:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 13:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 7:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 17:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RW | 1 | T | A | 4 | 5 | [6 empty] | NA- |  | RW0001_8+TA45 NA- | RW0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 4:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 14:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 5:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 15:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RW | 1 | T | A | 4 | 6 | [6 empty] | NA- |  | RW0001_8+TA46 NA- | RW0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 4:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 14:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 6:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 16:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RW | 1 | T | A | 5 | 6 | [6 empty] | NA- |  | RW0001_8+TA56 NA- | RW0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 5:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 15:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 6:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 16:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | EW8 | - | - | RW | 1 | T | A | 6 | 8 | [6 empty] | NA- |  | RW0001_8+TA68 NA- | RW0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 6:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 16:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 8:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 18:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RW | 1 | T | B | 1 | 2 | [6 empty] | NA- |  | RW0001_8+TB12 NA- | RW0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 1:1:Back | Broken Wire (# Broken Subconductors) | 4 | 11:1:Back | Broken Wire (# Broken Subconductors) | 4 | 2:1:Back | Broken Wire (# Broken Subconductors) | 4 | 12:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RW | 1 | T | B | 2 | 3 | [6 empty] | NA- |  | RW0001_8+TB23 NA- | RW0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 2:1:Back | Broken Wire (# Broken Subconductors) | 4 | 12:1:Back | Broken Wire (# Broken Subconductors) | 4 | 3:1:Back | Broken Wire (# Broken Subconductors) | 4 | 13:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RW | 1 | T | B | 1 | 3 | [6 empty] | NA- |  | RW0001_8+TB13 NA- | RW0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 1:1:Back | Broken Wire (# Broken Subconductors) | 4 | 11:1:Back | Broken Wire (# Broken Subconductors) | 4 | 3:1:Back | Broken Wire (# Broken Subconductors) | 4 | 13:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | EW7 | - | - | RW | 1 | T | B | 3 | 7 | [6 empty] | NA- |  | RW0001_8+TB37 NA- | RW0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 3:1:Back | Broken Wire (# Broken Subconductors) | 4 | 13:1:Back | Broken Wire (# Broken Subconductors) | 4 | 7:1:Back | Broken Wire (# Broken Subconductors) | 4 | 17:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RW | 1 | T | B | 4 | 5 | [6 empty] | NA- |  | RW0001_8+TB45 NA- | RW0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 4:1:Back | Broken Wire (# Broken Subconductors) | 4 | 14:1:Back | Broken Wire (# Broken Subconductors) | 4 | 5:1:Back | Broken Wire (# Broken Subconductors) | 4 | 15:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RW | 1 | T | B | 4 | 6 | [6 empty] | NA- |  | RW0001_8+TB46 NA- | RW0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 4:1:Back | Broken Wire (# Broken Subconductors) | 4 | 14:1:Back | Broken Wire (# Broken Subconductors) | 4 | 6:1:Back | Broken Wire (# Broken Subconductors) | 4 | 16:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RW | 1 | T | B | 5 | 6 | [6 empty] | NA- |  | RW0001_8+TB56 NA- | RW0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 5:1:Back | Broken Wire (# Broken Subconductors) | 4 | 15:1:Back | Broken Wire (# Broken Subconductors) | 4 | 6:1:Back | Broken Wire (# Broken Subconductors) | 4 | 16:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | EW8 | - | - | RW | 1 | T | B | 6 | 8 | [6 empty] | NA- |  | RW0001_8+TB68 NA- | RW0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 6:1:Back | Broken Wire (# Broken Subconductors) | 4 | 16:1:Back | Broken Wire (# Broken Subconductors) | 4 | 8:1:Back | Broken Wire (# Broken Subconductors) | 4 | 18:1:Back | Broken Wire (# Broken Subconductors) | 4
- | - | - | - | - | - | - | - | SECURITY LOADING - FAILURE CONTAINMENT - SNOW
1 | ALL | DC/SC | FC | ALL | - | - | - | RS | 1 | L | A | [8 empty] | NA+ |  | RS0001_8+LA NA+ | RS0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | Ahead Spans | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | ALL | - | - | - | RS | 1 | L | B | [8 empty] | NA+ |  | RS0001_8+LB NA+ | RS0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | Back Spans | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | ALL | - | - | - | RS | 1 | L | A | [8 empty] | NA- |  | RS0001_8+LA NA- | RS0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | Ahead Spans | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | ALL | - | - | - | RS | 1 | L | B | [8 empty] | NA- |  | RS0001_8+LB NA- | RS0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | Back Spans | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RS | 1 | T | A | 1 | [7 empty] | NA+ |  | RS0001_8+TA1 NA+ | RS0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 1:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 11:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RS | 1 | T | B | 1 | [7 empty] | NA+ |  | RS0001_8+TB1 NA+ | RS0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 1:1:Back | Broken Wire (# Broken Subconductors) | 4 | 11:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RS | 1 | T | A | 2 | [7 empty] | NA+ |  | RS0001_8+TA2 NA+ | RS0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 2:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 12:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RS | 1 | T | B | 2 | [7 empty] | NA+ |  | RS0001_8+TB2 NA+ | RS0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 2:1:Back | Broken Wire (# Broken Subconductors) | 4 | 12:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RS | 1 | T | A | 3 | [7 empty] | NA+ |  | RS0001_8+TA3 NA+ | RS0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 3:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 13:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RS | 1 | T | B | 3 | [7 empty] | NA+ |  | RS0001_8+TB3 NA+ | RS0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 3:1:Back | Broken Wire (# Broken Subconductors) | 4 | 13:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RS | 1 | T | A | 4 | [7 empty] | NA+ |  | RS0001_8+TA4 NA+ | RS0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 4:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 14:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RS | 1 | T | B | 4 | [7 empty] | NA+ |  | RS0001_8+TB4 NA+ | RS0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 4:1:Back | Broken Wire (# Broken Subconductors) | 4 | 14:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RS | 1 | T | A | 5 | [7 empty] | NA+ |  | RS0001_8+TA5 NA+ | RS0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 5:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 15:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RS | 1 | T | B | 5 | [7 empty] | NA+ |  | RS0001_8+TB5 NA+ | RS0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 5:1:Back | Broken Wire (# Broken Subconductors) | 4 | 15:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RS | 1 | T | A | 6 | [7 empty] | NA+ |  | RS0001_8+TA6 NA+ | RS0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 6:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 16:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RS | 1 | T | B | 6 | [7 empty] | NA+ |  | RS0001_8+TB6 NA+ | RS0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 6:1:Back | Broken Wire (# Broken Subconductors) | 4 | 16:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | EW7 | - | - | RS | 1 | T | A | 7 | [7 empty] | NA+ |  | RS0001_8+TA7 NA+ | RS0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 7:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 17:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | EW7 | - | - | RS | 1 | T | B | 7 | [7 empty] | NA+ |  | RS0001_8+TB7 NA+ | RS0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 7:1:Back | Broken Wire (# Broken Subconductors) | 4 | 17:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | EW8 | - | - | RS | 1 | T | A | 8 | [7 empty] | NA+ |  | RS0001_8+TA8 NA+ | RS0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 8:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 18:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | EW8 | - | - | RS | 1 | T | B | 8 | [7 empty] | NA+ |  | RS0001_8+TB8 NA+ | RS0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 8:1:Back | Broken Wire (# Broken Subconductors) | 4 | 18:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RS | 1 | T | A | 1 | [7 empty] | NA- |  | RS0001_8+TA1 NA- | RS0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 1:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 11:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RS | 1 | T | B | 1 | [7 empty] | NA- |  | RS0001_8+TB1 NA- | RS0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 1:1:Back | Broken Wire (# Broken Subconductors) | 4 | 11:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RS | 1 | T | A | 2 | [7 empty] | NA- |  | RS0001_8+TA2 NA- | RS0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 2:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 12:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RS | 1 | T | B | 2 | [7 empty] | NA- |  | RS0001_8+TB2 NA- | RS0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 2:1:Back | Broken Wire (# Broken Subconductors) | 4 | 12:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RS | 1 | T | A | 3 | [7 empty] | NA- |  | RS0001_8+TA3 NA- | RS0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 3:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 13:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RS | 1 | T | B | 3 | [7 empty] | NA- |  | RS0001_8+TB3 NA- | RS0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 3:1:Back | Broken Wire (# Broken Subconductors) | 4 | 13:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RS | 1 | T | A | 4 | [7 empty] | NA- |  | RS0001_8+TA4 NA- | RS0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 4:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 14:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RS | 1 | T | B | 4 | [7 empty] | NA- |  | RS0001_8+TB4 NA- | RS0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 4:1:Back | Broken Wire (# Broken Subconductors) | 4 | 14:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RS | 1 | T | A | 5 | [7 empty] | NA- |  | RS0001_8+TA5 NA- | RS0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 5:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 15:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RS | 1 | T | B | 5 | [7 empty] | NA- |  | RS0001_8+TB5 NA- | RS0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 5:1:Back | Broken Wire (# Broken Subconductors) | 4 | 15:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RS | 1 | T | A | 6 | [7 empty] | NA- |  | RS0001_8+TA6 NA- | RS0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 6:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 16:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | - | RS | 1 | T | B | 6 | [7 empty] | NA- |  | RS0001_8+TB6 NA- | RS0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 6:1:Back | Broken Wire (# Broken Subconductors) | 4 | 16:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | EW7 | - | - | RS | 1 | T | A | 7 | [7 empty] | NA- |  | RS0001_8+TA7 NA- | RS0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 7:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 17:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | EW7 | - | - | RS | 1 | T | B | 7 | [7 empty] | NA- |  | RS0001_8+TB7 NA- | RS0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 7:1:Back | Broken Wire (# Broken Subconductors) | 4 | 17:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | EW8 | - | - | RS | 1 | T | A | 8 | [7 empty] | NA- |  | RS0001_8+TA8 NA- | RS0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 8:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 18:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | EW8 | - | - | RS | 1 | T | B | 8 | [7 empty] | NA- |  | RS0001_8+TB8 NA- | RS0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 8:1:Back | Broken Wire (# Broken Subconductors) | 4 | 18:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RS | 1 | T | A | 1 | 2 | [6 empty] | NA+ |  | RS0001_8+TA12 NA+ | RS0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 1:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 11:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 2:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 12:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RS | 1 | T | A | 2 | 3 | [6 empty] | NA+ |  | RS0001_8+TA23 NA+ | RS0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 2:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 12:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 3:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 13:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RS | 1 | T | A | 1 | 3 | [6 empty] | NA+ |  | RS0001_8+TA13 NA+ | RS0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 1:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 11:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 3:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 13:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | EW7 | - | - | RS | 1 | T | A | 3 | 7 | [6 empty] | NA+ |  | RS0001_8+TA37 NA+ | RS0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 3:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 13:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 7:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 17:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RS | 1 | T | A | 4 | 5 | [6 empty] | NA+ |  | RS0001_8+TA45 NA+ | RS0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 4:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 14:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 5:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 15:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RS | 1 | T | A | 4 | 6 | [6 empty] | NA+ |  | RS0001_8+TA46 NA+ | RS0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 4:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 14:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 6:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 16:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RS | 1 | T | A | 5 | 6 | [6 empty] | NA+ |  | RS0001_8+TA56 NA+ | RS0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 5:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 15:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 6:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 16:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | EW8 | - | - | RS | 1 | T | A | 6 | 8 | [6 empty] | NA+ |  | RS0001_8+TA68 NA+ | RS0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 6:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 16:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 8:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 18:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RS | 1 | T | B | 1 | 2 | [6 empty] | NA+ |  | RS0001_8+TB12 NA+ | RS0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 1:1:Back | Broken Wire (# Broken Subconductors) | 4 | 11:1:Back | Broken Wire (# Broken Subconductors) | 4 | 2:1:Back | Broken Wire (# Broken Subconductors) | 4 | 12:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RS | 1 | T | B | 2 | 3 | [6 empty] | NA+ |  | RS0001_8+TB23 NA+ | RS0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 2:1:Back | Broken Wire (# Broken Subconductors) | 4 | 12:1:Back | Broken Wire (# Broken Subconductors) | 4 | 3:1:Back | Broken Wire (# Broken Subconductors) | 4 | 13:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RS | 1 | T | B | 1 | 3 | [6 empty] | NA+ |  | RS0001_8+TB13 NA+ | RS0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 1:1:Back | Broken Wire (# Broken Subconductors) | 4 | 11:1:Back | Broken Wire (# Broken Subconductors) | 4 | 3:1:Back | Broken Wire (# Broken Subconductors) | 4 | 13:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | EW7 | - | - | RS | 1 | T | B | 3 | 7 | [6 empty] | NA+ |  | RS0001_8+TB37 NA+ | RS0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 3:1:Back | Broken Wire (# Broken Subconductors) | 4 | 13:1:Back | Broken Wire (# Broken Subconductors) | 4 | 7:1:Back | Broken Wire (# Broken Subconductors) | 4 | 17:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RS | 1 | T | B | 4 | 5 | [6 empty] | NA+ |  | RS0001_8+TB45 NA+ | RS0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 4:1:Back | Broken Wire (# Broken Subconductors) | 4 | 14:1:Back | Broken Wire (# Broken Subconductors) | 4 | 5:1:Back | Broken Wire (# Broken Subconductors) | 4 | 15:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RS | 1 | T | B | 4 | 6 | [6 empty] | NA+ |  | RS0001_8+TB46 NA+ | RS0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 4:1:Back | Broken Wire (# Broken Subconductors) | 4 | 14:1:Back | Broken Wire (# Broken Subconductors) | 4 | 6:1:Back | Broken Wire (# Broken Subconductors) | 4 | 16:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RS | 1 | T | B | 5 | 6 | [6 empty] | NA+ |  | RS0001_8+TB56 NA+ | RS0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 5:1:Back | Broken Wire (# Broken Subconductors) | 4 | 15:1:Back | Broken Wire (# Broken Subconductors) | 4 | 6:1:Back | Broken Wire (# Broken Subconductors) | 4 | 16:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | EW8 | - | - | RS | 1 | T | B | 6 | 8 | [6 empty] | NA+ |  | RS0001_8+TB68 NA+ | RS0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 6:1:Back | Broken Wire (# Broken Subconductors) | 4 | 16:1:Back | Broken Wire (# Broken Subconductors) | 4 | 8:1:Back | Broken Wire (# Broken Subconductors) | 4 | 18:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RS | 1 | T | A | 1 | 2 | [6 empty] | NA- |  | RS0001_8+TA12 NA- | RS0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 1:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 11:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 2:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 12:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RS | 1 | T | A | 2 | 3 | [6 empty] | NA- |  | RS0001_8+TA23 NA- | RS0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 2:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 12:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 3:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 13:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RS | 1 | T | A | 1 | 3 | [6 empty] | NA- |  | RS0001_8+TA13 NA- | RS0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 1:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 11:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 3:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 13:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | EW7 | - | - | RS | 1 | T | A | 3 | 7 | [6 empty] | NA- |  | RS0001_8+TA37 NA- | RS0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 3:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 13:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 7:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 17:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RS | 1 | T | A | 4 | 5 | [6 empty] | NA- |  | RS0001_8+TA45 NA- | RS0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 4:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 14:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 5:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 15:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RS | 1 | T | A | 4 | 6 | [6 empty] | NA- |  | RS0001_8+TA46 NA- | RS0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 4:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 14:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 6:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 16:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RS | 1 | T | A | 5 | 6 | [6 empty] | NA- |  | RS0001_8+TA56 NA- | RS0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 5:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 15:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 6:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 16:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | EW8 | - | - | RS | 1 | T | A | 6 | 8 | [6 empty] | NA- |  | RS0001_8+TA68 NA- | RS0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 6:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 16:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 8:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 18:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RS | 1 | T | B | 1 | 2 | [6 empty] | NA- |  | RS0001_8+TB12 NA- | RS0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 1:1:Back | Broken Wire (# Broken Subconductors) | 4 | 11:1:Back | Broken Wire (# Broken Subconductors) | 4 | 2:1:Back | Broken Wire (# Broken Subconductors) | 4 | 12:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RS | 1 | T | B | 2 | 3 | [6 empty] | NA- |  | RS0001_8+TB23 NA- | RS0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 2:1:Back | Broken Wire (# Broken Subconductors) | 4 | 12:1:Back | Broken Wire (# Broken Subconductors) | 4 | 3:1:Back | Broken Wire (# Broken Subconductors) | 4 | 13:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RS | 1 | T | B | 1 | 3 | [6 empty] | NA- |  | RS0001_8+TB13 NA- | RS0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 1:1:Back | Broken Wire (# Broken Subconductors) | 4 | 11:1:Back | Broken Wire (# Broken Subconductors) | 4 | 3:1:Back | Broken Wire (# Broken Subconductors) | 4 | 13:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | EW7 | - | - | RS | 1 | T | B | 3 | 7 | [6 empty] | NA- |  | RS0001_8+TB37 NA- | RS0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 3:1:Back | Broken Wire (# Broken Subconductors) | 4 | 13:1:Back | Broken Wire (# Broken Subconductors) | 4 | 7:1:Back | Broken Wire (# Broken Subconductors) | 4 | 17:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RS | 1 | T | B | 4 | 5 | [6 empty] | NA- |  | RS0001_8+TB45 NA- | RS0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 4:1:Back | Broken Wire (# Broken Subconductors) | 4 | 14:1:Back | Broken Wire (# Broken Subconductors) | 4 | 5:1:Back | Broken Wire (# Broken Subconductors) | 4 | 15:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RS | 1 | T | B | 4 | 6 | [6 empty] | NA- |  | RS0001_8+TB46 NA- | RS0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 4:1:Back | Broken Wire (# Broken Subconductors) | 4 | 14:1:Back | Broken Wire (# Broken Subconductors) | 4 | 6:1:Back | Broken Wire (# Broken Subconductors) | 4 | 16:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | - | RS | 1 | T | B | 5 | 6 | [6 empty] | NA- |  | RS0001_8+TB56 NA- | RS0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 5:1:Back | Broken Wire (# Broken Subconductors) | 4 | 15:1:Back | Broken Wire (# Broken Subconductors) | 4 | 6:1:Back | Broken Wire (# Broken Subconductors) | 4 | 16:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | EW8 | - | - | RS | 1 | T | B | 6 | 8 | [6 empty] | NA- |  | RS0001_8+TB68 NA- | RS0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop' | No Limit |  | Yes | 6:1:Back | Broken Wire (# Broken Subconductors) | 4 | 16:1:Back | Broken Wire (# Broken Subconductors) | 4 | 8:1:Back | Broken Wire (# Broken Subconductors) | 4 | 18:1:Back | Broken Wire (# Broken Subconductors) | 4
- | - | - | - | - | - | - | - | SECURITY LOADING - FAILURE CONTAINMENT - THICK ICE
1 | ALL | DC/SC | FC | ALL | - | - | YES | RI | 1 | L | A | [8 empty] | NA+ |  | RI0001_8+LA NA+ | RI0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | Ahead Spans | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | ALL | - | - | YES | RI | 1 | L | B | [8 empty] | NA+ |  | RI0001_8+LB NA+ | RI0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | Back Spans | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | ALL | - | - | YES | RI | 1 | L | A | [8 empty] | NA- |  | RI0001_8+LA NA- | RI0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | Ahead Spans | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | ALL | - | - | YES | RI | 1 | L | B | [8 empty] | NA- |  | RI0001_8+LB NA- | RI0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | Back Spans | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | YES | RI | 1 | T | A | 1 | [7 empty] | NA+ |  | RI0001_8+TA1 NA+ | RI0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 1:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 11:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | YES | RI | 1 | T | B | 1 | [7 empty] | NA+ |  | RI0001_8+TB1 NA+ | RI0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 1:1:Back | Broken Wire (# Broken Subconductors) | 4 | 11:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | YES | RI | 1 | T | A | 2 | [7 empty] | NA+ |  | RI0001_8+TA2 NA+ | RI0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 2:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 12:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | YES | RI | 1 | T | B | 2 | [7 empty] | NA+ |  | RI0001_8+TB2 NA+ | RI0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 2:1:Back | Broken Wire (# Broken Subconductors) | 4 | 12:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | YES | RI | 1 | T | A | 3 | [7 empty] | NA+ |  | RI0001_8+TA3 NA+ | RI0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 3:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 13:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | YES | RI | 1 | T | B | 3 | [7 empty] | NA+ |  | RI0001_8+TB3 NA+ | RI0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 3:1:Back | Broken Wire (# Broken Subconductors) | 4 | 13:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | YES | RI | 1 | T | A | 7 | [7 empty] | NA+ |  | RI0001_8+TA7 NA+ | RI0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 7:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 17:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | YES | RI | 1 | T | B | 7 | [7 empty] | NA+ |  | RI0001_8+TB7 NA+ | RI0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 7:1:Back | Broken Wire (# Broken Subconductors) | 4 | 17:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | YES | RI | 1 | T | A | 8 | [7 empty] | NA+ |  | RI0001_8+TA8 NA+ | RI0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 8:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 18:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | YES | RI | 1 | T | B | 8 | [7 empty] | NA+ |  | RI0001_8+TB8 NA+ | RI0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 8:1:Back | Broken Wire (# Broken Subconductors) | 4 | 18:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | YES | RI | 1 | T | A | 1 | [7 empty] | NA- |  | RI0001_8+TA1 NA- | RI0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 1:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 11:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | YES | RI | 1 | T | B | 1 | [7 empty] | NA- |  | RI0001_8+TB1 NA- | RI0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 1:1:Back | Broken Wire (# Broken Subconductors) | 4 | 11:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | YES | RI | 1 | T | A | 2 | [7 empty] | NA- |  | RI0001_8+TA2 NA- | RI0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 2:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 12:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | YES | RI | 1 | T | B | 2 | [7 empty] | NA- |  | RI0001_8+TB2 NA- | RI0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 2:1:Back | Broken Wire (# Broken Subconductors) | 4 | 12:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | YES | RI | 1 | T | A | 3 | [7 empty] | NA- |  | RI0001_8+TA3 NA- | RI0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 3:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 13:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | YES | RI | 1 | T | B | 3 | [7 empty] | NA- |  | RI0001_8+TB3 NA- | RI0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 3:1:Back | Broken Wire (# Broken Subconductors) | 4 | 13:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | YES | RI | 1 | T | A | 7 | [7 empty] | NA- |  | RI0001_8+TA7 NA- | RI0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 7:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 17:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | YES | RI | 1 | T | B | 7 | [7 empty] | NA- |  | RI0001_8+TB7 NA- | RI0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 7:1:Back | Broken Wire (# Broken Subconductors) | 4 | 17:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | YES | RI | 1 | T | A | 8 | [7 empty] | NA- |  | RI0001_8+TA8 NA- | RI0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 8:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 18:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC/SC | FC | 1 | - | - | YES | RI | 1 | T | B | 8 | [7 empty] | NA- |  | RI0001_8+TB8 NA- | RI0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | 8:1:Back | Broken Wire (# Broken Subconductors) | 4 | 18:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | YES | RI | 1 | T | A | 1 | 2 | [6 empty] | NA+ |  | RI0001_8+TA12 NA+ | RI0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | 1:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 11:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 2:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 12:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | YES | RI | 1 | T | A | 2 | 3 | [6 empty] | NA+ |  | RI0001_8+TA23 NA+ | RI0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | 2:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 12:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 3:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 13:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | YES | RI | 1 | T | A | 1 | 3 | [6 empty] | NA+ |  | RI0001_8+TA13 NA+ | RI0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | 1:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 11:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 3:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 13:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | EW7 | - | YES | RI | 1 | T | A | 3 | 7 | [6 empty] | NA+ |  | RI0001_8+TA37 NA+ | RI0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | 3:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 13:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 7:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 17:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | YES | RI | 1 | T | A | 4 | 5 | [6 empty] | NA+ |  | RI0001_8+TA45 NA+ | RI0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | 4:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 14:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 5:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 15:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | YES | RI | 1 | T | A | 4 | 6 | [6 empty] | NA+ |  | RI0001_8+TA46 NA+ | RI0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | 4:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 14:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 6:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 16:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | YES | RI | 1 | T | A | 5 | 6 | [6 empty] | NA+ |  | RI0001_8+TA56 NA+ | RI0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | 5:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 15:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 6:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 16:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | EW8 | - | YES | RI | 1 | T | A | 6 | 8 | [6 empty] | NA+ |  | RI0001_8+TA68 NA+ | RI0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | 6:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 16:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 8:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 18:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | YES | RI | 1 | T | B | 1 | 2 | [6 empty] | NA+ |  | RI0001_8+TB12 NA+ | RI0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | 1:1:Back | Broken Wire (# Broken Subconductors) | 4 | 11:1:Back | Broken Wire (# Broken Subconductors) | 4 | 2:1:Back | Broken Wire (# Broken Subconductors) | 4 | 12:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | YES | RI | 1 | T | B | 2 | 3 | [6 empty] | NA+ |  | RI0001_8+TB23 NA+ | RI0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | 2:1:Back | Broken Wire (# Broken Subconductors) | 4 | 12:1:Back | Broken Wire (# Broken Subconductors) | 4 | 3:1:Back | Broken Wire (# Broken Subconductors) | 4 | 13:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | YES | RI | 1 | T | B | 1 | 3 | [6 empty] | NA+ |  | RI0001_8+TB13 NA+ | RI0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | 1:1:Back | Broken Wire (# Broken Subconductors) | 4 | 11:1:Back | Broken Wire (# Broken Subconductors) | 4 | 3:1:Back | Broken Wire (# Broken Subconductors) | 4 | 13:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | EW7 | - | YES | RI | 1 | T | B | 3 | 7 | [6 empty] | NA+ |  | RI0001_8+TB37 NA+ | RI0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | 3:1:Back | Broken Wire (# Broken Subconductors) | 4 | 13:1:Back | Broken Wire (# Broken Subconductors) | 4 | 7:1:Back | Broken Wire (# Broken Subconductors) | 4 | 17:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | YES | RI | 1 | T | B | 4 | 5 | [6 empty] | NA+ |  | RI0001_8+TB45 NA+ | RI0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | 4:1:Back | Broken Wire (# Broken Subconductors) | 4 | 14:1:Back | Broken Wire (# Broken Subconductors) | 4 | 5:1:Back | Broken Wire (# Broken Subconductors) | 4 | 15:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | YES | RI | 1 | T | B | 4 | 6 | [6 empty] | NA+ |  | RI0001_8+TB46 NA+ | RI0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | 4:1:Back | Broken Wire (# Broken Subconductors) | 4 | 14:1:Back | Broken Wire (# Broken Subconductors) | 4 | 6:1:Back | Broken Wire (# Broken Subconductors) | 4 | 16:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | YES | RI | 1 | T | B | 5 | 6 | [6 empty] | NA+ |  | RI0001_8+TB56 NA+ | RI0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | 5:1:Back | Broken Wire (# Broken Subconductors) | 4 | 15:1:Back | Broken Wire (# Broken Subconductors) | 4 | 6:1:Back | Broken Wire (# Broken Subconductors) | 4 | 16:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | EW8 | - | YES | RI | 1 | T | B | 6 | 8 | [6 empty] | NA+ |  | RI0001_8+TB68 NA+ | RI0001_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | 6:1:Back | Broken Wire (# Broken Subconductors) | 4 | 16:1:Back | Broken Wire (# Broken Subconductors) | 4 | 8:1:Back | Broken Wire (# Broken Subconductors) | 4 | 18:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | YES | RI | 1 | T | A | 1 | 2 | [6 empty] | NA- |  | RI0001_8+TA12 NA- | RI0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | 1:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 11:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 2:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 12:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | YES | RI | 1 | T | A | 2 | 3 | [6 empty] | NA- |  | RI0001_8+TA23 NA- | RI0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | 2:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 12:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 3:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 13:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | YES | RI | 1 | T | A | 1 | 3 | [6 empty] | NA- |  | RI0001_8+TA13 NA- | RI0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | 1:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 11:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 3:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 13:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | EW7 | - | YES | RI | 1 | T | A | 3 | 7 | [6 empty] | NA- |  | RI0001_8+TA37 NA- | RI0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | 3:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 13:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 7:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 17:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | YES | RI | 1 | T | A | 4 | 5 | [6 empty] | NA- |  | RI0001_8+TA45 NA- | RI0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | 4:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 14:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 5:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 15:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | YES | RI | 1 | T | A | 4 | 6 | [6 empty] | NA- |  | RI0001_8+TA46 NA- | RI0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | 4:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 14:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 6:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 16:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | YES | RI | 1 | T | A | 5 | 6 | [6 empty] | NA- |  | RI0001_8+TA56 NA- | RI0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | 5:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 15:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 6:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 16:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | EW8 | - | YES | RI | 1 | T | A | 6 | 8 | [6 empty] | NA- |  | RI0001_8+TA68 NA- | RI0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | 6:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 16:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 8:1:Ahead | Broken Wire (# Broken Subconductors) | 4 | 18:1:Ahead | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | YES | RI | 1 | T | B | 1 | 2 | [6 empty] | NA- |  | RI0001_8+TB12 NA- | RI0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | 1:1:Back | Broken Wire (# Broken Subconductors) | 4 | 11:1:Back | Broken Wire (# Broken Subconductors) | 4 | 2:1:Back | Broken Wire (# Broken Subconductors) | 4 | 12:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | YES | RI | 1 | T | B | 2 | 3 | [6 empty] | NA- |  | RI0001_8+TB23 NA- | RI0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | 2:1:Back | Broken Wire (# Broken Subconductors) | 4 | 12:1:Back | Broken Wire (# Broken Subconductors) | 4 | 3:1:Back | Broken Wire (# Broken Subconductors) | 4 | 13:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | YES | RI | 1 | T | B | 1 | 3 | [6 empty] | NA- |  | RI0001_8+TB13 NA- | RI0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | 1:1:Back | Broken Wire (# Broken Subconductors) | 4 | 11:1:Back | Broken Wire (# Broken Subconductors) | 4 | 3:1:Back | Broken Wire (# Broken Subconductors) | 4 | 13:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | EW7 | - | YES | RI | 1 | T | B | 3 | 7 | [6 empty] | NA- |  | RI0001_8+TB37 NA- | RI0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | 3:1:Back | Broken Wire (# Broken Subconductors) | 4 | 13:1:Back | Broken Wire (# Broken Subconductors) | 4 | 7:1:Back | Broken Wire (# Broken Subconductors) | 4 | 17:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | YES | RI | 1 | T | B | 4 | 5 | [6 empty] | NA- |  | RI0001_8+TB45 NA- | RI0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | 4:1:Back | Broken Wire (# Broken Subconductors) | 4 | 14:1:Back | Broken Wire (# Broken Subconductors) | 4 | 5:1:Back | Broken Wire (# Broken Subconductors) | 4 | 15:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | YES | RI | 1 | T | B | 4 | 6 | [6 empty] | NA- |  | RI0001_8+TB46 NA- | RI0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | 4:1:Back | Broken Wire (# Broken Subconductors) | 4 | 14:1:Back | Broken Wire (# Broken Subconductors) | 4 | 6:1:Back | Broken Wire (# Broken Subconductors) | 4 | 16:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | - | - | YES | RI | 1 | T | B | 5 | 6 | [6 empty] | NA- |  | RI0001_8+TB56 NA- | RI0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | 5:1:Back | Broken Wire (# Broken Subconductors) | 4 | 15:1:Back | Broken Wire (# Broken Subconductors) | 4 | 6:1:Back | Broken Wire (# Broken Subconductors) | 4 | 16:1:Back | Broken Wire (# Broken Subconductors) | 4
1 | ALL | DC | FC | 2 | EW8 | - | YES | RI | 1 | T | B | 6 | 8 | [6 empty] | NA- |  | RI0001_8+TB68 NA- | RI0001_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'Stop GL Max 800m' | No Limit |  | Yes | 6:1:Back | Broken Wire (# Broken Subconductors) | 4 | 16:1:Back | Broken Wire (# Broken Subconductors) | 4 | 8:1:Back | Broken Wire (# Broken Subconductors) | 4 | 18:1:Back | Broken Wire (# Broken Subconductors) | 4
- | - | - | - | - | - | - | - | DEFAULT CONSTRUCTION & MAINTENANCE LOADING CONDITIONS - NOTE THESE ARE "BACKGROUND" LOADING CRITERIA - THEY DO NOT REFLECT THE ACTUAL LOADING TO BE APPLIED TO THE STRUCTURE
1 | ALL | DC/SC | CM | - | - | - | - | CM | 1 | E | [9 empty] | NA+ |  | CM1+E NA+ | CM1 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | No
1 | ALL | DC/SC | CM | - | - | - | - | CM | 1 | D | A | [8 empty] | NA+ |  | CM1+DA NA+ | CM1 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 0
1 | ALL | DC/SC | CM | - | - | - | - | CM | 1 | D | B | [8 empty] | NA+ |  | CM1+DB NA+ | CM1 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 0
1 | ALL | DC/SC | CM | - | - | - | - | CM | 1 | E | [9 empty] | NA- |  | CM1+E NA- | CM1 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | No
1 | ALL | DC/SC | CM | - | - | - | - | CM | 1 | D | A | [8 empty] | NA- |  | CM1+DA NA- | CM1 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 0
1 | ALL | DC/SC | CM | - | - | - | - | CM | 1 | D | B | [8 empty] | NA- |  | CM1+DB NA- | CM1 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 0
1 | ALL | DC/SC | CM | - | - | YES | - | CM | 2 | E | [9 empty] | NA+ |  | CM2_A+E NA+ | CM2_A | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | No
1 | ALL | DC/SC | CM | - | - | YES | - | CM | 2 | D | A | [8 empty] | NA+ |  | CM2_A+DA NA+ | CM2_A | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | CM | - | - | YES | - | CM | 2 | D | B | [8 empty] | NA+ |  | CM2_A+DB NA+ | CM2_A | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | CM | - | - | YES | - | CM | 2 | E | [9 empty] | NA- |  | CM2_A+E NA- | CM2_A | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | No
1 | ALL | DC/SC | CM | - | - | YES | - | CM | 2 | D | A | [8 empty] | NA- |  | CM2_A+DA NA- | CM2_A | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | CM | - | - | YES | - | CM | 2 | D | B | [8 empty] | NA- |  | CM2_A+DB NA- | CM2_A | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | CM | - | - | - | YES | CM | 2S | E | [9 empty] | NA+ |  | CM2S_8+E NA+ | CM2S_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | CM | - | - | - | YES | CM | 2S | E | [9 empty] | NA- |  | CM2S_8+E NA- | CM2S_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | CM | - | - | - | YES | CM | 2S | D | A | [8 empty] | NA+ |  | CM2S_8+DA NA+ | CM2S_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Ice | 40 | Back Spans | % Wire Ice | 70
1 | ALL | DC/SC | CM | - | - | - | YES | CM | 2S | D | A | [8 empty] | NA- |  | CM2S_8+DA NA- | CM2S_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Ice | 40 | Back Spans | % Wire Ice | 70
1 | ALL | DC/SC | CM | - | - | - | YES | CM | 2S | D | B | [8 empty] | NA+ |  | CM2S_8+DB NA+ | CM2S_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Ice | 40 | Ahead Spans | % Wire Ice | 70
1 | ALL | DC/SC | CM | - | - | - | YES | CM | 2S | D | B | [8 empty] | NA- |  | CM2S_8+DB NA- | CM2S_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Ice | 40 | Ahead Spans | % Wire Ice | 70
1 | ALL | DC/SC | CM | - | - | - | YES | CM | 2I | E | [9 empty] | NA+ |  | CM2I_8+E NA+ | CM2I_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | CM | - | - | - | YES | CM | 2I | E | [9 empty] | NA- |  | CM2I_8+E NA- | CM2I_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | CM | - | - | - | YES | CM | 2I | D | A | [8 empty] | NA+ |  | CM2I_8+DA NA+ | CM2I_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Ice | 40 | Back Spans | % Wire Ice | 70
1 | ALL | DC/SC | CM | - | - | - | YES | CM | 2I | D | A | [8 empty] | NA- |  | CM2I_8+DA NA- | CM2I_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Ice | 40 | Back Spans | % Wire Ice | 70
1 | ALL | DC/SC | CM | - | - | - | YES | CM | 2I | D | B | [8 empty] | NA+ |  | CM2I_8+DB NA+ | CM2I_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Ice | 40 | Ahead Spans | % Wire Ice | 70
1 | ALL | DC/SC | CM | - | - | - | YES | CM | 2I | D | B | [8 empty] | NA- |  | CM2I_8+DB NA- | CM2I_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Ice | 40 | Ahead Spans | % Wire Ice | 70
1 | ALL | DC/SC | CM | - | - | YES | YES | CM | 3 | E | [9 empty] | NA+ |  | CM3_A8+E NA+ | CM3_A8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | CM | - | - | YES | YES | CM | 3 | D | A | [8 empty] | NA+ |  | CM3_A8+DA NA+ | CM3_A8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | CM | - | - | YES | YES | CM | 3 | D | B | [8 empty] | NA+ |  | CM3_A8+DB NA+ | CM3_A8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | CM | - | - | YES | YES | CM | 3 | E | [9 empty] | NA- |  | CM3_A8+E NA- | CM3_A8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | CM | - | - | YES | YES | CM | 3 | D | A | [8 empty] | NA- |  | CM3_A8+DA NA- | CM3_A8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | CM | - | - | YES | YES | CM | 3 | D | B | [8 empty] | NA- |  | CM3_A8+DB NA- | CM3_A8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Wind Pressure | 75
1 | ALL | DC/SC | CM | - | - | - | YES | CM | 3S | E | [9 empty] | NA+ |  | CM3S_8+E NA+ | CM3S_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | CM | - | - | - | YES | CM | 3S | E | [9 empty] | NA- |  | CM3S_8+E NA- | CM3S_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | CM | - | - | - | YES | CM | 3S | D | A | [8 empty] | NA+ |  | CM3S_8+DA NA+ | CM3S_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Ice | 40 | Back Spans | % Wire Ice | 70
1 | ALL | DC/SC | CM | - | - | - | YES | CM | 3S | D | A | [8 empty] | NA- |  | CM3S_8+DA NA- | CM3S_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Ice | 40 | Back Spans | % Wire Ice | 70
1 | ALL | DC/SC | CM | - | - | - | YES | CM | 3S | D | B | [8 empty] | NA+ |  | CM3S_8+DB NA+ | CM3S_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Ice | 40 | Ahead Spans | % Wire Ice | 70
1 | ALL | DC/SC | CM | - | - | - | YES | CM | 3S | D | B | [8 empty] | NA- |  | CM3S_8+DB NA- | CM3S_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Ice | 40 | Ahead Spans | % Wire Ice | 70
1 | ALL | DC/SC | CM | - | - | - | YES | CM | 3I | E | [9 empty] | NA+ |  | CM3I_8+E NA+ | CM3I_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | CM | - | - | - | YES | CM | 3I | E | [9 empty] | NA- |  | CM3I_8+E NA- | CM3I_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | CM | - | - | - | YES | CM | 3I | D | A | [8 empty] | NA+ |  | CM3I_8+DA NA+ | CM3I_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Ice | 40 | Back Spans | % Wire Ice | 70
1 | ALL | DC/SC | CM | - | - | - | YES | CM | 3I | D | A | [8 empty] | NA- |  | CM3I_8+DA NA- | CM3I_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Ahead Spans | % Wire Ice | 40 | Back Spans | % Wire Ice | 70
1 | ALL | DC/SC | CM | - | - | - | YES | CM | 3I | D | B | [8 empty] | NA+ |  | CM3I_8+DB NA+ | CM3I_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Ice | 40 | Ahead Spans | % Wire Ice | 70
1 | ALL | DC/SC | CM | - | - | - | YES | CM | 3I | D | B | [8 empty] | NA- |  | CM3I_8+DB NA- | CM3I_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | Yes | Back Spans | % Wire Ice | 40 | Ahead Spans | % Wire Ice | 70
- | - | - | - | - | - | - | - | REPLACEMENT CRITERIA LOAD CASES - APPLICABLE TO ALL STRUCTURE TYPES
1 | ALL | DC/SC | SER | - | - | YES | YES | RCW | [11 empty] | NA+ |  | RCW_A8+ NA+ | RCW_A8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | SER | - | - | YES | YES | RCW | [11 empty] | NA- |  | RCW_A8+ NA- | RCW_A8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | SER | - | - | - | YES | RCS | [11 empty] | NA+ |  | RCS_8+ NA+ | RCS_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | SER | - | - | - | YES | RCS | [11 empty] | NA- |  | RCS_8+ NA- | RCS_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | SER | - | - | - | YES | RCI | [11 empty] | NA+ |  | RCI_8+ NA+ | RCI_8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | SER | - | - | - | YES | RCI | [11 empty] | NA- |  | RCI_8+ NA- | RCI_8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | SER | - | - | YES | YES | CA6 | [11 empty] | NA+ |  | CA6_A8+ NA+ | CA6_A8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | SER | - | - | YES | YES | CA6 | [11 empty] | NA- |  | CA6_A8+ NA- | CA6_A8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | SER | - | - | YES | YES | CA1 | [11 empty] | NA+ |  | CA1_A8+ NA+ | CA1_A8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | SER | - | - | YES | YES | CA1 | [11 empty] | NA- |  | CA1_A8+ NA- | CA1_A8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | SER | - | - | YES | YES | CA0 | [11 empty] | NA+ |  | CA0_A8+ NA+ | CA0_A8 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
1 | ALL | DC/SC | SER | - | - | YES | YES | CA0 | [11 empty] | NA- |  | CA0_A8+ NA- | CA0_A8 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'GL Max 800m' | No Limit |  | No
- | - | - | - | - | - | - | - | SERVICEABILITY - CLEARANCES
1 | TWR | DC/SC | SER | - | - | - | - | EDS | [11 empty] | NA+ |  | EDS+ NA+ | EDS | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | No
1 | ALL | DC/SC | SER | - | - | - | - | EDW | [11 empty] | NA+ |  | EDW+ NA+ | EDW | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | No
1 | ALL | DC/SC | SER | - | - | - | - | EDW | [11 empty] | NA- |  | EDW+ NA- | EDW | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | No
1 | ALL | DC/SC | SER | - | - | YES | - | HWD | [11 empty] | NA+ |  | HWD_A120+ NA+ | HWD_A120 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | No
- | ALL | DC/SC | SER | - | - | - | - | HWD | [11 empty] | NA+ |  | -+ NA+ | - | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | No
- | ALL | DC/SC | SER | - | - | - | - | HWD | [11 empty] | NA+ |  | -+ NA+ | - | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | No
- | ALL | DC/SC | SER | - | - | - | - | HWD | [11 empty] | NA+ |  | -+ NA+ | - | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'All' | No Limit |  | No
1 | ALL | DC/SC | SER | - | - | YES | - | HWD | [11 empty] | NA- |  | HWD_A120+ NA- | HWD_A120 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | No
- | ALL | DC/SC | SER | - | - | - | - | HWD | [11 empty] | NA- |  | -+ NA- | - | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | No
- | ALL | DC/SC | SER | - | - | - | - | HWD | [11 empty] | NA- |  | -+ NA- | - | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | No
- | ALL | DC/SC | SER | - | - | - | - | HWD | [11 empty] | NA- |  | -+ NA- | - | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'All' | No Limit |  | No
1 | ALL | DC/SC | SER | - | - | YES | - | MWD | [11 empty] | NA+ |  | MWD_A120+ NA+ | MWD_A120 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | No
- | ALL | DC/SC | SER | - | - | - | - | MWD | [11 empty] | NA+ |  | -+ NA+ | - | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | No
- | ALL | DC/SC | SER | - | - | - | - | MWD | [11 empty] | NA+ |  | -+ NA+ | - | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | No
- | ALL | DC/SC | SER | - | - | - | - | MWD | [11 empty] | NA+ |  | -+ NA+ | - | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'All' | No Limit |  | No
1 | ALL | DC/SC | SER | - | - | YES | - | MWD | [11 empty] | NA- |  | MWD_A120+ NA- | MWD_A120 | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | No
- | ALL | DC/SC | SER | - | - | - | - | MWD | [11 empty] | NA- |  | -+ NA- | - | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | No
- | ALL | DC/SC | SER | - | - | - | - | MWD | [11 empty] | NA- |  | -+ NA- | - | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | No
- | ALL | DC/SC | SER | - | - | - | - | MWD | [11 empty] | NA- |  | -+ NA- | - | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'All' | No Limit |  | No
1 | ALL | DC/SC | SER | - | - | - | - | LLW | [11 empty] | NA+ |  | MOT_120+ NA+ | MOT_120 | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | No
- | ALL | DC/SC | SER | - | - | - | - | LLW | [11 empty] | NA+ |  | -+ NA+ | - | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | No
- | ALL | DC/SC | SER | - | - | - | - | LLW | [11 empty] | NA+ |  | -+ NA+ | - | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 'All' | No Limit |  | No
- | ALL | DC/SC | SER | - | - | - | - | LLW | [11 empty] | NA+ |  | -+ NA+ | - | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'All' | No Limit |  | No
- | - | - | - | - | - | - | - | SERVICEABILITY CASES FOR STEEL OR CONCRETE POLES DEPENDENT ON SUPPLY STANDARD (SEE INSTRUCTIONS NOTE 2.5)
- | SP | DC/SC | SER | - | - | - | - | EDW |  | SP | [9 empty] | NA+ |  | EDW+SP NA+ | EDW | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 0 | 0 | 0.4 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'PLS-POLE' | % Pole Height | 3 | No
- | SP | DC/SC | SER | - | - | - | - | EDW |  | SP | [9 empty] | NA- |  | EDW+SP NA- | EDW | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 0 | 0 | 0.4 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'PLS-POLE' | % Pole Height | 3 | No
- | SP | DC/SC | SER | - | - | YES |  | HWD |  | SP | [9 empty] | NA+ |  | HWD_A+SP NA+ | HWD_A | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 0 | 0.65 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'PLS-POLE' | % Pole Height | 5 | No
- | SP | DC/SC | SER | - | - | YES |  | HWD |  | SP | [9 empty] | NA- |  | HWD_A+SP NA- | HWD_A | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 0 | 0.65 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'PLS-POLE' | % Pole Height | 5 | No
- | XP | DC/SC | SER | - | - | - | - | EDS |  | XP | [9 empty] | NA+ |  | EDS+XP NA+ | EDS | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'PLS-POLE' | % Pole Height | 1 | No
- | XP | DC/SC | SER | - | - | - | - | EDS |  | XP | [9 empty] | NA- |  | EDS+XP NA- | EDS | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'PLS-POLE' | % Pole Height | 1 | No
- | XP | DC/SC | SER | - | - | - | - | EDW |  | XP | [9 empty] | NA+ |  | EDW+XP NA+ | EDW | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'PLS-POLE' | % Pole Height | 2 | No
- | XP | DC/SC | SER | - | - | - | - | EDW |  | XP | [9 empty] | NA- |  | EDW+XP NA- | EDW | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'PLS-POLE' | % Pole Height | 2 | No
- | XP | DC/SC | SER | - | - | YES | - | HWD |  | XP | [9 empty] | NA+ |  | HWD_A+XP NA+ | HWD_A | Creep FE | NA+ |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'PLS-POLE' | % Pole Height | 4 | No
- | XP | DC/SC | SER | - | - | YES | - | HWD |  | XP | [9 empty] | NA- |  | HWD_A+XP NA- | HWD_A | Creep FE | NA- |  | 1 | 1 | 1 | 1 | 1 | Wind on Face | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 'PLS-POLE' | % Pole Height | 4 | No
Note on A2: 1, 2 = One / two wires / phases broken ALL = All the options available for the selection criteria CM = Construction and Maintenance (default) loading case - actual to be modified to reflect actual works to be performed CP = Concrete Poles (to TP.PL 01.15) DC = Double Circuit structures FC = Failure Containment (Security) cirteria RP = These criteria identify those applicable to the selected Target reliability (Tab CONTROL) SC = Single Circuit structures SER = Serviceability load criteria SP = Steel Poles (to TP.PL 02.20) TWR = Lattice Steel Tower VUL = These criteria are applicable for Vulnerability analyses
Note on H2: The load cases for RSL / Security conditions represent the "target" condition for all lines. Select as applicable to reflect the agreed residual security target, i.e. 100Pa only on Strain structures only (select suspension structures in Tab Control, or delete as applicable); select the required number of broken phases / earthwire and combinations thereof. RSL torsion cases for DC towers consider breakages in one circuit only The following criteria do not directly address “double circuit - single circuit strung” conditions. However, the load cases will work for these conditions. C&M conditions are the default conditions; special attention to be made to address the site specific conditions.
Note on B7: ALL = Any structure type TWR = Lattice tower only SP = Steel Poles XP = Steel pole + defln limits CP = Concrete poles
Note on D7: VUL = Vulnerability RP = Reliability FC = Failure Containment SER = Serviceability
Note on X7: IF CELL IS SHADED RED INDICATES WEATHER CASE NOT FOUND

## Control
INSTRUCTIONS | STRUCTURE GROUPS | WEATHER CASES |  | LOAD CRITERIA |  | STAKING TABLE |  | PLS-CADD
| TP.DL 12.01 WEATHER AND LOAD CASE GENERATOR FOR PLS-CADD | [8 empty] | REVISION CONTROL for GIP_Standard T1-T3 Rev A
| PLS-CADD WC & LC Generator Master Rev H.xlsx | [8 empty] | Rev: | Date | Revision Description
SITE NAME | GIP_Standard | SECTION | T1-T3 |  |  | Revision | A |  |  | A | 17.07.23 | JW reviewed GP setup - new structures not yet in this sheet.
|  | VULNERABILITY ANALYSIS? | N
|  | Line Reliability (return period, years) | 300 | Years (default 300 for Towers; 150 for standard poles)
|  | Use this filename for this Spreadsheet | GIP_Standard_T1-T3_RP300yr_RevA Loading Criteria.xlsx
|  | For PLS-CADD CRITERIA FILE NAME employ | GIP_Standard_T1-T3_RevA Reliability Loading 300 yrRP.cri
|  | Select Conductor & Earthwire types & utilisation limits | (select *None* if not applicable) |  |  | VDC %UTS | MWT %UTS | MOT | Cable Filename
| Conductor (Required) | 1 | Chukar_NZ_ACSR_AC_Present |  |  | 22% | 70% | 120 | chukar_nz_acsr_ac_greased_04092013_l_downlead 6 degree creep.wir
| Conductor | 2 | *None* |  |  | 22% | 70% | 90 | chukar_nz_acsr_ac_greased_04092013_l.wir
| Conductor | 3 | *None* |  |  | 23% | 70% | 120 | zebra_acsr_gz_greased_pre1977_l.wir
| Conductor | 4 | *None*
| Earthwire | 1 | *None* |  |  | 22% | 70% |  | 7_3-05_scac_greased_l.wir
| Earthwire | 2 | *None*
| Earthwire | 3 | *None*
| Earthwire | 4 | *None*
LINE SECTION LOCATION INFORMATION
|  | Wind Loading Site Specific (SS) or Generic (GL) | SS | Enter site specific wind speeds to Tab Staking Table
|  | North or South Island | S | (N or S)
|  | Portion of Line <5km from Coast? | N | for tmin
|  | Max GROUND LEVEL Altitude along line section | 800 | m (NZGD2000 - refer ADEGL.02.25)
|  | Wind Zone (Ref TP.DL 12.01 Appendix B. Figure B-1) | A7 | (If more than one wind zone refer to Transpower)
|  | TP.DL 12.01 Ice Zone | S | Ref Appendix B. Figure B-2
|  | SECURITY Level (for RSL loading) Default = 1 | 1 | RSL Loading based on 100Pa Wind
|  | Failure Containment (FC) on all structures ? | N | In Staking table identify which structures are 'STOP' Structures
|  | Identify deflection & cracking specification, if applicable | N | "N" = Not applicable (towers), "SP" = Standard Steel / Concrete Pole to TP.PL 01.15
"XP" = Standard steel pole to TP.PL 01.20; "WP" = Standard Wood pole to TP.PL 01.11
|  | This ADDITIONAL data required when Generic loading selected | The following regional wind speed has been selected
|  | V1000,Z=10,Cat=2 | 46 | with | 0.953 | Mrp for 300 years return period
|  | Select Min Terrain Category | 2.5 | Ref AS/NZS 1170.2 4.2.1 & Amdt 2
|  |  | Structures | Condrs
|  | Select Average Height area centroid >GL (m) | 15 | 30
|  | Terrain Height Multiplier MZ,CAT | 0.97 | 1.05
|  | Wind speed Topographic factors | 1 | 1 | Effects of Mt, Ms,Mlee (Md = 1)
|  |  | Average span (m) | 350 | Span to be representative (small spans result in higher loading)
|  |  | Span Reduction Factor | 0.75262
|  | Employ the following generic wind speeds for V(rp1000,z=15,cat=2.5) | 45 | 42.5094 | m/s [Enter in Staking Table]
COMMENTS:
1
2
Note on G9: VDC = Maximum tangental tension for Vibration Damage Control
Note on H9: Max tangental tension under any loading condition
Note on I9: MOT = Maximum Operating temperature
Note on J9: The Filename is required for tab "Cables"
Note on D22: The heights available in the drop down list are defined in tab "Structure Groups"

## Staking Table
INSTRUCTIONS |  |  |  | WEATHER CASES | [16 empty] | Manual |  |  |  | GENERIC Wind speed (m/s) on
CONTROL INPUT |  |  |  | LOAD CRITERIA | [6 empty] | PLS-CADD WC & LC Generator Master Rev H.xlsx | [9 empty] | Allocate |  |  |  | V(rp1000,z=15,cat=2.5)
STRUCTURE GROUPS |  |  |  | PLS-CADD | [16 empty] | for Stop |  |  |  | Conductors |  |  | Structures
| GIP_Standard T1-T3 Rev A | [8 empty] | From PLS-CADD Model: | [10 empty] | /RSL loading |  |  |  | 49 | m/s |  | 45
PLS-CADD WC & LC Generator Master Rev H.xlsx | [6 empty] | Maximum Elevation | 800 | [14 empty] | Copy above into Comment columns below
[7 empty] | Minimum elevation | 800 |  |  | 0 | 0 | [8 empty] | 'Stop' |  | else enter site specific wind speeds in accordance with ADEGL.02.11
| Structure Number | Station (m) | Height Adjust. (m) | Offset Adjust. (m) | Orientation Angle (deg) | X Easting (m) | Y Northing (m) | Centerline Z Elevation (m) | TIN Z Elevation (m) | Ahead Span (m) | Line Angle (deg) | Sets In XY Structure Line Angle Calculation | Transverse Axis Azimuth (deg) | Structure Name | Structure Description | Struct. Height (m) | Embedded Length (m) | Structure Specific Material | Counter Weights (N) | Automatic Structure Group Membership | Manual Structure Group Membership | Structure Comment 1 | Structure Comment 2 | Structure Comment 3 | Structure Comment 4 | Structure Comment 5 | Structure Comment 6 | Structure Comment 7 | Structure Comment 8 | Structure Comment 9 | Structure Comment 10 | Structure Comment 11 | Structure Comment 12 | Structure Comment 13 | Structure Comment 14 | Structure Comment 15 | Structure Comment 16 | Structure Comment 17 | Structure Comment 18 | Structure Comment 19 | Structure Comment 20 | Structure Comment 21 | Structure Comment 22 | Structure Comment 23 | Structure Comment 24 | Structure Comment 25 | Structure Comment 26 | Structure Comment 27 | Structure Comment 28 | Structure Comment 29 | Structure Comment 30 | Structure Comment 31 | Structure Comment 32 | Structure Comment 33 | Structure Comment 34 | Structure Comment 35 | Structure Comment 36 | Structure Comment 37 | Structure Comment 38 | Structure Comment 39 | Structure Comment 40 | Structure Comment 41 | Structure Comment 42 | Structure Comment 43 | Structure Comment 44 | Structure Comment 45 | Structure Comment 46 | Structure Comment 47 | Structure Comment 48 | Structure Comment 49 | Structure Comment 50
| 1 |  | 25.005 |  |  |  |  | 800 |  |  |  | 1960-01-01 | 180 | C:\Users\ErtugrulKeles\Groundline\NZ-6585 TP Standard GIP - Documents\03 Operations\PLS-CAD Model\structures\tower\2DDHST\2dd-hst-ew2-str-tee-be5m-le9.0-9.0-9.0-9.0.tow | 2DD-HSTC Tower Data Input Rev A | 19.3 |  | 0 |  | 'All', 'Has DE', 'Not all sets DE', 'TOWER', 'TOWER has DE'
| 2 | 350 | 25.005 |  |  | 350 |  | 800 |  |  |  | 1960-01-01 | 180 | C:\Users\ErtugrulKeles\Groundline\NZ-6585 TP Standard GIP - Documents\03 Operations\PLS-CAD Model\structures\tower\2DDHST\2dd-hst-ew2-str-tee-be5m-le9.0-9.0-9.0-9.0.tow | 2DD-HSTC Tower Data Input Rev A | 19.3 |  | 0 |  | 'All', 'Has DE', 'Not all sets DE', 'TOWER', 'TOWER has DE'
| 3 | 700 | 25.005 |  |  | 700 |  | 800 |  |  |  | 1960-01-01 | 180 | C:\Users\ErtugrulKeles\Groundline\NZ-6585 TP Standard GIP - Documents\03 Operations\PLS-CAD Model\structures\tower\2DDHST\2dd-hst-ew2-str-tee-be5m-le9.0-9.0-9.0-9.0.tow | 2DD-HSTC Tower Data Input Rev A | 19.3 |  | 0 |  | 'All', 'Has DE', 'Not all sets DE', 'TOWER', 'TOWER has DE'
| 4 |  |  |  |  | 330 | -100 | 800 |  |  |  | 1960-01-01 | 90 | C:\Users\ErtugrulKeles\Groundline\NZ-6585 TP Standard GIP - Documents\03 Operations\PLS-CAD Model\structures\gantry\220kV A-FRAME Gantry.tow |  | 18.4 |  | 0 |  | 'All', 'Has DE', 'All sets DE', 'TOWER', 'TOWER has DE'
| 5 |  |  |  |  | 370 | -100 | 800 |  |  |  | 1960-01-01 | 90 | C:\Users\ErtugrulKeles\Groundline\NZ-6585 TP Standard GIP - Documents\03 Operations\PLS-CAD Model\structures\gantry\220kV A-FRAME Gantry.tow |  | 18.4 |  | 0 |  | 'All', 'Has DE', 'All sets DE', 'TOWER', 'TOWER has DE'
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
97a
98
99
100
101
102
103
104
105
106
107
108
109
110
111
112
113
114
115
116
117
118
119
120
121
122
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
142
143
144
145
146
147
148
149
150
151
152
153
154
155
156
157
158
159
160
161
162
163
164
165
166
167
168
169
170
171
172
173
174
175
176
177
178
179
180
181
182
183
184
185
186
187
188
189
190
191
192
193
194
195
196
197
198
199
200
201
202
203
204
205
206
207
208
209
210
211
212
213
214
215
216
217
218
219
220
221
222
223
224
225
226
227
228
229
230
231
232
233
234
235
236
237
238
239
240
241
242
243
244
245
246
247
248
249
250
251
252
253
254
255
256
257
258
259
WHI S/S
52(RDF-WHI A)
WRK2 S/S

## pls-cadd folders
INSTRUCTIONS | STRUCTURE GROUPS
STAKING TABLE | WEATHER CASES
CONTROL INPUT | LOAD CRITERIA
WHEN RESTORING BACKUP PLS-CADD FILE THIS TOOL SIMPLIFIES THE APPLICATION OF NEW FILE DIRECTORIES
Input Old "root" directory = | \\beca.net\data\pls\pls-cadd\2312972 - wrk-wkm c\as-building 20141205\PLS
Input New "root" directory = | Q:\ALB-HPI-A\_Master
These are the new directories (copy and paste) | Dump Existing file paths & names here
Q:\ALB-HPI-A\_Master\dxf\shapefiles | \\beca.net\data\pls\pls-cadd\2312972 - wrk-wkm c\as-building 20141205\pls\dxf\shapefiles
Q:\ALB-HPI-A\_Master\dxf | \\beca.net\data\pls\pls-cadd\2312972 - wrk-wkm c\as-building 20141205\pls\dxf
Q:\ALB-HPI-A\_Master\photos | \\beca.net\data\pls\pls-cadd\2312972 - wrk-wkm c\as-building 20141205\pls\photos
Q:\ALB-HPI-A\_Master\photos\als photos | \\beca.net\data\pls\pls-cadd\2312972 - wrk-wkm c\as-building 20141205\pls\photos\als photos
Q:\ALB-HPI-A\_Master\photos\orthophotos | \\beca.net\data\pls\pls-cadd\2312972 - wrk-wkm c\as-building 20141205\pls\photos\orthophotos
Q:\ALB-HPI-A\_Master\structures\tower\for construction | \\beca.net\data\pls\pls-cadd\2312972 - wrk-wkm c\as-building 20141205\pls\structures\tower\for construction
Q:\ALB-HPI-A\_Master\structures\tower\final models\2ddhst\received | \\beca.net\data\pls\pls-cadd\2312972 - wrk-wkm c\as-building 20141205\pls\structures\tower\final models\2ddhst\received
Q:\ALB-HPI-A\_Master\structures\tower\final models | \\beca.net\data\pls\pls-cadd\2312972 - wrk-wkm c\as-building 20141205\pls\structures\tower\final models
Q:\ALB-HPI-A\_Master\structures\tower\final models\2ddlsu | \\beca.net\data\pls\pls-cadd\2312972 - wrk-wkm c\as-building 20141205\pls\structures\tower\final models\2ddlsu
Q:\ALB-HPI-A\_Master\structures\tower\final models\2ddlst | \\beca.net\data\pls\pls-cadd\2312972 - wrk-wkm c\as-building 20141205\pls\structures\tower\final models\2ddlst
Q:\ALB-HPI-A\_Master\structures\tower\final models\2ddhsu | \\beca.net\data\pls\pls-cadd\2312972 - wrk-wkm c\as-building 20141205\pls\structures\tower\final models\2ddhsu
Q:\ALB-HPI-A\_Master\structures\tower\final models\2ddhst | \\beca.net\data\pls\pls-cadd\2312972 - wrk-wkm c\as-building 20141205\pls\structures\tower\final models\2ddhst
Q:\ALB-HPI-A\_Master\structures\stick | \\beca.net\data\pls\pls-cadd\2312972 - wrk-wkm c\as-building 20141205\pls\structures\stick
Q:\ALB-HPI-A\_Master\structures | \\beca.net\data\pls\pls-cadd\2312972 - wrk-wkm c\as-building 20141205\pls\structures
Q:\ALB-HPI-A\_Master | \\beca.net\data\pls\pls-cadd\2312972 - wrk-wkm c\as-building 20141205\pls
Q:\ALB-HPI-A\_Master\cables\temp earthwires | \\beca.net\data\pls\pls-cadd\2312972 - wrk-wkm c\as-building 20141205\pls\cables\temp earthwires
Q:\ALB-HPI-A\_Master\cables | \\beca.net\data\pls\pls-cadd\2312972 - wrk-wkm c\as-building 20141205\pls\cables

## Ref
REFERENCE AND LOOKUP DATA |  |  |  |  | DO NOT MODIFY AT ALL - PLEASE REPORT ALL PROBLEMS
Wind Speed MRP factor to convert V1000 to target reliability
From TP.DL 12.01 Issue 4 Appendix C | [15 empty] | DERIVATION OF GENERIC WIND PRESSURES
|  |  | Max Wind (MW) |  | Min Temp (MT) |  |  |  | Table 5 Nominal Extreme Wind Pressures (Pa)
| Y, m, d | Years | AMW | WMW | AMT | WMT |  |  | Component (Obstacle) Type |  |  |  | Wind Region |  |  | Region | A7
| 1000 Yrs | 1000 | 1 | 1 | 0.6 | 0.6 | [6 empty] | A6, A7 | W |  | Return Period | 300
| 500 Yrs | 500 | 0.978 | 0.964 | 0.587 | 0.578 |  |  | Conductors & Earthwires (excluding SRF, TSRF) |  |  |  | 1000 | 1200 |  | Wind direction | All | Default All
| 450 Yrs | 450 | 0.973 | 0.959 | 0.584 | 0.575 |  |  | Insulators & Pole supports (circular, 12 or 16 sided) |  |  |  | 1200 | 1600 |  | V1000 | 46
| 400 Yrs | 400 | 0.967 | 0.954 | 0.58 | 0.572 |  |  | Lattice Towers (flat sided members) |  |  |  | 3000 | 4000 |  | MRP | 0.953 | for V300 years
| 350 Yrs | 350 | 0.96 | 0.948 | 0.576 | 0.569 | [10 empty] | Structures | Conductors
| 300 Yrs | 300 | 0.953 | 0.94 | 0.572 | 0.564 |  |  | Above wind prerssures assume |  |  | Default |  | Selected |  | Terrain Category | 2.5 | 2.5
| 250 Yrs | 250 | 0.943 | 0.932 | 0.566 | 0.559 |  |  | Terrain category |  |  | 2.5 |  | 2.5 |  | Z obstacle CG (m) >GL | 15 | 30
| 200 Yrs | 200 | 0.932 | 0.922 | 0.559 | 0.553 |  |  | Obstacle Height |  |  | 15 | Condrs | 30 |  | Md | 1 | 1
| 150 Yrs | 150 | 0.916 | 0.908 | 0.55 | 0.545 | [6 empty] | Towers | 15 |  | M(z,cat) | 0.97 | 1.05
| 100 Yrs | 100 | 0.894 | 0.889 | 0.536 | 0.533 |  |  | Return Period RP |  |  | 150 |  | 300 |  | Mt, Ms | 1 | 1
| 75 Yrs | 75 | 0.878 | 0.875 | 0.527 | 0.525 |  |  | Lattice Tower solidity ratio |  |  | 0.25 |  |  |  | V(rp300,z=15,cat=2.5) | 42.5229 | 46.0299 | m/s
| 50 Yrs | 50 | 0.854 | 0.855 | 0.512 | 0.513 | [9 empty] | P(rp300,z=15,cat=2.5) | 1084.9162 | 1271.251 | Pa
| 40 Yrs | 40 | 0.84 | 0.844 | 0.504 | 0.506 | [9 empty] | MRP 1m | 0.314 | 0.314 | Imth return period
| 30 Yrs | 30 | 0.822 | 0.829 | 0.493 | 0.497 | [9 empty] | V(rp1m,z=15,cat=2.5) | 14.0107 | 15.1662
| 25 Yrs | 25 | 0.811 | 0.82 | 0.486 | 0.492 | [9 empty] | P(rp1m,z=15,cat=2.5) | 117.7795 | 138.0082
| 20 Yrs | 20 | 0.796 | 0.808 | 0.478 | 0.485 | [9 empty] | HWD (0.5P) | 542.4581 | 635.6255 | Pa
| 15 Yrs | 15 | 0.777 | 0.793 | 0.466 | 0.476 | [9 empty] | V(rp1000,z=15,cat=2.5) | 45 | 49
| 10 Yrs | 10 | 0.749 | 0.772 | 0.449 | 0.463
| 5 Yrs | 5 | 0.698 | 0.734 | 0.419 | 0.44 | [9 empty] | Wind Direction Factor Md | A6 | A7 | W
| 4 Yrs | 4 | 0.681 | 0.721 | 0.408 | 0.433 | [9 empty] | All | 1 | 1 | 1
| 3 Yrs | 3 | 0.658 | 0.705 | 0.395 | 0.423 | [9 empty] | N | 0.85 | 0.9 | 1
| 2 Yrs | 2 | 0.625 | 0.682 | 0.375 | 0.409 |  | DO NOT MODIFY AT ALL - PLEASE REPORT ALL PROBLEMS | [7 empty] | NE | 0.95 | 0.9 | 0.95
| 1 Yr | 1 | 0.565 | 0.642 | 0.339 | 0.385 | [9 empty] | E | 1 | 0.8 | 0.8
| 9 m | 0.75 | 0.539 | 0.624 | 0.324 | 0.375 | [9 empty] | SE | 0.95 | 0.9 | 0.9
| 6 m | 0.5 | 0.501 | 0.6 | 0.301 | 0.36 | [9 empty] | S | 0.85 | 0.9 | 1
| 5 m | 0.41667 | 0.484 | 0.588 | 0.29 | 0.353 | [9 empty] | SW | 0.95 | 0.9 | 1
| 3 m | 0.25 | 0.433 | 0.556 | 0.26 | 0.334 | [9 empty] | W | 1 | 1 | 0.9
| 2 m | 0.16667 | 0.39 | 0.531 | 0.234 | 0.318 | [9 empty] | NW | 0.95 | 1 | 0.95
| 1 m | 0.083333 | 0.314 | 0.485 | 0.188 | 0.291
| 3 w | 0.057692 | 0.271 | 0.461 | 0.163 | 0.276 | [9 empty] | Regional Wind Speed | V1000
| 2 w | 0.038462 | 0.222 | 0.433 | 0.133 | 0.26 | [9 empty] | A6 | 46
| 1 w | 0.019231 | 0.133 | 0.384 | 0.08 | 0.231 | [9 empty] | A7 | 46
| 4 days | 0.010959 | 0.057 | 0.344 | 0.034 | 0.206 | [9 empty] | W | 53
| 1 day | 0.0027397 | - | 0.24 | - | 0.144
Terrain Categories
Ref AS/NZS 1170.2 Amdt 2 |  | Brief Description (see standard for full description) | [12 empty] | DO NOT MODIFY AT ALL - PLEASE REPORT ALL PROBLEMS
[Terrains] | 1 | Terrain Category 1 (TC1) Very exposed open terrain with few or no obstructions
| 1.5 | Open water surfaces subjected to shoaling waves at serviceability and ultimate wind speeds
| 2 | Open terrain, including grassland, with well-scattered obstructions having heights generally from 1.5 m to 5 m
| 2.5 | Terrain with a few trees or isolated obstructions. This category is intermediate between TC2 and TC3
| 3 | Terrain with numerous closely spaced obstructions having heights generally from 3 m to 10 m.
| 3.5 | [This category is intermediate between TC3 and TC4]
| 4 | Terrain with numerous large, high (10 m to 30 m tall) and closely-spaced constructions | [9 empty] | North Island |  | South Island
[12 empty] | ≤5km Coast? |  | ≤5km Coast?
|  | North Island |  | South Island | [7 empty] | Y | N | Y | N
Everyday wind (100Pa) or still air | ted | Central Plateau: | 10 | Inland (>25km) | 5 |  |  |  |  | Selected | SY | NY | NN | SY | SN
|  | Remainder: | 10 | Remainder: | 5 |  |  |  | Altitude (m) | ted | 5 | 10 | 10 | 5 | 5
Maximum wind | tmw |  | 15 – 0.006H |  | 10 – 0.006H |  |  |  | 800 | tmw | 5 | 10 | 10 | 5 | 5
Min temp + wind (0.6Vdes = 0.36Pdes) & Coincident ice & wind | tmin & tice | ≤5 km of coast -3 – 0.0085H |  | ≤5 km of coast -5 – 0.0085H |  |  |  |  | ≤5km Coast | Selected | SN | -3 | -5 | -5 | -7
|  | >5 km from coast -5 – 0.0085H |  | >5 km from coast -7 – 0.0085H | [5 empty] | tmin, tice | -14 | -10 | -12 | -12 | -14
Wet Snow | tsnow | -5 |  | -5 | [5 empty] | tsnow | -5 | -5 | -5 | -5 | -5
Construction & Maintenance | tcm | 5 |  | 5 | [5 empty] | tcm | 5 | 5 | 5 | 5 | 5
DO NOT MODIFY AT ALL - PLEASE REPORT ALL PROBLEMS
[11 empty] | Condr 1 | Condr2 | Condr3 | Condr4
Clearance / Serviceability Condition |  | Wind Pressure | Phase conductor temperature with coincident wind (interpolate for intermediate temperatures) *1
Max design condr temp | tmax | 0 Pa | 50 | 60 | 70 | 80 | 90 | 100 | 120 | tmax | 120 | 90 | 120 | 0 | MOT
Continuous wind blowout | tedd | 100 Pa | 35 | 36 | 37 | 38 | 39 | 40 | 42 | tedd | 42 | 39 | 42 | 0 | EDD
| thwd | RP 3yrs | 32 | 33 | 34 | 34 | 35 | 36 | 37 | thwd | 37 | 35 | 37 | 0 | HWD
Max Wind Easement Check | tmwd | RP 50yrs | 32 | 33 | 34 | 34 | 34 | 35 | 35 | tmwd | 35 | 34 | 35 | 0 | MWD
NOTE - LOOKUP FORMULAE TO BE MODIFIED TO CATER FOR 150°
|  |  |  | Requires rework of rating spreadhseet | [6 empty] | DO NOT MODIFY AT ALL - PLEASE REPORT ALL PROBLEMS
DO NOT MODIFY AT ALL - PLEASE REPORT ALL PROBLEMS
ICE - SNOW LOADING - LOOKUP TABLE FOR RADIAL THICKNESS, COINCIDENT WIND, DENSITIES & COINCIDENT TEMPERATURES
Table 8 Extreme Snow and Ice Loading | [12 empty] | Extreme Snow (20Pa coincident wind); tsnow = -5 |  |  | "Thin" Ice / High coincident wind |  |  | "Thick" Ice / Low Coincident wind (20MPa)
Thick Ice Density (N/m3) for conductor dia less than or equal to (mm) WITH RADIAL ICE THICKNESS OF (mm)
[5 empty] | Ice Density for conductor dia (max) | [7 empty] | radial thickness (mm) |  |  | Radial thickness (mm) |  |  | Radial Thickness (mm)
| Zone | Altitude | Type | Radial thick (mm) | 16 | 27 | 45 | Wind Pressure |  |  |  | Zone | N0 | N1 | S | N0 | N1 | S | N0 | N1 | S
| N0 | ≤ 500 | None | 0 | 0 | 0 | 0 | 0 |  |  | Altitude (m) max | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 1
|  | >500 ≤600 | Snow | 3 | 3900 | 3900 | 3900 | 20 Pa |  |  |  | 100.1 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0
| N1 | ≤200 | None | 0 | 0 | 0 | 0 | 0 |  |  |  | 200.1 | 0 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Thick | 1 | 16 | 27 | 45 | Min
|  | >200 ≤600 | Snow | 3 | 3900 | 3900 | 3900 | 20 Pa |  |  |  | 500.1 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 5350 | 5350 | 5450 | 5550 | 5350
| N0 & N1 | ≤600 | None | 0 | 0 | 0 | 0 | 0 |  |  |  | 600.1 | 30 | 30 | 30 | 5 | 5 | 5 | 30 | 30 | 50 |  | 31 | 30 | 5350 | 5350 | 5450 | 5550 | 5350
|  | ≤900 | Thick Ice | 3 | 5350 | 5450 | 5550 | 20 Pa |  |  |  | 700.1 | 30 | 30 | 30 | 5 | 5 | 8 | 30 | 30 | 55 |  | 36 | 35 | 5000 | 5000 | 5100 | 5200 | 5000
|  | ≤1200 | Thick Ice | 3.5 | 5000 | 5100 | 5200 | 20 Pa |  |  |  | 900.1 | 30 | 30 | 30 | 8 | 8 | 10 | 35 | 35 | 60 |  | 41 | 40 | 4800 | 4800 | 4850 | 4950 | 4800
|  | ≤600 | None | 0 | 0 | 0 | 0 | 0 |  |  |  | 1200.1 | 30 | 30 | 30 | 10 | 10 | 12 | 40 | 40 | 70 |  | 51 | 50 | 3850 | 3850 | 3950 | 4050 | 3850
|  | >1200 | Thick Ice | 4 | 4800 | 4850 | 4950 | 20 Pa |  |  |  | 5000 | 30 | 30 | 30 | 10 | 10 | 12 | 40 | 40 | 70 |  | 56 | 55 | 3550 | 3550 | 3650 | 3750 | 3550
|  | >600 | Thin Ice | 0.5 | 6850 | 6850 | 6850 | RP 1 month |  |  | Wind pressure | Pa/Mrp | 20 | 20 | 20 | 0.083333 | 0.083333 | 1 | 20 | 20 | 20 |  | 61 | 60 | 3300 | 3300 | 3400 | 3500 | 3300
|  | >900 | Thin Ice | 0.8 | 6850 | 6850 | 6850 | RP 1 month |  |  | Density | N/m3 | 3900 | 3900 | 3900 | 6850 | 6850 | 6850 | LOOKUP | LOOKUP | LOOKUP |  | 71 | 70 | 2950 | 2950 | 3050 | 3150 | 2950
|  | >1200 | Thin Ice | 1 | 6850 | 6850 | 6850 | RP 1 month
| S | ≤100 | Snow | 1 | 3900 | 3900 | 3900 | 20 Pa |  | TEST the formula below | [14 empty] | Coincident temperatures
|  | >100 ≤600 | Snow | 3 | 3900 | 3900 | 3900 | 20 Pa |  | Ice / Snow Zone | S |  | Thick(cm) | Density | Pressure | Thick(cm) | Density | RP &Mrp | Thick(cm) | Density | Pressure |  |  |  | Snow | -5
|  | ≤700 | Thick Ice | 5 | 3850 | 3950 | 4050 | 20 Pa |  | Wind Zone | A7 |  | 3 | 3900 | 20 | 0.8 | 6850 | 1 | 5.5 | 3550 | 20 |  |  |  | Ice | Distance from coast
|  | ≤900 | Thick Ice | 5.5 | 3550 | 3650 | 3750 | 20 Pa |  | Altitude | 800 |  | Temp | -5 |  | Temp | -14 | 0.565 | Temp | -14 |  |  |  |  | Alt | <5km | >5km
|  | ≤1200 | Thick Ice | 6 | 3300 | 3400 | 3500 | 20 Pa |  | Dist_from_coast | >5km | [12 empty] | [Ice-Snow Zone] | N0 | -3 | -5
|  | >1200 | Thick Ice | 7 | 2950 | 3050 | 3150 | 20 Pa |  | [List] | <5km | [13 empty] | N1 | -3 | -5
|  | >600 | Thin Ice | 0.5 | 6850 | 6850 | 6850 | RP 1 year |  |  | >5km |  |  |  | ° | [9 empty] | S | -5 | -7
|  | >700 | Thin Ice | 0.8 | 6850 | 6850 | 6850 | RP 1 year |  |  |  |  | DO NOT MODIFY AT ALL - PLEASE REPORT ALL PROBLEMS
|  | >900 | Thin Ice | 1 | 6850 | 6850 | 6850 | RP 1 year
|  | >1200 | Thin Ice | 1.2 | 6850 | 6850 | 6850 | RP 1 year
DO NOT MODIFY AT ALL - PLEASE REPORT ALL PROBLEMS
| Table 11 Failure Containment - Reduced Ice and Snow conditions |  |  |  |  | Also employed for CM3 | [6 empty] | FAILURE CONTAINMENT | [5 empty] | "Thick" Ice / Low Coincident wind (20MPa)
| Zone | Ground Altitude (m) | Type of accretion | Radial Thickness (mm) (33% of Table 8 values) | Density (N/m3) | [7 empty] | RSL Snow (No wind); tsnow = -5
| N0 | >500 ≤600 | Snow | 10 | 3900 | [7 empty] | radial thickness (mm) | [5 empty] | Radial Thickness (mm)
| N1 | >200 ≤600 | Snow | 10 | 3900 | [6 empty] | Zone | N0 | N1 | S |  |  | Zone | N0 | N1 | S
| N0&N1 | >600 ≤900 | Thick Ice | 10 | 6850 | [6 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
| N0&N1 | >900 ≤1200 | Thick Ice | 11 | 6850 | [6 empty] | 50.0001 | 0 | 0 | 10 |  |  | 50.0001 | 0 | 0 | 0
| N0&N1 | >1200 | Thick Ice | 13 | 6850 | [6 empty] | 200.0001 | 0 | 10 | 10 |  |  | 200.0001 | 0 | 0 | 0
| S | ≤50 | Snow | 0 | 0 | [6 empty] | 500.0001 | 10 | 10 | 10 |  |  | 500.0001 | 0 | 0 | 0
| S | >50 ≤600 | Snow | 10 | 3900 | [6 empty] | 600.0001 | 10 | 10 | 10 |  |  | 600.0001 | 10 | 10 | 16
| S | >600 ≤750 | Thick Ice | 16 | 6850 | [6 empty] | 750.0001 | 10 | 10 | 10 |  |  | 750.0001 | 10 | 10 | 18
| S | >750 ≤900 | Thick Ice | 18 | 6850 | [6 empty] | 900 | 10 | 10 | 10 |  |  | 900 | 10 | 10 | 20
| S | >900 ≤1200 | Thick Ice | 20 | 6850 | [6 empty] | 1200.0001 | 10 | 10 | 10 |  |  | 1200.0001 | 11 | 11 | 23
| S | >1200 | Thick Ice | 23 | 6850 | [6 empty] | 5000 | 10 | 10 | 10 |  |  | 5000 | 13 | 13 | 23
[13 empty] | Thick(cm) | Density | Pressure | Temp |  |  | Thick(cm) | Density | Pressure | Temp
|  |  | DO NOT MODIFY AT ALL - PLEASE REPORT ALL PROBLEMS | [7 empty] | RSL& | CM2 | 0.75 | 3900 | 20 | -5 | RSL& | CM2 | 1.35 | 6850 | 20 | -14
[12 empty] | CM3 | 1 | 3900 | 20 | -5 |  | CM3 | 1.8 | 6850 | 20 | -14
Table 7 Drag Factors for Pole Shapes | [11 empty] | m/s
Support Shape |  | Cp | [9 empty] | 14 | 31862.069
Circular; 16 sided |  | 1.2 | [14 empty] | DO NOT MODIFY AT ALL - PLEASE REPORT ALL PROBLEMS
12 sided |  | 1.3
8 or 6 sided |  | 1.4
Square, rectangular |  | 2.2
[13 empty] | 1 | 11 | 2 | 12 | 3 | 13 | 4 | 14 | 5 | 15 | 6 | 16 | 7 | 17 | 8 | 18
[11 empty] | DC | A123 | 70 | 40 | 70 | 40 | 70 | 40 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
[11 empty] | DC | A456 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 40 | 70 | 40 | 70 | 40 | 70 | 70 | 70 | 70
[11 empty] | DC | B123 | 40 | 70 | 40 | 70 | 40 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
[11 empty] | DC | B456 | 70 | 70 | 70 | 70 | 70 | 70 | 40 | 70 | 40 | 70 | 40 | 70 | 70 | 70 | 70 | 70
[11 empty] | SC | A12 | 70 | 40 | 70 | 40 | 70 | 70 | [6 empty] | 70 | 70 | 70 | 70
[12 empty] | A23 | 70 | 70 | 70 | 40 | 70 | 40 | [6 empty] | 70 | 70 | 70 | 70
[12 empty] | B12 | 40 | 70 | 40 | 70 | 70 | 70 | [6 empty] | 70 | 70 | 70 | 70
[12 empty] | B23 | 70 | 70 | 40 | 70 | 40 | 70 | [6 empty] | 70 | 70 | 70 | 70
DO NOT MODIFY AT ALL - PLEASE REPORT ALL PROBLEMS
17
7
18
8
x
y
13
3
16
6
x
y
12
2
15
5
x
y
11
1
14
4
x
y
Note on D53: Was 5
Note on F53: Was 2

## Weather Cases All
INSTRUCTIONS |  | STAKING TABLE |  | CONTROL INPUT |  |  | STRUCTURE GROUPS |  |  | LOAD CRITERIA |  |  | PLS-CADD
PLS-CADD WEATHER CASES |  |  | GIP_Standard T1-T3 Rev A
[7 empty] | FOLLOWING WEATHER CASES APPLICABLE TO SITES WITH GROUND ELEVATIONS < | 800 | m | FOR DEFAULT TP.DL 12.01 ANALYSES
PLS-CADD WC & LC Generator Master Rev H.xlsx |  |  |  | 1) Select Weather Case "1" (checks to see if the case is "loaded") - These also include the default weather cases for Safety, Serviceability, etc.
2) Cases with "1" are those that are Lines with more than one wind region. Select "W" (=Wind) after resetting previous columns
3) "Repeat" Cases for Lines with more than one height range. Select "H" (=Height) after resetting previous columns
CONTROL COLUMNS |  |  |  | CASE SELECTION |  |  | PLS-CADD DATA INPUT [Criteria \ Weather ]
WEATHER CASE | Weather Case ID | Weather Case Return Period (Years) | Coincident Wind Return Period (years) | Weather case reqd [Select 1] | Wind Region [Select A, W] | Height Dependent Case [Select H] | Description | Air Density Factor (Q) (kg/m^3) (Pa/(m/s)^2) | Wind Velocity (m/s) | Wind Pressure (Pa) | Wire Ice Thickness (cm) | Wire Ice Density (N/m^3) | Wire Ice Load (N/m) | Wire Temp. (deg C) | Ambient Temp. (deg C) | Weather Load Factor | NESC Constant (N/m) | Wire Wind Height Adjust Model | Wire Gust Response Factor | Notes
RELIABILITY CONDITIONS |  |  |  | - | - | -
Maximum Wind conditions | MW | 1000 | 1000 | - | A | H | MW1000_A8 | 0.6 | 1 | 0.6 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw | Applicable to Normal & Differential loading
Maximum Wind conditions | MW | 500 | 500 | - | A | H | MW0500_A8 | 0.6 | 0.978 | 0.57389 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw
Maximum Wind conditions | MW | 400 | 400 | - | A | H | MW0400_A8 | 0.6 | 0.967 | 0.56105 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw
Maximum Wind conditions | MW | 300 | 300 | 1 | A | H | MW0300_A8 | 0.6 | 0.953 | 0.54493 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw
Maximum Wind conditions | MW | 250 | 250 | - | A | H | MW0250_A8 | 0.6 | 0.943 | 0.53355 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw
Maximum Wind conditions | MW | 200 | 200 | - | A | H | MW0200_A8 | 0.6 | 0.932 | 0.52117 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw
Maximum Wind conditions | MW | 150 | 150 | - | A | H | MW0150_A8 | 0.6 | 0.916 | 0.50343 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw
Maximum Wind conditions | MW | 100 | 100 | - | A | H | MW0100_A8 | 0.6 | 0.894 | 0.47954 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw | Applicable to Normal & Differential loading
Maximum Wind conditions | MW | 75 | 75 | - | A | H | MW0075_A8 | 0.6 | 0.878 | 0.46253 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw
Maximum Wind conditions | MW | 50 | 50 | - | A | H | MW0050_A8 | 0.6 | 0.854 | 0.43759 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw
Maximum Wind conditions | MW | 25 | 25 | - | A | H | MW0025_A8 | 0.6 | 0.811 | 0.39463 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw
Maximum Wind conditions | MW | 15 | 15 | - | A | H | MW0015_A8 | 0.6 | 0.777 | 0.36224 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw | 10 year no replacement
Maximum Wind conditions | MW | 10 | 10 | - | A | H | MW0010_A8 | 0.6 | 0.749 | 0.3366 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw | 6 year prioritise
Maximum Wind conditions | MW | 4 | 4 | - | A | H | MW0004_A8 | 0.6 | 0.681 | 0.27826 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw | Orange Tag
Maximum Wind conditions | MW | 2 | 2 | - | A | H | MW0002_A8 | 0.6 | 0.625 | 0.23438 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw | Red Tag
Minimum Temperature with wind | MT | 1000 | 1000 | - | A | H | MT1000_A8 | 0.6 | 0.6 | 0.216 | 0 | 0 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmin
Minimum Temperature with wind | MT | 500 | 500 | - | A | H | MT0500_A8 | 0.6 | 0.587 | 0.20674 | 0 | 0 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmin
Minimum Temperature with wind | MT | 400 | 400 | - | A | H | MT0400_A8 | 0.6 | 0.58 | 0.20184 | 0 | 0 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmin
Minimum Temperature with wind | MT | 300 | 300 | 1 | A | H | MT0300_A8 | 0.6 | 0.572 | 0.19631 | 0 | 0 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmin
Minimum Temperature with wind | MT | 250 | 250 | - | A | H | MT0250_A8 | 0.6 | 0.566 | 0.19221 | 0 | 0 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmin
Minimum Temperature with wind | MT | 200 | 200 | - | A | H | MT0200_A8 | 0.6 | 0.559 | 0.18749 | 0 | 0 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmin
Minimum Temperature with wind | MT | 150 | 150 | - | A | H | MT0150_A8 | 0.6 | 0.55 | 0.1815 | 0 | 0 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmin
Minimum Temperature with wind | MT | 100 | 100 | - | A | H | MT0100_A8 | 0.6 | 0.536 | 0.17238 | 0 | 0 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmin
Minimum Temperature with wind | MT | 75 | 75 | - | A | H | MT0075_A8 | 0.6 | 0.527 | 0.16664 | 0 | 0 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmin
Minimum Temperature with wind | MT | 50 | 50 | - | A | H | MT0050_A8 | 0.6 | 0.512 | 0.15729 | 0 | 0 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmin
Minimum Temperature with wind | MT | 25 | 25 | - | A | H | MT0025_A8 | 0.6 | 0.486 | 0.14172 | 0 | 0 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmin
Minimum Temperature with wind | MT | 15 | 15 | - | A | H | MT0015_A8 | 0.6 | 0.466 | 0.13029 | 0 | 0 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmin | Equivalent to 10 year no replacement
Minimum Temperature with wind | MT | 10 | 10 | - | A | H | MT0010_A8 | 0.6 | 0.449 | 0.12096 | 0 | 0 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmin | Equivalent to 6 year prioritise
Minimum Temperature with wind | MT | 4 | 4 | - | A | H | MT0004_A8 | 0.6 | 0.408 | 0.099878 | 0 | 0 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmin | Equivalent to Orange Tag
Minimum Temperature with wind | MT | 2 | 2 | - | A | H | MT0002_A8 | 0.6 | 0.375 | 0.084375 | 0 | 0 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmin | Equivalent to Red Tag
Extreme Snow | ES | 50 | - | 1 | - | H | ES0050_8 | 0.6 | 5.7735 | 20 | 3 | 3900 | 0 | -5 |  | 1 |  | None | 1.2 | tsnow | Applicable to Normal & Differential loading
Extreme Snow | ES | 50 | - | - | - | H | ES0050_1 | 0.6 | 5.7735 | 20 | 1 | 3900 | 0 | -5 |  | 1 |  | None | 1.2
Thin Ice with wind | TI | 50 | 1 | 1 | A | H | TI0050_A8 | 0.6 | 0.565 | 0.19153 | 0.8 | 6850 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1.2 | tice | Applicable to Normal & Differential loading
Thin Ice with wind | TI | 50 | 1 | - | A | H | TI0050_A12 | 0.6 | 0.565 | 0.19153 | 1 | 6850 | 0 | -17 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1.2
Thin Ice with wind | TI | 50 | 1 | - | A | H | TI0050_A9 | 0.6 | 0.565 | 0.19153 | 0.8 | 6850 | 0 | -15 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1.2
Thin Ice with wind | TI | 50 | 1 | - | A | H | TI0050_A7 | 0.6 | 0.565 | 0.19153 | 0.5 | 6850 | 0 | -13 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1.2
Extreme (thick) ice | EI | 50 | - | 1 | - | H | EI0050_8 | 0.6 | 5.7735 | 20 | 5.5 | 3550 | 0 | -14 |  | 1 |  | None | 1.2 | tice
Extreme (thick) ice | EI | 50 | - | - | - | H | EI0050_12 | 0.6 | 5.7735 | 20 | 6 | 3300 | 0 | -17 |  | 1 |  | None | 1.2
Extreme (thick) ice | EI | 50 | - | - | - | H | EI0050_9 | 0.6 | 5.7735 | 20 | 5.5 | 3550 | 0 | -15 |  | 1 |  | None | 1.2
Extreme (thick) ice | EI | 50 | - | - | - | H | EI0050_7 | 0.6 | 5.7735 | 20 | 5 | 3850 | 0 | -13 |  | 1 |  | None | 1.2
SECURITY CONDITIONS | - | Security Level |  | - | - | - | [6 empty] | 0
Cascade & RSL Wind | RW | 1 | - | 1 | - | H | RW0001_8 | 0.6 | 12.9099 | 100 | 0 | 0 | 0 | 5 |  | 1 |  | None | 1 | ted | Applicable to Cascade and Torsional loading
Cascade & RSL Snow | RS | 1 | - | 1 | - | H | RS0001_8 | 0.6 | 0 | 0 | 1 | 3900 | 0 | -5 |  | 1 |  | None | 1.2 | tsnow | Applicable to Cascade and Torsional loading
Cascade & RSL Thick Ice | RI | 1 | - | 1 | - | H | RI0001_8 | 0.6 | 0 | 0 | 1.8 | 6850 | 0 | -14 |  | 1 |  | None | 1.2 | tice | Applicable to Cascade and Torsional loading
SAFETY LOADING |  |  |  | - | - | - | [6 empty] | 0
Default C&M | CM1 | - | - | 1 | - | - | CM1 | 0.6 | 12.9099 | 100 | 0 | 0 | 0 | 5 |  | 1 |  | None | 1 | tcm
Extended C&M Works (Summer) | CM2 | - | 1 | 1 | A | - | CM2_A | 0.6 | 0.565 | 0.19153 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tcm |  | Rev H
Extended C&M Works (with snow) | CM2S | - | - | 1 | - | H | CM2S_8 | 0.6 | 5.7735 | 20 | 1 | 3900 | 0 | -5 |  | 1 |  | None | 1.2 | tsnow | New - to cover non-summer months; if required | Rev H
Extended C&M Works (with Ice) | CM2I | - | - | 1 | - | H | CM2I_8 | 0.6 | 5.7735 | 20 | 1.8 | 6850 | 0 | -14 |  | 1 |  | None | 1.2 | tice | New - to cover non-summer months; if required | Rev H
Delayed Strengthening (Summer) | CM3 | - | 4 | 1 | A | H | CM3_A8 | 0.6 | 0.681 | 0.27826 | 0 | 0 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmin
Delayed Strengthening (Snow) | CM3S | - | - | 1 | - | H | CM3S_8 | 0.6 | 5.7735 | 20 | 1 | 3900 | 0 | -5 |  | 1 |  | None | 1.2 | tsnow | New - to cover non-summer months | Rev H
Delayed Strengthening (Ice) | CM3I | - | - | 1 | - | H | CM3I_8 | 0.6 | 5.7735 | 20 | 1.8 | 6850 | 0 | -14 |  | 1 |  | None | 1.2 | tice | New - to cover non-summer months | Rev H
SERVICEABILITY CONDITIONS |  | %CBL or temp |  | - | - | -
Vibration Damage Control | VDC | - | - | 1 | - | - | VDC | 0.6 | 7.0711 | 30 | 0 | 0 | 0 | 5 |  | 1 |  | None | 1
Everyday still air | EDS | - | - | 1 | - | - | EDS | 0.6 | 0 | 0 | 0 | 0 | 0 | 5 |  | 1 |  | None | 1 | ted
Everyday still air Condr 1 | EDS | - | - | 1 | - | - | EDS_120(tedd) | 0.6 | 0 | 0 | 0 | 0 | 0 | 42 |  | 1 |  | None | 1
Everyday still air Condr 2 | EDS | - | - | - | - | - | EDS_90(tedd) | 0.6 | 0 | 0 | 0 | 0 | 0 | 39 |  | 1 |  | None | 1
Everyday still air Condr 3 | EDS | - | - | - | - | - | EDS_120(tedd) | 0.6 | 0 | 0 | 0 | 0 | 0 | 42 |  | 1 |  | None | 1
Everyday still air Condr 4 | EDS | - | - | - | - | - | EDS_(tedd) | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 |  | None | 1 | ted
Everyday Wind (Structural) | EDW | - | - | 1 | - | - | EDW | 0.6 | 12.9099 | 100 | 0 | 0 | 0 | 5 |  | 1 |  | None | 1 | ted
Falling Tree Deflection TP.SS 02.18 | FTD | - | - | 1 | - | - | FTD | 0.6 | 18.2574 | 200 | 0 | 0 | 0 | 42 |  | 1 |  | None | 1 | tedd | New | Rev H
Maximum Operating Temperature Condr 1 | MOT | 120 | - | 1 | - | - | MOT_120 | 0.6 | 0 | 0 | 0 | 0 | 0 | 120 |  | 1 |  | None | 1 | tmax
Maximum Operating Temperature Condr 2 | MOT | 90 | - | - | - | - | MOT_90 | 0.6 | 0 | 0 | 0 | 0 | 0 | 90 |  | 1 |  | None | 1 | tmax
Maximum Operating Temperature Condr 3 | MOT | 120 | - | - | - | - | MOT_120 | 0.6 | 0 | 0 | 0 | 0 | 0 | 120 |  | 1 |  | None | 1 | tmax
Maximum Operating Temperature Condr 4 | MOT | 0 | - | - | - | - | MOT_0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 |  | None | 1 | tmax
Everyday wind deflection Condr 1 | EDD | 120 | - | 1 | - | - | EDD_120 | 0.6 | 12.9099 | 100 | 0 | 0 | 0 | 42 |  | 1 |  | None | 1 | tedd
Everyday wind deflection Condr 2 | EDD | 90 | - | - | - | - | EDD_90 | 0.6 | 12.9099 | 100 | 0 | 0 | 0 | 39 |  | 1 |  | None | 1 | tedd
Everyday wind deflection Condr 3 | EDD | 120 | - | - | - | - | EDD_120 | 0.6 | 12.9099 | 100 | 0 | 0 | 0 | 42 |  | 1 |  | None | 1 | tedd
Everyday wind deflection Condr 4 | EDD | 0 | - | - | - | - | EDD_0 | 0.6 | 12.9099 | 100 | 0 | 0 | 0 | 0 |  | 1 |  | None | 1 | tedd
High Wind Deflection (Structural) | HWD |  | 3 | - | A | - | HWD_A | 0.6 | 0.658 | 0.25978 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | ted
High Wind Deflection Condr 1 | HWD | 120 | 3 | 1 | A | - | HWD_A120 | 0.6 | 0.658 | 0.25978 | 0 | 0 | 0 | 37 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | thwd
High Wind Deflection Condr 2 | HWD | 90 | 3 | - | A | - | HWD_A90 | 0.6 | 0.658 | 0.25978 | 0 | 0 | 0 | 35 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | thwd
High Wind Deflection Condr 3 | HWD | 120 | 3 | - | A | - | HWD_A120 | 0.6 | 0.658 | 0.25978 | 0 | 0 | 0 | 37 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | thwd
High Wind Deflection Condr 4 | HWD | 0 | 3 | - | A | - | HWD_A0 | 0.6 | 0.658 | 0.25978 | 0 | 0 | 0 | 0 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | thwd
Maximum Wind deflection (Structural) | MWD |  | 50 | - | A | H | MWD_A8 | 0.6 | 0.854 | 0.43759 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw
Maximum Wind deflection Condr 1 | MWD | 120 | 50 | 1 | A | - | MWD_A120 | 0.6 | 0.854 | 0.43759 | 0 | 0 | 0 | 35 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmwd
Maximum Wind deflection Condr 2 | MWD | 90 | 50 | - | A | - | MWD_A90 | 0.6 | 0.854 | 0.43759 | 0 | 0 | 0 | 34 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmwd
Maximum Wind deflection Condr 3 | MWD | 120 | 50 | - | A | - | MWD_A120 | 0.6 | 0.854 | 0.43759 | 0 | 0 | 0 | 35 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmwd
Maximum Wind deflection Condr 4 | MWD | 0 | 50 | - | A | - | MWD_A0 | 0.6 | 0.854 | 0.43759 | 0 | 0 | 0 | 0 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmwd
Snow Deflection – Still air | SDS | - | - | 1 | - | H | SDS_8 | 0.6 | 0 | 0 | 3 | 3900 | 0 | -5 |  | 1 |  | None | 1.2 | tsnow
Snow Deflection – Still air | SDS | - | - | - | - | H | SDS_1 | 0.6 | 0 | 0 | 1 | 3900 | 0 | -5 |  | 1 |  | None | 1.2
Snow Deflection – Wind 50%Pdes | SDD | - | - | 1 | - | H | SDD_8 | 0.6 | 4.0825 | 10 | 3 | 3900 | 0 | -5 |  | 1 |  | None | 1.2 | tsnow
Snow Deflection – Wind 50%Pdes | SDD | - | - | - | - | H | SDD_1 | 0.6 | 4.0825 | 10 | 1 | 3900 | 0 | -5 |  | 1 |  | None | 1.2
Snow Deflection – No snow | SDO | - | - | 1 | - | - | SDO | 0.6 | 0 | 0 | 0 | 0 | 0 | -5 |  | 1 |  | None | 1 | tsnow
Thin Ice – Still air | TIS | - | - | 1 | - | H | TIS_8 | 0.6 | 0 | 0 | 0.8 | 6850 | 0 | -14 |  | 1 |  | None | 1.2 | tice
Thin Ice – Still air | TIS | - | - | - | - | H | TIS_12 | 0.6 | 0 | 0 | 1 | 6850 | 0 | -17 |  | 1 |  | None | 1.2
Thin Ice – Still air | TIS | - | - | - | - | H | TIS_9 | 0.6 | 0 | 0 | 0.8 | 6850 | 0 | -15 |  | 1 |  | None | 1.2
Thin Ice – Still air | TIS | - | - | - | - | H | TIS_7 | 0.6 | 0 | 0 | 0.5 | 6850 | 0 | -13 |  | 1 |  | None | 1.2
Thin Ice Deflection – 50%Pdes | TID | - | - | 1 | A | H | TID_A8 | 0.6 | 0.39952 | 0.095767 | 0.8 | 6850 | 0 | -14 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1.2 | tice
Thin Ice Deflection – 50%Pdes | TID | - | - | - | A | H | TID_A12 | 0.6 | 0.39952 | 0.095767 | 1 | 6850 | 0 | -17 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1.2
Thin Ice Deflection – 50%Pdes | TID | - | - | - | A | H | TID_A9 | 0.6 | 0.39952 | 0.095767 | 0.8 | 6850 | 0 | -15 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1.2
Thin Ice Deflection – 50%Pdes | TID | - | - | - | A | H | TID_A7 | 0.6 | 0.39952 | 0.095767 | 0.5 | 6850 | 0 | -13 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1.2
Thin (and thick) Ice – No Ice | TIO | - | - | 1 | - | - | TIO | 0.6 | 0 | 0 | 0 | 0 | 0 | -14 |  | 1 |  | None | 1 | tice
Extreme (thick) Ice – Still Air | EIS | - | - | 1 | - | H | EIS_8 | 0.6 | 0 | 0 | 5.5 | 3550 | 0 | -14 |  | 1 |  | None | 1.2 | tice
Extreme (thick) Ice – Still Air | EIS | - | - | - | - | H | EIS_12 | 0.6 | 0 | 0 | 6 | 3300 | 0 | -17 |  | 1 |  | None | 1.2
Extreme (thick) Ice – Still Air | EIS | - | - | - | - | H | EIS_9 | 0.6 | 0 | 0 | 5.5 | 3550 | 0 | -15 |  | 1 |  | None | 1.2
Extreme (thick) Ice – Still Air | EIS | - | - | - | - | H | EIS_7 | 0.6 | 0 | 0 | 5 | 3850 | 0 | -13 |  | 1 |  | None | 1.2
Extreme (thick) Ice Deflection – 50%Pdes | EID | - | - | 1 | - | H | EID_8 | 0.6 | 4.0825 | 10 | 5.5 | 3550 | 0 | -14 |  | 1 |  | None | 1.2 | tice
Extreme (thick) Ice Deflection – 50%Pdes | EID | - | - | - | - | H | EID_12 | 0.6 | 4.0825 | 10 | 6 | 3300 | 0 | -17 |  | 1 |  | None | 1.2
Extreme (thick) Ice Deflection – 50%Pdes | EID | - | - | - | - | H | EID_9 | 0.6 | 4.0825 | 10 | 5.5 | 3550 | 0 | -15 |  | 1 |  | None | 1.2
Extreme (thick) Ice Deflection – 50%Pdes | EID | - | - | - | - | H | EID_7 | 0.6 | 4.0825 | 10 | 5 | 3850 | 0 | -13 |  | 1 |  | None | 1.2
Minimum Temp Still air | MTS | - | - | 1 | - | H | MTS_8 | 0.6 | 0 | 0 | 0 | 0 | 0 | -14 |  | 1 |  | None | 1 | tmin
Support replace criteria 10 year for wind | RCW | 15 | 15 | 1 | A | H | RCW_A8 | 0.6 | 0.777 | 0.36224 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw
CA criteria wind 6 year | CA6 | 10 | 10 | 1 | A | H | CA6_A8 | 0.6 | 0.749 | 0.3366 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw
CA criteria Wind Orange Tag | CA1 | 4 | 4 | 1 | A | H | CA1_A8 | 0.6 | 0.681 | 0.27826 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw
CA criteria Wind Red Tag | CA0 | 2 | 2 | 1 | A | H | CA0_A8 | 0.6 | 0.625 | 0.23438 | 0 | 0 | 0 | 5 |  | 1 |  | Apply Span Specific Wind & Ice Adj. | 1 | tmw
Support Replacement criteria snow | RCS |  | - | 1 | - | H | RCS_8 | 0.6 | 0 | 0 | 1 | 3900 | 0 | -5 |  | 1 |  | None | 1.2 | tsnow
Support Replacement criteria ice | RCI |  | - | 1 | - | H | RCI_8 | 0.6 | 0 | 0 | 1.8 | 6850 | 0 | -14 |  | 1 |  | None | 1.2 | tice
SPECIAL (if required) |  |  |  | - | - | -
Seismic / Earthquake | EQ | 500 | - | - | - | - | EQ_8 | 0.6 | 0 | 0 | 0 | 0 | 0 | 5 |  | 1 |  | None | 1 | ted
Note on E8: ONLY SELECT THOSE CASES WITH "1"
Note on F8: Select only if Line crosses over the wind Region Boundary between W and A6/A7
Note on G8: Required for lines with more than one height boundary layer
Note on H8: Refer to TP. 12.01 Section 8

## Conductor-Properties (hidden)
Conductor Data (extracted from CONDPARA (R5) - Imp to Metric v4.xlsx)
Name | Sort Id | Equ.Area | O/a Dia. | Weight | Actual CSA | Breaking Load | E | Ther.Exp | Add. Wt. | Add. Area | Creep Allow
|  | sq.mm | (mm) | (N/m) | (sq.mm) | (kN) | (kN/sq.mm) | (/deg.C) | (N/m) | (mm/m) | °C
SELECT |  |  | 1e-07 | 1e-07 | 1e-07 | 1e-07 | 1e-07 | 1e-07
*None* |  |  | 1e-07
19_2.87_SCGZ | SC/GZ |  | 14.35 | 9.64 | 122.92 | 162.245 | 189.606 | 1.15e-05 |  |  | 0
19_3.26_SCAC | SC/AC |  | 16.3 | 10.4336 | 158.5911 | 191.2608 | 154.5915 | 1.29e-05 |  |  | 0
19_3.26_SCAC_Present | SC/AC |  | 16.3 | 10.4412 | 158.5911 | 191.2608 | 154.5915 | 1.29e-05 |  |  | 0
7_2.59_SCAC | SC/AC |  | 7.77 | 2.5028 | 36.8797 | 44.4769 | 156.7641 | 1.29e-05 |  |  | 0
7_2.59_SCAC_Present | SC/AC |  | 7.77 | 2.5028 | 36.8797 | 44.4769 | 156.7641 | 1.29e-05 |  |  | 0
7_2.59_SCGZ | SC/GZ |  | 7.7724 | 2.8917 | 36.9025 | 47.8629 | 189.6058 | 1.152e-05 |  |  | 0
7_2.64_SCGZ | SC/GZ |  | 7.9248 | 3.0097 | 38.3638 | 49.8201 | 189.6058 | 1.152e-05 |  |  | 0
7_3.05_SCAC | SC/AC |  | 9.15 | 3.4291 | 51.1432 | 61.6787 | 156.7641 | 1.29e-05 |  |  | 0
7_3.05_SCAC_Present | SC/AC |  | 9.15 | 3.4291 | 51.1432 | 61.6787 | 156.7641 | 1.29e-05 |  |  | 0
7_3.05_SCGZ | SC/GZ |  | 9.144 | 3.9982 | 51.076 | 68.5026 | 189.6058 | 1.152e-05 |  |  | 0
7_3.18_SCAC | SC/AC |  | 9.54 | 3.7183 | 55.5958 | 67.0486 | 156.7641 | 1.29e-05 |  |  | 0
7_3.18_SCAC_Present | SC/AC |  | 9.54 | 3.7183 | 55.5958 | 67.0486 | 156.7641 | 1.29e-05 |  |  | 0
7_3.18_SCGZ | SC/GZ |  | 9.525 | 4.3376 | 55.4212 | 68.7695 | 189.6058 | 1.152e-05 |  |  | 0
7_3.68_SCGZ | SC/GZ |  | 11.049 | 5.8351 | 74.574 | 92.523 | 189.6058 | 1.152e-05 |  |  | 0
7_3.71_SCAC | SC/AC |  | 11.13 | 5.0221 | 75.6721 | 91.2605 | 156.7641 | 1.29e-05 |  |  | 0
7_3.71_SCAC_Present | SC/AC |  | 11.13 | 5.0221 | 75.6721 | 91.2605 | 156.7641 | 1.29e-05 |  |  | 0
7_3.71_SCGZ | SC/GZ |  | 11.1252 | 5.9162 | 75.6069 | 93.8575 | 189.6058 | 1.152e-05 |  |  | 0
7_4.25_SCAC | SC/AC |  | 12.75 | 6.5568 | 99.3 | 119.76 | 156.7641 | 1.29e-05 |  |  | 0
7_4.25_SCAC_Present | SC/AC |  | 12.75 | 6.5568 | 99.3 | 119.76 | 156.7641 | 1.29e-05 |  |  | 0
Centipede AAC_Present | AAC |  | 26.46 | 11.6201 | 415.2171 | 63.113 | 64.0823 | 2.3e-05 |  |  | 23
Chukar_(M)_ACSR_GZ_Pre1994 | ACSR/GZ |  | 40.68 | 31.7898 | 968.0965 | 227.6 | 68.9476 | 1.98e-05 |  |  | 23
Chukar_ACSR_GZ_Pre1994 | ACSR/GZ |  | 40.68 | 31.7898 | 975.8 | 227.3754 | 68.9476 | 1.98e-05 |  |  | 23
Chukar_NZ_ACSR_AC_Present | ACSR/AC |  | 40.73 | 30.8467 | 978.8486 | 214.9968 | 69.8575 | 2.1319e-05 |  |  | 30
Chukar_NZ_ACSR_GZ_Pre1994 | ACSR/GZ |  | 40.7 | 31.6855 | 978.8 | 233 | 66.5 | 2.07e-05 |  |  | 23
Cicada_AAC_Present | AAC |  | 32.55 | 17.5846 | 628.3441 | 95.5083 | 64.0823 | 2.3e-05 |  |  | 23
Cockroach_AAC_Present | AAC |  | 21.1 | 7.3325 | 265.747 | 40.3935 | 64.5118 | 2.3e-05 |  |  | 23
Coyote_ACSR_AC_Present | ACSR/AC |  | 15.89 | 4.9749 | 151.8004 | 46.8481 | 74.846 | 2.0312e-05 |  |  | 30
Coyote_ACSR_GZ_Pre1994 | ACSR/GZ |  | 15.89 | 5.3243 | 151.8 | 46.3 | 75 | 1.89e-05 |  |  | 14
Cricket_ACSR_AC_Present | ACSR/AC |  | 17.5 | 6.3269 | 181.6233 | 66.7687 | 80.4466 | 1.9391e-05 |  |  | 30
Cu_19_2.34 | HD Copper |  | 11.68 | 7.2038 | 80.37 | 33.59 | 124 | 1.7e-05
Cu_19_2.57 | HD Copper |  | 12.83 | 8.6821 | 96.87 | 40.35 | 124 | 1.7e-05
Cu_37_1.83 | HD Copper |  | 12.81 | 8.6547 | 94.4 | 40.15 | 124 | 1.7e-05
Cu_37_2.62 | HD Copper |  | 18.31 | 17.6884 | 194.98 | 81.21 | 124 | 1.7e-05
Cu_7_2.64 | HD Copper |  | 7.92 | 3.3735 | 38.035 | 16.13 | 124 | 1.7e-05
Cu_7_3.45 | HD Copper |  | 10.36 | 5.7689 | 65.06 | 26.73 | 124 | 1.7e-05
Dog_ACSR_AC_Present | ACSR/AC |  | 14.15 | 3.7873 | 118.536 | 33.0356 | 72.8005 | 2.0625e-05 |  |  | 30
Dog_ACSR_GZ_Pre1994 | ACSR/GZ |  | 14.15 | 3.9632 | 118.5 | 32.7 | 76 | 1.98e-05 |  |  | 17
Goat_ACSR_AC_Present | ACSR/AC |  | 25.97 | 13.9653 | 399.9811 | 135.3558 | 80.4466 | 1.9391e-05 |  |  | 30
Goat_ACSR_GZ_Pre1994 | ACSR/GZ |  | 25.97 | 14.9946 | 400 | 135.8 | 80 | 1.78e-05 |  |  | 14
Hare_ACSR_AC_Present | ACSR/AC |  | 14.16 | 4.0618 | 122.4819 | 39.1592 | 75.9116 | 2.0129e-05 |  |  | 30
Hare_ACSR_GZ_Pre1994 | ACSR/GZ |  | 14.16 | 4.2698 | 122.5 | 36 | 80 | 1.91e-05 |  |  | 17
Hyena_ACSR_AC_Present | ACSR/AC |  | 14.57 | 4.2876 | 126.4326 | 41.6499 | 77.4839 | 1.9816e-05 |  |  | 30
Krypton_AAAC_Present | AAAC |  | 16.25 | 4.3491 | 157.62 | 37.43 | 65 | 2.3e-05 |  |  | 30
Lacrosse_ACSR_AC_Present | ACSR/AC |  | 33.75 | 21.1871 | 671.9572 | 193.6907 | 72.9497 | 2.0659e-05 |  |  | 30
Lutetium_AAAC_Present | AAAC |  | 17.5 | 5.0439 | 182.8014 | 41.6787 | 64.5118 | 2.3e-05 |  |  | 30
Mink_ACSR_AC_Present | ACSR/AC |  | 10.98 | 2.4256 | 73.6462 | 21.8308 | 75.9116 | 2.0129e-05 |  |  | 30
Mink_ACSR_GZ_Pre1994 | ACSR/GZ |  | 10.98 | 2.562 | 73.65 | 21.8 | 79 | 1.91e-05 |  |  | 17
Moa_ACSR_AC_Present | ACSR/AC |  | 38.43 | 25.7048 | 871.9358 | 178.7994 | 67.4352 | 2.1819e-05 |  |  | 30
Moa_ACSR_GZ_Pre1994 | ACSR/GZ |  | 38.4 | 26.8892 | 870.2 | 181 | 63 | 2.09e-05 |  |  | 23
Neon_AAAC_Present | AAAC |  | 18.75 | 5.7902 | 209.8486 | 47.8455 | 64.5118 | 2.3e-05 |  |  | 30
Nitrogen_AAAC_Present | AAAC |  | 21 | 7.3193 | 261.5376 | 62.1152 | 64.0823 | 2.3e-05 |  |  | 30
Nobelium_AAAC_Present | AAAC |  | 22.75 | 8.59 | 306.9434 | 72.8991 | 64.0823 | 2.3e-05 |  |  | 30
OPGW_70mm2_Hitachi_(12F) | OPGW |  | 12.2 | 4.6091 | 76.73 | 78.665 | 139.0583 | 1.34e-05
OPGW_70mm2_J-Power_(12F) | OPGW |  | 12.2 | 4.8445 | 88.29 | 78.7 | 139.1 | 1.34e-05
OPGW_109mm2_SFPOC_(24F) | OPGW |  | 13.9 | 7.404 | 109 | 140 | 162 | 1.3e-05
OPGW_120mm2_J-Power_(24F) | OPGW |  | 15.2 | 7.8944 | 136.7 | 137.2 | 136 | 1.36e-05
OPGW_120mm2_Hitachi_(12F) | OPGW |  | 15.2 | 7.8159 | 136.7 | 136.7 | 136.2 | 1.36e-05
OPGW_127mm2_SFPOC_(144F) | OPGW |  | 16 | 8.9044 | 127 | 155 | 162 | 1.3e-05
OPGW_174mm2_SFPOC_(24F) | OPGW |  | 17.4 | 5.8055 | 174 | 65 | 75.554 | 1.99e-05
Oxygen_AAAC_Present | AAAC |  | 23.75 | 9.29 | 336.6904 | 73.5668 | 64.5118 | 2.3e-05 |  |  | 30
Partridge_ACSR_AC_Present | ACSR/AC |  | 16.28 | 5.1853 | 156.8655 | 49.7197 | 75.6362 | 2.0174e-05 |  |  | 30
Pheasant_ACSR_AC_Present | ACSR/AC |  | 35.1 | 23.2161 | 726.7889 | 188.5029 | 72.9497 | 2.0659e-05 |  |  | 30
Pheasant_ACSR_GZ_Pre1994 | ACSR/GZ |  | 35.1 | 24.6675 | 726.4 | 196.3 | 70.5 | 1.96e-05 |  |  | 17
Phosphorous_AAAC_Present | AAAC |  | 26.25 | 11.4364 | 408.6525 | 93.1728 | 64.0823 | 2.3e-05 |  |  | 30
Pigeon_ACSR_AC_Present | ACSR/AC |  | 12.741 | 3.2562 | 99.1636 | 27.9879 | 75.9116 | 2.0129e-05 |  |  | 30
Pigeon_ACSR_GZ_Pre1994 | ACSR/GZ |  | 12.74 | 3.4561 | 99.2 | 29.5 | 80 | 1.91e-05 |  |  | 0
Selenium_AAAC_Present | AAAC |  | 29.25 | 14.2949 | 506.0419 | 113.8594 | 63.6944 | 2.3e-05 |  |  | 30
Silicon_AAAC_Present | AAAC |  | 31.5 | 16.5787 | 586.8888 | 126.768 | 63.6944 | 2.3e-05 |  |  | 30
Skunk_ACSR_AC_Present | ACSR/AC |  | 12.95 | 4.2602 | 100.1021 | 55.3512 | 97.7758 | 1.7126e-05 |  |  | 30
Skunk_ACSR_GZ_Pre1994 | ACSR/GZ |  | 12.95 | 4.2602 | 100.1 | 52.9 | 97.7758 | 1.7126e-05 |  |  | 8
Sulphur_AAAC_Present | AAAC |  | 33.75 | 19.0317 | 673.7244 | 145.5245 | 63.6944 | 2.3e-05 |  |  | 30
Uranus_AAC_Present | AAC |  | 29.25 | 14.2949 | 506.0419 | 75.1472 | 63.6944 | 2.3e-05 |  |  | 23
Ursula_AAC_Present | AAC |  | 31.5 | 16.5787 | 586.8888 | 87.153 | 63.6944 | 2.3e-05 |  |  | 23
Venus_AAC_Present | AAC |  | 33.75 | 19.0317 | 673.7244 | 97.0163 | 63.6944 | 2.3e-05 |  |  | 23
Weke_AAC_Present | AAC |  | 14.16 | 3.3869 | 122.4819 | 18.6172 | 65.4347 | 2.3e-05 |  |  | 23
Wolf_ACSR_AC_Present | ACSR/AC |  | 18.13 | 6.8362 | 194.9356 | 71.6625 | 80.4466 | 1.9391e-05 |  |  | 30
Wolf_ACSR_GZ_Pre1994 | ACSR/GZ |  | 18.13 | 7.3991 | 194.9 | 69.2 | 80 | 1.78e-05 |  |  | 14
Zebra_ACSR_AC_Present | ACSR/AC |  | 28.62 | 15.4442 | 484.4779 | 137.8141 | 73.3531 | 2.0617e-05 |  |  | 30
Zebra_ACSR_GZ_Pre1994 | ACSR/GZ |  | 28.62 | 16.4714 | 484.5 | 131.9 | 71 | 1.94e-05 |  |  | 17