## User Guide
SPREADSHEET "SITE SPECIFIC WIND SPEEDS" DEVELOPS SITE-SPECIFIC TERRAIN AND TOPOGRAPHICAL DATA INTO SITE WIND SPEEDS AND EVALUATES CRITICAL DIRECTIONS AND SPEEDS FOR INPUT TO PLS-CADD AND OTHER SPREADSHEETS REQUIRING WIND SPEEDS ON STRUCTURES AND CABLES (CONDUCTORS AND EARTHWIRES)
Introduction: PLS-CADD only permits a single global terrain category to be applied to the whole line model, including structures and cables. This is a fundamental shortcoming for transmission lines as Terrain Category, by definition, changes with site location and wind direction. Transpower obtains from a preffered supplier (PS) WAsP generated topographical multipliers and upwind terrain categories for each site in the eight cardinal wind directions in accordance with AS/NZS 1170.2 and TP.DL 12.01. This spreadsheet develops this data into site specific wind speeds in the eight cardinal directions at the "equivalent" centroid of area of the obstacle (structure or cables). The spreadsheet further evaluates the wind speeds in relation to the line and structure orientation and then, subject to input selection criteria, presents the 'critical' wind speed(s) corrected for the applicable terrain category as is necessary for input to PLS-CADD for line and structure analysis. The wind speeds are also corrected to cater for the effects of wind speed span reduction factor. Note the effects of TSRF are not considered. These wind speeds shall be adopted for all PLS-CADD models whether for risk assessment, structural analysis or maintenance prioritisation. This spreadsheet contains 9 tabs in addition to this user guide
- QA: Revision and Quality control
- Site data: This tab isthe PS deliverable (containing PS supplied topographical multipliers and terrain categories) for advised site locations and heights
- Site Wind: This tab develops the PS supplied and Site data into site specific wind speeds for all sites (structures and cables) in the 8 cardinal directions at height "Z"
- V1000 Design Wind: This tab evaluates the cardinal site wind speeds and selects those that lie within azimuth boundaries of the structure transverse axis or conductor perpendicular
- Charts: This tab graphically presents the critical wind speeds and associated terrain categories selected under tab "Design Wind"
- Structure Data: This tab provides the ability to calculate required data should the automated data not be correct, e.g. Structure heights in Staking table
- Staking Table: The PLS-CADD report used by "Site data" to determine the structure height data; also used to populate the Comment fields with the output wind speeds
- Span Heights: A PLS-CADD report used by "Site data" to determine the average height of the conductors within the spans.
- Ref: Contains reference information relating to AS/NZS 1170.2 and data lookup tables used by the spreadsheet.
General Summary: NOTE - THE SPREADSHEET IS POPULATED FOR 50 STRUCTURES (TO PROVIDE A REPRESENTATIVE EXAMPLE) HOWEVER ALL FORMULAE MAY BE REPLICATED DOWN BY ROW TO SUIT THE ACTUAL NUMBER OF STRUCTURES (MAXIMUM 1000) [the Graphs in Tab "Charts" will require the axes to be manually formatted] The PLS-CADD line model shall be interrogated to provide the following reports (see ADEGL_02_11 for parameters to be adopted): - Staking Table (see Guidelines below). - Terrain Clearances By Survey Point Report (see Guidelines in Tab "Span Heights") The data from the above PLS-CADD reports shall be 'dumped' into spreadsheet Tabs "Staking Table" and "Terrain heights" respectively. - In "Structure Data" check the automatic links to "Staking Table" correctly identify the structure the structure heights are correct. (employ the tab "charts" for a visual check of the line route and whether the conductors curves are spatially above the ground line) The above data automatically links into the tab "Site data" which is the ONLY information that is necessary to be issued to the PS. - When all data is confirmed correct, in Tab "Site Data" right click the tab name "Site Data" and use the "Move or Copy" to copy the tab to a new spreadsheet for Issue to NIWA (convert all formulae to values). - After the PS has returned the requsiste data (Terrain Categories and Terrain Wind Speed Multipliers) copy this data back into the master Asset spreadsheet (tab "Site Data"); - In "Structure Data" check the automatic links to "Staking Table" correctly identify the structure type (SUS, STR, DE are the only allowable structure functions) and that the structure wind centroid is correct for the type of structure (Gantry = 100%, all others 50%)
Data Input: The following cell coding is employed in this spreadsheet
Required data: Inputs: Note: The complete spreadsheet depends on the "structure number" in the Staking table: Wind Region: The applicable wind region for the line. Refer to Tab "Ref" or AS/NZS 1170.2 Amdt 1 Figure 3.1(B). If the line traverses more than one wind region two spreadsheets will be required; one for each region. The spreadsheets should overlap by at least one complete line section (strain structure to strain structure).
Obstacle locations: The NZTM coordinates are required for each site for which wind data is required. For structures - employ the coordinates from the relevant PLS-CADD line model. These may be obtained directly from the line staking table (a tab has been provided to permit a direct data dump which is automatically linked to the "Site data" tab). These coordinates shall adopt New Zealand Transverse Mercator Projection (NZTM). For Spans the coordinates are derived automatically from the structure coordinates assuming the span is represented by the location half way between adjacent structures. The user shall ensure the mid-span coordinates reference the correct "adjacent" structures (e.g. gantries).
Obstacle heights: The heights of the obstacles (structures and conductors) in order to establish the relevant averaging distances upwind of the obstacles necessary to be considered when determining the relevant topographical and terrain data: For structures - employ the maximum height of the structure; The spreadsheet directly links to the staking table on the assumption this correctly represents the overall height of the structure. However some PLS-CADD models have "structure heights" that are the representative of the distance to the underside of the crossarm or other. The suitability of this data should be checked and corrected as necessary. For Spans - the height of the conductors is derived from the "Span Heights" tab representing the largest "clearance" between ground and any conductor/earthwire within each span. All entered and calculated data is required to be checked, reviewed and approved (details to be entered in tab "QA") before forwarding the spreadsheet to the preferred Supplier.
PLS-CADD reports: The following reports are to be extracted from the PLS-CADD Line Model and inserted into the spreadsheet: STAKING TABLE: Copy and paste the complete report into the "Staking Table" tab. Note: It is necessary to confirm the validity of the structure heights as input to PLS-CADD as these may only represent the height of the bottom crossarm. If necessary correct the heights for each structure type. TERRAIN CLEARANCES BY SURVEY POINT REPORT STRUCTURE DATA: This tab extracts structure infromation from the staking table. Data in this tab is to be reviewed by the user to determine if it is realistic. Structure heights from the staking table may be bottom cross-arm heights, full structure heights should be used. If the centroid of a particular structure differs from the default percentage used for the line, the percentage should be changed in column F, "Structure wind loading centroid (%)". Dead end towers are not identified automatically, change the Structure type in column D to "DE".
ACTIONS BY PREFERRED SUPPLIER a) Verify the wind region b) enter the upwind terrain category and topographic wind speed multipliers for the spans and structures, c) complete the QA tab, d) return the spreadsheet to the Transpower Project engineer.
Theory: Topographical multipliers and terrain categories are obtained from PS following the guidelines in ADEGL_02_11 and the master spreadsheet AAA-BBB-C-NN Site WAsP data_RevXX.xlsx. For analysis: - Structure sites are defined by the PLS-CADD coordinates; - Span sites are defined and calculated at the mid point between their adjacent supporting structures. The relevant height Z adopted for determination of the Site Design wind speeds (for the calculation of MZ,CAT) is taken as: - Structures centroid of wind area is a function of the structure height (numerous analyses have indicated the centroid is approximately 40-45% of the overall height for double circuit towers). This however can change depending on the structure / circuit configuration. - Spans; The centroid is taken as the average distance between all conductors and earthwires in the span and the ground (evaluated by interrogation of PLS-CADD "Terrain Clearances By Survey Point" report for the weather case Min Temp - still Air. Terrain categories are rounded down to the nearest 0.5 (deemed more realistic than adopting 0.1 intervals due to differentiation difficulties between roughness types).
Analysis of structures has determined that the critical wind angle is typically within ±15° of the transverse axis for the majority of structures. This does not apply to terminal structures, structures with large turnoff angles or structures that have large differences in longitudinal tension. To address these aspects ADEGL_02_11 assumes the critical wind speed on a structure or span will be the largest wind speed at the effective area-centroid height Z within a specified angle from the structure transverse axis or conductor perpendicular. This angle tolerance shall be a minimum of ±25° to ensure that a minimum of one cardinal wind direction will always be selected. Default angles shall be ±25° for all spans; ±25° for towers with a turn off angle between 0° and <20°; ±45° for towers with a turn off angle ≥20° and <60° (to provide additional security for ”angle” towers); and, ±90° for all other towers and for all dead end towers.
To obtain the structure transverse / conductor perpendicular Azimuth to North the following has been adopted:
- Structures: The structure transverse azimuth is directly read from the PLS-CADD staking table
- Spans (Conductors): The bearing (azimuth) of the conductor is calculated from the coordinates of the adjacent structures; for checking purposes the following may be adopted
Output: 'Site Wind' tab: This tab presents the evaluated wind speeds at the selected heights or area centroids in the eight cardinal directions incorporating all wind speed multipliers applicable to that site and selected heights. These wind speeds can be employed for analysis of individual structures. 'V1000 Design Wind' tab presents the maximum site specific wind speeds that fall within ±θ of the structure Transverse Axis Azimuth or conductor perpendicular. The Transpower default angles are: • ±25° for all spans • ±25° for towers with a turn off angle between 0° and <20° • ±45° for towers with a turn off angle ≥20° and <60° (to provide additional security for ”angle” towers) • ±90° for all other towers and for all dead end towers
Note 1: The wind speeds in the RED columns are those that are required to be input into PLS-CADD. To facilitate this formulae are provided in Tab "Staking Table" that will permit the staking table to be updated with the correct wind speeds (see Row 1 tab "Staking Table"). The complete staking table should then be copied back into PLS-CADD.
Note 2: The span lengths are calculated from the Structure Coordinates and compared against the PLS-CADD span length; If there is a difference of more than 0.01m in span length a conditional formatting formula will turn the cell red; Normally any errors are due to circuit splits that jump a structure, e.g. gantries connecting to the terminal tower, tee-off structures, etc. No cells should be blue otherwise the incorrect SRF will be applied.
Note 3: The effects of Span Reduction Factor are included in the span-specific wind speeds
Note 4:The PLS-CADD comment field into which the data is pasted is chosen in the "Span Specific Wind & Ice Adjustments" window (Menu path: Criteria/Code Specific Wind and Terrain Parameters/Span Specific Wind & Ice Adjustments). "Wire wind velocity factor for ahead span" and "Structure wind velocity factor (also applies to insulators)" are the fields to be modified. The design winds are V1000 wind speeds, line reliability level/wind return period (MRP) is dealt with in each weather case by applying a multiplier to the wind speed.
PLS-CADD: All load cases shall be developed using the standard Transpower weather case and load criteria generator (PLS-CADD WC & LC Generator.xlsx) Note: For all Weather Cases: The "Wire Wind Height Adjust Model" shall be set to "Apply Span Specific Wind & Ice Adj." and the "Wire Gust Response Factor" set to "1". This addresses the fact that the input site specific wind speeds already cater for terrain category, height, span reduction factor and direction. This effectively ignores the TP.DL 12.01 requirement for a tension section reduction factor (TSRF) to be applied when calculating tensions.
The table below contains examples of weather cases (extracted from the PLS-CADD WC & LC Generator)
Load Criteria: “Structure Wind Load Model” should be set to “Wind on Face”. Applying TPNZ will give incorrect loads as the wind speed in the staking table is already at the structure centroid height.
LAA = BI - (180-D)/2
LINE AHEAD
STRUCTURE TRANSVERSE AZIMUTH "STA"
+SO
Orientation Angle
D = Line
Angle
All angles +ve clockwise when looking ahead
CONDUCTOR WIND TRANSVERSE AZIMUTH =
POSITIVE TRANS) STA - SO + D/2
NEGATIVE TRANS) STA - SO +D/2 + 180
Bisector BI = STA-SO
CWTA = BI - (180-D)/2 +90
CWTA = BI - (180-D)/2 + 270
N
NE
S
E
SE
W
NW
SW
CONTAINS FORMULAE IN CASE OF ACCIDENTAL DELETION
DATA TO BE ENTERED
COMPUTED DATA (TO BE CHECKED)
MANUALLY ADJUSTED FORMULA (CHECK AS ASSET SPECIFIC)
DATA PROVIDED BY PREFERRED SUPPLIER
WIND SPEEDS TO BE TRANSFERRED TO PLS-CADD
(AUTO LINKED TO STAKING TABLE)

## QA
QUALITY AND REVISION CONTROL
Date | Revision | Details | Prepared by | Checked by | Approved By
29.6.2014 | DRAFT4 | Presentation reformatted for issue and discussion with NIWA | DAH
18.7.2014 | DRAFT5 | Corrected azimuth calculations; corrected lookup for critical wind directions for 0/360° Simplified all critical wind direction lookups | DAH
25.7.2014 | DRAFT6 | Reformatted spreadsheet to remove duplication and to standardise with NIWA data template | DAH
27.7.2014 | DRAFT7 | Adopted maximum clearance for conductor height Rewrote user guide Added hyperlinks Submitted for Review and approval | DAH
2014-12-19 | DRAFT8 | Included Line Reliability IIA (RP = 300 years); Modified output (wind speeds) to 2 decimal places for transfer to Staking Table | DAH
2015-06-23 | DRAFT9 | Added Column M in Staking Table "Sets In XY Structure Line Angle Calculation" to match PLS upgrade | DAH
2015-08-18 | DRAFT10 | Corrected formula influenced by PLS staking table change, updated user guide, increased allowable number of structures. | MW
2015-10-09 | DRAFT12 | Added multiple wind angle functionality to design wind tab. Added structure specific centroid height percentage. Corrected wind angle selection error. Updated user guide. | MW
2015-11-18 | DRAFT13 | Added Structure Function tab and updated the multiple wind angle functionality on the design wind tab. Updated user guide. | MW
2015-11-25 | DRAFT14 | Staking table: revised lookup formulae for Structure comments 4 & 7 to reference comum B (not W) Started Cell protection (unprotect) | DAH
2015-12-04 | DRAFT15 | Removed structure function tab, created Structure Data tab, removed line schedule tab. | MW
2015-12-04 | A | FORMAL ISSUE | MW | DAH | MC
2016-02-02 | DRAFTB1 | V1000 design wind values formatted to show 2 decimal points | MW
2016-02-25 | DRAFTB2 | Restricted the allowable values in the structure function column, "Structure Data" tab. | MW
2016-07-08 | DRAFTB3 | Reduced the number of "example" structures to 50 to reduce file size Modified User Guide to Provide General Summary and to reflect that only one Master Spreadsheet is now required | MW/DAH
2016-07-12 | B | FORMAL ISSUE | MW | DAH | MC
2017-07-28 | DRAFTC1 | V1000 Design Wind: Added columns for SRF correction for span wind speeds Staking Table: Redirected Span wind speed column Z (Structure Comment 4) to the SRF corrected wind speed (tab V1000 Column AN) Added conditional formatting to "Span" to compare with the PLS-CADD staking table. Cell turns blue if the difference is more than 0.002m User Guide: Revised Introduction to identify that span wind speeds are corrected for Wind Pressure Revised PLS-CADD section to remove requirement to use TPNZ or TPNZ 2008. Included reference to TP Standard PLS-CADD WC & LC Generator; Changed PLS-CADD Graphic to reflect TP.DL 12.01 WC naming convention. Modified the text for V1000 Design Wind PLS-CADD interfaces to address the above revisions Updated the Mzcat calculation, terrain category is no longer rounded down to the nearest 0.5. Ref: Added Mzcat table | MW/DAH
2016-08-01 | C | FORMAL ISSUE | MW | DAH
2017-06-20 | C+1 | Removed WHI S/S and 52(RDF-WHI A) ahead span coordinates as they aren't in model. Copied WRK1 S/S aheadspan coordinates and factors to WRK2 S/S. Corrected asimuth to north formula error. | MW
USER GUIDE

## Site data
NIWA WAsP Analysis | [15 empty] | INPUTS
REF: ADEGL_02_11 | [14 empty] | Wind Region | A7 | Refer AS/NZS 1170.2 Figure 3.1(B)
|  | Project Name: | [12 empty] | Equivalent V1000 Wind Speed | 46 | m/s From AS/NZS1170.2 Table 3.1 (Region A1 to A7=46; W=53)
Project Code:
|  | Asset: | WRK-WHI A
NIWA Analysis Date:
|  | Analysis By: | Richard Turner, Sylvia Nichol, Stuart Moore | [11 empty] | V1000 for Asset: | 46 | m/s
|  | NIWA data Filename: | WRK-WHI A PLS-CADD Wind Speeds RevA
|  | PLS-CADD Model Filename: | wrk-whi-a clearance-assessment gl 20110614.xyz
[5 empty] | DATA PROVIDED BY NIWA - STRUCTURES | [20 empty] | DATA PROVIDED BY NIWA - MID SPANS
STRUCTURE SITES |  |  |  |  | NIWA REF UID | SITE UPWIND TERRAIN CATEGORIES | [7 empty] | TOPOGRAPHIC MULTIPLIERS (MT) | [7 empty] | MIDSPAN SITES (AHEAD) |  |  |  | NIWA REF UID | SITE UPWIND TERRAIN CATEGORIES | [7 empty] | TOPOGRAPHIC MULTIPLIERS (MT)
Site ID | NZTM 2000 (NZGD 2000) |  |  | Structure Height above GL (m) | [17 empty] | Site ID | NZTM 2000 |  | Condr Height above GL (m)
| X Easting (m) | Y Northing (m) | Z Ground Level (m) |  |  | N | NE | E | SE | S | SW | W | NW | N | NE | E | SE | S | SW | W | NW |  | X Easting (m) | Y Northing (m) |  |  | N | NE | E | SE | S | SW | W | NW | N | NE | E | SE | S | SW | W | NW
Structure Number | X Easting (m) | Y Northing (m) | Centerline Z Elevation (m) | - | [17 empty] | Structure Number | #VALUE! | #VALUE! | - | 0.5
1 | 0 | 0 | 800 | 45 | 1 | 2.6 | 2.2 | 2.2 | 2.3 | 2.2 | 2.5 | 2.6 | 2.6 | 0.87 | 0.99 | 0.96 | 0.85 | 0.87 | 0.99 | 0.96 | 0.85 | 1 | 175 | 0 | 50.93 | 1.5 | 2.6 | 2.2 | 2.2 | 2.3 | 2.2 | 2.4 | 2.6 | 2.6 | 0.87 | 1 | 0.96 | 0.83 | 0.87 | 1 | 0.96 | 0.83
2 | 350 | 0 | 800 | 45 | 2 | 2.6 | 2.2 | 2.2 | 2.3 | 2.2 | 2.4 | 2.6 | 2.7 | 0.87 | 0.99 | 0.96 | 0.83 | 0.87 | 0.99 | 0.96 | 0.83 | 2 | 525 | 0 | 50.95 | 2.5 | 2.4 | 2.2 | 2.2 | 2.3 | 2.2 | 2.5 | 2.5 | 2.7 | 0.87 | 0.99 | 0.96 | 0.83 | 0.87 | 0.99 | 0.96 | 0.83
3 | 700 | 0 | 800 | 45 | 3 | 2.4 | 2.1 | 2.3 | 2.2 | 2.3 | 2.6 | 2.5 | 2.7 | 0.88 | 1 | 0.96 | 0.83 | 0.88 | 1 | 0.96 | 0.83 | 3 | 515 | -50 | 45.96 | 3.5 | 2.3 | 2.1 | 2.3 | 2.3 | 2.3 | 2.4 | 2.5 | 2.6 | 0.87 | 1 | 0.96 | 0.83 | 0.87 | 1 | 0.96 | 0.83
4 | 330 | -100 | 800 | 20 | 4 | 2.3 | 2.1 | 2.3 | 2.4 | 2.3 | 2.3 | 2.5 | 2.5 | 0.87 | 1 | 0.97 | 0.83 | 0.87 | 1 | 0.97 | 0.83 | 4 | 350 | -100 | 42.7 | 4.5 | 2.2 | 2.1 | 2.4 | 2.5 | 2.3 | 2.3 | 2.4 | 2.4 | 0.86 | 0.99 | 0.96 | 0.82 | 0.86 | 0.99 | 0.96 | 0.82
5 | 370 | -100 | 800 | 20 | 5 | 2.2 | 2.1 | 2.4 | 2.4 | 2.3 | 2.3 | 2.3 | 2.4 | 0.86 | 0.97 | 0.95 | 0.82 | 0.86 | 0.97 | 0.95 | 0.82 | 5 | #VALUE! | #VALUE! | 36.34 | 5.5 | 2.1 | 2.3 | 2.4 | 2.3 | 2.2 | 2.3 | 2.1 | 2.2 | 0.79 | 0.94 | 0.94 | 0.81 | 0.79 | 0.94 | 0.94 | 0.81
0 | - | - | - | - | 6 | 2.2 | 2.5 | 2.1 | 2.1 | 2.3 | 2.2 | 2.2 | 2.1 | 0.94 | 1.01 | 1.1 | 1.04 | 0.94 | 1.01 | 1.1 | 1.04 | 0 | #VALUE! | #VALUE! | - | 6.5 | 2.3 | 2.4 | 2.1 | 2.1 | 2.3 | 2.2 | 2.4 | 2.2 | 0.95 | 1.01 | 1.1 | 1.05 | 0.95 | 1.01 | 1.1 | 1.05
0 | - | - | - | - | 7 | 2.3 | 2.3 | 2.1 | 2.1 | 2.2 | 2.3 | 2.4 | 2.2 | 0.99 | 1.04 | 1.06 | 1.01 | 0.99 | 1.04 | 1.06 | 1.01 | 0 | #VALUE! | #VALUE! | - | 7.5 | 2.4 | 2.2 | 2.1 | 2.1 | 2.1 | 2.3 | 2.4 | 2.3 | 0.97 | 1 | 1.08 | 1.05 | 0.97 | 1 | 1.08 | 1.05
0 | - | - | - | - | 8 | 2.4 | 2.2 | 2.1 | 2.1 | 2.1 | 2.2 | 2.4 | 2.4 | 0.94 | 1.03 | 1.06 | 0.97 | 0.94 | 1.03 | 1.06 | 0.97 | 0 | #VALUE! | #VALUE! | - | 8.5 | 2.4 | 2.2 | 2.1 | 2.1 | 2.1 | 2.2 | 2.4 | 2.4 | 0.86 | 0.95 | 1.06 | 0.99 | 0.86 | 0.95 | 1.06 | 0.99
0 | - | - | - | - | 9 | 2.3 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.3 | 2.3 | 0.95 | 0.97 | 1.08 | 1.06 | 0.95 | 0.97 | 1.08 | 1.06 | 0 | #VALUE! | #VALUE! | - | 9.5 | 2.2 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.2 | 2.2 | 0.99 | 0.97 | 1.08 | 1.09 | 0.99 | 0.97 | 1.08 | 1.09
0 | - | - | - | - | 10 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.2 | 0.99 | 0.96 | 1.05 | 1.08 | 0.99 | 0.96 | 1.05 | 1.08 | 0 | #VALUE! | #VALUE! | - | 10.5 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 0.95 | 0.99 | 1.05 | 1.01 | 0.95 | 0.99 | 1.05 | 1.01
0 | - | - | - | - | 11 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 0.94 | 0.96 | 1.05 | 1.03 | 0.94 | 0.96 | 1.05 | 1.03 | 0 | #VALUE! | #VALUE! | - | 11.5 | 2.1 | 2.1 | 2.1 | 2.1 | 2.2 | 2.1 | 2.1 | 2.1 | 1.03 | 0.97 | 0.94 | 0.99 | 1.03 | 0.97 | 0.94 | 0.99
0 | - | - | - | - | 12 | 2.1 | 2.1 | 2.1 | 2.1 | 2.2 | 2.1 | 2.1 | 2.1 | 1.13 | 1.15 | 1.18 | 1.15 | 1.13 | 1.15 | 1.18 | 1.15 | 0 | #VALUE! | #VALUE! | - | 12.5 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.2 | 2.1 | 2.1 | 1.03 | 0.95 | 0.79 | 0.88 | 1.03 | 0.95 | 0.79 | 0.88
0 | - | - | - | - | 13 | 2.1 | 2.2 | 2.1 | 2.1 | 2.1 | 2.2 | 2.1 | 2.1 | 1.01 | 0.99 | 1.04 | 1.06 | 1.01 | 0.99 | 1.04 | 1.06 | 0 | #VALUE! | #VALUE! | - | 13.5 | 2.1 | 2.2 | 2.1 | 2.1 | 2.1 | 2.2 | 2.1 | 2.1 | 1.03 | 0.97 | 0.96 | 1.01 | 1.03 | 0.97 | 0.96 | 1.01
0 | - | - | - | - | 14 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.2 | 2.1 | 1.05 | 0.95 | 0.97 | 1.06 | 1.05 | 0.95 | 0.97 | 1.06 | 0 | #VALUE! | #VALUE! | - | 14.5 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 1.08 | 0.95 | 0.99 | 1.1 | 1.08 | 0.95 | 0.99 | 1.1
0 | - | - | - | - | 15 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.2 | 1.03 | 0.97 | 1.06 | 1.1 | 1.03 | 0.97 | 1.06 | 1.1 | 0 | #VALUE! | #VALUE! | - | 15.5 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 1.04 | 1.03 | 1.06 | 1.06 | 1.04 | 1.03 | 1.06 | 1.06
0 | - | - | - | - | 16 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 1.04 | 1.04 | 1.03 | 1.04 | 1.04 | 1.04 | 1.03 | 1.04 | 0 | #VALUE! | #VALUE! | - | 16.5 | 2.1 | 2.2 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 1.06 | 1.04 | 0.99 | 1.01 | 1.06 | 1.04 | 0.99 | 1.01
0 | - | - | - | - | 17 | 2.1 | 2.2 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 1.06 | 1.04 | 0.97 | 0.99 | 1.06 | 1.04 | 0.97 | 0.99 | 0 | #VALUE! | #VALUE! | - | 17.5 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 1.05 | 1.05 | 0.96 | 0.97 | 1.05 | 1.05 | 0.96 | 0.97
0 | - | - | - | - | 18 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 1.04 | 1.04 | 0.96 | 0.96 | 1.04 | 1.04 | 0.96 | 0.96 | 0 | #VALUE! | #VALUE! | - | 18.5 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 1 | 1.03 | 0.97 | 0.95 | 1 | 1.03 | 0.97 | 0.95
0 | - | - | - | - | 19 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 0.97 | 1.03 | 1 | 0.95 | 0.97 | 1.03 | 1 | 0.95 | 0 | #VALUE! | #VALUE! | - | 19.5 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 0.97 | 1.01 | 1 | 0.96 | 0.97 | 1.01 | 1 | 0.96
0 | - | - | - | - | 20 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 0.96 | 0.99 | 1 | 0.97 | 0.96 | 0.99 | 1 | 0.97 | 0 | #VALUE! | #VALUE! | - | 20.5 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 0.94 | 0.97 | 1 | 0.96 | 0.94 | 0.97 | 1 | 0.96
0 | - | - | - | - | 21 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 0.86 | 0.95 | 1.03 | 0.94 | 0.86 | 0.95 | 1.03 | 0.94 | 0 | #VALUE! | #VALUE! | - | 21.5 | 2.1 | 2.1 | 2.2 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 0.94 | 0.96 | 1 | 0.97 | 0.94 | 0.96 | 1 | 0.97
0 | - | - | - | - | 22 | 2.1 | 2.1 | 2.2 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 0.86 | 0.92 | 1.04 | 1 | 0.86 | 0.92 | 1.04 | 1 | 0 | #VALUE! | #VALUE! | - | 22.5 | 2.1 | 2.2 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 0.85 | 0.91 | 1.04 | 0.99 | 0.85 | 0.91 | 1.04 | 0.99
0 | - | - | - | - | 23 | 2.1 | 2.2 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 0.85 | 0.87 | 1.03 | 1 | 0.85 | 0.87 | 1.03 | 1 | 0 | #VALUE! | #VALUE! | - | 23.5 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.3 | 2.1 | 2.1 | 0.81 | 0.81 | 0.99 | 1 | 0.81 | 0.81 | 0.99 | 1
0 | - | - | - | - | 24 | 2.1 | 2.1 | 2.2 | 2.3 | 2.2 | 2.5 | 2.2 | 2.1 | 0.87 | 0.9 | 1.16 | 1.13 | 0.87 | 0.9 | 1.16 | 1.13 | 0 | #VALUE! | #VALUE! | - | 24.5 | 2.1 | 2.1 | 2.4 | 2.5 | 2.4 | 2.6 | 2.4 | 2.1 | 0.93 | 0.93 | 1.08 | 1.08 | 0.93 | 0.93 | 1.08 | 1.08
0 | - | - | - | - | 25 | 2.1 | 2.1 | 2.5 | 2.5 | 2.7 | 2.8 | 2.6 | 2.1 | 1.06 | 0.86 | 1.13 | 1.28 | 1.06 | 0.86 | 1.13 | 1.28 | 0 | #VALUE! | #VALUE! | - | 25.5 | 2.1 | 2.2 | 2.6 | 2.5 | 2.8 | 2.8 | 2.7 | 2.1 | 1.02 | 0.77 | 0.77 | 1.02 | 1.02 | 0.77 | 0.77 | 1.02
0 | - | - | - | - | 26 | 2.1 | 2.4 | 2.5 | 2.6 | 2.8 | 2.8 | 2.9 | 2.2 | 1.12 | 0.73 | 1.05 | 1.38 | 1.12 | 0.73 | 1.05 | 1.38 | 0 | #VALUE! | #VALUE! | - | 26.5 | 2.1 | 2.5 | 2.4 | 2.6 | 2.8 | 2.8 | 2.8 | 2.2 | 1.21 | 0.8 | 1.04 | 1.39 | 1.21 | 0.8 | 1.04 | 1.39
0 | - | - | - | - | 27 | 2.1 | 2.6 | 2.3 | 2.7 | 2.9 | 2.9 | 2.9 | 2.2 | 0.98 | 0.73 | 1.04 | 1.47 | 0.98 | 0.73 | 1.04 | 1.47 | 0 | #VALUE! | #VALUE! | - | 27.5 | 2.1 | 2.6 | 2.3 | 2.7 | 3 | 3 | 3 | 2.3 | 0.74 | 0.79 | 1.05 | 1.53 | 0.74 | 0.79 | 1.05 | 1.53
0 | - | - | - | - | 28 | 2.1 | 2.6 | 2.3 | 2.8 | 3.1 | 3 | 3 | 2.4 | 1.31 | 0.86 | 1.01 | 1.48 | 1.31 | 0.86 | 1.01 | 1.48 | 0 | #VALUE! | #VALUE! | - | 28.5 | 2.1 | 2.6 | 2.3 | 2.7 | 3.1 | 3 | 3 | 2.6 | 1.24 | 0.79 | 1.08 | 1.52 | 1.24 | 0.79 | 1.08 | 1.52
0 | - | - | - | - | 29 | 2.3 | 2.6 | 2.3 | 2.8 | 3.1 | 3 | 3 | 2.7 | 1.48 | 1.01 | 0.91 | 1.39 | 1.48 | 1.01 | 0.91 | 1.39 | 0 | #VALUE! | #VALUE! | - | 29.5 | 2.5 | 2.4 | 2.4 | 3 | 3 | 3 | 3 | 2.8 | 0.59 | 0.88 | 0.91 | 1.02 | 0.59 | 0.88 | 0.91 | 1.02
0 | - | - | - | - | 30 | 2.7 | 2.3 | 2.6 | 3 | 3 | 3 | 3 | 3 | 1.44 | 1.09 | 0.69 | 1.12 | 1.44 | 1.09 | 0.69 | 1.12 | 0 | #VALUE! | #VALUE! | - | 30.5 | 2.9 | 2.4 | 2.8 | 3 | 3 | 3 | 3 | 3 | 1.1 | 0.77 | 0.59 | 0.85 | 1.1 | 0.77 | 0.59 | 0.85
0 | - | - | - | - | 31 | 3 | 2.6 | 2.9 | 2.9 | 3 | 3 | 3 | 3 | 1.3 | 1.05 | 0.68 | 0.96 | 1.3 | 1.05 | 0.68 | 0.96 | 0 | #VALUE! | #VALUE! | - | 31.5 | 2.9 | 2.8 | 2.8 | 2.9 | 3 | 3 | 3 | 3 | 1.01 | 0.96 | 0.68 | 0.75 | 1.01 | 0.96 | 0.68 | 0.75
0 | - | - | - | - | 32 | 3.1 | 2.9 | 2.8 | 3 | 2.8 | 3 | 3 | 3 | 1.09 | 1.11 | 0.82 | 0.8 | 1.09 | 1.11 | 0.82 | 0.8 | 0 | #VALUE! | #VALUE! | - | 32.5 | 3 | 2.9 | 2.8 | 3 | 2.7 | 3 | 3 | 3 | 0.93 | 1 | 0.82 | 0.73 | 0.93 | 1 | 0.82 | 0.73
0 | - | - | - | - | 33 | 3 | 2.9 | 2.9 | 3 | 2.5 | 2.9 | 3 | 3 | 1 | 1.18 | 0.93 | 0.69 | 1 | 1.18 | 0.93 | 0.69 | 0 | #VALUE! | #VALUE! | - | 33.5 | 3 | 2.9 | 3 | 3 | 2.3 | 2.4 | 3 | 3 | 0.77 | 0.99 | 0.79 | 0.59 | 0.77 | 0.99 | 0.79 | 0.59
0 | - | - | - | - | 34 | 3 | 2.9 | 3 | 2.8 | 2.1 | 2.1 | 2.7 | 3 | 1.01 | 1.03 | 1.07 | 1.05 | 1.01 | 1.03 | 1.07 | 1.05 | 0 | #VALUE! | #VALUE! | - | 34.5 | 3 | 3 | 3 | 2.8 | 2.1 | 2.1 | 2.5 | 2.9 | 1.22 | 1.18 | 1.03 | 1.07 | 1.22 | 1.18 | 1.03 | 1.07
0 | - | - | - | - | 35 | 3 | 3 | 3 | 2.6 | 2.1 | 2.1 | 2.3 | 2.7 | 1.13 | 1.11 | 1.08 | 1.1 | 1.13 | 1.11 | 1.08 | 1.1 | 0 | #VALUE! | #VALUE! | - | 35.5 | 3 | 3 | 3 | 2.6 | 2.1 | 2.1 | 2.2 | 2.6 | 0.9 | 1.07 | 1.03 | 0.83 | 0.9 | 1.07 | 1.03 | 0.83
0 | - | - | - | - | 36 | 3 | 3 | 3 | 2.6 | 2.2 | 2.1 | 2.1 | 2.4 | 1.21 | 1.11 | 1.15 | 1.25 | 1.21 | 1.11 | 1.15 | 1.25 | 0 | #VALUE! | #VALUE! | - | 36.5 | 3 | 3 | 3 | 2.6 | 2.2 | 2.1 | 2.1 | 2.3 | 1.21 | 1.19 | 1.1 | 1.11 | 1.21 | 1.19 | 1.1 | 1.11
0 | - | - | - | - | 37 | 3 | 3 | 3 | 2.6 | 2.2 | 2.1 | 2.1 | 2.3 | 1.2 | 1.15 | 1.15 | 1.2 | 1.2 | 1.15 | 1.15 | 1.2 | 0 | #VALUE! | #VALUE! | - | 37.5 | 3 | 3 | 3 | 2.6 | 2.2 | 2.1 | 2.1 | 2.3 | 0.91 | 1.04 | 0.93 | 0.78 | 0.91 | 1.04 | 0.93 | 0.78
0 | - | - | - | - | 38 | 3 | 3 | 3 | 2.6 | 2.2 | 2.1 | 2.1 | 2.3 | 1.1 | 1.29 | 1.19 | 0.98 | 1.1 | 1.29 | 1.19 | 0.98 | 0 | #VALUE! | #VALUE! | - | 38.5 | 3 | 3 | 3 | 2.6 | 2.1 | 2.1 | 2.1 | 2.4 | 1.03 | 0.85 | 0.82 | 1 | 1.03 | 0.85 | 0.82 | 1
0 | - | - | - | - | 39 | 3 | 3 | 3 | 2.6 | 2.1 | 2.1 | 2.2 | 2.4 | 1.1 | 1.06 | 1 | 1.06 | 1.1 | 1.06 | 1 | 1.06 | 0 | #VALUE! | #VALUE! | - | 39.5 | 3 | 3 | 3 | 2.6 | 2.1 | 2.1 | 2.2 | 2.4 | 1.17 | 1.25 | 1.21 | 1.13 | 1.17 | 1.25 | 1.21 | 1.13
0 | - | - | - | - | 40 | 3 | 3 | 3 | 2.6 | 2.1 | 2.1 | 2.2 | 2.4 | 1.1 | 1.17 | 1.18 | 1.1 | 1.1 | 1.17 | 1.18 | 1.1 | 0 | #VALUE! | #VALUE! | - | 40.5 | 3 | 3 | 3 | 2.6 | 2.1 | 2.1 | 2.1 | 2.4 | 1.06 | 1.24 | 1.19 | 0.99 | 1.06 | 1.24 | 1.19 | 0.99
0 | - | - | - | - | 41 | 3 | 2.7 | 2.7 | 2.5 | 2.1 | 2.1 | 2.1 | 2.3 | 1.15 | 1.24 | 1.23 | 1.13 | 1.15 | 1.24 | 1.23 | 1.13 | 0 | #VALUE! | #VALUE! | - | 41.5 | 3 | 2.7 | 2.7 | 2.5 | 2.1 | 2.1 | 2.1 | 2.3 | 1.15 | 1.27 | 1.16 | 1.02 | 1.15 | 1.27 | 1.16 | 1.02
0 | - | - | - | - | 42 | 3 | 2.7 | 2.7 | 2.3 | 2.1 | 2.1 | 2.1 | 2.3 | 1.09 | 1.2 | 1.16 | 1.03 | 1.09 | 1.2 | 1.16 | 1.03 | 0 | #VALUE! | #VALUE! | - | 42.5 | 2.8 | 2.6 | 2.6 | 2.3 | 2.1 | 2.1 | 2.1 | 2.3 | 1.06 | 1.22 | 1.17 | 1.01 | 1.06 | 1.22 | 1.17 | 1.01
0 | - | - | - | - | 43 | 2.6 | 2.5 | 2.4 | 2.3 | 2.1 | 2.1 | 2.1 | 2.3 | 1.19 | 1.28 | 1.16 | 1.07 | 1.19 | 1.28 | 1.16 | 1.07 | 0 | #VALUE! | #VALUE! | - | 43.5 | 2.6 | 2.4 | 2.5 | 2.3 | 2.1 | 2.1 | 2.1 | 2.3 | 1.15 | 1.19 | 1.12 | 1.08 | 1.15 | 1.19 | 1.12 | 1.08
0 | - | - | - | - | 44 | 2.5 | 2.5 | 2.5 | 2.5 | 2.1 | 2.1 | 2.1 | 2.3 | 1.08 | 1.18 | 1.15 | 1.04 | 1.08 | 1.18 | 1.15 | 1.04 | 0 | #VALUE! | #VALUE! | - | 44.5 | 2.5 | 2.7 | 2.7 | 2.5 | 2.1 | 2.1 | 2.1 | 2.2 | 1.19 | 1.17 | 1.08 | 1.11 | 1.19 | 1.17 | 1.08 | 1.11
0 | - | - | - | - | 45 | 2.5 | 2.6 | 2.7 | 2.6 | 2.2 | 2.1 | 2.1 | 2.1 | 1.11 | 1.14 | 1.11 | 1.08 | 1.11 | 1.14 | 1.11 | 1.08 | 0 | #VALUE! | #VALUE! | - | 45.5 | 2.7 | 2.7 | 2.9 | 2.6 | 2.2 | 2.2 | 2.1 | 2.2 | 1.14 | 1.18 | 1.14 | 1.1 | 1.14 | 1.18 | 1.14 | 1.1
0 | - | - | - | - | 46 | 2.7 | 2.8 | 2.9 | 2.6 | 2.3 | 2.2 | 2.1 | 2.2 | 1.18 | 1.21 | 1.14 | 1.1 | 1.18 | 1.21 | 1.14 | 1.1 | 0 | #VALUE! | #VALUE! | - | 46.5 | 2.8 | 2.9 | 3 | 2.6 | 2.3 | 2.3 | 2.2 | 2.3 | 1.11 | 1.23 | 1.16 | 1.03 | 1.11 | 1.23 | 1.16 | 1.03
0 | - | - | - | - | 47 | 2.8 | 3 | 3 | 2.6 | 2.2 | 2.3 | 2.2 | 2.3 | 1.07 | 1.2 | 1.16 | 1.03 | 1.07 | 1.2 | 1.16 | 1.03 | 0 | #VALUE! | #VALUE! | - | 47.5 | 2.9 | 3 | 3 | 2.6 | 2.1 | 2.3 | 2.2 | 2.3 | 1.17 | 1.2 | 1.1 | 1.07 | 1.17 | 1.2 | 1.1 | 1.07
0 | - | - | - | - | 48 | 2.9 | 3 | 3 | 2.6 | 2.1 | 2.1 | 2.4 | 2.3 | 1.09 | 1.22 | 1.19 | 1.06 | 1.09 | 1.22 | 1.19 | 1.06 | 0 | #VALUE! | #VALUE! | - | 48.5 | 3 | 3 | 3 | 2.6 | 2.2 | 2.2 | 2.3 | 2.3 | 1.12 | 1.22 | 1.23 | 1.15 | 1.12 | 1.22 | 1.23 | 1.15
0 | - | - | - | - | 49 | 3 | 3 | 3 | 2.6 | 2.5 | 2.4 | 2.2 | 2.4 | 1.09 | 1.19 | 1.26 | 1.18 | 1.09 | 1.19 | 1.26 | 1.18 | 0 | #VALUE! | #VALUE! | - | 49.5 | 3 | 3 | 3 | 2.6 | 2.6 | 2.7 | 2.4 | 2.4 | 1.12 | 1.21 | 1.18 | 1.09 | 1.12 | 1.21 | 1.18 | 1.09 |  | 0
0 | - | - | - | - | 50 | 3 | 3 | 3 | 2.6 | 2.7 | 2.7 | 2.3 | 2.3 | 1.13 | 1.09 | 1.15 | 1.18 | 1.13 | 1.09 | 1.15 | 1.18 | 0 | #VALUE! | #VALUE! | - | 50.5 | 3 | 3 | 3 | 2.6 | az | 2.9 | 2.5 | 2.3 | 1.08 | 1.06 | 1.06 | 1.08 | 1.08 | 1.06 | 1.06 | 1.08
0 | - | - | - | - | 51 | 3 | 3 | 3 | 2.5 | 2.4 | 2.8 | 2.7 | 2.4 | 1.16 | 1.14 | 1.08 | 1.11 | 1.16 | 1.14 | 1.08 | 1.11 | 0 | #VALUE! | #VALUE! | - | 51.5 | 3 | 3 | 3 | 2.5 | 2.4 | 2.8 | 2.6 | 2.4 | 1.18 | 1.14 | 1.11 | 1.15 | 1.18 | 1.14 | 1.11 | 1.15
0 | - | - | - | - | 52 | 3 | 3 | 2.9 | 2.4 | 2.4 | 2.7 | 2.5 | 2.4 | 1.11 | 1.12 | 1.14 | 1.12 | 1.11 | 1.12 | 1.14 | 1.12 | 0 | #VALUE! | #VALUE! | - | 52.5 | 3 | 3 | 2.9 | 2.4 | 2.4 | 2.5 | 2.3 | 2.6 | 1.11 | 1.12 | 1.15 | 1.14 | 1.11 | 1.12 | 1.15 | 1.14
0 | - | - | - | - | 53 | 3 | 3 | 2.9 | 2.4 | 2.4 | 2.4 | 2.3 | 2.8 | 1.11 | 1.14 | 1.18 | 1.16 | 1.11 | 1.14 | 1.18 | 1.16 | 0 | #VALUE! | #VALUE! | - | 53.5 | 3 | 3 | 3 | 2.5 | 2.4 | 2.4 | 2.4 | 2.9 | 1.11 | 1.02 | 0.96 | 1.05 | 1.11 | 1.02 | 0.96 | 1.05
0 | - | - | - | - | 54 | 3 | 3 | 3 | 2.5 | 2.4 | 2.4 | 2.4 | 3 | 1.11 | 1.06 | 1.05 | 1.09 | 1.11 | 1.06 | 1.05 | 1.09 | 0 | #VALUE! | #VALUE! | - | 54.5 | 3 | 3 | 3 | 2.5 | 2.4 | 2.4 | 2.4 | 2.9 | 1.1 | 1.08 | 1.06 | 1.09 | 1.1 | 1.08 | 1.06 | 1.09
0 | - | - | - | - | 55 | 3 | 3 | 3 | 2.6 | 2.5 | 2.5 | 2.4 | 2.8 | 1.08 | 1.08 | 1.09 | 1.09 | 1.08 | 1.08 | 1.09 | 1.09 | 0 | #VALUE! | #VALUE! | - | 55.5 | 3 | 3 | 2.8 | 2.8 | 2.5 | 2.4 | 2.4 | 2.8 | 1.08 | 1.06 | 1.09 | 1.12 | 1.08 | 1.06 | 1.09 | 1.12
0 | - | - | - | - | 56 | 3 | 2.9 | 2.7 | 2.7 | 2.7 | 2.4 | 2.4 | 2.7 | 1.08 | 1.06 | 1.09 | 1.11 | 1.08 | 1.06 | 1.09 | 1.11 | 0 | #VALUE! | #VALUE! | - | 56.5 | 3 | 2.7 | 2.5 | 2.8 | 2.9 | 2.4 | 2.4 | 2.8 | 1.08 | 1.03 | 1.06 | 1.09 | 1.08 | 1.03 | 1.06 | 1.09
0 | - | - | - | - | 57 | 2.8 | 2.7 | 2.4 | 2.7 | 3 | 2.8 | 2.4 | 2.8 | 1.08 | 1.03 | 1.06 | 1.11 | 1.08 | 1.03 | 1.06 | 1.11 | 0 | #VALUE! | #VALUE! | - | 57.5 | 2.8 | 2.6 | 2.6 | 2.7 | 3 | 2.9 | 2.6 | 2.8 | 1.08 | 1.03 | 1.05 | 1.09 | 1.08 | 1.03 | 1.05 | 1.09
0 | - | - | - | - | 58 | 2.7 | 2.6 | 2.7 | 2.8 | 2.9 | 3 | 2.8 | 2.7 | 1.11 | 1.04 | 1.09 | 1.16 | 1.11 | 1.04 | 1.09 | 1.16 | 0 | #VALUE! | #VALUE! | - | 58.5 | 2.4 | 2.5 | 2.8 | 2.7 | 2.8 | 3 | 2.9 | 2.6 | 1.11 | 1.06 | 1.11 | 1.15 | 1.11 | 1.06 | 1.11 | 1.15
0 | - | - | - | - | 59 | 2.4 | 2.7 | 2.9 | 2.7 | 2.6 | 3 | 3 | 2.6 | 1.11 | 1.07 | 1.11 | 1.15 | 1.11 | 1.07 | 1.11 | 1.15 | 0 | #VALUE! | #VALUE! | - | 59.5 | 2.5 | 2.8 | 3 | 2.6 | 2.4 | 2.7 | 3 | 2.5 | 1.11 | 1.08 | 1.11 | 1.14 | 1.11 | 1.08 | 1.11 | 1.14
0 | - | - | - | - | 60 | 2.7 | 3 | 3 | 2.6 | 2.4 | 2.6 | 2.9 | 2.7 | 1.09 | 1.08 | 1.11 | 1.12 | 1.09 | 1.08 | 1.11 | 1.12 | 0 | #VALUE! | #VALUE! | - | 60.5 | 2.8 | 3 | 3 | 2.7 | 2.5 | 2.5 | 2.8 | 2.7 | 1.11 | 1.09 | 1.11 | 1.12 | 1.11 | 1.09 | 1.11 | 1.12
0 | - | - | - | - | 61 | 3 | 3 | 3 | 2.6 | 2.5 | 2.5 | 2.6 | 2.9 | 1.11 | 1.09 | 1.11 | 1.11 | 1.11 | 1.09 | 1.11 | 1.11 | 0 | #VALUE! | #VALUE! | - | 61.5 | 3 | 3 | 3 | 2.6 | 2.5 | 2.6 | 2.4 | 2.8 | 1.11 | 1.09 | 1.11 | 1.12 | 1.11 | 1.09 | 1.11 | 1.12
0 | - | - | - | - | 62 | 3 | 3 | 3 | 2.8 | 2.5 | 2.6 | 2.4 | 2.8 | 1.11 | 1.08 | 1.12 | 1.14 | 1.11 | 1.08 | 1.12 | 1.14 | 0 | #VALUE! | #VALUE! | - | 62.5 | 3 | 3 | 3 | 2.8 | 2.7 | 2.6 | 2.4 | 2.8 | 1.11 | 1.08 | 1.11 | 1.14 | 1.11 | 1.08 | 1.11 | 1.14
0 | - | - | - | - | 63 | 3 | 3 | 3 | 2.8 | 2.7 | 2.6 | 2.4 | 2.8 | 1.09 | 1.11 | 1.12 | 1.12 | 1.09 | 1.11 | 1.12 | 1.12 | 0 | #VALUE! | #VALUE! | - | 63.5 | 3 | 3 | 3 | 2.9 | 2.9 | 2.7 | 2.4 | 2.8 | 1.09 | 1.12 | 1.14 | 1.11 | 1.09 | 1.12 | 1.14 | 1.11
0 | - | - | - | - | 64 | 3 | 3 | 3 | 3 | 3 | 2.8 | 2.4 | 2.8 | 1.11 | 1.14 | 1.14 | 1.09 | 1.11 | 1.14 | 1.14 | 1.09 | 0 | #VALUE! | #VALUE! | - | 64.5 | 3 | 3 | 3 | 3 | 3 | 2.9 | 2.7 | 2.8 | 1.11 | 1.15 | 1.15 | 1.11 | 1.11 | 1.15 | 1.15 | 1.11
0 | - | - | - | - | 65 | 3 | 3 | 3 | 3 | 3 | 2.9 | 2.8 | 2.8 | 1.12 | 1.18 | 1.16 | 1.11 | 1.12 | 1.18 | 1.16 | 1.11 | 0 | #VALUE! | #VALUE! | - | 65.5 | 3 | 3 | 3 | 3 | 3 | 3 | 2.9 | 2.9 | 1.09 | 1.15 | 1.15 | 1.09 | 1.09 | 1.15 | 1.15 | 1.09
0 | - | - | - | - | 66 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 1.09 | 1.12 | 1.15 | 1.11 | 1.09 | 1.12 | 1.15 | 1.11 | 0 | #VALUE! | #VALUE! | - | 66.5 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 1.13 | 1.11 | 1.09 | 1.12 | 1.13 | 1.11 | 1.09 | 1.12
0 | - | - | - | - | 67 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 1.15 | 1.11 | 1.08 | 1.12 | 1.15 | 1.11 | 1.08 | 1.12 | 0 | #VALUE! | #VALUE! | - | 67.5 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 1.15 | 1.11 | 1.06 | 1.12 | 1.15 | 1.11 | 1.06 | 1.12
0 | - | - | - | - | 68 | 3 | 3 | 3 | 2.8 | 3 | 3 | 3 | 3 | 1.12 | 1.12 | 1.09 | 1.08 | 1.12 | 1.12 | 1.09 | 1.08 | 0 | #VALUE! | #VALUE! | - | 68.5 | 3 | 2.9 | 2.6 | 2.7 | 3 | 3 | 3 | 3 | 1.12 | 1.1 | 1.08 | 1.09 | 1.12 | 1.1 | 1.08 | 1.09
0 | - | - | - | - | 69 | 3 | 2.8 | 2.8 | 2.8 | 2.9 | 3 | 3 | 3 | 1.12 | 1.09 | 1.05 | 1.07 | 1.12 | 1.09 | 1.05 | 1.07 | 0 | #VALUE! | #VALUE! | - | 69.5 | 2.9 | 2.7 | 2.7 | 2.5 | 2.8 | 3 | 3 | 3 | 1.12 | 1.09 | 1.02 | 1.05 | 1.12 | 1.09 | 1.02 | 1.05
0 | - | - | - | - | 70 | 2.7 | 2.6 | 2.6 | 2.6 | 2.7 | 2.9 | 3 | 3 | 1.1 | 1.12 | 1.06 | 1.03 | 1.1 | 1.12 | 1.06 | 1.03 | 0 | #VALUE! | #VALUE! | - | 70.5 | 2.7 | 2.6 | 2.6 | 2.6 | 2.7 | 2.8 | 2.9 | 2.9 | 1.1 | 1.12 | 1.1 | 1.08 | 1.1 | 1.12 | 1.1 | 1.08
0 | - | - | - | - | 71 | 2.7 | 2.6 | 2.6 | 2.6 | 2.6 | 2.7 | 2.8 | 2.7 | 1.1 | 1.09 | 1.12 | 1.15 | 1.1 | 1.09 | 1.12 | 1.15 | 0 | #VALUE! | #VALUE! | - | 71.5 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.7 | 2.7 | 2.7 | 1.13 | 1.11 | 1.09 | 1.13 | 1.13 | 1.11 | 1.09 | 1.13
0 | - | - | - | - | 72 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.8 | 2.8 | 2.6 | 1.13 | 1.11 | 1.09 | 1.12 | 1.13 | 1.11 | 1.09 | 1.12 | 0 | #VALUE! | #VALUE! | - | 72.5 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.7 | 2.7 | 2.6 | 1.13 | 1.11 | 1.09 | 1.12 | 1.13 | 1.11 | 1.09 | 1.12
0 | - | - | - | - | 73 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 1.12 | 1.08 | 1.12 | 1.15 | 1.12 | 1.08 | 1.12 | 1.15 | 0 | #VALUE! | #VALUE! | - | 73.5 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 1.08 | 1.12 | 1.15 | 1.12 | 1.08 | 1.12 | 1.15 | 1.12
0 | - | - | - | - | 74 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 1.11 | 1.12 | 1.15 | 1.14 | 1.11 | 1.12 | 1.15 | 1.14 | 0 | #VALUE! | #VALUE! | - | 74.5 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 1.08 | 1.15 | 1.13 | 1.06 | 1.08 | 1.15 | 1.13 | 1.06
0 | - | - | - | - | 75 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 1.09 | 1.13 | 1.12 | 1.06 | 1.09 | 1.13 | 1.12 | 1.06 | 0 | #VALUE! | #VALUE! | - | 75.5 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 1.09 | 1.13 | 1.12 | 1.08 | 1.09 | 1.13 | 1.12 | 1.08
0 | - | - | - | - | 76 | 2.6 | 2.6 | 2.8 | 2.6 | 2.5 | 2.6 | 2.6 | 2.6 | 1.09 | 1.13 | 1.11 | 1.08 | 1.09 | 1.13 | 1.11 | 1.08 | 0 | #VALUE! | #VALUE! | - | 76.5 | 2.6 | 2.6 | 2.8 | 2.4 | 2.4 | 2.6 | 2.6 | 2.6 | 1.09 | 1.12 | 1.12 | 1.08 | 1.09 | 1.12 | 1.12 | 1.08
0 | - | - | - | - | 77 | 2.6 | 2.7 | 2.3 | 2.2 | 2.2 | 2.5 | 2.6 | 2.6 | 1.08 | 1.12 | 1.12 | 1.09 | 1.08 | 1.12 | 1.12 | 1.09 | 0 | #VALUE! | #VALUE! | - | 77.5 | 2.6 | 2.7 | 2.4 | 2.1 | 2.1 | 2.3 | 2.6 | 2.6 | 1.08 | 1.11 | 1.12 | 1.11 | 1.08 | 1.11 | 1.12 | 1.11
0 | - | - | - | - | 78 | 2.7 | 2.7 | 2.1 | 2.1 | 2.1 | 2.1 | 2.5 | 2.6 | 1.08 | 1.09 | 1.13 | 1.11 | 1.08 | 1.09 | 1.13 | 1.11 | 0 | #VALUE! | #VALUE! | - | 78.5 | 2.6 | 2.3 | 2.2 | 2.1 | 2.1 | 2.1 | 2.4 | 2.7 | 1.08 | 1.09 | 1.13 | 1.12 | 1.08 | 1.09 | 1.13 | 1.12
0 | - | - | - | - | 79 | 2.5 | 2.4 | 2.3 | 2.1 | 2.1 | 2.1 | 2.2 | 2.7 | 1.08 | 1.09 | 1.13 | 1.12 | 1.08 | 1.09 | 1.13 | 1.12 | 0 | #VALUE! | #VALUE! | - | 79.5 | 2.4 | 2.4 | 2.3 | 2.1 | 2.1 | 2.1 | 2.1 | 2.4 | 1.06 | 1.09 | 1.13 | 1.11 | 1.06 | 1.09 | 1.13 | 1.11
0 | - | - | - | - | 80 | 2.2 | 2.3 | 2.3 | 2.2 | 2.1 | 2.1 | 2.1 | 2.1 | 1.08 | 1.11 | 1.12 | 1.11 | 1.08 | 1.11 | 1.12 | 1.11 | 0 | #VALUE! | #VALUE! | - | 80.5 | 2.2 | 2.2 | 2.3 | 2.6 | 2.1 | 2.1 | 2.1 | 2.1 | 1.11 | 1.11 | 1.12 | 1.11 | 1.11 | 1.11 | 1.12 | 1.11
0 | - | - | - | - | 81 | 2.2 | 2.3 | 2.4 | 2.6 | 2.1 | 2.1 | 2.1 | 2.1 | 1.16 | 1.16 | 1.11 | 1.11 | 1.16 | 1.16 | 1.11 | 1.11 | 0 | #VALUE! | #VALUE! | - | 81.5 | 2.2 | 2.3 | 2.6 | 2.8 | 2.3 | 2.1 | 2.1 | 2.1 | 1.15 | 1.14 | 1.08 | 1.09 | 1.15 | 1.14 | 1.08 | 1.09
0 | - | - | - | - | 82 | 2.2 | 2.6 | 2.7 | 2.7 | 2.4 | 2.1 | 2.1 | 2.1 | 1.14 | 1.12 | 1.08 | 1.09 | 1.14 | 1.12 | 1.08 | 1.09 | 0 | #VALUE! | #VALUE! | - | 82.5 | 2.3 | 2.7 | 2.7 | 2.7 | 2.7 | 2.1 | 2.1 | 2.1 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11
0 | - | - | - | - | 83 | 2.5 | 2.6 | 2.7 | 2.7 | 2.8 | 2.4 | 2.1 | 2.1 | 1.11 | 1.11 | 1.11 | 1.09 | 1.11 | 1.11 | 1.11 | 1.09 | 0 | #VALUE! | #VALUE! | - | 83.5 | 2.6 | 2.5 | 2.5 | 2.4 | 2.7 | 2.7 | 2.3 | 2.4 | 1.11 | 1.11 | 1.11 | 1.09 | 1.11 | 1.11 | 1.11 | 1.09
0 | - | - | - | - | 84 | 2.6 | 2.5 | 2.4 | 2.2 | 2.6 | 2.6 | 2.6 | 2.5 | 1.09 | 1.09 | 1.11 | 1.11 | 1.09 | 1.09 | 1.11 | 1.11 | 0 | #VALUE! | #VALUE! | - | 84.5 | 2.6 | 2.4 | 2.2 | 2.1 | 2.2 | 2.5 | 2.8 | 2.8 | 1.11 | 1.09 | 1.09 | 1.11 | 1.11 | 1.09 | 1.09 | 1.11
0 | - | - | - | - | 85 | 2.5 | 2.2 | 2.1 | 2.1 | 2.1 | 2.3 | 2.7 | 2.7 | 1.11 | 1.12 | 1.09 | 1.08 | 1.11 | 1.12 | 1.09 | 1.08 | 0 | #VALUE! | #VALUE! | - | 85.5 | 2.4 | 2.2 | 2.1 | 2.1 | 2.1 | 2.1 | 2.5 | 2.6 | 1.12 | 1.12 | 1.08 | 1.08 | 1.12 | 1.12 | 1.08 | 1.08
0 | - | - | - | - | 86 | 2.2 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.3 | 2.4 | 1.14 | 1.12 | 1.06 | 1.08 | 1.14 | 1.12 | 1.06 | 1.08 | 0 | #VALUE! | #VALUE! | - | 86.5 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.2 | 2.3 | 1.14 | 1.12 | 1.08 | 1.09 | 1.14 | 1.12 | 1.08 | 1.09
0 | - | - | - | - | 87 | 2.1 | 2.1 | 2.2 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 1.12 | 1.12 | 1.09 | 1.09 | 1.12 | 1.12 | 1.09 | 1.09 | 0 | #VALUE! | #VALUE! | - | 87.5 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 1.12 | 1.11 | 1.09 | 1.11 | 1.12 | 1.11 | 1.09 | 1.11
0 | - | - | - | - | 88 | 2.1 | 2.2 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 1.09 | 1.11 | 1.11 | 1.11 | 1.09 | 1.11 | 1.11 | 1.11 | 0 | #VALUE! | #VALUE! | - | 88.5 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 1.09 | 1.11 | 1.11 | 1.11 | 1.09 | 1.11 | 1.11 | 1.11
0 | - | - | - | - | 89 | 2.2 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 1.11 | 1.09 | 1.09 | 1.11 | 1.11 | 1.09 | 1.09 | 1.11 | 0 | #VALUE! | #VALUE! | - | 89.5 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 1.12 | 1.09 | 1.09 | 1.12 | 1.12 | 1.09 | 1.09 | 1.12
0 | - | - | - | - | 90 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 1.12 | 1.08 | 1.1 | 1.12 | 1.12 | 1.08 | 1.1 | 1.12 | 0 | #VALUE! | #VALUE! | - | 90.5 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 1.12 | 1.08 | 1.1 | 1.14 | 1.12 | 1.08 | 1.1 | 1.14
0 | - | - | - | - | 91 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 1.11 | 1.08 | 1.11 | 1.12 | 1.11 | 1.08 | 1.11 | 1.12 | 0 | #VALUE! | #VALUE! | - | 91.5 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 1.11 | 1.1 | 1.11 | 1.12 | 1.11 | 1.1 | 1.11 | 1.12
0 | - | - | - | - | 92 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 1.11 | 1.1 | 1.11 | 1.13 | 1.11 | 1.1 | 1.11 | 1.13 | 0 | #VALUE! | #VALUE! | - | 92.5 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 1.11 | 1.1 | 1.11 | 1.13 | 1.11 | 1.1 | 1.11 | 1.13
0 | - | - | - | - | 93 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 1.08 | 1.1 | 1.15 | 1.13 | 1.08 | 1.1 | 1.15 | 1.13 | 0 | #VALUE! | #VALUE! | - | 93.5 | 2.1 | 2.1 | 2.1 | 2.1 | 2.2 | 2.1 | 2.1 | 2.1 | 1.07 | 1.1 | 1.15 | 1.12 | 1.07 | 1.1 | 1.15 | 1.12
0 | - | - | - | - | 94 | 2.1 | 2.1 | 2.2 | 2.1 | 2.2 | 2.1 | 2.1 | 2.1 | 1.07 | 1.11 | 1.17 | 1.12 | 1.07 | 1.11 | 1.17 | 1.12 | 0 | #VALUE! | #VALUE! | - | 94.5 | 2.1 | 2.1 | 2.3 | 2.1 | 2.1 | 2.2 | 2.1 | 2.1 | 1.08 | 1.1 | 1.14 | 1.14 | 1.08 | 1.1 | 1.14 | 1.14
0 | - | - | - | - | 95 | 2.1 | 2.2 | 2.2 | 2.1 | 2.1 | 2.1 | 2.2 | 2.1 | 1.11 | 1.11 | 1.12 | 1.11 | 1.11 | 1.11 | 1.12 | 1.11 | 0 | #VALUE! | #VALUE! | - | 95.5 | 2.1 | 2.2 | 2.2 | 2.1 | 2.1 | 2.1 | 2.2 | 2.1 | 1.08 | 1.15 | 1.17 | 1.1 | 1.08 | 1.15 | 1.17 | 1.1
0 | - | - | - | - | 96 | 2.2 | 2.2 | 2.1 | 2.2 | 2.1 | 2.1 | 2.2 | 2.1 | 1.18 | 1.14 | 1.07 | 1.11 | 1.18 | 1.14 | 1.07 | 1.11 | 0 | #VALUE! | #VALUE! | - | 96.5 | 2.3 | 2.1 | 2.1 | 2.3 | 2.2 | 2.1 | 2.1 | 2.1 | 1.14 | 1.12 | 1.07 | 1.08 | 1.14 | 1.12 | 1.07 | 1.08
0 | - | - | - | - | 97 | 2.2 | 2.1 | 2.2 | 2.2 | 2.3 | 2.1 | 2.1 | 2.2 | 1.11 | 1.11 | 1.08 | 1.09 | 1.11 | 1.11 | 1.08 | 1.09 | 0 | #VALUE! | #VALUE! | - | 97.5 | 2.1 | 2.1 | 2.3 | 2.2 | 2.3 | 2.1 | 2.1 | 2.1 | 1.11 | 1.11 | 1.08 | 1.09 | 1.11 | 1.11 | 1.08 | 1.09
0 | - | - | - | - | 98 | 2.1 | 2.2 | 2.3 | 2.1 | 2.2 | 2.3 | 2.2 | 2.1 | 1.12 | 1.11 | 1.08 | 1.09 | 1.12 | 1.11 | 1.08 | 1.09 | 0 | #VALUE! | #VALUE! | - | 98.5 | 2.2 | 2.2 | 2.3 | 2.1 | 2.1 | 2.3 | 2.2 | 2.2 | 1.12 | 1.08 | 1.08 | 1.12 | 1.12 | 1.08 | 1.08 | 1.12
0 | - | - | - | - | 99 | 2.2 | 2.2 | 2.2 | 2.1 | 2.1 | 2.2 | 2.3 | 2.3 | 1.11 | 1.07 | 1.1 | 1.14 | 1.11 | 1.07 | 1.1 | 1.14 | 0 | #VALUE! | #VALUE! | - | 99.5 | 2.2 | 2.2 | 2.2 | 2.1 | 2.1 | 2.1 | 2.3 | 2.2 | 1.11 | 1.07 | 1.11 | 1.14 | 1.11 | 1.07 | 1.11 | 1.14
0 | - | - | - | - | 100 | 2.2 | 2.2 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.3 | 1.11 | 1.07 | 1.1 | 1.14 | 1.11 | 1.07 | 1.1 | 1.14 | 0 | #VALUE! | #VALUE! | - | 100.5 | 2.2 | 2.2 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.3 | 1.11 | 1.07 | 1.1 | 1.14 | 1.11 | 1.07 | 1.1 | 1.14
0 | - | - | - | - | 101 | 2.2 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.2 | 1.11 | 1.08 | 1.08 | 1.13 | 1.11 | 1.08 | 1.08 | 1.13 | 0 | #VALUE! | #VALUE! | - | 101.5 | 2.2 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 1.11 | 1.08 | 1.08 | 1.13 | 1.11 | 1.08 | 1.08 | 1.13
0 | - | - | - | - | 102 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 1.11 | 1.08 | 1.08 | 1.13 | 1.11 | 1.08 | 1.08 | 1.13 | 0 | #VALUE! | #VALUE! | - | 102.5 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 1.11 | 1.08 | 1.08 | 1.11 | 1.11 | 1.08 | 1.08 | 1.11
0 | - | - | - | - | 103 | 2.1 | 2.1 | 2.1 | 2.2 | 2.1 | 2.2 | 2.1 | 2.1 | 1.07 | 1.04 | 1.1 | 1.11 | 1.07 | 1.04 | 1.1 | 1.11 | 0 | #VALUE! | #VALUE! | - | 103.5 | 2.1 | 2.1 | 2.1 | 2.2 | 2.2 | 2.1 | 2.1 | 2.1 | 1.11 | 1.04 | 1.04 | 1.11 | 1.11 | 1.04 | 1.04 | 1.11
0 | - | - | - | - | 104 | 2.1 | 2.1 | 2.1 | 2.2 | 2.2 | 2.1 | 2.1 | 2.1 | 1.11 | 1.04 | 1.04 | 1.1 | 1.11 | 1.04 | 1.04 | 1.1 | 0 | #VALUE! | #VALUE! | - | 104.5 | 2.1 | 2.2 | 2.2 | 2.2 | 2.3 | 2.1 | 2.1 | 2.1 | 1.1 | 1.04 | 1.03 | 1.08 | 1.1 | 1.04 | 1.03 | 1.08
0 | - | - | - | - | 105 | 2.1 | 2.2 | 2.3 | 2.3 | 2.3 | 2.2 | 2.1 | 2.1 | 1.1 | 1.07 | 1.03 | 1.05 | 1.1 | 1.07 | 1.03 | 1.05 | 0 | #VALUE! | #VALUE! | - | 105.5 | 2.2 | 2.4 | 2.6 | 2.5 | 2.5 | 2.2 | 2.2 | 2.1 | 1.08 | 1.08 | 0.98 | 0.98 | 1.08 | 1.08 | 0.98 | 0.98
0 | - | - | - | - | 106 | 2.2 | 2.5 | 2.7 | 2.6 | 2.6 | 2.3 | 2.1 | 2.1 | 1.17 | 1.17 | 1.09 | 1.09 | 1.17 | 1.17 | 1.09 | 1.09 | 0 | #VALUE! | #VALUE! | - | 106.5 | 2.4 | 2.9 | 2.6 | 2.6 | 2.7 | 2.6 | 2.1 | 2.1 | 0.99 | 0.94 | 1.07 | 1.1 | 0.99 | 0.94 | 1.07 | 1.1
0 | - | - | - | - | 107 | 2.7 | 2.9 | 2.6 | 2.6 | 2.9 | 2.6 | 2.3 | 2.2 | 1.12 | 1.22 | 1.07 | 0.96 | 1.12 | 1.22 | 1.07 | 0.96 | 0 | #VALUE! | #VALUE! | - | 107.5 | 2.9 | 2.9 | 2.6 | 2.6 | 2.9 | 2.6 | 2.4 | 2.4 | 1.16 | 1.18 | 1.13 | 1.13 | 1.16 | 1.18 | 1.13 | 1.13
0 | - | - | - | - | 108 | 2.9 | 2.9 | 2.7 | 2.7 | 2.9 | 2.7 | 2.5 | 2.7 | 1.02 | 1.19 | 1.19 | 1.02 | 1.02 | 1.19 | 1.19 | 1.02 | 0 | #VALUE! | #VALUE! | - | 108.5 | 2.8 | 3 | 2.8 | 2.8 | 3 | 2.8 | 2.6 | 2.8 | 1.08 | 1.02 | 1.11 | 1.17 | 1.08 | 1.02 | 1.11 | 1.17
0 | - | - | - | - | 109 | 2.9 | 3 | 2.9 | 2.9 | 3 | 3 | 2.7 | 2.8 | 1.16 | 1.24 | 1.17 | 1.08 | 1.16 | 1.24 | 1.17 | 1.08 | 0 | #VALUE! | #VALUE! | - | 109.5 | 3 | 3 | 3 | 3 | 3 | 3 | 2.8 | 2.8 | 1.15 | 1.25 | 1.38 | 1.28 | 1.15 | 1.25 | 1.38 | 1.28
0 | - | - | - | - | 110 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2.9 | 0.98 | 1.3 | 1.7 | 1.54 | 0.98 | 1.3 | 1.7 | 1.54 | 0 | #VALUE! | #VALUE! | - | 110.5 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2.9 | 0.92 | 1.34 | 1.67 | 1.35 | 0.92 | 1.34 | 1.67 | 1.35
0 | - | - | - | - | 111 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 1.35 | 1.41 | 1.62 | 1.57 | 1.35 | 1.41 | 1.62 | 1.57 | 0 | #VALUE! | #VALUE! | - | 111.5 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 1.47 | 1.47 | 1.22 | 1.2 | 1.47 | 1.47 | 1.22 | 1.2
0 | - | - | - | - | 112 | 3 | 3 | 2.8 | 2.8 | 3 | 3 | 3 | 3 | 1.7 | 1.7 | 1.45 | 1.57 | 1.7 | 1.7 | 1.45 | 1.57 | 0 | #VALUE! | #VALUE! | - | 112.5 | 3 | 3 | 2.6 | 2.8 | 3 | 3 | 3 | 3 | 1.21 | 1.02 | 0.82 | 1.04 | 1.21 | 1.02 | 0.82 | 1.04
0 | - | - | - | - | 113 | 3 | 2.8 | 2.7 | 2.8 | 2.9 | 3 | 3 | 3 | 1.11 | 1.25 | 1.46 | 1.35 | 1.11 | 1.25 | 1.46 | 1.35 | 0 | #VALUE! | #VALUE! | - | 113.5 | 3 | 2.5 | 2.6 | 3 | 3 | 3 | 3 | 3 | 0.71 | 0.92 | 1.05 | 0.88 | 0.71 | 0.92 | 1.05 | 0.88
0 | - | - | - | - | 114 | 2.5 | 2.7 | 2.8 | 2.9 | 2.9 | 2.9 | 2.9 | 2.8 | 0.93 | 1.17 | 1.47 | 1.29 | 0.93 | 1.17 | 1.47 | 1.29 | 0 | #VALUE! | #VALUE! | - | 114.5 | 2.5 | 2.7 | 2.7 | 2.8 | 2.8 | 3 | 2.9 | 2.7 | 1.15 | 1 | 1.38 | 1.49 | 1.15 | 1 | 1.38 | 1.49
0 | - | - | - | - | 115 | 2.7 | 2.7 | 2.8 | 2.7 | 2.9 | 3 | 2.8 | 2.7 | 1.36 | 1.05 | 1.03 | 1.36 | 1.36 | 1.05 | 1.03 | 1.36 | 0 | #VALUE! | #VALUE! | - | 115.5 | 2.7 | 2.7 | 2.7 | 2.8 | 2.9 | 3 | 2.9 | 2.8 | 1.3 | 1.03 | 0.87 | 1.19 | 1.3 | 1.03 | 0.87 | 1.19
0 | - | - | - | - | 116 | 2.6 | 2.7 | 2.7 | 2.7 | 2.8 | 2.9 | 2.9 | 2.8 | 1.3 | 1.13 | 0.9 | 1.11 | 1.3 | 1.13 | 0.9 | 1.11 | 0 | #VALUE! | #VALUE! | - | 116.5 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.9 | 2.8 | 1.06 | 0.96 | 0.75 | 0.88 | 1.06 | 0.96 | 0.75 | 0.88
0 | - | - | - | - | 117 | 2.7 | 2.7 | 2.8 | 2.7 | 2.7 | 2.7 | 2.9 | 2.8 | 1.13 | 1.02 | 0.89 | 1.02 | 1.13 | 1.02 | 0.89 | 1.02 | 0 | #VALUE! | #VALUE! | - | 117.5 | 2.7 | 2.7 | 2.9 | 2.8 | 2.7 | 2.7 | 2.7 | 2.7 | 1.02 | 0.96 | 0.74 | 0.81 | 1.02 | 0.96 | 0.74 | 0.81
0 | - | - | - | - | 118 | 2.7 | 2.9 | 2.8 | 2.8 | 2.7 | 2.7 | 2.5 | 2.5 | 1.45 | 1.25 | 1.03 | 1.25 | 1.45 | 1.25 | 1.03 | 1.25 | 0 | #VALUE! | #VALUE! | - | 118.5 | 2.7 | 2.9 | 2.9 | 2.7 | 2.5 | 2.5 | 2.6 | 2.5 | 0.99 | 1.02 | 0.81 | 0.78 | 0.99 | 1.02 | 0.81 | 0.78
0 | - | - | - | - | 119 | 2.8 | 2.8 | 2.9 | 2.6 | 2.5 | 2.5 | 2.5 | 2.5 | 1.41 | 1.24 | 0.97 | 1.18 | 1.41 | 1.24 | 0.97 | 1.18 | 0 | #VALUE! | #VALUE! | - | 119.5 | 2.8 | 2.9 | 2.9 | 2.6 | 2.5 | 2.5 | 2.5 | 2.5 | 0.94 | 0.95 | 0.81 | 0.79 | 0.94 | 0.95 | 0.81 | 0.79
0 | - | - | - | - | 120 | 2.7 | 2.9 | 2.9 | 2.7 | 2.6 | 2.6 | 2.6 | 2.6 | 1.29 | 1.04 | 0.68 | 1.02 | 1.29 | 1.04 | 0.68 | 1.02 | 0 | #VALUE! | #VALUE! | - | 120.5 | 2.7 | 2.9 | 2.9 | 2.6 | 2.6 | 2.5 | 2.5 | 2.5 | 1.24 | 1.01 | 0.7 | 0.98 | 1.24 | 1.01 | 0.7 | 0.98
0 | - | - | - | - | 121 | 2.7 | 2.9 | 2.9 | 2.7 | 2.6 | 2.6 | 2.5 | 2.4 | 1.19 | 0.91 | 0.84 | 1.15 | 1.19 | 0.91 | 0.84 | 1.15 | 0 | #VALUE! | #VALUE! | - | 121.5 | 2.7 | 2.9 | 2.7 | 2.6 | 2.6 | 2.5 | 2.4 | 2.4 | 0.82 | 0.85 | 0.91 | 0.88 | 0.82 | 0.85 | 0.91 | 0.88
0 | - | - | - | - | 122 | 2.7 | 2.7 | 2.9 | 2.5 | 2.5 | 2.4 | 2.4 | 2.4 | 1.28 | 0.98 | 1.07 | 1.35 | 1.28 | 0.98 | 1.07 | 1.35 | 0 | #VALUE! | #VALUE! | - | 122.5 | 2.6 | 2.8 | 2.9 | 2.6 | 2.6 | 2.4 | 2.4 | 2.4 | 1.18 | 1.01 | 0.98 | 1.15 | 1.18 | 1.01 | 0.98 | 1.15
0 | - | - | - | - | 123 | 2.7 | 2.9 | 2.9 | 2.5 | 2.5 | 2.4 | 2.4 | 2.4 | 1 | 1.04 | 1.18 | 1.14 | 1 | 1.04 | 1.18 | 1.14 | 0 | #VALUE! | #VALUE! | - | 123.5 | 2.7 | 3 | 2.9 | 2.7 | 2.7 | 2.4 | 2.4 | 2.4 | 0.87 | 0.8 | 1.04 | 1.1 | 0.87 | 0.8 | 1.04 | 1.1
0 | - | - | - | - | 124 | 2.8 | 3 | 2.9 | 2.7 | 2.7 | 2.5 | 2.4 | 2.4 | 0.98 | 0.7 | 1.06 | 1.31 | 0.98 | 0.7 | 1.06 | 1.31 | 0 | #VALUE! | #VALUE! | - | 124.5 | 2.9 | 3 | 2.9 | 2.8 | 2.8 | 2.6 | 2.5 | 2.5 | 0.76 | 0.67 | 0.94 | 1.03 | 0.76 | 0.67 | 0.94 | 1.03
0 | - | - | - | - | 125 | 2.9 | 3 | 2.9 | 2.8 | 2.8 | 2.5 | 2.5 | 2.5 | 0.81 | 0.76 | 1.1 | 1.16 | 0.81 | 0.76 | 1.1 | 1.16 | 0 | #VALUE! | #VALUE! | - | 125.5 | 3 | 3 | 2.9 | 2.9 | 2.9 | 2.6 | 2.5 | 2.6 | 0.7 | 0.94 | 1.1 | 0.59 | 0.7 | 0.94 | 1.1 | 0.59
0 | - | - | - | - | 126 | 3 | 3 | 2.9 | 2.9 | 3 | 2.7 | 2.6 | 2.7 | 0.73 | 0.88 | 1.17 | 0.66 | 0.73 | 0.88 | 1.17 | 0.66 | 0 | #VALUE! | #VALUE! | - | 126.5 | 3 | 3 | 3 | 3 | 3 | 2.9 | 2.6 | 2.6 | 0.76 | 0.59 | 0.77 | 0.97 | 0.76 | 0.59 | 0.77 | 0.97
0 | - | - | - | - | 127 | 2.9 | 3 | 3 | 3 | 3 | 3 | 2.7 | 2.7 | 1.3 | 0.88 | 1.22 | 1.57 | 1.3 | 0.88 | 1.22 | 1.57 | 0 | #VALUE! | #VALUE! | - | 127.5 | 2.9 | 3 | 3 | 3 | 3 | 3 | 2.9 | 2.8 | 1.23 | 0.66 | 0.69 | 0.89 | 1.23 | 0.66 | 0.69 | 0.89
0 | - | - | - | - | 128 | 2.8 | 3 | 3 | 3 | 3 | 3 | 3 | 2.8 | 1.31 | 1.05 | 0.88 | 1.18 | 1.31 | 1.05 | 0.88 | 1.18 | 0 | #VALUE! | #VALUE! | - | 128.5 | 2.9 | 3 | 3 | 3 | 2.9 | 3 | 3 | 3 | 1.22 | 1 | 1.09 | 1.29 | 1.22 | 1 | 1.09 | 1.29
0 | - | - | - | - | 129 | 3 | 3 | 3 | 3 | 2.9 | 2.9 | 3 | 3 | 1.17 | 1.03 | 1.17 | 1.29 | 1.17 | 1.03 | 1.17 | 1.29 | 0 | #VALUE! | #VALUE! | - | 129.5 | 3 | 3 | 3 | 3 | 3 | 2.7 | 3 | 3 | 1.03 | 1.07 | 1.17 | 1.14 | 1.03 | 1.07 | 1.17 | 1.14
0 | - | - | - | - | 130 | 3 | 3 | 3 | 3 | 3 | 2.6 | 3 | 3 | 1.1 | 1.13 | 1.23 | 1.2 | 1.1 | 1.13 | 1.23 | 1.2 | 0 | #VALUE! | #VALUE! | - | 130.5 | 3 | 3 | 3 | 3 | 3 | 2.7 | 2.8 | 3 | 0.83 | 1.05 | 1.27 | 1.1 | 0.83 | 1.05 | 1.27 | 1.1
0 | - | - | - | - | 131 | 3 | 3 | 3 | 3 | 3 | 2.9 | 2.6 | 3 | 1.04 | 1.04 | 1.18 | 1.17 | 1.04 | 1.04 | 1.18 | 1.17 | 0 | #VALUE! | #VALUE! | - | 131.5 | 3 | 3 | 3 | 3 | 3 | 3 | 2.7 | 2.9 | 1.11 | 1.23 | 1.16 | 1.03 | 1.11 | 1.23 | 1.16 | 1.03
0 | - | - | - | - | 132 | 3 | 3 | 3 | 3 | 3 | 2.9 | 2.9 | 2.7 | 1.31 | 1 | 1.1 | 1.39 | 1.31 | 1 | 1.1 | 1.39 | 0 | #VALUE! | #VALUE! | - | 132.5 | 3 | 3 | 3 | 3.1 | 3 | 2.9 | 2.9 | 2.8 | 1.1 | 0.88 | 0.93 | 1.12 | 1.1 | 0.88 | 0.93 | 1.12
0 | - | - | - | - | 133 | 3 | 3 | 3 | 3.1 | 3 | 2.9 | 2.9 | 2.9 | 1.09 | 0.87 | 0.87 | 1.09 | 1.09 | 0.87 | 0.87 | 1.09 | 0 | #VALUE! | #VALUE! | - | 133.5 | 3 | 3 | 3 | 3.1 | 3 | 3 | 3 | 3 | 0.74 | 1.05 | 1.13 | 0.84 | 0.74 | 1.05 | 1.13 | 0.84
0 | - | - | - | - | 134 | 3 | 3 | 3.1 | 3.1 | 3 | 3 | 3 | 3 | 1.04 | 1.4 | 1.38 | 1.03 | 1.04 | 1.4 | 1.38 | 1.03 | 0 | #VALUE! | #VALUE! | - | 134.5 | 3 | 3 | 3.1 | 3.1 | 3 | 3 | 3 | 3 | 1.13 | 1.28 | 1.28 | 1.13 | 1.13 | 1.28 | 1.28 | 1.13
0 | - | - | - | - | 135 | 3 | 3 | 3.1 | 3.1 | 3 | 3 | 3 | 3 | 1.2 | 1.29 | 1.26 | 1.16 | 1.2 | 1.29 | 1.26 | 1.16 | 0 | #VALUE! | #VALUE! | - | 135.5 | 3 | 3 | 3.1 | 3.1 | 3 | 3 | 3 | 3.1 | 1.32 | 1.37 | 1.07 | 1 | 1.32 | 1.37 | 1.07 | 1
0 | - | - | - | - | 136 | 3 | 3.1 | 3.1 | 3 | 3 | 3 | 3 | 3.1 | 1.7 | 1.7 | 1.25 | 1.29 | 1.7 | 1.7 | 1.25 | 1.29 | 0 | #VALUE! | #VALUE! | - | 136.5 | 3 | 3.1 | 3.1 | 3 | 3 | 3 | 3 | 3.1 | 1.37 | 1.68 | 1.54 | 1.19 | 1.37 | 1.68 | 1.54 | 1.19
0 | - | - | - | - | 137 | 3 | 3.1 | 3.1 | 3 | 3 | 3 | 3 | 3.1 | 1.36 | 1.7 | 1.42 | 1.02 | 1.36 | 1.7 | 1.42 | 1.02 | 0 | #VALUE! | #VALUE! | - | 137.5 | 3.1 | 3.1 | 3.1 | 3 | 3 | 3 | 3 | 3.1 | 1.5 | 1.7 | 1.51 | 1.18 | 1.5 | 1.7 | 1.51 | 1.18
0 | - | - | - | - | 138 | 3.1 | 3.1 | 3.1 | 3 | 3 | 3 | 3 | 3 | 1.7 | 1.7 | 1.58 | 1.38 | 1.7 | 1.7 | 1.58 | 1.38 | 0 | #VALUE! | #VALUE! | - | 138.5 | 3.1 | 3.1 | 3.1 | 3 | 3 | 3 | 3 | 3 | 1.27 | 1.67 | 1.4 | 0.91 | 1.27 | 1.67 | 1.4 | 0.91
0 | - | - | - | - | 139 | 3.1 | 3.1 | 3.1 | 3.1 | 3 | 3 | 3 | 3.1 | 1.52 | 1.7 | 1.7 | 1.63 | 1.52 | 1.7 | 1.7 | 1.63 | 0 | #VALUE! | #VALUE! | - | 139.5 | 3.1 | 3.1 | 3 | 3.1 | 3.1 | 2.8 | 3 | 3 | 1.19 | 1.49 | 1.43 | 1.13 | 1.19 | 1.49 | 1.43 | 1.13
0 | - | - | - | - | 140 | 3.1 | 3.1 | 2.9 | 3.1 | 3.1 | 3 | 2.9 | 3 | 1.56 | 1.64 | 1.7 | 1.7 | 1.56 | 1.64 | 1.7 | 1.7 | 0 | #VALUE! | #VALUE! | - | 140.5 | 3.1 | 3 | 2.8 | 3 | 3.1 | 3.1 | 2.9 | 3 | 1.44 | 1.7 | 1.37 | 0.72 | 1.44 | 1.7 | 1.37 | 0.72
0 | - | - | - | - | 141 | 3.1 | 2.9 | 2.6 | 2.8 | 3 | 3.1 | 3 | 3.1 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 0 | #VALUE! | #VALUE! | - | 141.5 | 3.1 | 2.9 | 2.6 | 2.8 | 3 | 3 | 3 | 3.1 | 1.23 | 1.7 | 1.7 | 1.62 | 1.23 | 1.7 | 1.7 | 1.62
0 | - | - | - | - | 142 | 3 | 2.7 | 2.5 | 2.7 | 3.1 | 3 | 3 | 3.1 | 1.5 | 1.7 | 1.7 | 1.58 | 1.5 | 1.7 | 1.7 | 1.58 | 0 | #VALUE! | #VALUE! | - | 142.5 | 3.1 | 2.7 | 2.6 | 2.7 | 2.9 | 2.9 | 3.1 | 3.1 | 1.09 | 1.49 | 1.11 | 0.71 | 1.09 | 1.49 | 1.11 | 0.71
0 | - | - | - | - | 143 | 2.9 | 2.6 | 2.6 | 2.8 | 2.8 | 3 | 2.9 | 3.1 | 1.7 | 1.7 | 1.7 | 1.46 | 1.7 | 1.7 | 1.7 | 1.46 | 0 | #VALUE! | #VALUE! | - | 143.5 | 2.9 | 2.7 | 2.7 | 2.8 | 2.9 | 2.9 | 2.9 | 3 | 1.37 | 1.7 | 1.7 | 1.31 | 1.37 | 1.7 | 1.7 | 1.31
0 | - | - | - | - | 144 | 3.1 | 2.7 | 2.6 | 2.9 | 3 | 3 | 3 | 3 | 1.27 | 1.7 | 1.7 | 1.6 | 1.27 | 1.7 | 1.7 | 1.6 | 0 | #VALUE! | #VALUE! | - | 144.5 | 3.1 | 2.7 | 2.6 | 2.8 | 3 | 3 | 3 | 3 | 1.29 | 1.56 | 1.7 | 1.53 | 1.29 | 1.56 | 1.7 | 1.53
0 | - | - | - | - | 145 | 3.1 | 2.7 | 2.6 | 2.7 | 3 | 3 | 3 | 2.9 | 1.35 | 1.54 | 1.56 | 1.36 | 1.35 | 1.54 | 1.56 | 1.36 | 0 | #VALUE! | #VALUE! | - | 145.5 | 3 | 2.7 | 2.6 | 2.7 | 3 | 3 | 3 | 2.9 | 1.3 | 1.3 | 1.38 | 1.38 | 1.3 | 1.3 | 1.38 | 1.38
0 | - | - | - | - | 146 | 3 | 2.7 | 2.6 | 2.6 | 2.9 | 2.8 | 3 | 2.9 | 1.17 | 1.35 | 1.39 | 1.22 | 1.17 | 1.35 | 1.39 | 1.22 | 0 | #VALUE! | #VALUE! | - | 146.5 | 3 | 2.7 | 2.5 | 2.8 | 2.8 | 2.8 | 2.9 | 2.9 | 0.65 | 1.05 | 0.87 | 0.91 | 0.65 | 1.05 | 0.87 | 0.91
0 | - | - | - | - | 147 | 3 | 2.6 | 2.5 | 2.6 | 2.6 | 2.6 | 2.8 | 2.8 | 1.26 | 1.12 | 0.87 | 1.05 | 1.26 | 1.12 | 0.87 | 1.05 | 0 | #VALUE! | #VALUE! | - | 147.5 | 3 | 2.4 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 3 | 1 | 1.02 | 1 | 0.97 | 1 | 1.02 | 1 | 0.97
0 | - | - | - | - | 148 | 2.8 | 2.5 | 2.5 | 2.6 | 2.6 | 2.6 | 2.6 | 2.8 | 1.16 | 1.14 | 1.43 | 1.44 | 1.16 | 1.14 | 1.43 | 1.44 | 0 | #VALUE! | #VALUE! | - | 148.5 | 2.8 | 2.6 | 2.5 | 2.5 | 2.5 | 2.4 | 2.4 | 2.7 | 0.59 | 0.64 | 0.81 | 0.71 | 0.59 | 0.64 | 0.81 | 0.71
0 | - | - | - | - | 149 | 2.7 | 2.4 | 2.5 | 2.4 | 2.3 | 2.4 | 2.4 | 2.5 | 1.62 | 1.7 | 1.57 | 1.29 | 1.62 | 1.7 | 1.57 | 1.29 | 0 | #VALUE! | #VALUE! | - | 149.5 | 2.6 | 2.6 | 2.6 | 2.5 | 2.3 | 2.5 | 2.3 | 2.4 | 0.78 | 0.98 | 1.35 | 1.17 | 0.78 | 0.98 | 1.35 | 1.17
0 | - | - | - | - | 150 | 2.6 | 2.4 | 2.4 | 2.4 | 2.4 | 2.5 | 2.4 | 2.4 | 1.49 | 1.14 | 1.43 | 1.7 | 1.49 | 1.14 | 1.43 | 1.7 | 0 | #VALUE! | #VALUE! | - | 150.5 | 2.6 | 2.4 | 2.4 | 2.4 | 2.4 | 2.5 | 2.4 | 2.4 | 1.26 | 1.06 | 1.12 | 1.29 | 1.26 | 1.06 | 1.12 | 1.29
0 | - | - | - | - | 151 | 2.6 | 2.4 | 2.5 | 2.5 | 2.4 | 2.5 | 2.5 | 2.4 | 1.45 | 1.25 | 1.66 | 1.7 | 1.45 | 1.25 | 1.66 | 1.7 | 0 | #VALUE! | #VALUE! | - | 151.5 | 2.5 | 2.5 | 2.5 | 2.7 | 2.5 | 2.5 | 2.5 | 2.4 | 1.32 | 1.3 | 1.63 | 1.64 | 1.32 | 1.3 | 1.63 | 1.64
0 | - | - | - | - | 152 | 2.4 | 2.4 | 2.5 | 2.4 | 2.6 | 2.4 | 2.5 | 2.5 | 1.2 | 1.36 | 1.7 | 1.65 | 1.2 | 1.36 | 1.7 | 1.65 | 0 | #VALUE! | #VALUE! | - | 152.5 | 2.4 | 2.5 | 2.5 | 2.3 | 2.7 | 2.5 | 2.4 | 2.4 | 1.09 | 1.16 | 1.05 | 0.98 | 1.09 | 1.16 | 1.05 | 0.98
0 | - | - | - | - | 153 | 2.7 | 2.7 | 2.3 | 2.3 | 2.6 | 2.9 | 2.3 | 2.3 | 0.92 | 1.1 | 1.15 | 0.99 | 0.92 | 1.1 | 1.15 | 0.99 | 0 | #VALUE! | #VALUE! | - | 153.5 | 2.8 | 2.4 | 2.3 | 2.3 | 2.6 | 2.9 | 2.5 | 2.3 | 0.71 | 0.86 | 0.59 | 0.59 | 0.71 | 0.86 | 0.59 | 0.59
0 | - | - | - | - | 154 | 2.8 | 2.3 | 2.3 | 2.5 | 2.7 | 2.8 | 2.8 | 2.3 | 1.15 | 0.95 | 0.95 | 1.15 | 1.15 | 0.95 | 0.95 | 1.15 | 0 | #VALUE! | #VALUE! | - | 154.5 | 2.6 | 2.3 | 2.3 | 2.7 | 2.7 | 2.7 | 2.7 | 2.5 | 0.97 | 0.94 | 0.91 | 0.96 | 0.97 | 0.94 | 0.91 | 0.96
0 | - | - | - | - | 155 | 2.5 | 2.2 | 2.3 | 2.8 | 2.8 | 2.7 | 2.7 | 2.5 | 0.92 | 0.95 | 0.85 | 0.81 | 0.92 | 0.95 | 0.85 | 0.81 | 0 | #VALUE! | #VALUE! | - | 155.5 | 2.5 | 2.3 | 2.4 | 2.7 | 2.8 | 2.7 | 2.8 | 2.7 | 0.99 | 0.92 | 0.74 | 0.83 | 0.99 | 0.92 | 0.74 | 0.83
0 | - | - | - | - | 156 | 2.4 | 2.3 | 2.5 | 2.6 | 2.7 | 2.7 | 2.8 | 2.8 | 0.94 | 0.94 | 0.87 | 0.87 | 0.94 | 0.94 | 0.87 | 0.87 | 0 | #VALUE! | #VALUE! | - | 156.5 | 2.3 | 2.4 | 2.5 | 2.6 | 2.7 | 2.8 | 2.8 | 2.7 | 0.95 | 0.96 | 0.85 | 0.83 | 0.95 | 0.96 | 0.85 | 0.83
0 | - | - | - | - | 157 | 2.4 | 2.6 | 2.4 | 2.5 | 2.6 | 2.7 | 2.7 | 2.8 | 0.97 | 0.96 | 0.81 | 0.81 | 0.97 | 0.96 | 0.81 | 0.81 | 0 | #VALUE! | #VALUE! | - | 157.5 | 2.6 | 2.6 | 2.4 | 2.5 | 2.7 | 2.7 | 2.8 | 2.8 | 0.97 | 0.94 | 0.72 | 0.76 | 0.97 | 0.94 | 0.72 | 0.76
0 | - | - | - | - | 158 | 2.7 | 2.6 | 2.6 | 2.7 | 2.8 | 2.7 | 2.8 | 2.8 | 0.99 | 0.96 | 0.71 | 0.74 | 0.99 | 0.96 | 0.71 | 0.74 | 0 | #VALUE! | #VALUE! | - | 158.5 | 2.9 | 2.4 | 2.5 | 2.5 | 2.9 | 2.7 | 2.7 | 2.7 | 0.81 | 0.79 | 0.62 | 0.59 | 0.81 | 0.79 | 0.62 | 0.59
0 | - | - | - | - | 159 | 2.8 | 2.4 | 2.4 | 2.4 | 2.9 | 2.8 | 2.7 | 2.8 | 0.88 | 0.73 | 0.68 | 0.85 | 0.88 | 0.73 | 0.68 | 0.85 | 0 | #VALUE! | #VALUE! | - | 159.5 | 2.7 | 2.5 | 2.5 | 2.5 | 2.9 | 2.8 | 2.7 | 2.8 | 0.91 | 0.78 | 0.59 | 0.59 | 0.91 | 0.78 | 0.59 | 0.59
0 | - | - | - | - | 160 | 2.5 | 2.5 | 2.4 | 2.7 | 2.9 | 3 | 3.1 | 2.8 | 1.09 | 0.77 | 0.65 | 0.92 | 1.09 | 0.77 | 0.65 | 0.92 | 0 | #VALUE! | #VALUE! | - | 160.5 | 2.5 | 2.5 | 2.5 | 2.8 | 2.9 | 2.9 | 3.1 | 2.8 | 0.98 | 0.69 | 0.76 | 1.04 | 0.98 | 0.69 | 0.76 | 1.04
0 | - | - | - | - | 161 | 2.5 | 2.5 | 2.6 | 2.8 | 2.8 | 2.8 | 2.7 | 2.8 | 1 | 0.72 | 0.78 | 1.18 | 1 | 0.72 | 0.78 | 1.18 | 0 | #VALUE! | #VALUE! | - | 161.5 | 2.4 | 2.4 | 2.6 | 2.8 | 2.8 | 2.8 | 2.7 | 2.8 | 0.66 | 0.82 | 1.09 | 1.38 | 0.66 | 0.82 | 1.09 | 1.38
0 | - | - | - | - | 162 | 2.6 | 2.5 | 2.5 | 2.7 | 2.7 | 2.8 | 2.7 | 2.7 | 0.8 | 1.07 | 1.46 | 1.7 | 0.8 | 1.07 | 1.46 | 1.7 | 0 | #VALUE! | #VALUE! | - | 162.5 | 2.4 | 2.5 | 2.6 | 2.6 | 2.7 | 2.9 | 2.8 | 2.8 | 0.98 | 0.88 | 0.88 | 0.84 | 0.98 | 0.88 | 0.88 | 0.84
0 | - | - | - | - | 163 | 2.9 | 2.7 | 2.8 | 2.6 | 2.6 | 2.7 | 2.7 | 2.7 | 1.23 | 1.5 | 1.7 | 1.7 | 1.23 | 1.5 | 1.7 | 1.7 | 0 | #VALUE! | #VALUE! | - | 163.5 | 2.8 | 2.7 | 2.8 | 2.6 | 2.6 | 2.6 | 2.8 | 2.7 | 1.1 | 1.13 | 1.09 | 1.1 | 1.1 | 1.13 | 1.09 | 1.1
0 | - | - | - | - | 164 | 2.7 | 2.7 | 2.5 | 2.4 | 2.4 | 2.4 | 2.6 | 2.8 | 1.37 | 1.04 | 1.61 | 1.7 | 1.37 | 1.04 | 1.61 | 1.7 | 0 | #VALUE! | #VALUE! | - | 164.5 | 2.7 | 2.7 | 2.8 | 2.6 | 2.6 | 2.6 | 2.6 | 2.7 | 0.62 | 0.64 | 0.81 | 0.79 | 0.62 | 0.64 | 0.81 | 0.79
0 | - | - | - | - | 165 | 2.6 | 2.7 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 1.32 | 0.78 | 1.35 | 1.7 | 1.32 | 0.78 | 1.35 | 1.7 | 0 | #VALUE! | #VALUE! | - | 165.5 | 2.8 | 2.8 | 2.6 | 2.4 | 2.4 | 2.6 | 2.6 | 2.6 | 0.59 | 0.59 | 0.76 | 0.59 | 0.59 | 0.59 | 0.76 | 0.59
0 | - | - | - | - | 166 | 2.6 | 2.7 | 2.6 | 2.5 | 2.5 | 2.5 | 2.8 | 2.7 | 1.7 | 1.48 | 1.15 | 1.68 | 1.7 | 1.48 | 1.15 | 1.68 | 0 | #VALUE! | #VALUE! | - | 166.5 | 2.6 | 2.5 | 2.4 | 2.4 | 2.4 | 2.5 | 2.6 | 2.8 | 0.8 | 0.83 | 0.64 | 0.68 | 0.8 | 0.83 | 0.64 | 0.68
0 | - | - | - | - | 167 | 2.5 | 2.4 | 2.4 | 2.7 | 2.6 | 2.5 | 2.6 | 2.5 | 1.54 | 1.54 | 1.7 | 1.7 | 1.54 | 1.54 | 1.7 | 1.7 | 0 | #VALUE! | #VALUE! | - | 167.5 | 2.4 | 2.4 | 2.4 | 2.8 | 2.6 | 2.5 | 2.5 | 2.5 | 1.7 | 1.7 | 1.59 | 1.67 | 1.7 | 1.7 | 1.59 | 1.67
0 | - | - | - | - | 168 | 2.5 | 2.4 | 2.5 | 2.9 | 2.5 | 2.5 | 2.5 | 2.5 | 1.7 | 1.64 | 1.4 | 1.63 | 1.7 | 1.64 | 1.4 | 1.63 | 0 | #VALUE! | #VALUE! | - | 168.5 | 2.4 | 2.4 | 2.6 | 2.9 | 2.6 | 2.7 | 2.4 | 2.6 | 1.65 | 1.6 | 1.28 | 1.35 | 1.65 | 1.6 | 1.28 | 1.35
0 | - | - | - | - | 169 | 2.4 | 2.4 | 2.8 | 3 | 2.6 | 2.8 | 2.5 | 2.6 | 1.68 | 1.6 | 1.27 | 1.37 | 1.68 | 1.6 | 1.27 | 1.37 | 0 | #VALUE! | #VALUE! | - | 169.5 | 2.4 | 2.4 | 2.8 | 3 | 2.8 | 2.8 | 2.6 | 2.4 | 1.45 | 1.51 | 1.29 | 1.24 | 1.45 | 1.51 | 1.29 | 1.24
0 | - | - | - | - | 170 | 2.4 | 2.5 | 3 | 2.9 | 2.9 | 2.8 | 2.7 | 2.4 | 1.48 | 1.42 | 1.4 | 1.46 | 1.48 | 1.42 | 1.4 | 1.46 | 0 | #VALUE! | #VALUE! | - | 170.5 | 2.4 | 2.7 | 3 | 3 | 2.9 | 2.8 | 2.7 | 2.5 | 1.35 | 1.43 | 1.56 | 1.49 | 1.35 | 1.43 | 1.56 | 1.49
0 | - | - | - | - | 171 | 2.4 | 2.7 | 3 | 3 | 2.8 | 2.6 | 2.7 | 2.5 | 1.3 | 1.31 | 1.5 | 1.48 | 1.3 | 1.31 | 1.5 | 1.48 | 0 | #VALUE! | #VALUE! | - | 171.5 | 2.6 | 2.8 | 3 | 3 | 2.8 | 2.8 | 2.6 | 2.6 | 1.1 | 1.06 | 0.99 | 1.05 | 1.1 | 1.06 | 0.99 | 1.05
0 | - | - | - | - | 172 | 2.8 | 3 | 3 | 2.9 | 2.8 | 3 | 2.8 | 2.6 | 1.1 | 0.83 | 1.04 | 1.25 | 1.1 | 0.83 | 1.04 | 1.25 | 0 | #VALUE! | #VALUE! | - | 172.5 | 2.7 | 3 | 2.9 | 2.8 | 2.8 | 3 | 3 | 2.7 | 0.81 | 0.84 | 0.59 | 0.74 | 0.81 | 0.84 | 0.59 | 0.74
0 | - | - | - | - | 173 | 2.7 | 2.9 | 2.7 | 2.4 | 2.6 | 3 | 2.9 | 2.9 | 1.01 | 1.26 | 1.23 | 0.97 | 1.01 | 1.26 | 1.23 | 0.97 | 0 | #VALUE! | #VALUE! | - | 173.5 | 2.7 | 2.8 | 2.2 | 2.3 | 2.4 | 3 | 2.9 | 2.9 | 0.96 | 0.79 | 0.93 | 1.08 | 0.96 | 0.79 | 0.93 | 1.08
0 | - | - | - | - | 174 | 2.8 | 2.9 | 2.3 | 2.1 | 2.2 | 2.9 | 3 | 3 | 1.28 | 1.03 | 1.24 | 1.46 | 1.28 | 1.03 | 1.24 | 1.46 | 0 | #VALUE! | #VALUE! | - | 174.5 | 2.8 | 2.7 | 2.2 | 2.1 | 2.1 | 2.7 | 3 | 3 | 1.07 | 1.04 | 1.05 | 1.07 | 1.07 | 1.04 | 1.05 | 1.07
0 | - | - | - | - | 175 | 2.8 | 2.3 | 2.2 | 2.1 | 2.1 | 2.3 | 2.8 | 2.9 | 1.3 | 1.11 | 0.87 | 1.12 | 1.3 | 1.11 | 0.87 | 1.12 | 0 | #VALUE! | #VALUE! | - | 175.5 | 2.7 | 2.2 | 2.2 | 2.2 | 2.1 | 2.2 | 2.7 | 2.8 | 1 | 0.86 | 0.9 | 1.04 | 1 | 0.86 | 0.9 | 1.04
0 | - | - | - | - | 176 | 2.5 | 2.2 | 2.2 | 2.2 | 2.1 | 2.2 | 2.7 | 2.8 | 1.3 | 1.13 | 0.95 | 1.15 | 1.3 | 1.13 | 0.95 | 1.15 | 0 | #VALUE! | #VALUE! | - | 176.5 | 2.6 | 2.2 | 2.2 | 2.2 | 2.1 | 2.2 | 2.6 | 2.8 | 1.11 | 1.16 | 1.13 | 1.08 | 1.11 | 1.16 | 1.13 | 1.08
0 | - | - | - | - | 177 | 2.4 | 2.2 | 2.2 | 2.2 | 2.1 | 2.1 | 2.4 | 2.7 | 1.12 | 1.21 | 1.02 | 0.9 | 1.12 | 1.21 | 1.02 | 0.9 | 0 | #VALUE! | #VALUE! | - | 177.5 | 2.2 | 2.2 | 2.2 | 2.2 | 2.1 | 2.1 | 2.3 | 2.4 | 0.83 | 0.73 | 0.87 | 0.96 | 0.83 | 0.73 | 0.87 | 0.96
0 | - | - | - | - | 178 | 2.2 | 2.2 | 2.2 | 2.2 | 2.1 | 2.1 | 2.3 | 2.6 | 1.1 | 0.97 | 0.9 | 1.04 | 1.1 | 0.97 | 0.9 | 1.04 | 0 | #VALUE! | #VALUE! | - | 178.5 | 2.1 | 2.2 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.2 | 0.92 | 0.87 | 0.78 | 0.85 | 0.92 | 0.87 | 0.78 | 0.85
0 | - | - | - | - | 179 | 2.1 | 2.2 | 2.1 | 2.2 | 2.1 | 2.1 | 2.1 | 2.1 | 1.08 | 1.04 | 0.91 | 0.95 | 1.08 | 1.04 | 0.91 | 0.95 | 0 | #VALUE! | #VALUE! | - | 179.5 | 2.1 | 2.1 | 2.1 | 2.2 | 2.1 | 2.1 | 2.1 | 2.1 | 0.85 | 0.72 | 0.81 | 0.92 | 0.85 | 0.72 | 0.81 | 0.92
0 | - | - | - | - | 180 | 2.2 | 2.1 | 2.1 | 2.3 | 2.1 | 2.1 | 2.1 | 2.1 | 1.17 | 0.85 | 0.88 | 1.19 | 1.17 | 0.85 | 0.88 | 1.19 | 0 | #VALUE! | #VALUE! | - | 180.5 | 2.2 | 2.1 | 2.2 | 2.2 | 2.1 | 2.1 | 2.1 | 2.1 | 1.23 | 1.05 | 0.94 | 1.15 | 1.23 | 1.05 | 0.94 | 1.15
0 | - | - | - | - | 181 | 2.1 | 2.1 | 2.3 | 2.3 | 2.2 | 2.1 | 2.1 | 2.1 | 1.13 | 1.05 | 0.91 | 1 | 1.13 | 1.05 | 0.91 | 1 | 0 | #VALUE! | #VALUE! | - | 181.5 | 2.1 | 2.2 | 2.3 | 2.3 | 2.2 | 2.1 | 2.1 | 2.1 | 0.83 | 0.94 | 0.9 | 0.79 | 0.83 | 0.94 | 0.9 | 0.79
0 | - | - | - | - | 182 | 2.2 | 2.2 | 2.2 | 2.3 | 2.3 | 2.1 | 2.1 | 2.1 | 1.1 | 0.95 | 0.76 | 0.95 | 1.1 | 0.95 | 0.76 | 0.95 | 0 | #VALUE! | #VALUE! | - | 182.5 | 2.2 | 2.3 | 2.1 | 2.2 | 2.2 | 2.2 | 2.1 | 2.1 | 0.97 | 1.03 | 0.81 | 0.76 | 0.97 | 1.03 | 0.81 | 0.76
0 | - | - | - | - | 183 | 2.2 | 2.3 | 2.1 | 2.1 | 2.1 | 2.3 | 2.1 | 2.1 | 1.06 | 1.06 | 0.86 | 0.86 | 1.06 | 1.06 | 0.86 | 0.86 | 0 | #VALUE! | #VALUE! | - | 183.5 | 2.3 | 2.2 | 2.1 | 2.1 | 2.1 | 2.3 | 2.2 | 2.1 | 0.59 | 0.72 | 0.59 | 0.72 | 0.59 | 0.72 | 0.59 | 0.72
0 | - | - | - | - | 184 | 2.4 | 2.1 | 2.1 | 2.1 | 2.1 | 2.3 | 2.2 | 2.2 | 0.94 | 1 | 0.92 | 0.85 | 0.94 | 1 | 0.92 | 0.85 | 0 | #VALUE! | #VALUE! | - | 184.5 | 2.3 | 2.1 | 2.1 | 2.1 | 2.1 | 2.2 | 2.3 | 2.2 | 0.88 | 0.99 | 1 | 0.91 | 0.88 | 0.99 | 1 | 0.91
0 | - | - | - | - | 185 | 2.2 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.3 | 2.3 | 1.1 | 1.12 | 1.31 | 1.29 | 1.1 | 1.12 | 1.31 | 1.29 | 0 | #VALUE! | #VALUE! | - | 185.5 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.2 | 2.2 | 1.01 | 1.06 | 1 | 0.94 | 1.01 | 1.06 | 1 | 0.94
0 | - | - | - | - | 186 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.2 | 2.2 | 0.96 | 0.91 | 0.86 | 0.91 | 0.96 | 0.91 | 0.86 | 0.91 | 0 | #VALUE! | #VALUE! | - | 186.5 | 2.1 | 2.1 | 2.1 | 2.1 | 2.2 | 2.1 | 2.1 | 2.1 | 0.9 | 0.77 | 0.73 | 0.85 | 0.9 | 0.77 | 0.73 | 0.85
0 | - | - | - | - | 187 | 2.1 | 2.1 | 2.1 | 2.2 | 2.4 | 2.1 | 2.1 | 2.1 | 1 | 1.1 | 0.97 | 0.85 | 1 | 1.1 | 0.97 | 0.85 | 0 | #VALUE! | #VALUE! | - | 187.5 | 2.1 | 2.1 | 2.1 | 2.4 | 2.7 | 2.1 | 2.1 | 2.1 | 1.08 | 1.33 | 1.35 | 1.1 | 1.08 | 1.33 | 1.35 | 1.1
0 | - | - | - | - | 188 | 2.1 | 2.1 | 2.2 | 2.6 | 2.9 | 2.2 | 2.1 | 2.1 | 1.08 | 1.37 | 1.45 | 1.18 | 1.08 | 1.37 | 1.45 | 1.18 | 0 | #VALUE! | #VALUE! | - | 188.5 | 2.1 | 2.1 | 2.4 | 2.7 | 3 | 2.5 | 2.1 | 2.1 | 1.1 | 1.26 | 1.32 | 1.18 | 1.1 | 1.26 | 1.32 | 1.18
0 | - | - | - | - | 189 | 2.1 | 2.1 | 2.6 | 2.8 | 3 | 2.7 | 2.2 | 2.1 | 1.22 | 1.14 | 1.01 | 1.09 | 1.22 | 1.14 | 1.01 | 1.09 | 0 | #VALUE! | #VALUE! | - | 189.5 | 2.1 | 2.2 | 2.8 | 2.9 | 3 | 2.9 | 2.3 | 2.2 | 1.01 | 1.13 | 1.13 | 1.01 | 1.01 | 1.13 | 1.13 | 1.01
0 | - | - | - | - | 190 | 2.2 | 2.4 | 2.8 | 2.9 | 3 | 3 | 2.7 | 2.3 | 1.17 | 1.03 | 1.15 | 1.28 | 1.17 | 1.03 | 1.15 | 1.28 | 0 | #VALUE! | #VALUE! | - | 190.5 | 2.4 | 2.5 | 2.8 | 3 | 3 | 3 | 2.8 | 2.5 | 0.91 | 1.01 | 0.91 | 0.79 | 0.91 | 1.01 | 0.91 | 0.79
0 | - | - | - | - | 191 | 2.6 | 2.5 | 2.9 | 2.9 | 3 | 3 | 3 | 2.6 | 1.14 | 1.06 | 0.95 | 1.04 | 1.14 | 1.06 | 0.95 | 1.04 | 0 | #VALUE! | #VALUE! | - | 191.5 | 2.7 | 2.5 | 2.9 | 2.9 | 3 | 3 | 3 | 2.7 | 0.85 | 0.82 | 0.72 | 0.74 | 0.85 | 0.82 | 0.72 | 0.74
0 | - | - | - | - | 192 | 2.8 | 2.5 | 2.8 | 2.9 | 3 | 3 | 3 | 2.7 | 1.04 | 0.96 | 0.88 | 0.97 | 1.04 | 0.96 | 0.88 | 0.97 | 0 | #VALUE! | #VALUE! | - | 192.5 | 2.8 | 2.5 | 2.8 | 2.9 | 3 | 3 | 3 | 2.9 | 0.94 | 0.94 | 0.83 | 0.83 | 0.94 | 0.94 | 0.83 | 0.83
0 | - | - | - | - | 193 | 2.8 | 2.6 | 3 | 2.8 | 2.9 | 3 | 3 | 2.9 | 1.57 | 1.35 | 1.08 | 1.35 | 1.57 | 1.35 | 1.08 | 1.35 | 0 | #VALUE! | #VALUE! | - | 193.5 | 2.9 | 2.6 | 3 | 2.8 | 2.7 | 2.9 | 3 | 2.9 | 1.33 | 1.32 | 1.14 | 1.15 | 1.33 | 1.32 | 1.14 | 1.15
0 | - | - | - | - | 194 | 2.9 | 2.7 | 3 | 2.8 | 2.6 | 2.8 | 3 | 2.9 | 1.29 | 1.14 | 1.11 | 1.26 | 1.29 | 1.14 | 1.11 | 1.26 | 0 | #VALUE! | #VALUE! | - | 194.5 | 3 | 2.9 | 2.9 | 2.6 | 2.3 | 2.5 | 3 | 2.9 | 0.73 | 0.66 | 0.82 | 0.87 | 0.73 | 0.66 | 0.82 | 0.87
0 | - | - | - | - | 195 | 3 | 3 | 2.8 | 2.2 | 2.1 | 2.2 | 2.8 | 2.9 | 1.3 | 1.13 | 1.05 | 1.23 | 1.3 | 1.13 | 1.05 | 1.23 | 0 | #VALUE! | #VALUE! | - | 195.5 | 2.9 | 2.9 | 2.7 | 2.2 | 2.1 | 2.1 | 2.4 | 2.9 | 1.36 | 1.19 | 0.8 | 1.01 | 1.36 | 1.19 | 0.8 | 1.01
0 | - | - | - | - | 196 | 2.8 | 2.8 | 2.3 | 2.2 | 2.1 | 2.1 | 2.1 | 2.9 | 1.37 | 1.12 | 0.76 | 1.08 | 1.37 | 1.12 | 0.76 | 1.08 | 0 | #VALUE! | #VALUE! | - | 196.5 | 2.6 | 2.5 | 2.2 | 2.2 | 2.3 | 2.4 | 2.1 | 2.4 | 0.98 | 0.73 | 0.87 | 1.1 | 0.98 | 0.73 | 0.87 | 1.1
0 | - | - | - | - | 197 | 2.4 | 2.3 | 2.2 | 2.2 | 2.5 | 2.7 | 2.3 | 2.2 | 1.26 | 0.99 | 0.97 | 1.23 | 1.26 | 0.99 | 0.97 | 1.23 | 0 | #VALUE! | #VALUE! | - | 197.5 | 2.3 | 2.2 | 2.2 | 2.4 | 2.5 | 2.8 | 2.3 | 2.1 | 1.12 | 0.9 | 0.83 | 1.07 | 1.12 | 0.9 | 0.83 | 1.07
0 | - | - | - | - | 198 | 2.2 | 2.2 | 2.2 | 2.5 | 2.3 | 2.9 | 2.7 | 2.2 | 1.49 | 1.11 | 0.81 | 1.25 | 1.49 | 1.11 | 0.81 | 1.25 | 0 | #VALUE! | #VALUE! | - | 198.5 | 2.2 | 2.2 | 2.4 | 2.3 | 2.2 | 2.8 | 2.8 | 2.2 | 0.99 | 0.59 | 0.92 | 1.31 | 0.99 | 0.59 | 0.92 | 1.31
0 | - | - | - | - | 199 | 2.3 | 2.2 | 2.4 | 2.1 | 2.2 | 2.7 | 2.9 | 2.4 | 1.24 | 0.59 | 0.94 | 1.7 | 1.24 | 0.59 | 0.94 | 1.7 | 0 | #VALUE! | #VALUE! | - | 199.5 | 2.3 | 2.4 | 2.1 | 2.1 | 2.2 | 2.2 | 2.8 | 2.5 | 0.92 | 0.59 | 1.01 | 1.38 | 0.92 | 0.59 | 1.01 | 1.38
0 | - | - | - | - | 200 | 2.4 | 2.2 | 2.1 | 2.2 | 2.2 | 2.1 | 2.6 | 2.4 | 0.87 | 0.59 | 1.11 | 1.42 | 0.87 | 0.59 | 1.11 | 1.42 | 0 | #VALUE! | #VALUE! | - | 200.5 | 2.5 | 2.1 | 2.1 | 2.3 | 2.2 | 2.1 | 2.4 | 2.4 | 1.08 | 0.75 | 1.06 | 1.33 | 1.08 | 0.75 | 1.06 | 1.33
0 | - | - | - | - | 201 | 2.3 | 2.1 | 2.1 | 2.3 | 2.2 | 2.1 | 2.2 | 2.3 | 1.29 | 1.15 | 1.12 | 1.26 | 1.29 | 1.15 | 1.12 | 1.26 | 0 | #VALUE! | #VALUE! | - | 201.5 | 2.2 | 2.1 | 2.1 | 2.3 | 2.2 | 2.1 | 2.1 | 2.3 | 1.38 | 1.38 | 1.24 | 1.22 | 1.38 | 1.38 | 1.24 | 1.22
0 | - | - | - | - | 202 | 2.1 | 2.1 | 2.2 | 2.3 | 2.1 | 2.1 | 2.1 | 2.2 | 1.3 | 1.12 | 1.15 | 1.32 | 1.3 | 1.12 | 1.15 | 1.32 | 0 | #VALUE! | #VALUE! | - | 202.5 | 2.1 | 2.1 | 2.2 | 2.2 | 2.1 | 2.1 | 2.1 | 2.2 | 1.31 | 1.16 | 0.9 | 1.1 | 1.31 | 1.16 | 0.9 | 1.1
0 | - | - | - | - | 203 | 2.1 | 2.2 | 2.2 | 2.2 | 2.2 | 2.1 | 2.1 | 2.2 | 1.32 | 1.14 | 1.17 | 1.34 | 1.32 | 1.14 | 1.17 | 1.34 | 0 | #VALUE! | #VALUE! | - | 203.5 | 2.2 | 2.2 | 2.1 | 2.4 | 2.3 | 2.2 | 2.1 | 2.2 | 1.11 | 1.11 | 1.09 | 1.09 | 1.11 | 1.11 | 1.09 | 1.09
0 | - | - | - | - | 204 | 2.3 | 2.1 | 2.1 | 2.7 | 2.6 | 2.2 | 2.1 | 2.2 | 1.2 | 1.13 | 1.31 | 1.37 | 1.2 | 1.13 | 1.31 | 1.37 | 0 | #VALUE! | #VALUE! | - | 204.5 | 2.3 | 2.1 | 2.3 | 2.7 | 2.6 | 2.4 | 2.1 | 2.2 | 0.97 | 1.01 | 1.01 | 0.97 | 0.97 | 1.01 | 1.01 | 0.97
0 | - | - | - | - | 205 | 2.3 | 2.1 | 2.4 | 2.6 | 2.6 | 2.6 | 2.2 | 2.2 | 1.04 | 1.02 | 0.97 | 0.98 | 1.04 | 1.02 | 0.97 | 0.98 | 0 | #VALUE! | #VALUE! | - | 205.5 | 2.2 | 2.5 | 2.5 | 2.7 | 2.6 | 2.7 | 2.4 | 2.2 | 0.79 | 0.82 | 0.83 | 0.81 | 0.79 | 0.82 | 0.83 | 0.81
0 | - | - | - | - | 206 | 2.4 | 2.4 | 2.7 | 2.7 | 2.6 | 2.6 | 2.7 | 2.4 | 0.95 | 0.83 | 0.94 | 1.05 | 0.95 | 0.83 | 0.94 | 1.05 | 0 | #VALUE! | #VALUE! | - | 206.5 | 2.4 | 2.5 | 2.8 | 2.7 | 2.6 | 2.7 | 2.7 | 2.7 | 0.9 | 0.74 | 0.6 | 0.79 | 0.9 | 0.74 | 0.6 | 0.79
0 | - | - | - | - | 207 | 2.7 | 2.7 | 2.9 | 2.6 | 2.8 | 2.7 | 2.5 | 2.7 | 0.76 | 0.59 | 0.76 | 0.96 | 0.76 | 0.59 | 0.76 | 0.96 | 0 | #VALUE! | #VALUE! | - | 207.5 | 2.6 | 2.9 | 3 | 2.6 | 2.8 | 2.8 | 2.4 | 2.6 | 0.78 | 0.79 | 0.85 | 0.85 | 0.78 | 0.79 | 0.85 | 0.85
0 | - | - | - | - | 208 | 2.8 | 3 | 2.9 | 2.4 | 2.9 | 2.9 | 2.5 | 2.5 | 0.87 | 0.62 | 0.86 | 1.06 | 0.87 | 0.62 | 0.86 | 1.06 | 0 | #VALUE! | #VALUE! | - | 208.5 | 2.8 | 3 | 2.4 | 2.4 | 3 | 3 | 2.8 | 2.5 | 0.64 | 0.78 | 0.96 | 0.85 | 0.64 | 0.78 | 0.96 | 0.85
0 | - | - | - | - | 209 | 2.8 | 2.6 | 2.5 | 2.6 | 2.7 | 3 | 3 | 2.6 | 1.01 | 0.96 | 1.09 | 1.13 | 1.01 | 0.96 | 1.09 | 1.13 | 0 | #VALUE! | #VALUE! | - | 209.5 | 2.7 | 2.4 | 2.7 | 2.6 | 2.3 | 2.9 | 3 | 2.7 | 0.68 | 0.9 | 0.83 | 0.6 | 0.68 | 0.9 | 0.83 | 0.6
0 | - | - | - | - | 210 | 2.4 | 2.5 | 3 | 2.2 | 2.1 | 2.4 | 3 | 2.8 | 1.05 | 1.08 | 1.14 | 1.1 | 1.05 | 1.08 | 1.14 | 1.1 | 0 | #VALUE! | #VALUE! | - | 210.5 | 2.2 | 3 | 2.8 | 2.2 | 2.1 | 2.1 | 2.8 | 2.7 | 1.17 | 1.09 | 0.9 | 0.99 | 1.17 | 1.09 | 0.9 | 0.99
0 | - | - | - | - | 211 | 2.6 | 3 | 2.6 | 2.1 | 2.1 | 2.1 | 2.4 | 2.6 | 1.32 | 1.08 | 0.94 | 1.21 | 1.32 | 1.08 | 0.94 | 1.21 | 0 | #VALUE! | #VALUE! | - | 211.5 | 2.8 | 3 | 2.4 | 2.1 | 2.2 | 2.1 | 2.2 | 2.5 | 0.97 | 1.15 | 0.96 | 0.74 | 0.97 | 1.15 | 0.96 | 0.74
0 | - | - | - | - | 212 | 2.9 | 2.9 | 2.4 | 2.1 | 2.2 | 2.1 | 2.1 | 2.5 | 1.15 | 1.1 | 1.22 | 1.27 | 1.15 | 1.1 | 1.22 | 1.27 | 0 | #VALUE! | #VALUE! | - | 212.5 | 2.9 | 2.8 | 2.4 | 2.1 | 2.2 | 2.2 | 2.1 | 2.5 | 1.06 | 1.06 | 1.08 | 1.08 | 1.06 | 1.06 | 1.08 | 1.08
0 | - | - | - | - | 213 | 2.8 | 2.8 | 2.4 | 2.1 | 2.2 | 2.2 | 2.1 | 2.4 | 0.91 | 1.04 | 1.12 | 1 | 0.91 | 1.04 | 1.12 | 1 | 0 | #VALUE! | #VALUE! | - | 213.5 | 2.6 | 2.7 | 2.1 | 2.2 | 2.4 | 2.3 | 2.2 | 2.2 | 0.99 | 1.01 | 0.87 | 0.85 | 0.99 | 1.01 | 0.87 | 0.85
0 | - | - | - | - | 214 | 2.4 | 2.4 | 2.1 | 2.2 | 2.5 | 2.4 | 2.2 | 2.1 | 1.09 | 1 | 1.17 | 1.24 | 1.09 | 1 | 1.17 | 1.24 | 0 | #VALUE! | #VALUE! | - | 214.5 | 2.3 | 2.2 | 2.1 | 2.3 | 2.6 | 2.5 | 2.2 | 2.1 | 0.91 | 1.04 | 0.97 | 0.85 | 0.91 | 1.04 | 0.97 | 0.85
0 | - | - | - | - | 215 | 2.2 | 2.1 | 2.2 | 2.5 | 2.5 | 2.6 | 2.3 | 2.1 | 0.99 | 0.99 | 1.06 | 1.05 | 0.99 | 0.99 | 1.06 | 1.05 | 0 | #VALUE! | #VALUE! | - | 215.5 | 2.1 | 2.1 | 2.3 | 2.6 | 2.6 | 2.6 | 2.5 | 2.1 | 1.01 | 0.88 | 0.77 | 0.91 | 1.01 | 0.88 | 0.77 | 0.91
0 | - | - | - | - | 216 | 2.1 | 2.2 | 2.2 | 2.7 | 2.4 | 2.6 | 2.6 | 2.1 | 0.95 | 0.9 | 1.1 | 1.14 | 0.95 | 0.9 | 1.1 | 1.14 | 0 | #VALUE! | #VALUE! | - | 216.5 | 2.1 | 2.2 | 2.3 | 2.8 | 2.4 | 2.7 | 2.5 | 2.2 | 0.59 | 0.59 | 0.83 | 0.92 | 0.59 | 0.59 | 0.83 | 0.92
0 | - | - | - | - | 217 | 2.1 | 2.3 | 2.5 | 2.7 | 2.7 | 2.8 | 2.6 | 2.5 | 1.19 | 0.95 | 0.88 | 1.14 | 1.19 | 0.95 | 0.88 | 1.14 | 0 | #VALUE! | #VALUE! | - | 217.5 | 2.3 | 2.5 | 2.6 | 2.7 | 2.7 | 2.7 | 2.7 | 2.4 | 0.78 | 0.59 | 0.81 | 1.01 | 0.78 | 0.59 | 0.81 | 1.01
0 | - | - | - | - | 218 | 2.7 | 2.7 | 2.7 | 2.4 | 2.3 | 2.8 | 2.8 | 2.4 | 1.54 | 1.31 | 1.31 | 1.54 | 1.54 | 1.31 | 1.31 | 1.54 | 0 | #VALUE! | #VALUE! | - | 218.5 | 2.5 | 2.7 | 2.7 | 2.3 | 2.2 | 2.4 | 2.9 | 2.4 | 0.99 | 1.15 | 0.96 | 0.74 | 0.99 | 1.15 | 0.96 | 0.74
0 | - | - | - | - | 219 | 2.8 | 2.5 | 2.4 | 2.2 | 2.2 | 2.2 | 2.7 | 2.7 | 1.44 | 1.23 | 0.85 | 1.1 | 1.44 | 1.23 | 0.85 | 1.1 | 0 | #VALUE! | #VALUE! | - | 219.5 | 2.7 | 2.7 | 2.5 | 2.2 | 2.2 | 2.2 | 2.4 | 2.9 | 1.1 | 1.05 | 0.95 | 1.01 | 1.1 | 1.05 | 0.95 | 1.01
0 | - | - | - | - | 220 | 2.6 | 2.6 | 2.5 | 2.3 | 2.2 | 2.2 | 2.2 | 2.7 | 0.96 | 0.92 | 0.99 | 1.01 | 0.96 | 0.92 | 0.99 | 1.01 | 0 | #VALUE! | #VALUE! | - | 220.5 | 2.4 | 2.4 | 2.5 | 2.2 | 2.1 | 2.2 | 2.2 | 2.4 | 1.09 | 0.78 | 0.6 | 0.59 | 1.09 | 0.78 | 0.6 | 0.59
0 | - | - | - | - | 221 | 2.4 | 2.4 | 2.5 | 2.2 | 2.1 | 2.1 | 2.2 | 2.2 | 1.06 | 0.86 | 0.94 | 1.13 | 1.06 | 0.86 | 0.94 | 1.13 | 0 | #VALUE! | #VALUE! | - | 221.5 | 2.3 | 2.6 | 2.2 | 2.2 | 2.1 | 2.1 | 2.2 | 2.2 | 0.6 | 0.68 | 0.83 | 0.86 | 0.6 | 0.68 | 0.83 | 0.86
0 | - | - | - | - | 222 | 2.3 | 2.4 | 2.2 | 2.2 | 2.1 | 2.1 | 2.1 | 2.2 | 1.29 | 1.19 | 1.08 | 1.19 | 1.29 | 1.19 | 1.08 | 1.19 | 0 | #VALUE! | #VALUE! | - | 222.5 | 2.4 | 2.3 | 2.2 | 2.1 | 2.1 | 2.1 | 2.1 | 2.2 | 1.22 | 1.22 | 0.95 | 0.95 | 1.22 | 1.22 | 0.95 | 0.95
0 | - | - | - | - | 223 | 2.4 | 2.2 | 2.2 | 2.1 | 2.1 | 2.2 | 2.1 | 2.2 | 1.17 | 1.19 | 1.04 | 1.03 | 1.17 | 1.19 | 1.04 | 1.03 | 0 | #VALUE! | #VALUE! | - | 223.5 | 2.3 | 2.2 | 2.2 | 2.1 | 2.1 | 2.2 | 2.1 | 2.1 | 0.6 | 0.73 | 0.59 | 0.59 | 0.6 | 0.73 | 0.59 | 0.59
0 | - | - | - | - | 224 | 2.2 | 2.2 | 2.2 | 2.1 | 2.1 | 2.2 | 2.2 | 2.1 | 0.91 | 1.03 | 1.21 | 1.12 | 0.91 | 1.03 | 1.21 | 1.12 | 0 | #VALUE! | #VALUE! | - | 224.5 | 2.2 | 2.2 | 2.1 | 2.1 | 2.1 | 2.2 | 2.1 | 2.1 | 0.81 | 0.95 | 1.14 | 1.03 | 0.81 | 0.95 | 1.14 | 1.03
0 | - | - | - | - | 225 | 2.2 | 2.2 | 2.1 | 2.1 | 2.2 | 2.2 | 2.1 | 2.2 | 1.15 | 0.9 | 1.03 | 1.26 | 1.15 | 0.9 | 1.03 | 1.26 | 0 | #VALUE! | #VALUE! | - | 225.5 | 2.2 | 2.2 | 2.1 | 2.2 | 2.3 | 2.2 | 2.2 | 2.1 | 1.35 | 1.03 | 0.62 | 1.03 | 1.35 | 1.03 | 0.62 | 1.03
0 | - | - | - | - | 226 | 2.1 | 2.1 | 2.1 | 2.2 | 2.3 | 2.2 | 2.2 | 2.1 | 0.96 | 1.12 | 1.18 | 1.04 | 0.96 | 1.12 | 1.18 | 1.04 | 0 | #VALUE! | #VALUE! | - | 226.5 | 2.1 | 2.1 | 2.1 | 2.2 | 2.2 | 2.2 | 2.2 | 2.1 | 1.18 | 1.26 | 1.18 | 1.09 | 1.18 | 1.26 | 1.18 | 1.09
0 | - | - | - | - | 227 | 2.1 | 2.1 | 2.1 | 2.2 | 2.2 | 2.2 | 2.2 | 2.1 | 1.13 | 1.33 | 1.17 | 0.92 | 1.13 | 1.33 | 1.17 | 0.92 | 0 | #VALUE! | #VALUE! | - | 227.5 | 2.1 | 2.1 | 2.3 | 2.2 | 2.3 | 2.2 | 2.2 | 2.1 | 0.9 | 0.86 | 0.97 | 0.59 | 0.9 | 0.86 | 0.97 | 0.59
0 | - | - | - | - | 228 | 2.2 | 2.3 | 2.2 | 2.2 | 2.3 | 2.1 | 2.2 | 2.3 | 1.19 | 1.08 | 1.13 | 1.23 | 1.19 | 1.08 | 1.13 | 1.23 | 0 | #VALUE! | #VALUE! | - | 228.5 | 2.2 | 2.2 | 2.2 | 2.2 | 2.1 | 2.2 | 2.2 | 2.2 | 0.86 | 1.03 | 0.97 | 0.79 | 0.86 | 1.03 | 0.97 | 0.79
0 | - | - | - | - | 229 | 2.2 | 2.2 | 2.1 | 2.2 | 2.4 | 2.2 | 2.2 | 2.3 | 1.41 | 1.12 | 0.88 | 1.24 | 1.41 | 1.12 | 0.88 | 1.24 | 0 | #VALUE! | #VALUE! | - | 229.5 | 2.2 | 2.2 | 2.2 | 2.4 | 2.6 | 2.4 | 2.1 | 2.4 | 1.12 | 0.97 | 0.92 | 1.06 | 1.12 | 0.97 | 0.92 | 1.06
0 | - | - | - | - | 230 | 2.2 | 2.1 | 2.5 | 2.6 | 2.8 | 2.6 | 2.1 | 2.3 | 1.24 | 1.04 | 0.79 | 1.05 | 1.24 | 1.04 | 0.79 | 1.05 | 0 | #VALUE! | #VALUE! | - | 230.5 | 2.2 | 2.3 | 2.8 | 2.8 | 3 | 2.9 | 2.5 | 2.1 | 0.59 | 0.82 | 1 | 0.73 | 0.59 | 0.82 | 1 | 0.73
0 | - | - | - | - | 231 | 2.4 | 2.8 | 2.8 | 2.6 | 2.9 | 2.9 | 2.9 | 2.4 | 1.45 | 1.21 | 1.04 | 1.31 | 1.45 | 1.21 | 1.04 | 1.31 | 0 | #VALUE! | #VALUE! | - | 231.5 | 2.4 | 2.9 | 2.8 | 2.5 | 2.7 | 3 | 2.9 | 2.5 | 1.32 | 1.46 | 1.17 | 0.97 | 1.32 | 1.46 | 1.17 | 0.97
0 | - | - | - | - | 232 | 2.6 | 2.9 | 2.7 | 2.3 | 2.4 | 3 | 3 | 2.6 | 1.46 | 1.69 | 1.53 | 1.24 | 1.46 | 1.69 | 1.53 | 1.24 | 0 | #VALUE! | #VALUE! | - | 232.5 | 2.7 | 2.9 | 2.6 | 2.2 | 2.2 | 2.8 | 3 | 2.8 | 0.72 | 1.04 | 1.14 | 0.85 | 0.72 | 1.04 | 1.14 | 0.85
0 | - | - | - | - | 233 | 2.8 | 2.8 | 2.4 | 2.2 | 2.1 | 2.5 | 3 | 2.9 | 1.42 | 1.47 | 1.21 | 1.14 | 1.42 | 1.47 | 1.21 | 1.14 | 0 | #VALUE! | #VALUE! | - | 233.5 | 2.8 | 2.7 | 2.4 | 2.2 | 2.1 | 2.3 | 2.4 | 2.9 | 1.27 | 1.33 | 1.01 | 0.94 | 1.27 | 1.33 | 1.01 | 0.94
0 | - | - | - | - | 234 | 2.8 | 2.5 | 2.4 | 2.3 | 2.1 | 2.1 | 2.9 | 3 | 0.94 | 1.19 | 1.31 | 1.09 | 0.94 | 1.19 | 1.31 | 1.09 | 0 | #VALUE! | #VALUE! | - | 234.5 | 2.6 | 2.4 | 2.5 | 2.4 | 2.2 | 2.1 | 2.4 | 2.8 | 0.87 | 0.95 | 0.92 | 0.83 | 0.87 | 0.95 | 0.92 | 0.83
0 | - | - | - | - | 235 | 2.4 | 2.4 | 2.7 | 2.5 | 2.1 | 2.2 | 2.1 | 2.4 | 1.04 | 0.85 | 0.96 | 1.13 | 1.04 | 0.85 | 0.96 | 1.13 | 0 | #VALUE! | #VALUE! | - | 235.5 | 2.4 | 2.6 | 2.5 | 2.4 | 2.1 | 2.2 | 2.1 | 2.1 | 0.73 | 0.59 | 0.67 | 0.79 | 0.73 | 0.59 | 0.67 | 0.79
0 | - | - | - | - | 236 | 2.5 | 2.5 | 2.3 | 2.3 | 2.1 | 2.1 | 2.2 | 2.2 | 1.08 | 0.74 | 0.72 | 1.04 | 1.08 | 0.74 | 0.72 | 1.04 | 0 | #VALUE! | #VALUE! | - | 236.5 | 2.7 | 2.4 | 2.2 | 2.3 | 2.1 | 2.1 | 2.2 | 2.2 | 0.85 | 0.65 | 0.59 | 0.59 | 0.85 | 0.65 | 0.59 | 0.59
0 | - | - | - | - | 237 | 2.8 | 2.2 | 2.2 | 2.2 | 2.1 | 2.1 | 2.1 | 2.3 | 0.92 | 0.62 | 0.81 | 1.09 | 0.92 | 0.62 | 0.81 | 1.09 | 0 | #VALUE! | #VALUE! | - | 237.5 | 2.7 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.3 | 0.59 | 0.59 | 0.73 | 0.87 | 0.59 | 0.59 | 0.73 | 0.87
0 | - | - | - | - | 238 | 2.4 | 2.2 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.4 | 1.15 | 0.96 | 0.69 | 0.95 | 1.15 | 0.96 | 0.69 | 0.95 | 0 | #VALUE! | #VALUE! | - | 238.5 | 2.3 | 2.1 | 2.1 | 2.2 | 2.2 | 2.1 | 2.1 | 2.3 | 0.88 | 0.86 | 0.91 | 0.94 | 0.88 | 0.86 | 0.91 | 0.94
0 | - | - | - | - | 239 | 2.2 | 2.1 | 2.1 | 2.2 | 2.2 | 2.1 | 2.1 | 2.2 | 1.36 | 1.17 | 1.13 | 1.32 | 1.36 | 1.17 | 1.13 | 1.32 | 0 | #VALUE! | #VALUE! | - | 239.5 | 2.1 | 2.1 | 2.2 | 2.2 | 2.2 | 2.1 | 2.1 | 2.2 | 0.88 | 1.03 | 1.06 | 0.94 | 0.88 | 1.03 | 1.06 | 0.94
0 | - | - | - | - | 240 | 2.1 | 2.1 | 2.3 | 2.3 | 2.3 | 2.3 | 2.1 | 2.2 | 1.08 | 1.1 | 1.17 | 1.14 | 1.08 | 1.1 | 1.17 | 1.14 | 0 | #VALUE! | #VALUE! | - | 240.5 | 2.1 | 2.4 | 2.5 | 2.2 | 2.3 | 2.3 | 2.2 | 2.1 | 0.87 | 0.96 | 0.9 | 0.79 | 0.87 | 0.96 | 0.9 | 0.79
0 | - | - | - | - | 241 | 2.1 | 2.6 | 2.1 | 2.1 | 2.3 | 2.3 | 2.3 | 2.2 | 1.09 | 0.88 | 0.85 | 1.05 | 1.09 | 0.88 | 0.85 | 1.05 | 0 | #VALUE! | #VALUE! | - | 241.5 | 2.1 | 2.5 | 2.1 | 2.1 | 2.3 | 2.3 | 2.3 | 2.2 | 0.97 | 0.78 | 0.59 | 0.65 | 0.97 | 0.78 | 0.59 | 0.65
0 | - | - | - | - | 242 | 2.3 | 2.4 | 2.1 | 2.1 | 2.1 | 2.2 | 2.3 | 2.2 | 0.99 | 0.78 | 0.59 | 0.83 | 0.99 | 0.78 | 0.59 | 0.83 | 0 | #VALUE! | #VALUE! | - | 242.5 | 2.4 | 2.3 | 2.1 | 2.1 | 2.1 | 2.3 | 2.3 | 2.2 | 1.01 | 0.77 | 0.71 | 0.96 | 1.01 | 0.77 | 0.71 | 0.96
0 | - | - | - | - | 243 | 2.4 | 2.2 | 2.1 | 2.1 | 2.1 | 2.3 | 2.3 | 2.2 | 0.96 | 0.81 | 0.82 | 0.97 | 0.96 | 0.81 | 0.82 | 0.97 | 0 | #VALUE! | #VALUE! | - | 243.5 | 2.3 | 2.1 | 2.1 | 2.1 | 2.1 | 2.2 | 2.3 | 2.2 | 0.82 | 0.78 | 0.73 | 0.77 | 0.82 | 0.78 | 0.73 | 0.77
0 | - | - | - | - | 244 | 2.2 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.3 | 2.2 | 1.17 | 0.87 | 0.91 | 1.19 | 1.17 | 0.87 | 0.91 | 1.19 | 0 | #VALUE! | #VALUE! | - | 244.5 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.2 | 2.2 | 1.03 | 0.88 | 1.17 | 1.28 | 1.03 | 0.88 | 1.17 | 1.28
0 | - | - | - | - | 245 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 0.97 | 0.94 | 1.12 | 1.15 | 0.97 | 0.94 | 1.12 | 1.15 | 0 | #VALUE! | #VALUE! | - | 245.5 | 2.1 | 2.1 | 2.2 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 0.85 | 1 | 1.14 | 1.03 | 0.85 | 1 | 1.14 | 1.03
0 | - | - | - | - | 246 | 2.1 | 2.2 | 2.2 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 0.9 | 1.28 | 1.69 | 1.38 | 0.9 | 1.28 | 1.69 | 1.38 | 0 | #VALUE! | #VALUE! | - | 246.5 | 2.1 | 2.2 | 2.3 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 0.73 | 1.06 | 1.35 | 1.09 | 0.73 | 1.06 | 1.35 | 1.09
0 | - | - | - | - | 247 | 2.1 | 2.2 | 2.4 | 2.2 | 2.2 | 2.2 | 2.1 | 2.1 | 1.18 | 1.21 | 1.36 | 1.35 | 1.18 | 1.21 | 1.36 | 1.35 | 0 | #VALUE! | #VALUE! | - | 247.5 | 2.2 | 2.2 | 2.4 | 2.4 | 2.4 | 2.3 | 2.1 | 2.1 | 0.78 | 1.12 | 1.26 | 0.99 | 0.78 | 1.12 | 1.26 | 0.99
0 | - | - | - | - | 248 | 2.2 | 2.2 | 2.4 | 2.5 | 2.3 | 2.3 | 2.1 | 2.1 | 1.1 | 1.05 | 1.36 | 1.38 | 1.1 | 1.05 | 1.36 | 1.38 | 0 | #VALUE! | #VALUE! | - | 248.5 | 2.2 | 2.2 | 2.5 | 2.4 | 2.3 | 2.2 | 2.1 | 2.1 | 0.9 | 1.18 | 1.13 | 0.83 | 0.9 | 1.18 | 1.13 | 0.83
0 | - | - | - | - | 249 | 2.2 | 2.2 | 2.3 | 2.5 | 2.5 | 2.4 | 2.1 | 2.1 | 1.09 | 1.36 | 1.6 | 1.38 | 1.09 | 1.36 | 1.6 | 1.38 | 0 | #VALUE! | #VALUE! | - | 249.5 | 2.2 | 2.4 | 2.4 | 2.5 | 2.6 | 2.3 | 2.1 | 2.2 | 0.73 | 0.92 | 1.05 | 0.9 | 0.73 | 0.92 | 1.05 | 0.9
0 | - | - | - | - | 250 | 2.2 | 2.7 | 2.2 | 2.7 | 2.7 | 2.6 | 2.1 | 2.3 | 1.15 | 1 | 0.97 | 1.13 | 1.15 | 1 | 0.97 | 1.13 | 0 | #VALUE! | #VALUE! | - | 250.5 | 2.3 | 2.3 | 2.3 | 2.9 | 2.9 | 2.5 | 2.4 | 2.4 | 1.09 | 1.05 | 0.99 | 1.03 | 1.09 | 1.05 | 0.99 | 1.03
0 | - | - | - | - | 251 | 2.4 | 2.3 | 2.6 | 2.9 | 3 | 2.8 | 2.5 | 2.4 | 1.55 | 1.14 | 0.94 | 1.4 | 1.55 | 1.14 | 0.94 | 1.4 | 0 | #VALUE! | #VALUE! | - | 251.5 | 2.4 | 2.3 | 2.8 | 2.9 | 3 | 3 | 2.5 | 2.4 | 1.17 | 0.85 | 0.92 | 1.22 | 1.17 | 0.85 | 0.92 | 1.22
0 | - | - | - | - | 252 | 2.3 | 2.6 | 2.9 | 2.9 | 3 | 3 | 2.6 | 2.3 | 0.95 | 1.12 | 1.17 | 1.01 | 0.95 | 1.12 | 1.17 | 1.01 | 0 | #VALUE! | #VALUE! | - | 252.5 | 2.3 | 2.9 | 2.9 | 2.9 | 3 | 3 | 2.8 | 2.3 | 0.59 | 0.71 | 0.86 | 0.59 | 0.59 | 0.71 | 0.86 | 0.59
0 | - | - | - | - | 253 | 2.8 | 2.8 | 2.9 | 2.9 | 3 | 3 | 2.9 | 2.4 | 0.78 | 0.76 | 0.95 | 0.96 | 0.78 | 0.76 | 0.95 | 0.96 | 0 | #VALUE! | #VALUE! | - | 253.5 | 2.8 | 2.9 | 2.9 | 3 | 3 | 3 | 2.9 | 2.6 | 0.74 | 0.99 | 1.04 | 0.82 | 0.74 | 0.99 | 1.04 | 0.82
0 | - | - | - | - | 254 | 2.8 | 3 | 2.8 | 2.9 | 2.9 | 3 | 2.9 | 2.8 | 0.99 | 1.03 | 1.15 | 1.13 | 0.99 | 1.03 | 1.15 | 1.13 | 0 | #VALUE! | #VALUE! | - | 254.5 | 2.8 | 3 | 2.7 | 2.7 | 2.9 | 3 | 2.9 | 2.9 | 0.99 | 0.91 | 0.83 | 0.92 | 0.99 | 0.91 | 0.83 | 0.92
0 | - | - | - | - | 255 | 2.9 | 3 | 2.6 | 2.7 | 2.9 | 3 | 2.9 | 2.9 | 0.97 | 0.92 | 1.06 | 1.1 | 0.97 | 0.92 | 1.06 | 1.1 | 0 | #VALUE! | #VALUE! | - | 255.5 | 3 | 2.9 | 2.6 | 2.6 | 2.8 | 3 | 2.9 | 2.9 | 0.86 | 1 | 0.83 | 0.65 | 0.86 | 1 | 0.83 | 0.65
0 | - | - | - | - | 256 | 3 | 2.9 | 2.6 | 2.6 | 2.6 | 3 | 2.9 | 2.9 | 0.99 | 1.04 | 1.1 | 1.06 | 0.99 | 1.04 | 1.1 | 1.06 | 0 | #VALUE! | #VALUE! | - | 256.5 | 2.9 | 2.9 | 2.6 | 2.6 | 2.5 | 2.9 | 2.9 | 2.9 | 1 | 1.04 | 1.06 | 1.04 | 1 | 1.04 | 1.06 | 1.04
0 | - | - | - | - | 257 | 2.9 | 2.8 | 2.5 | 2.5 | 2.4 | 2.8 | 2.9 | 2.9 | 1.12 | 0.95 | 1.13 | 1.27 | 1.12 | 0.95 | 1.13 | 1.27 | 0 | #VALUE! | #VALUE! | - | 257.5 | 2.9 | 2.7 | 2.7 | 2.4 | 2.4 | 2.6 | 2.9 | 2.9 | 0.92 | 1.04 | 0.91 | 0.77 | 0.92 | 1.04 | 0.91 | 0.77
0 | - | - | - | - | 258 | 2.8 | 2.6 | 2.9 | 2.5 | 2.2 | 2.6 | 2.7 | 2.7 | 1.17 | 1.09 | 1.1 | 1.18 | 1.17 | 1.09 | 1.1 | 1.18 | 0 | #VALUE! | #VALUE! | - | 258.5 | 2.8 | 2.8 | 2.9 | 2.4 | 2.2 | 2.4 | 2.6 | 2.5 | 1.1 | 1 | 0.78 | 0.92 | 1.1 | 1 | 0.78 | 0.92
0 | - | - | - | - | 259 | 2.7 | 2.8 | 2.9 | 2.4 | 2.1 | 2.2 | 2.7 | 2.4 | 1.4 | 1.21 | 1.01 | 1.24 | 1.4 | 1.21 | 1.01 | 1.24 | 0 | #VALUE! | #VALUE! | - | 259.5 | 2.7 | 2.8 | 2.9 | 2.4 | 2.1 | 2.1 | 2.7 | 2.5 | 0.92 | 1.06 | 0.86 | 0.68 | 0.92 | 1.06 | 0.86 | 0.68
0 | - | - | - | - | 260 | 2.6 | 2.9 | 2.4 | 2.4 | 2.1 | 2.1 | 2.6 | 2.6 | 0.99 | 1.01 | 0.95 | 0.92 | 0.99 | 1.01 | 0.95 | 0.92 | 0 | #VALUE! | #VALUE! | - | 260.5 | 2.6 | 2.8 | 2.4 | 2.4 | 2.1 | 2.1 | 2.6 | 2.6 | 0.99 | 1.01 | 0.96 | 0.94 | 0.99 | 1.01 | 0.96 | 0.94
0 | - | - | - | - | 261 | 2.6 | 2.8 | 2.3 | 2.3 | 2.1 | 2.1 | 2.5 | 2.6 | 0.99 | 1.01 | 0.96 | 0.94 | 0.99 | 1.01 | 0.96 | 0.94 | 0 | - | - | - | 261.5
0 | - | - | - | - | 262 | 2.6 | 2.8 | 2.3 | 2.3 | 2.1 | 2.1 | 2.5 | 2.6 | 0.99 | 1.03 | 0.96 | 0.92 | 0.99 | 1.03 | 0.96 | 0.92 | 0 | - | - | - | 262.5
0 | - | - | - | - | 263 | 2.6 | 2.2 | 2.2 | 2.3 | 2.2 | 2.4 | 2.6 | 2.6 | 0.87 | 0.99 | 0.96 | 0.83 | 0.87 | 0.99 | 0.96 | 0.83 | 0 | 1870405.748 | 5720226.7145 | - | 263.5 | 2.6 | 2.2 | 2.2 | 2.3 | 2.2 | 2.4 | 2.6 | 2.6 | 0.87 | 1 | 0.96 | 0.83 | 0.87 | 1 | 0.96 | 0.83 | Copied coordinates and multipliers from WRK1 S/S
CONTAINS FORMULAE IN CASE OF ACCIDENTAL DELETION
DATA TO BE ENTERED
COMPUTED DATA (TO BE CHECKED)
MANUALLY ADJUSTED FORMULA (CHECK AS ASSET SPECIFIC)
DATA PROVIDED BY NIWA
USER GUIDE
Note on A11: This data is derived directly from the PLS-CADD staking table Structure heights need to be verified
Note on W11: the Mid-span site is defined as the middle point between adjacent structures irrespective of terrain
Note on E12: Maximum overall Height of the object (as PLS-CADD staking table; if these are not correct modify to suit). These heights are only required for NIWA terrain definition
Note on Z12: Based on maximum "clearance" in span to all conductors These heights are only required for NIWA terrain definition

## Site Wind
NIWA WAsP Analysis - Selection of critical Design Wind Speeds | [21 empty] | INPUTS (linked to Site WAsP data)
REF: ADEGL_02_11 | [20 empty] | Wind Region | A7
|  | Project Name: | 0 | [17 empty] | Equivalent V1000 Wind Speed | 46
|  | Project Code: | 0
|  | Asset: | WRK-WHI A
|  | NIWA Analysis Date: | 0
|  | Analysis By: | Richard Turner, Sylvia Nichol, Stuart Moore | [17 empty] | V1000 for Asset: | 46 | m/s
AVERAGE HEIGHT OF CONDUCTORS DERIVED FROM TERRAIN CLEARANCES BY SURVEY POINT
CONTROL |  |  |  |  | DERIVED DATA - STRUCTURES | [16 empty] | DERIVED DATA - SPANS
STRUCTURES |  |  |  | Structure wind loading centroid (%) | Centroid of wind area agl (m) | SITE UPWIND MZ,CAT FOR HEIGHT "Z" ABOVE GROUND | [7 empty] | DESIGN WIND SPEEDS V1000,β,Z,CAT m/s @"Z" AGL (inc MD (below),Mt,Ms,MZ,CAT) | [7 empty] | Avg Ht AGL of all condrs in span (m) | SITE UPWIND MZ,CAT FOR HEIGHT "Z" ABOVE GROUND | [7 empty] | DESIGN DESIGN WIND SPEEDS V1000,β,Z,CAT m/s @"Z" AGL (inc MD (below),Mt,Ms,MZ,CAT)
Structure Number | NZTM 2000 |  | Structure Height above GL (m) |  |  | N | NE | E | SE | S | SW | W | NW | N | NE | E | SE | S | SW | W | NW |  | N | NE | E | SE | S | SW | W | NW | N | NE | E | SE | S | SW | W | NW
| X Easting (m) | Y Northing (m) |  |  |  | DESIGN WIND SPEEDS V1000,β,Z,CAT m/s @"Z" AGL (inc MD (below),Mt,Ms,MZ,CAT) N: 0.9; DESIGN WIND SPEEDS V1000,β,Z,CAT m/s @"Z" AGL (inc MD (below),Mt,Ms,MZ,CAT) NE: 0.9; DESIGN WIND SPEEDS V1000,β,Z,CAT m/s @"Z" AGL (inc MD (below),Mt,Ms,MZ,CAT) E: 0.8; DESIGN WIND SPEEDS V1000,β,Z,CAT m/s @"Z" AGL (inc MD (below),Mt,Ms,MZ,CAT) SE: 0.9; DESIGN WIND SPEEDS V1000,β,Z,CAT m/s @"Z" AGL (inc MD (below),Mt,Ms,MZ,CAT) S: 0.9; DESIGN WIND SPEEDS V1000,β,Z,CAT m/s @"Z" AGL (inc MD (below),Mt,Ms,MZ,CAT) SW: 0.9; DESIGN WIND SPEEDS V1000,β,Z,CAT m/s @"Z" AGL (inc MD (below),Mt,Ms,MZ,CAT) W: 1; DESIGN WIND SPEEDS V1000,β,Z,CAT m/s @"Z" AGL (inc MD (below),Mt,Ms,MZ,CAT) NW: 1 | [9 empty] | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 1 | 1
Structure Number | - | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | No Data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 0 | 0 | 45 | 100% | 45 | 1.101 | 1.147 | 1.147 | 1.1355 | 1.147 | 1.1125 | 1.101 | 1.101 | 39.6558 | 47.0109 | 40.5212 | 39.9582 | 41.3126 | 45.5969 | 48.6202 | 43.0491 | 25 | 1.022 | 1.074 | 1.074 | 1.061 | 1.074 | 1.048 | 1.022 | 1.022 | 36.8104 | 44.4636 | 37.9423 | 36.4581 | 38.6833 | 43.3872 | 45.1315 | 39.02
2 | 350 | 0 | 45 | 50% | 23 | 1.0116 | 1.0652 | 1.0652 | 1.0518 | 1.0652 | 1.0384 | 1.0116 | 0.9982 | 36.4358 | 43.6583 | 37.6314 | 36.142 | 38.3664 | 42.5599 | 44.6723 | 38.1113 | 33 | 1.084 | 1.108 | 1.108 | 1.096 | 1.108 | 1.072 | 1.072 | 1.048 | 39.0435 | 45.4125 | 39.1434 | 37.6608 | 39.9079 | 43.937 | 47.3395 | 40.0126
3 | 700 | 0 | 45 | 50% | 23 | 1.0384 | 1.0786 | 1.0518 | 1.0652 | 1.0518 | 1.0116 | 1.025 | 0.9982 | 37.831 | 44.654 | 37.158 | 36.6024 | 38.3192 | 41.8802 | 45.264 | 38.1113 | 33 | 1.096 | 1.12 | 1.096 | 1.096 | 1.096 | 1.084 | 1.072 | 1.06 | 39.4757 | 46.368 | 38.7195 | 37.6608 | 39.4757 | 44.8776 | 47.3395 | 40.4708
4 | 330 | -100 | 20 | 50% | 10 | 0.949 | 0.983 | 0.949 | 0.932 | 0.949 | 0.949 | 0.915 | 0.915 | 34.1811 | 40.6962 | 33.8755 | 32.0254 | 34.1811 | 39.2886 | 40.8273 | 34.9347 | 28 | 1.0872 | 1.0996 | 1.0624 | 1.05 | 1.0748 | 1.0748 | 1.0624 | 1.0624 | 38.7087 | 45.0682 | 37.5325 | 35.6454 | 38.2672 | 44.0518 | 46.9156 | 40.0737
5 | 370 | -100 | 20 | 50% | 10 | 0.966 | 0.983 | 0.932 | 0.932 | 0.949 | 0.949 | 0.949 | 0.932 | 34.3935 | 39.4753 | 32.5827 | 31.6395 | 33.7882 | 38.1099 | 41.4713 | 35.155 | 22 | 1.0744 | 1.0472 | 1.0336 | 1.0472 | 1.0608 | 1.0472 | 1.0744 | 1.0608 | 35.1393 | 40.7528 | 35.7543 | 35.1168 | 34.6945 | 40.7528 | 46.4571 | 39.5254
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | - | - | - | 50% | - | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | No Data | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CONTAINS FORMULAE IN CASE OF ACCIDENTAL DELETION
DATA TO BE ENTERED
COMPUTED DATA (TO BE CHECKED)
MANUALLY ADJUSTED FORMULA (CHECK AS ASSET SPECIFIC)
DATA PROVIDED BY NIWA
USER GUIDE
Note on E10: Value entered in tab "Structure Data"
Note on D11: Maximum overall Height of the object (as PLS-CADD staking table); if these are not correct modify to suit in 'Structure Data'

## V1000 Design Wind
Evaluation of Critical Wind Speeds by direction for input to PLS-CADD
REF: ADEGL_02_11
|  | Project Name: | 0
|  | Project Code: | 0
|  | Asset: | WRK-WHI A
|  | NIWA Analysis Date: | 0
|  | Analysis By: | Richard Turner, Sylvia Nichol, Stuart Moore
SELECT Wind Angle range (±θ) to structure trans axis
|  |  | 25 |  | SUS | or towers with a turn off angle between 0° and <20°
|  |  | 45 |  | STR | or towers with a turn off angle ≥20° and <60° (to provide additional security for ”angle” towers)
|  |  | 90 |  | DE | or all other towers and for all dead end towers | [14 empty] | 25 |  | Wind Angle (θ) to trans azimuth
|  |  | STRUCTURES | [17 empty] | CALCULATED FROM COORDINATES |  |  | SPANS
Structure Number | NZTM 2000 Structure Co-ordinates |  | Line Angle (°) | Structure Function | Wind Angle Range | Structure Trans Axis Azimuth (°) | Structure Trans Axis Azimuth +180° (°) | WIND SPEEDS VDES,β,Z,CAT WITHIN SELECTED BOUNDARIES (m/s) | [7 empty] | SUMMARY |  |  |  |  | Bearing span ahead (°) Azimuth to North | Span +Trans Axis Azimuth (°) | Span -Trans Axis Azimuth +180° (°) | WIND SPEEDS VDES,β,Z,CAT WITHIN SELECTED BOUNDARIES (m/s) | [7 empty] | SUMMARY |  |  |  |  | CORRECTED FOR SPAN REDUCTION FACTOR
| X Easting (m) | Y Northing (m) | [5 empty] | N | NE | E | SE | S | SW | W | NW | V1000,β,Z,CAT | Height "Z" (m) | Direction β | Terrain Category CAT | V1000,β,10,2 (for reference) |  |  |  | N | NE | E | SE | S | SW | W | NW | V1000,β,Z,CAT | Height "Z" (m) | Direction β | Terrain Category CAT | V1000,β,10,2 (for reference) | Span Ahead (m) | Span Reduction Factor | V1000,β,Z,CAT (inc SRF)
[8 empty] | 0 | 45 | 90 | 135 | 180 | 225 | 270 | 315 | [8 empty] | 0 | 45 | 90 | 135 | 180 | 225 | 270 | 315
Structure Number | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
1 | 0 | 0 | 0 | STR | 45 | 180 | 0 | 39.6558 | 47.0109 | - | 39.9582 | 41.3126 | 45.5969 | - | 43.0491 | 47.01 | 45 | NE | 2 | 41 | 90 | 180 | 0 | 36.8104 | - | - | - | 38.6833 | - | - | - | 38.68 | 25 | S | 2 | 36 | 350 | 0.77312 | 34.01
2 | 350 | 0 | 0 | STR | 45 | 180 | 0 | 36.4358 | 43.6583 | - | 36.142 | 38.3664 | 42.5599 | - | 38.1113 | 43.66 | 23 | NE | 2 | 40 | 90 | 180 | 0 | 39.0435 | - | - | - | 39.9079 | - | - | - | 39.91 | 33 | S | 2 | 36 | 350 | 0.79091 | 35.49
3 | 700 | 0 | 0 | STR | 45 | 180 | 0 | 37.831 | 44.654 | - | 36.6024 | 38.3192 | 41.8802 | - | 38.1113 | 44.65 | 23 | NE | 2 | 41 | 255 | 345 | 165 | 39.4757 | - | - | - | 39.4757 | - | - | - | 39.48 | 33 | N | 2 | 35 | 383.275 | 0.78262 | 34.93
4 | 330 | -100 | 0 | DE | 90 | 270 | 90 | 34.1811 | 40.6962 | 33.8755 | 32.0254 | 34.1811 | 39.2886 | 40.8273 | 34.9347 | 40.83 | 10 | W | 2.5 | 44 | 90 | 180 | 0 | 38.7087 | - | - | - | 38.2672 | - | - | - | 38.71 | 28 | N | 2 | 35 | 40 | 0.94842 | 37.7
5 | 370 | -100 | 0 | DE | 90 | 270 | 90 | 34.3935 | 39.4753 | 32.5827 | 31.6395 | 33.7882 | 38.1099 | 41.4713 | 35.155 | 41.47 | 10 | W | 2 | 42 | - | - | - | - | - | - | - | - | - | - | - | 0 | 22 | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | 264.761 | #VALUE! | #VALUE!
97a | 1898711.297 | 5689922.97 | 0 | STR | 25 | 218 | 38 | - | #VALUE! | - | - | - | #VALUE! | - | - | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | 264.352 | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
- | - | - | - | #N/A | #VALUE! | - | - | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | 0 | - | - | - | 0 | #VALUE! | #VALUE! | #VALUE!
USER GUIDE
CONTAINS FORMULAE IN CASE OF ACCIDENTAL DELETION
DATA TO BE ENTERED
COMPUTED DATA (TO BE CHECKED)
WIND SPEEDS TO BE TRANSFERRED TO PLS-CADD
(AUTO LINKED TO STAKING TABLE)
CHECK SPAN AHEAD VALUE
MANUALLY ADJUSTED FORMULA (CHECK AS ASSET SPECIFIC)
Note on G13: Direct from Staking table
Note on V13: Required for Span wind selection
Note on T14: Note Terrain Category is rounded down to the nearest multiple of 0.5
Note on AJ14: Note Terrain Category is rounded down to the nearest multiple of 0.5
Note on AL14: Cell turns red if the span does not agree with that given in the PLS-CADD staking table ; if necessary modifyt formula for identify the correct coordinates - ditto for the span ahead azimuth

## Charts
USER GUIDE

## Structure Data
THIS WORKSHEET CAN BE ADAPTED TO INDEPENDENTLY CALCULATE REQUIRED DATA
(e.g. STRUCTURE HEIGHTS, wind height centroids) | [7 empty] | SUS
- MODIFY TO SUIT ACTUAL DATA REQUIREMENT | [7 empty] | STR
|  |  |  | DEFAULT STRUCTURE WIND LOADING CENTROID TAKEN AS | 50% | OF STRUCTURE HEIGHT |  | DE
Twr No | Contract | Type | Function | OVERALL | WIND | WIND
(from staking table) | (from staking table) | (from staking table) | (from staking table) | HEIGHT [m] | CENTROID % | CENTROID [m] | Comments | WORKING COLUMNS (USER INPUT AS REQUIRED)
Structure Number |  |  | #N/A | #N/A | 0.5 | #N/A
1 |  |  | STR | 44.305 | 100% | 44.305 | Gantry | 2DD-HSTC Tower Data Input Rev A-str | 'All', 'Has DE', 'Not all sets DE', 'TOWER', 'TOWER has DE'
2 |  |  | STR | 44.305 | 50% | 22.1525 |  | 2DD-HSTC Tower Data Input Rev A-str | 'All', 'Has DE', 'Not all sets DE', 'TOWER', 'TOWER has DE'
3 |  |  | STR | 44.305 | 50% | 22.1525 |  | 2DD-HSTC Tower Data Input Rev A-str | 'All', 'Has DE', 'Not all sets DE', 'TOWER', 'TOWER has DE'
4 |  |  | DE | 19.4 | 50% | 9.7 |  | gantry | 'All', 'Has DE', 'All sets DE', 'TOWER', 'TOWER has DE'
5 |  |  | DE | 19.4 | 50% | 9.7 |  | gantry | 'All', 'Has DE', 'All sets DE', 'TOWER', 'TOWER has DE'
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | STR | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 100% | #N/A | Gantry | 0 | 0
0 |  |  | #N/A | #N/A | 50% | #N/A |  | 0 | 0
0 |  |  | #N/A | #N/A | 100% | #N/A | Gantry | 0 | 0
USER GUIDE
CONTAINS FORMULAE IN CASE OF ACCIDENTAL DELETION
DATA TO BE ENTERED
COMPUTED DATA (TO BE CHECKED)
MANUALLY ADJUSTED FORMULA (CHECK AS ASSET SPECIFIC)
DATA PROVIDED BY NIWA

## Staking Table
|  | Project Name: | 0 |  |  |  | TAKE CARE THE PLS-CADD MODEL STAKING TABLE ADOPTS THE SAME COLUMN DEFINITIONS AS PER ADEGL.02.06 | [12 empty] | These are the default Structure Comment column definitions in accordance with ADEGL.02.06 |  | Structure Number | Construction Number | Structure Photo | Wire wind velocity factor / speed Ahead Span | Wire ice load Ahead Span | Wire Ice thikcness factor Ahead Span | Wind velocity factor / speed Structure | TC Span | TC Structure | Tower / Pole Number | Tower Contract -Type OR Pole Length-Tip Capacity | Insulator Type OR Std. Structure Number | Common Body Length OR Pole Material | Body Extn. OR Crossarms | Leg Extn. OR No. Guys | Loss/Gain Pole Embed. | Struct. Dwg. Reference | Ruling Span | Wind Span (Wed) | Weight Span (Max Op.) | Weight Span (ted) | Insulator Attachment Height Above CP | Insulator Attachment RL | Conductor Attachment Type | Insulator Assembly Number | Conductor Weights | Number of Earthwires | Earthwire Attachment Type | Earthwire Assembly Number | Foundation Type | Foundation Dwg. Number | Comments | undefined | undefined | undefined | undefined | undefined | undefined | undefined | undefined | undefined | undefined | undefined | undefined | undefined | undefined | undefined | undefined | undefined | undefined
|  | Project Code: | 0 |  |  | This row contains formulae for back feeding into PLS-CADD - DO NOT DELETE - SEE COLUMN Y | [17 empty] | Copy these formulae down the column after copying and pasting Staking table >
|  | Asset: | WRK-WHI A |  |  | Coordinates based on NZTM2000 |  |  | 0
PLS-CADD DATA DUMP = "STAKING TABLE"
Row # | Structure Number | Station (m) | Height Adjust. (m) | Offset Adjust. (m) | Orientation Angle (deg) | X Easting (m) | Y Northing (m) | Centerline Z Elevation (m) | TIN Z Elevation (m) | Ahead Span (m) | Line Angle (deg) | Sets In XY Structure Line Angle Calculation | Transverse Axis Azimuth (deg) | Structure Name | Structure Description | Struct. Height (m) | Embedded Length (m) | Structure Specific Material | Counter Weights (N) | Automatic Structure Group Membership | Manual Structure Group Membership | Structure Comment 1 | Structure Comment 2 | Structure Comment 3 | Structure Comment 4 | Structure Comment 5 | Structure Comment 6 | Structure Comment 7 | Structure Comment 8 | Structure Comment 9 | Structure Comment 10 | Structure Comment 11 | Structure Comment 12 | Structure Comment 13 | Structure Comment 14 | Structure Comment 15 | Structure Comment 16 | Structure Comment 17 | Structure Comment 18 | Structure Comment 19 | Structure Comment 20 | Structure Comment 21 | Structure Comment 22 | Structure Comment 23 | Structure Comment 24 | Structure Comment 25 | Structure Comment 26 | Structure Comment 27 | Structure Comment 28 | Structure Comment 29 | Structure Comment 30 | Structure Comment 31 | Structure Comment 32 | Structure Comment 33 | Structure Comment 34 | Structure Comment 35 | Structure Comment 36 | Structure Comment 37 | Structure Comment 38 | Structure Comment 39 | Structure Comment 40 | Structure Comment 41 | Structure Comment 42 | Structure Comment 43 | Structure Comment 44 | Structure Comment 45 | Structure Comment 46 | Structure Comment 47 | Structure Comment 48 | Structure Comment 49 | Structure Comment 50
1 | 1 |  | 25.005 |  |  |  |  | 800 |  | 350 |  | 1960-01-01 | 180 | C:\Users\ErtugrulKeles\Groundline\NZ-6585 TP Standard GIP - Documents\03 Operations\PLS-CAD Model\structures\tower\2DDHST\2dd-hst-ew2-str-tee-be5m-le9.0-9.0-9.0-9.0.tow | 2DD-HSTC Tower Data Input Rev A-str | 19.3 |  | 0 |  | 'All', 'Has DE', 'Not all sets DE', 'TOWER', 'TOWER has DE' |  |  | Back | t | 34.01 |  |  | 47.01
2 | 2 | 350 | 25.005 |  |  | 350 |  | 800 |  | 350 |  | 1960-01-01 | 180 | C:\Users\ErtugrulKeles\Groundline\NZ-6585 TP Standard GIP - Documents\03 Operations\PLS-CAD Model\structures\tower\2DDHST\2dd-hst-ew2-str-tee-be5m-le9.0-9.0-9.0-9.0.tow | 2DD-HSTC Tower Data Input Rev A-str | 19.3 |  | 0 |  | 'All', 'Has DE', 'Not all sets DE', 'TOWER', 'TOWER has DE' |  |  | GIP | t | 35.49 |  |  | 43.66
3 | 3 | 700 | 25.005 |  |  | 700 |  | 800 |  |  |  | 1960-01-01 | 180 | C:\Users\ErtugrulKeles\Groundline\NZ-6585 TP Standard GIP - Documents\03 Operations\PLS-CAD Model\structures\tower\2DDHST\2dd-hst-ew2-str-tee-be5m-le9.0-9.0-9.0-9.0.tow | 2DD-HSTC Tower Data Input Rev A-str | 19.3 |  | 0 |  | 'All', 'Has DE', 'Not all sets DE', 'TOWER', 'TOWER has DE' |  |  | Ahead | t | 34.93 |  |  | 44.65
4 | 4 | 10000000000 | 1 |  | 180 | 330 | -100 | 800 |  |  |  | 1960-01-01 | 270 | C:\Users\ErtugrulKeles\Groundline\NZ-6585 TP Standard GIP - Documents\03 Operations\PLS-CAD Model\structures\gantry\220kV A-FRAME Gantry.tow | gantry | 18.4 |  | 0 |  | 'All', 'Has DE', 'All sets DE', 'TOWER', 'TOWER has DE' |  |  | Gantry | g | 37.7 |  |  | 40.83
5 | 5 | 10000000100 | 1 |  | 180 | 370 | -100 | 800 |  |  |  | 1960-01-01 | 270 | C:\Users\ErtugrulKeles\Groundline\NZ-6585 TP Standard GIP - Documents\03 Operations\PLS-CAD Model\structures\gantry\220kV A-FRAME Gantry.tow | gantry | 18.4 |  | 0 |  | 'All', 'Has DE', 'All sets DE', 'TOWER', 'TOWER has DE' |  |  | Gantry | g | 37.7 |  |  | 41.47
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100
101
102
103
104
105
106
107
108
109
110
111
112
113
114
115
116
117
118
119
120
121
122
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
142
143
144
145
146
147
148
149
150
151
152
153
154
155
156
157
158
159
160
161
162
163
164
165
166
167
168
169
170
171
172
173
174
175
176
177
178
179
180
181
182
183
184
185
186
187
188
189
190
191
192
193
194
195
196
197
198
199
200
201
202
203
204
205
206
207
208
209
210
211
212
213
214
215
216
217
218
219
220
221
222
223
224
225
226
227
228
229
230
231
232
233
234
235
236
237
238
239
240
241
242
243
244
245
246
247
248
249
250
251
252
253
254
255
256
257
258
259
260
261
262
263
USER GUIDE

## Span Heights
For NIWA topo factors only
PLS-CADD DATA DUMP = "TERRAIN CLEARANCES BY SURVEY POINT REPORT" (use variables as shown in screen shot) | [10 empty] | Structure - span ahead | Max "clearance" to GL | Conductor elevation
Row # | Point ID | Feature Code Description | Station (m) | Offset (m) | Z (m) | Height (m) | Clearance Margin Vert. (m) | Clearance Margin Horiz. (m) | OK | Comment
1 | TIN-INTERP | Interpolated Ground | -1.23 | -7.54 | 369.41 | 0 | 16.42 | 0 | OK | Ground clear controls. | WRK1 S/S | 35.4 | 385.83
2 | TIN-INTERP | Interpolated Ground | 2.09 | -4.84 | 369.42 | 0 | 14.6 | 0 | OK | Ground clear controls. | WRK1 S/S | 35.4 | 384.02
3 | TIN-INTERP | Interpolated Ground | 2.9 | -0.44 | 369.43 | 0 | 14.33 | 0 | OK | Ground clear controls. | WRK1 S/S | 35.4 | 383.76
4 | TIN-INTERP | Interpolated Ground | 3.71 | 4.07 | 371.7 | 0 | 35.4 | 0 | OK | Ground clear controls. | WRK1 S/S | 35.4 | 407.1
5 | TIN-INTERP | Interpolated Ground | 38.48 | -2.74 | 369.28 | 0 | 29.09 | 0 | OK | Ground clear controls. | WRK1 S/S | 29.09 | 398.37
6 | TIN-INTERP | Interpolated Ground | 42.08 | -4.26 | 369.12 | 0 | 24.53 | 0 | OK | Ground clear controls. | WRK1 S/S | 24.53 | 393.65
7 | TIN-INTERP | Interpolated Ground | 42.82 | -3.09 | 369.12 | 0 | 20.68 | 0 | OK | Ground clear controls. | WRK1 S/S | 20.68 | 389.8
8 | TIN-INTERP | Interpolated Ground | 43.25 | -1.94 | 369.17 | 0 | 16.9 | 0 | OK | Ground clear controls. | WRK1 S/S | 16.9 | 386.07
9 | TIN-INTERP | Interpolated Ground | 61.13 | -0.01 | 371.72 | 0 | 35.41 | 0 | OK | Ground clear controls. | 1 | 50.93 | 407.13
10 | TIN-INTERP | Interpolated Ground | 61.13 | -0.01 | 371.72 | 0 | 35.41 | 0 | OK | Ground clear controls. | 1 | 50.93 | 407.13
11 | TIN-INTERP | Interpolated Ground | 64.55 | 4.13 | 371.94 | 0 | 27.65 | 0 | OK | Ground clear controls. | 1 | 50.93 | 399.59
12 | TIN-INTERP | Interpolated Ground | 64.72 | 4.5 | 371.96 | 0 | 22.17 | 0 | OK | Ground clear controls. | 1 | 50.93 | 394.13
13 | TIN-INTERP | Interpolated Ground | 64.74 | -4.07 | 371.86 | 0 | 27.72 | 0 | OK | Ground clear controls. | 1 | 50.93 | 399.58
14 | TIN-INTERP | Interpolated Ground | 64.89 | -4.47 | 371.81 | 0 | 22.31 | 0 | OK | Ground clear controls. | 1 | 50.93 | 394.12
15 | TIN-INTERP | Interpolated Ground | 64.95 | 4.67 | 371.94 | 0 | 16.7 | 0 | OK | Ground clear controls. | 1 | 50.93 | 388.64
16 | TIN-INTERP | Interpolated Ground | 65.16 | -4.63 | 371.82 | 0 | 16.81 | 0 | OK | Ground clear controls. | 1 | 50.93 | 388.63
17 | TIN-INTERP | Interpolated Ground | 101.13 | 0.04 | 371.94 | 0 | 32.87 | 0 | OK | Ground clear controls. | 1 | 50.93 | 404.81
18 | TIN-INTERP | Interpolated Ground | 104.54 | 4.53 | 371.78 | 0 | 24.77 | 0 | OK | Ground clear controls. | 1 | 50.93 | 396.55
19 | TIN-INTERP | Interpolated Ground | 104.71 | 5.11 | 371.76 | 0 | 19.92 | 0 | OK | Ground clear controls. | 1 | 50.93 | 391.68
20 | TIN-INTERP | Interpolated Ground | 104.74 | -4.03 | 371.87 | 0 | 24.68 | 0 | OK | Ground clear controls. | 1 | 50.93 | 396.55
21 | TIN-INTERP | Interpolated Ground | 104.89 | -4.61 | 371.89 | 0 | 19.65 | 0 | OK | Ground clear controls. | 1 | 50.93 | 391.54
22 | TIN-INTERP | Interpolated Ground | 104.95 | 5.1 | 371.74 | 0 | 14.67 | 0 | OK | Ground clear controls. | 1 | 50.93 | 386.41
23 | TIN-INTERP | Interpolated Ground | 105.16 | -4.6 | 371.88 | 0 | 14.41 | 0 | OK | Ground clear controls. | 1 | 50.93 | 386.29
24 | TIN-INTERP | Interpolated Ground | 141.13 | 0.09 | 371.28 | 0 | 32.19 | 0 | OK | Ground clear controls. | 1 | 50.93 | 403.47
25 | TIN-INTERP | Interpolated Ground | 144.54 | 4.93 | 371.29 | 0 | 23.36 | 0 | OK | Ground clear controls. | 1 | 50.93 | 394.65
26 | TIN-INTERP | Interpolated Ground | 144.71 | 5.72 | 371.31 | 0 | 18.87 | 0 | OK | Ground clear controls. | 1 | 50.93 | 390.18
27 | TIN-INTERP | Interpolated Ground | 144.74 | -4 | 371.25 | 0 | 23.37 | 0 | OK | Ground clear controls. | 1 | 50.93 | 394.62
28 | TIN-INTERP | Interpolated Ground | 144.89 | -4.75 | 371.27 | 0 | 18.66 | 0 | OK | Ground clear controls. | 1 | 50.93 | 389.93
29 | TIN-INTERP | Interpolated Ground | 144.94 | 5.54 | 371.31 | 0 | 13.78 | 0 | OK | Ground clear controls. | 1 | 50.93 | 385.09
30 | TIN-INTERP | Interpolated Ground | 145.16 | -4.57 | 371.27 | 0 | 13.58 | 0 | OK | Ground clear controls. | 1 | 50.93 | 384.85
31 | TIN-INTERP | Interpolated Ground | 181.13 | 0.14 | 370.93 | 0 | 32.18 | 0 | OK | Ground clear controls. | 1 | 50.93 | 403.11
32 | TIN-INTERP | Interpolated Ground | 184.54 | 5.32 | 370.85 | 0 | 23.03 | 0 | OK | Ground clear controls. | 1 | 50.93 | 393.88
33 | TIN-INTERP | Interpolated Ground | 184.7 | 6.33 | 370.77 | 0 | 18.89 | 0 | OK | Ground clear controls. | 1 | 50.93 | 389.66
34 | TIN-INTERP | Interpolated Ground | 184.74 | -3.96 | 370.93 | 0 | 22.88 | 0 | OK | Ground clear controls. | 1 | 50.93 | 393.81
35 | TIN-INTERP | Interpolated Ground | 184.89 | -4.89 | 370.94 | 0 | 18.36 | 0 | OK | Ground clear controls. | 1 | 50.93 | 389.3
36 | TIN-INTERP | Interpolated Ground | 184.94 | 5.97 | 370.83 | 0 | 13.83 | 0 | OK | Ground clear controls. | 1 | 50.93 | 384.66
37 | TIN-INTERP | Interpolated Ground | 185.16 | -4.54 | 370.94 | 0 | 13.39 | 0 | OK | Ground clear controls. | 1 | 50.93 | 384.33
38 | TIN-INTERP | Interpolated Ground | 221.13 | 0.19 | 370.63 | 0 | 33.12 | 0 | OK | Ground clear controls. | 1 | 50.93 | 403.75
39 | TIN-INTERP | Interpolated Ground | 224.54 | 5.72 | 370.57 | 0 | 23.65 | 0 | OK | Ground clear controls. | 1 | 50.93 | 394.22
40 | TIN-INTERP | Interpolated Ground | 224.7 | 6.94 | 370.56 | 0 | 19.53 | 0 | OK | Ground clear controls. | 1 | 50.93 | 390.09
41 | TIN-INTERP | Interpolated Ground | 224.74 | -3.92 | 370.85 | 0 | 23.27 | 0 | OK | Ground clear controls. | 1 | 50.93 | 394.12
42 | TIN-INTERP | Interpolated Ground | 224.89 | -5.03 | 370.81 | 0 | 18.84 | 0 | OK | Ground clear controls. | 1 | 50.93 | 389.65
43 | TIN-INTERP | Interpolated Ground | 224.94 | 6.4 | 370.57 | 0 | 14.55 | 0 | OK | Ground clear controls. | 1 | 50.93 | 385.12
44 | TIN-INTERP | Interpolated Ground | 225.16 | -4.51 | 370.99 | 0 | 13.72 | 0 | OK | Ground clear controls. | 1 | 50.93 | 384.71
45 | TIN-INTERP | Interpolated Ground | 261.13 | 0.24 | 370.7 | 0 | 34.65 | 0 | OK | Ground clear controls. | 1 | 50.93 | 405.35
46 | TIN-INTERP | Interpolated Ground | 264.54 | 6.11 | 370.42 | 0 | 25.27 | 0 | OK | Ground clear controls. | 1 | 50.93 | 395.69
47 | TIN-INTERP | Interpolated Ground | 264.69 | 7.55 | 370.49 | 0 | 20.99 | 0 | OK | Ground clear controls. | 1 | 50.93 | 391.48
48 | TIN-INTERP | Interpolated Ground | 264.74 | -3.88 | 370.42 | 0 | 25.11 | 0 | OK | Ground clear controls. | 1 | 50.93 | 395.53
49 | TIN-INTERP | Interpolated Ground | 264.88 | -5.17 | 370.41 | 0 | 20.56 | 0 | OK | Ground clear controls. | 1 | 50.93 | 390.97
50 | TIN-INTERP | Interpolated Ground | 264.94 | 6.83 | 370.63 | 0 | 15.87 | 0 | OK | Ground clear controls. | 1 | 50.93 | 386.5
51 | TIN-INTERP | Interpolated Ground | 265.16 | -4.48 | 370.39 | 0 | 15.63 | 0 | OK | Ground clear controls. | 1 | 50.93 | 386.02
52 | TIN-INTERP | Interpolated Ground | 301.13 | 0.29 | 370.63 | 0 | 37.33 | 0 | OK | Ground clear controls. | 1 | 50.93 | 407.96
53 | TIN-INTERP | Interpolated Ground | 304.53 | 6.51 | 370.76 | 0 | 27.54 | 0 | OK | Ground clear controls. | 1 | 50.93 | 398.3
54 | TIN-INTERP | Interpolated Ground | 304.69 | 8.16 | 370.69 | 0 | 23.16 | 0 | OK | Ground clear controls. | 1 | 50.93 | 393.85
55 | TIN-INTERP | Interpolated Ground | 304.74 | -3.84 | 370.6 | 0 | 27.45 | 0 | OK | Ground clear controls. | 1 | 50.93 | 398.05
56 | TIN-INTERP | Interpolated Ground | 304.88 | -5.31 | 370.66 | 0 | 22.61 | 0 | OK | Ground clear controls. | 1 | 50.93 | 393.27
57 | TIN-INTERP | Interpolated Ground | 304.93 | 7.27 | 370.77 | 0 | 18 | 0 | OK | Ground clear controls. | 1 | 50.93 | 388.77
58 | TIN-INTERP | Interpolated Ground | 305.16 | -4.45 | 370.63 | 0 | 17.6 | 0 | OK | Ground clear controls. | 1 | 50.93 | 388.23
59 | TIN-INTERP | Interpolated Ground | 341.13 | 0.34 | 370.74 | 0 | 40.81 | 0 | OK | Ground clear controls. | 1 | 50.93 | 411.55
60 | TIN-INTERP | Interpolated Ground | 344.53 | 6.91 | 370.65 | 0 | 31.37 | 0 | OK | Ground clear controls. | 1 | 50.93 | 402.02
61 | TIN-INTERP | Interpolated Ground | 344.68 | 8.77 | 370.63 | 0 | 26.55 | 0 | OK | Ground clear controls. | 1 | 50.93 | 397.18
62 | TIN-INTERP | Interpolated Ground | 344.74 | -3.8 | 370.66 | 0 | 31.04 | 0 | OK | Ground clear controls. | 1 | 50.93 | 401.7
63 | TIN-INTERP | Interpolated Ground | 344.88 | -5.45 | 370.68 | 0 | 25.86 | 0 | OK | Ground clear controls. | 1 | 50.93 | 396.54
64 | TIN-INTERP | Interpolated Ground | 344.93 | 7.7 | 370.61 | 0 | 21.33 | 0 | OK | Ground clear controls. | 1 | 50.93 | 391.94
65 | TIN-INTERP | Interpolated Ground | 345.16 | -4.42 | 370.67 | 0 | 20.69 | 0 | OK | Ground clear controls. | 1 | 50.93 | 391.36
66 | TIN-INTERP | Interpolated Ground | 381.13 | 0.38 | 370.91 | 0 | 45.21 | 0 | OK | Ground clear controls. | 1 | 50.93 | 416.12
67 | TIN-INTERP | Interpolated Ground | 384.53 | 7.3 | 370.85 | 0 | 36.03 | 0 | OK | Ground clear controls. | 1 | 50.93 | 406.88
68 | TIN-INTERP | Interpolated Ground | 384.68 | 9.38 | 370.82 | 0 | 30.66 | 0 | OK | Ground clear controls. | 1 | 50.93 | 401.48
69 | TIN-INTERP | Interpolated Ground | 384.74 | -3.76 | 370.87 | 0 | 35.59 | 0 | OK | Ground clear controls. | 1 | 50.93 | 406.46
70 | TIN-INTERP | Interpolated Ground | 384.88 | -5.59 | 370.85 | 0 | 29.96 | 0 | OK | Ground clear controls. | 1 | 50.93 | 400.81
71 | TIN-INTERP | Interpolated Ground | 384.93 | 8.13 | 370.81 | 0 | 25.21 | 0 | OK | Ground clear controls. | 1 | 50.93 | 396.02
72 | TIN-INTERP | Interpolated Ground | 385.16 | -4.39 | 370.83 | 0 | 24.58 | 0 | OK | Ground clear controls. | 1 | 50.93 | 395.41
73 | TIN-INTERP | Interpolated Ground | 421.13 | 0.43 | 370.77 | 0 | 50.93 | 0 | OK | Ground clear controls. | 1 | 50.93 | 421.7
74 | TIN-INTERP | Interpolated Ground | 423.37 | -5.84 | 371.06 | 0 | 34.94 | 0 | OK | Ground clear controls. | 2 | 50.95 | 406
75 | TIN-INTERP | Interpolated Ground | 423.37 | -4.45 | 371.08 | 0 | 29.17 | 0 | OK | Ground clear controls. | 2 | 50.95 | 400.25
76 | TIN-INTERP | Interpolated Ground | 423.37 | -3.8 | 371.05 | 0 | 41.18 | 0 | OK | Ground clear controls. | 2 | 50.95 | 412.23
77 | TIN-INTERP | Interpolated Ground | 423.47 | 0.43 | 371.08 | 0 | 50.95 | 0 | OK | Ground clear controls. | 2 | 50.95 | 422.03
78 | TIN-INTERP | Interpolated Ground | 424.78 | 7.66 | 371 | 0 | 41.46 | 0 | OK | Ground clear controls. | 2 | 47.79 | 412.46
79 | TIN-INTERP | Interpolated Ground | 424.98 | 8.51 | 370.96 | 0 | 29.63 | 0 | OK | Ground clear controls. | 2 | 47.79 | 400.59
80 | TIN-INTERP | Interpolated Ground | 425.18 | 9.94 | 370.93 | 0 | 35.38 | 0 | OK | Ground clear controls. | 2 | 47.79 | 406.31
81 | TIN-INTERP | Interpolated Ground | 462.43 | -5.88 | 370.97 | 0 | 31.85 | 0 | OK | Ground clear controls. | 2 | 47.79 | 402.82
82 | TIN-INTERP | Interpolated Ground | 462.7 | -4.5 | 370.95 | 0 | 26.36 | 0 | OK | Ground clear controls. | 2 | 47.79 | 397.31
83 | TIN-INTERP | Interpolated Ground | 462.76 | -3.88 | 370.93 | 0 | 37.63 | 0 | OK | Ground clear controls. | 2 | 47.79 | 408.56
84 | TIN-INTERP | Interpolated Ground | 463.47 | 0.36 | 370.93 | 0 | 47.79 | 0 | OK | Ground clear controls. | 2 | 47.79 | 418.72
85 | TIN-INTERP | Interpolated Ground | 464.78 | 7.22 | 370.86 | 0 | 37.85 | 0 | OK | Ground clear controls. | 2 | 45.53 | 408.71
86 | TIN-INTERP | Interpolated Ground | 464.98 | 8.01 | 370.85 | 0 | 26.78 | 0 | OK | Ground clear controls. | 2 | 45.53 | 397.63
87 | TIN-INTERP | Interpolated Ground | 465.18 | 9.45 | 370.85 | 0 | 32.26 | 0 | OK | Ground clear controls. | 2 | 45.53 | 403.11
88 | TIN-INTERP | Interpolated Ground | 502.43 | -5.99 | 370.79 | 0 | 29.81 | 0 | OK | Ground clear controls. | 2 | 45.53 | 400.6
89 | TIN-INTERP | Interpolated Ground | 502.7 | -4.59 | 370.79 | 0 | 24.46 | 0 | OK | Ground clear controls. | 2 | 45.53 | 395.25
90 | TIN-INTERP | Interpolated Ground | 502.76 | -4.01 | 370.8 | 0 | 35.19 | 0 | OK | Ground clear controls. | 2 | 45.53 | 405.99
91 | TIN-INTERP | Interpolated Ground | 503.47 | 0.3 | 370.77 | 0 | 45.53 | 0 | OK | Ground clear controls. | 2 | 45.53 | 416.3
92 | TIN-INTERP | Interpolated Ground | 504.77 | 6.77 | 370.74 | 0 | 35.36 | 0 | OK | Ground clear controls. | 2 | 44.49 | 406.1
93 | TIN-INTERP | Interpolated Ground | 504.97 | 7.52 | 370.76 | 0 | 24.8 | 0 | OK | Ground clear controls. | 2 | 44.49 | 395.56
94 | TIN-INTERP | Interpolated Ground | 505.17 | 8.96 | 370.7 | 0 | 30.18 | 0 | OK | Ground clear controls. | 2 | 44.49 | 400.88
95 | TIN-INTERP | Interpolated Ground | 542.43 | -6.11 | 370.61 | 0 | 28.74 | 0 | OK | Ground clear controls. | 2 | 44.49 | 399.35
96 | TIN-INTERP | Interpolated Ground | 542.7 | -4.69 | 370.59 | 0 | 23.52 | 0 | OK | Ground clear controls. | 2 | 44.49 | 394.11
97 | TIN-INTERP | Interpolated Ground | 542.76 | -4.15 | 370.57 | 0 | 33.96 | 0 | OK | Ground clear controls. | 2 | 44.49 | 404.53
98 | TIN-INTERP | Interpolated Ground | 543.47 | 0.23 | 370.58 | 0 | 44.18 | 0 | OK | Ground clear controls. | 2 | 44.49 | 414.76
99 | TIN-INTERP | Interpolated Ground | 544.77 | 6.32 | 370.58 | 0 | 34.01 | 0 | OK | Ground clear controls. | 2 | 44.49 | 404.59
100 | TIN-INTERP | Interpolated Ground | 544.97 | 7.02 | 370.57 | 0 | 23.81 | 0 | OK | Ground clear controls. | 2 | 44.49 | 394.38
101 | TIN-INTERP | Interpolated Ground | 545.17 | 8.48 | 370.59 | 0 | 29.03 | 0 | OK | Ground clear controls. | 2 | 44.49 | 399.62
102 | TIN-INTERP | Interpolated Ground | 582.43 | -6.22 | 370.63 | 0 | 28.44 | 0 | OK | Ground clear controls. | 2 | 44.49 | 399.07
103 | TIN-INTERP | Interpolated Ground | 582.7 | -4.79 | 370.64 | 0 | 23.21 | 0 | OK | Ground clear controls. | 2 | 44.49 | 393.85
104 | TIN-INTERP | Interpolated Ground | 582.76 | -4.28 | 370.58 | 0 | 33.57 | 0 | OK | Ground clear controls. | 2 | 44.49 | 404.15
105 | TIN-INTERP | Interpolated Ground | 583.47 | 0.17 | 370.61 | 0 | 43.5 | 0 | OK | Ground clear controls. | 2 | 44.49 | 414.11
106 | TIN-INTERP | Interpolated Ground | 584.77 | 5.87 | 370.67 | 0 | 33.55 | 0 | OK | Ground clear controls. | 2 | 44.49 | 404.22
107 | TIN-INTERP | Interpolated Ground | 584.97 | 6.53 | 370.67 | 0 | 23.43 | 0 | OK | Ground clear controls. | 2 | 44.49 | 394.1
108 | TIN-INTERP | Interpolated Ground | 585.17 | 7.99 | 370.63 | 0 | 28.69 | 0 | OK | Ground clear controls. | 2 | 44.49 | 399.32
109 | TIN-INTERP | Interpolated Ground | 622.43 | -6.34 | 370.86 | 0 | 28.87 | 0 | OK | Ground clear controls. | 2 | 44.49 | 399.73
110 | TIN-INTERP | Interpolated Ground | 622.7 | -4.88 | 370.94 | 0 | 23.54 | 0 | OK | Ground clear controls. | 2 | 44.49 | 394.48
111 | TIN-INTERP | Interpolated Ground | 622.76 | -4.41 | 370.98 | 0 | 33.9 | 0 | OK | Ground clear controls. | 2 | 44.49 | 404.88
112 | TIN-INTERP | Interpolated Ground | 623.47 | 0.11 | 370.92 | 0 | 43.42 | 0 | OK | Ground clear controls. | 2 | 44.49 | 414.34
113 | TIN-INTERP | Interpolated Ground | 624.77 | 5.42 | 370.85 | 0 | 34.12 | 0 | OK | Ground clear controls. | 2 | 44.49 | 404.97
114 | TIN-INTERP | Interpolated Ground | 624.96 | 6.03 | 370.85 | 0 | 23.85 | 0 | OK | Ground clear controls. | 2 | 44.49 | 394.7
115 | TIN-INTERP | Interpolated Ground | 625.16 | 7.5 | 370.79 | 0 | 29.18 | 0 | OK | Ground clear controls. | 2 | 44.49 | 399.97
116 | TIN-INTERP | Interpolated Ground | 662.43 | -6.45 | 370.87 | 0 | 30.49 | 0 | OK | Ground clear controls. | 2 | 44.49 | 401.36
117 | TIN-INTERP | Interpolated Ground | 662.7 | -4.98 | 370.83 | 0 | 25.19 | 0 | OK | Ground clear controls. | 2 | 44.49 | 396.02
118 | TIN-INTERP | Interpolated Ground | 662.76 | -4.54 | 370.83 | 0 | 35.88 | 0 | OK | Ground clear controls. | 2 | 44.49 | 406.71
119 | TIN-INTERP | Interpolated Ground | 663.47 | 0.04 | 370.97 | 0 | 44.49 | 0 | OK | Ground clear controls. | 2 | 44.49 | 415.46
120 | TIN-INTERP | Interpolated Ground | 664.76 | 4.97 | 370.84 | 0 | 35.99 | 0 | OK | Ground clear controls. | 2 | 35.99 | 406.83
121 | TIN-INTERP | Interpolated Ground | 664.96 | 5.54 | 370.86 | 0 | 25.34 | 0 | OK | Ground clear controls. | 2 | 30.78 | 396.2
122 | TIN-INTERP | Interpolated Ground | 665.16 | 7.01 | 370.81 | 0 | 30.78 | 0 | OK | Ground clear controls. | 2 | 30.78 | 401.59
123 | TIN-INTERP | Interpolated Ground | 688.4 | 5.25 | 370.86 | 0 | 26.63 | 0 | OK | Ground clear controls. | 3 | 45.96 | 397.49
124 | TIN-INTERP | Interpolated Ground | 688.48 | 6.73 | 370.85 | 0 | 32.13 | 0 | OK | Ground clear controls. | 3 | 45.96 | 402.98
125 | TIN-INTERP | Interpolated Ground | 688.58 | 4.7 | 370.83 | 0 | 37.64 | 0 | OK | Ground clear controls. | 3 | 45.96 | 408.47
126 | TIN-INTERP | Interpolated Ground | 688.59 | -5.04 | 370.92 | 0 | 26.58 | 0 | OK | Ground clear controls. | 3 | 45.96 | 397.5
127 | TIN-INTERP | Interpolated Ground | 688.73 | -4.62 | 370.95 | 0 | 37.53 | 0 | OK | Ground clear controls. | 3 | 45.96 | 408.48
128 | TIN-INTERP | Interpolated Ground | 688.81 | 0 | 370.67 | 0 | 45.96 | 0 | OK | Ground clear controls. | 3 | 45.96 | 416.63
129 | TIN-INTERP | Interpolated Ground | 688.87 | -6.53 | 370.93 | 0 | 32.04 | 0 | OK | Ground clear controls. | 3 | 45.43 | 402.97
130 | TIN-INTERP | Interpolated Ground | 728.39 | 5.05 | 370.71 | 0 | 24.71 | 0 | OK | Ground clear controls. | 3 | 45.43 | 395.42
131 | TIN-INTERP | Interpolated Ground | 728.48 | 6.53 | 370.71 | 0 | 30.07 | 0 | OK | Ground clear controls. | 3 | 45.43 | 400.78
132 | TIN-INTERP | Interpolated Ground | 728.58 | 4.53 | 370.72 | 0 | 35.19 | 0 | OK | Ground clear controls. | 3 | 45.43 | 405.91
133 | TIN-INTERP | Interpolated Ground | 728.59 | -5.01 | 370.61 | 0 | 24.78 | 0 | OK | Ground clear controls. | 3 | 45.43 | 395.39
134 | TIN-INTERP | Interpolated Ground | 728.73 | -4.55 | 370.64 | 0 | 35.28 | 0 | OK | Ground clear controls. | 3 | 45.43 | 405.92
135 | TIN-INTERP | Interpolated Ground | 728.81 | 0 | 370.7 | 0 | 43.79 | 0 | OK | Ground clear controls. | 3 | 45.43 | 414.49
136 | TIN-INTERP | Interpolated Ground | 728.87 | -6.49 | 370.49 | 0 | 30.25 | 0 | OK | Ground clear controls. | 3 | 45.43 | 400.74
137 | TIN-INTERP | Interpolated Ground | 768.39 | 4.85 | 370.51 | 0 | 23.76 | 0 | OK | Ground clear controls. | 3 | 45.43 | 394.27
138 | TIN-INTERP | Interpolated Ground | 768.48 | 6.34 | 370.51 | 0 | 29.03 | 0 | OK | Ground clear controls. | 3 | 45.43 | 399.54
139 | TIN-INTERP | Interpolated Ground | 768.58 | 4.35 | 370.5 | 0 | 33.97 | 0 | OK | Ground clear controls. | 3 | 45.43 | 404.47
140 | TIN-INTERP | Interpolated Ground | 768.59 | -4.99 | 370.51 | 0 | 23.68 | 0 | OK | Ground clear controls. | 3 | 45.43 | 394.19
141 | TIN-INTERP | Interpolated Ground | 768.73 | -4.48 | 370.54 | 0 | 33.93 | 0 | OK | Ground clear controls. | 3 | 45.43 | 404.47
142 | TIN-INTERP | Interpolated Ground | 768.81 | 0 | 370.51 | 0 | 42.69 | 0 | OK | Ground clear controls. | 3 | 45.43 | 413.2
143 | TIN-INTERP | Interpolated Ground | 768.87 | -6.44 | 370.52 | 0 | 28.96 | 0 | OK | Ground clear controls. | 3 | 45.43 | 399.48
144 | TIN-INTERP | Interpolated Ground | 808.39 | 4.65 | 370.34 | 0 | 23.67 | 0 | OK | Ground clear controls. | 3 | 45.43 | 394.01
145 | TIN-INTERP | Interpolated Ground | 808.48 | 6.14 | 370.38 | 0 | 28.9 | 0 | OK | Ground clear controls. | 3 | 45.43 | 399.28
146 | TIN-INTERP | Interpolated Ground | 808.58 | 4.17 | 370.32 | 0 | 33.83 | 0 | OK | Ground clear controls. | 3 | 45.43 | 404.15
147 | TIN-INTERP | Interpolated Ground | 808.59 | -4.96 | 370.27 | 0 | 23.64 | 0 | OK | Ground clear controls. | 3 | 45.43 | 393.91
148 | TIN-INTERP | Interpolated Ground | 808.73 | -4.41 | 370.28 | 0 | 33.86 | 0 | OK | Ground clear controls. | 3 | 45.43 | 404.14
149 | TIN-INTERP | Interpolated Ground | 808.81 | 0 | 370.26 | 0 | 42.52 | 0 | OK | Ground clear controls. | 3 | 45.43 | 412.78
150 | TIN-INTERP | Interpolated Ground | 808.87 | -6.4 | 370.28 | 0 | 28.9 | 0 | OK | Ground clear controls. | 3 | 45.43 | 399.18
151 | TIN-INTERP | Interpolated Ground | 848.39 | 4.46 | 370.12 | 0 | 24.55 | 0 | OK | Ground clear controls. | 3 | 45.43 | 394.67
152 | TIN-INTERP | Interpolated Ground | 848.48 | 5.94 | 370.1 | 0 | 29.89 | 0 | OK | Ground clear controls. | 3 | 45.43 | 399.99
153 | TIN-INTERP | Interpolated Ground | 848.58 | 3.99 | 370.16 | 0 | 34.81 | 0 | OK | Ground clear controls. | 3 | 45.43 | 404.97
154 | TIN-INTERP | Interpolated Ground | 848.59 | -4.93 | 370.25 | 0 | 24.29 | 0 | OK | Ground clear controls. | 3 | 45.43 | 394.54
155 | TIN-INTERP | Interpolated Ground | 848.73 | -4.35 | 370.24 | 0 | 34.67 | 0 | OK | Ground clear controls. | 3 | 45.43 | 404.91
156 | TIN-INTERP | Interpolated Ground | 848.81 | 0 | 370.16 | 0 | 43.07 | 0 | OK | Ground clear controls. | 3 | 45.43 | 413.23
157 | TIN-INTERP | Interpolated Ground | 848.87 | -6.36 | 370.3 | 0 | 29.55 | 0 | OK | Ground clear controls. | 3 | 45.43 | 399.85
158 | TIN-INTERP | Interpolated Ground | 888.39 | 4.26 | 369.55 | 0 | 26.67 | 0 | OK | Ground clear controls. | 3 | 45.43 | 396.22
159 | TIN-INTERP | Interpolated Ground | 888.48 | 5.74 | 369.61 | 0 | 32.05 | 0 | OK | Ground clear controls. | 3 | 45.43 | 401.66
160 | TIN-INTERP | Interpolated Ground | 888.58 | 3.82 | 369.47 | 0 | 37.46 | 0 | OK | Ground clear controls. | 3 | 45.43 | 406.93
161 | TIN-INTERP | Interpolated Ground | 888.59 | -4.9 | 370.25 | 0 | 25.83 | 0 | OK | Ground clear controls. | 3 | 45.43 | 396.08
162 | TIN-INTERP | Interpolated Ground | 888.73 | -4.28 | 370.13 | 0 | 36.67 | 0 | OK | Ground clear controls. | 3 | 45.43 | 406.8
163 | TIN-INTERP | Interpolated Ground | 888.81 | 0 | 369.12 | 0 | 45.43 | 0 | OK | Ground clear controls. | 3 | 45.43 | 414.55
164 | TIN-INTERP | Interpolated Ground | 888.87 | -6.32 | 370.24 | 0 | 31.25 | 0 | OK | Ground clear controls. | 3 | 31.25 | 401.49
165 | TIN-INTERP | Interpolated Ground | 912.25 | -6.3 | 369.88 | 0 | 32.62 | 0 | OK | Ground clear controls. | 4 | 42.7 | 402.5
166 | TIN-INTERP | Interpolated Ground | 912.51 | -4.24 | 369.7 | 0 | 38.3 | 0 | OK | Ground clear controls. | 4 | 42.7 | 408
167 | TIN-INTERP | Interpolated Ground | 912.79 | -4.89 | 369.69 | 0 | 27.31 | 0 | OK | Ground clear controls. | 4 | 42.7 | 397
168 | TIN-INTERP | Interpolated Ground | 914.83 | 3.73 | 369.62 | 0 | 38.38 | 0 | OK | Ground clear controls. | 4 | 42.7 | 408
169 | TIN-INTERP | Interpolated Ground | 915.31 | 4.17 | 369.71 | 0 | 27.29 | 0 | OK | Ground clear controls. | 4 | 42.7 | 397
170 | TIN-INTERP | Interpolated Ground | 915.57 | 5.66 | 369.82 | 0 | 32.67 | 0 | OK | Ground clear controls. | 4 | 42.7 | 402.49
171 | TIN-INTERP | Interpolated Ground | 952.25 | -6.31 | 369.02 | 0 | 29.42 | 0 | OK | Ground clear controls. | 4 | 42.7 | 398.44
172 | TIN-INTERP | Interpolated Ground | 952.51 | -4.26 | 369.05 | 0 | 34.92 | 0 | OK | Ground clear controls. | 4 | 42.7 | 403.97
173 | TIN-INTERP | Interpolated Ground | 952.79 | -4.9 | 369.03 | 0 | 23.95 | 0 | OK | Ground clear controls. | 4 | 42.7 | 392.98
174 | TIN-INTERP | Interpolated Ground | 954.83 | 3.8 | 369.1 | 0 | 34.81 | 0 | OK | Ground clear controls. | 4 | 42.7 | 403.91
175 | TIN-INTERP | Interpolated Ground | 955.31 | 4.24 | 369.07 | 0 | 23.84 | 0 | OK | Ground clear controls. | 4 | 42.7 | 392.91
176 | TIN-INTERP | Interpolated Ground | 955.57 | 5.73 | 369.04 | 0 | 29.31 | 0 | OK | Ground clear controls. | 4 | 42.7 | 398.35
177 | TIN-INTERP | Interpolated Ground | 992.25 | -6.32 | 370.62 | 0 | 24.69 | 0 | OK | Ground clear controls. | 4 | 42.7 | 395.31
178 | TIN-INTERP | Interpolated Ground | 992.51 | -4.27 | 370.95 | 0 | 29.92 | 0 | OK | Ground clear controls. | 4 | 42.7 | 400.87
179 | TIN-INTERP | Interpolated Ground | 992.79 | -4.9 | 370.8 | 0 | 19.08 | 0 | OK | Ground clear controls. | 4 | 42.7 | 389.88
180 | TIN-INTERP | Interpolated Ground | 994.83 | 3.87 | 371.78 | 0 | 28.98 | 0 | OK | Ground clear controls. | 4 | 42.7 | 400.76
181 | TIN-INTERP | Interpolated Ground | 995.31 | 4.31 | 371.76 | 0 | 18.01 | 0 | OK | Ground clear controls. | 4 | 42.7 | 389.77
182 | TIN-INTERP | Interpolated Ground | 995.57 | 5.8 | 371.6 | 0 | 23.57 | 0 | OK | Ground clear controls. | 4 | 42.7 | 395.17
183 | TIN-INTERP | Interpolated Ground | 1032.25 | -6.34 | 368.22 | 0 | 24.89 | 0 | OK | Ground clear controls. | 4 | 42.7 | 393.11
184 | TIN-INTERP | Interpolated Ground | 1032.51 | -4.29 | 368.15 | 0 | 30.55 | 0 | OK | Ground clear controls. | 4 | 42.7 | 398.7
185 | TIN-INTERP | Interpolated Ground | 1032.79 | -4.91 | 368.21 | 0 | 19.49 | 0 | OK | Ground clear controls. | 4 | 42.7 | 387.7
186 | TIN-INTERP | Interpolated Ground | 1034.83 | 3.94 | 367.96 | 0 | 30.6 | 0 | OK | Ground clear controls. | 4 | 42.7 | 398.56
187 | TIN-INTERP | Interpolated Ground | 1035.31 | 4.39 | 367.9 | 0 | 19.66 | 0 | OK | Ground clear controls. | 4 | 42.7 | 387.56
188 | TIN-INTERP | Interpolated Ground | 1035.57 | 5.87 | 367.69 | 0 | 25.25 | 0 | OK | Ground clear controls. | 4 | 42.7 | 392.94
189 | TIN-INTERP | Interpolated Ground | 1072.25 | -6.35 | 363.92 | 0 | 27.92 | 0 | OK | Ground clear controls. | 4 | 42.7 | 391.84
190 | TIN-INTERP | Interpolated Ground | 1072.51 | -4.31 | 363.92 | 0 | 33.52 | 0 | OK | Ground clear controls. | 4 | 42.7 | 397.44
191 | TIN-INTERP | Interpolated Ground | 1072.79 | -4.92 | 363.92 | 0 | 22.53 | 0 | OK | Ground clear controls. | 4 | 42.7 | 386.45
192 | TIN-INTERP | Interpolated Ground | 1074.83 | 4 | 363.92 | 0 | 33.36 | 0 | OK | Ground clear controls. | 4 | 42.7 | 397.28
193 | TIN-INTERP | Interpolated Ground | 1075.31 | 4.46 | 363.92 | 0 | 22.37 | 0 | OK | Ground clear controls. | 4 | 42.7 | 386.29
194 | TIN-INTERP | Interpolated Ground | 1075.57 | 5.95 | 363.92 | 0 | 27.72 | 0 | OK | Ground clear controls. | 4 | 42.7 | 391.64
195 | TIN-INTERP | Interpolated Ground | 1112.25 | -6.36 | 363.89 | 0 | 27.6 | 0 | OK | Ground clear controls. | 4 | 42.7 | 391.49
196 | TIN-INTERP | Interpolated Ground | 1112.51 | -4.33 | 363.9 | 0 | 33.21 | 0 | OK | Ground clear controls. | 4 | 42.7 | 397.11
197 | TIN-INTERP | Interpolated Ground | 1112.79 | -4.92 | 363.89 | 0 | 22.23 | 0 | OK | Ground clear controls. | 4 | 42.7 | 386.12
198 | TIN-INTERP | Interpolated Ground | 1114.83 | 4.07 | 363.9 | 0 | 33.05 | 0 | OK | Ground clear controls. | 4 | 42.7 | 396.95
199 | TIN-INTERP | Interpolated Ground | 1115.31 | 4.53 | 363.9 | 0 | 22.06 | 0 | OK | Ground clear controls. | 4 | 42.7 | 385.96
200 | TIN-INTERP | Interpolated Ground | 1115.57 | 6.02 | 363.9 | 0 | 27.4 | 0 | OK | Ground clear controls. | 4 | 42.7 | 391.3
201 | TIN-INTERP | Interpolated Ground | 1152.25 | -6.37 | 363.87 | 0 | 28.2 | 0 | OK | Ground clear controls. | 4 | 42.7 | 392.07
202 | TIN-INTERP | Interpolated Ground | 1152.51 | -4.34 | 363.87 | 0 | 33.83 | 0 | OK | Ground clear controls. | 4 | 42.7 | 397.7
203 | TIN-INTERP | Interpolated Ground | 1152.79 | -4.93 | 363.87 | 0 | 22.84 | 0 | OK | Ground clear controls. | 4 | 42.7 | 386.71
204 | TIN-INTERP | Interpolated Ground | 1154.83 | 4.14 | 363.88 | 0 | 33.67 | 0 | OK | Ground clear controls. | 4 | 42.7 | 397.55
205 | TIN-INTERP | Interpolated Ground | 1155.31 | 4.6 | 363.88 | 0 | 22.69 | 0 | OK | Ground clear controls. | 4 | 42.7 | 386.57
206 | TIN-INTERP | Interpolated Ground | 1155.57 | 6.09 | 363.88 | 0 | 28.01 | 0 | OK | Ground clear controls. | 4 | 42.7 | 391.89
207 | TIN-INTERP | Interpolated Ground | 1192.25 | -6.39 | 363.85 | 0 | 29.72 | 0 | OK | Ground clear controls. | 4 | 42.7 | 393.57
208 | TIN-INTERP | Interpolated Ground | 1192.51 | -4.36 | 363.85 | 0 | 35.36 | 0 | OK | Ground clear controls. | 4 | 42.7 | 399.21
209 | TIN-INTERP | Interpolated Ground | 1192.79 | -4.94 | 363.85 | 0 | 24.37 | 0 | OK | Ground clear controls. | 4 | 42.7 | 388.22
210 | TIN-INTERP | Interpolated Ground | 1194.83 | 4.2 | 363.85 | 0 | 35.23 | 0 | OK | Ground clear controls. | 4 | 42.7 | 399.08
211 | TIN-INTERP | Interpolated Ground | 1195.31 | 4.67 | 363.85 | 0 | 24.26 | 0 | OK | Ground clear controls. | 4 | 42.7 | 388.11
212 | TIN-INTERP | Interpolated Ground | 1195.57 | 6.16 | 363.85 | 0 | 29.58 | 0 | OK | Ground clear controls. | 4 | 42.7 | 393.43
213 | TIN-INTERP | Interpolated Ground | 1232.25 | -6.4 | 363.83 | 0 | 32.17 | 0 | OK | Ground clear controls. | 4 | 42.7 | 396
214 | TIN-INTERP | Interpolated Ground | 1232.51 | -4.38 | 363.83 | 0 | 37.81 | 0 | OK | Ground clear controls. | 4 | 42.7 | 401.64
215 | TIN-INTERP | Interpolated Ground | 1232.79 | -4.94 | 363.83 | 0 | 26.83 | 0 | OK | Ground clear controls. | 4 | 42.7 | 390.66
216 | TIN-INTERP | Interpolated Ground | 1234.83 | 4.27 | 363.83 | 0 | 37.72 | 0 | OK | Ground clear controls. | 4 | 42.7 | 401.55
217 | TIN-INTERP | Interpolated Ground | 1235.31 | 4.74 | 363.83 | 0 | 26.76 | 0 | OK | Ground clear controls. | 4 | 42.7 | 390.59
218 | TIN-INTERP | Interpolated Ground | 1235.57 | 6.24 | 363.83 | 0 | 32.09 | 0 | OK | Ground clear controls. | 4 | 42.7 | 395.92
219 | TIN-INTERP | Interpolated Ground | 1272.25 | -6.41 | 365.2 | 0 | 34.16 | 0 | OK | Ground clear controls. | 4 | 42.7 | 399.36
220 | TIN-INTERP | Interpolated Ground | 1272.51 | -4.39 | 365.44 | 0 | 39.55 | 0 | OK | Ground clear controls. | 4 | 42.7 | 404.99
221 | TIN-INTERP | Interpolated Ground | 1272.79 | -4.95 | 365.42 | 0 | 28.6 | 0 | OK | Ground clear controls. | 4 | 42.7 | 394.02
222 | TIN-INTERP | Interpolated Ground | 1274.83 | 4.34 | 364.91 | 0 | 40.05 | 0 | OK | Ground clear controls. | 4 | 42.7 | 404.96
223 | TIN-INTERP | Interpolated Ground | 1275.31 | 4.81 | 364.83 | 0 | 29.17 | 0 | OK | Ground clear controls. | 4 | 42.7 | 394
224 | TIN-INTERP | Interpolated Ground | 1275.57 | 6.31 | 364.8 | 0 | 34.55 | 0 | OK | Ground clear controls. | 4 | 42.7 | 399.35
225 | TIN-INTERP | Interpolated Ground | 1312.25 | -6.43 | 366.53 | 0 | 37.11 | 0 | OK | Ground clear controls. | 4 | 42.7 | 403.64
226 | TIN-INTERP | Interpolated Ground | 1312.51 | -4.41 | 366.58 | 0 | 42.7 | 0 | OK | Ground clear controls. | 4 | 42.7 | 409.28
227 | TIN-INTERP | Interpolated Ground | 1312.79 | -4.96 | 366.65 | 0 | 31.65 | 0 | OK | Ground clear controls. | 4 | 40.26 | 398.3
228 | TIN-INTERP | Interpolated Ground | 1314.83 | 4.4 | 369.06 | 0 | 40.26 | 0 | OK | Ground clear controls. | 4 | 40.26 | 409.32
229 | TIN-INTERP | Interpolated Ground | 1315.31 | 4.89 | 369.39 | 0 | 28.98 | 0 | OK | Ground clear controls. | 4 | 34.55 | 398.37
230 | TIN-INTERP | Interpolated Ground | 1315.57 | 6.38 | 369.23 | 0 | 34.51 | 0 | OK | Ground clear controls. | 4 | 34.55 | 403.74
231 | TIN-INTERP | Interpolated Ground | 1352.25 | -6.44 | 379.27 | 0 | 29.59 | 0 | OK | Ground clear controls. | 4 | 34.55 | 408.86
232 | TIN-INTERP | Interpolated Ground | 1352.51 | -4.43 | 379.93 | 0 | 34.55 | 0 | OK | Ground clear controls. | 4 | 34.55 | 414.48
233 | TIN-INTERP | Interpolated Ground | 1352.79 | -4.96 | 379.79 | 0 | 23.73 | 0 | OK | Ground clear controls. | 4 | 32.52 | 403.52
234 | TIN-INTERP | Interpolated Ground | 1354.83 | 4.47 | 385 | 0 | 29.61 | 0 | OK | Ground clear controls. | 4 | 32.52 | 414.61
235 | TIN-INTERP | Interpolated Ground | 1355.31 | 4.96 | 385.44 | 0 | 18.23 | 0 | OK | Ground clear controls. | 4 | 32.52 | 403.67
236 | TIN-INTERP | Interpolated Ground | 1355.57 | 6.45 | 386.15 | 0 | 22.93 | 0 | OK | Ground clear controls. | 4 | 32.52 | 409.08
237 | TIN-INTERP | Interpolated Ground | 1392.25 | -6.45 | 397.59 | 0 | 17.42 | 0 | OK | Ground clear controls. | 4 | 32.52 | 415.01
238 | TIN-INTERP | Interpolated Ground | 1392.51 | -4.44 | 398.41 | 0 | 22.21 | 0 | OK | Ground clear controls. | 4 | 32.52 | 420.62
239 | TIN-INTERP | Interpolated Ground | 1392.79 | -4.97 | 398.39 | 0 | 11.27 | 0 | OK | Ground clear controls. | 4 | 32.52 | 409.66
240 | TIN-INTERP | Interpolated Ground | 1394.83 | 4.54 | 399.25 | 0 | 21.61 | 0 | OK | Ground clear controls. | 4 | 32.52 | 420.86
241 | TIN-INTERP | Interpolated Ground | 1395.31 | 5.03 | 399.28 | 0 | 10.64 | 0 | OK | Ground clear controls. | 4 | 32.52 | 409.92
242 | TIN-INTERP | Interpolated Ground | 1395.57 | 6.52 | 399.5 | 0 | 15.87 | 0 | OK | Ground clear controls. | 4 | 32.52 | 415.37
243 | TIN-INTERP | Interpolated Ground | 1432.25 | -6.47 | 399.38 | 0 | 22.73 | 0 | OK | Ground clear controls. | 4 | 32.52 | 422.11
244 | TIN-INTERP | Interpolated Ground | 1432.51 | -4.46 | 399.51 | 0 | 28.19 | 0 | OK | Ground clear controls. | 4 | 32.52 | 427.7
245 | TIN-INTERP | Interpolated Ground | 1432.79 | -4.98 | 399.55 | 0 | 17.2 | 0 | OK | Ground clear controls. | 4 | 32.52 | 416.75
246 | TIN-INTERP | Interpolated Ground | 1434.83 | 4.61 | 400.85 | 0 | 27.2 | 0 | OK | Ground clear controls. | 4 | 32.52 | 428.05
247 | TIN-INTERP | Interpolated Ground | 1435.31 | 5.1 | 400.97 | 0 | 16.16 | 0 | OK | Ground clear controls. | 4 | 32.52 | 417.13
248 | TIN-INTERP | Interpolated Ground | 1435.57 | 6.6 | 401.3 | 0 | 21.32 | 0 | OK | Ground clear controls. | 4 | 32.52 | 422.62
249 | TIN-INTERP | Interpolated Ground | 1472.25 | -6.48 | 402.9 | 0 | 27.25 | 0 | OK | Ground clear controls. | 4 | 32.52 | 430.15
250 | TIN-INTERP | Interpolated Ground | 1472.51 | -4.48 | 403.19 | 0 | 32.52 | 0 | OK | Ground clear controls. | 4 | 32.52 | 435.71
251 | TIN-INTERP | Interpolated Ground | 1472.79 | -4.98 | 403.16 | 0 | 21.61 | 0 | OK | Ground clear controls. | 4 | 31.43 | 424.77
252 | TIN-INTERP | Interpolated Ground | 1474.83 | 4.67 | 404.76 | 0 | 31.43 | 0 | OK | Ground clear controls. | 4 | 31.43 | 436.19
253 | TIN-INTERP | Interpolated Ground | 1475.31 | 5.17 | 404.88 | 0 | 20.4 | 0 | OK | Ground clear controls. | 4 | 25.74 | 425.28
254 | TIN-INTERP | Interpolated Ground | 1475.57 | 6.67 | 405.09 | 0 | 25.74 | 0 | OK | Ground clear controls. | 4 | 25.74 | 430.83
255 | TIN-INTERP | Interpolated Ground | 1487.68 | -6.49 | 404.45 | 0 | 29.06 | 0 | OK | Ground clear controls. | 5 | 36.34 | 433.51
256 | TIN-INTERP | Interpolated Ground | 1487.71 | -4.49 | 404.85 | 0 | 34.16 | 0 | OK | Ground clear controls. | 5 | 36.34 | 439.01
257 | TIN-INTERP | Interpolated Ground | 1487.8 | 4.69 | 405.61 | 0 | 33.4 | 0 | OK | Ground clear controls. | 5 | 36.34 | 439.01
258 | TIN-INTERP | Interpolated Ground | 1487.8 | -4.99 | 404.78 | 0 | 23.25 | 0 | OK | Ground clear controls. | 5 | 36.34 | 428.03
259 | TIN-INTERP | Interpolated Ground | 1487.81 | 6.69 | 406.11 | 0 | 27.41 | 0 | OK | Ground clear controls. | 5 | 36.34 | 433.52
260 | TIN-INTERP | Interpolated Ground | 1487.91 | 5.19 | 405.72 | 0 | 22.31 | 0 | OK | Ground clear controls. | 5 | 36.34 | 428.03
261 | TIN-INTERP | Interpolated Ground | 1527.68 | -6.5 | 409.34 | 0 | 23.9 | 0 | OK | Ground clear controls. | 5 | 36.34 | 433.24
262 | TIN-INTERP | Interpolated Ground | 1527.71 | -4.5 | 409.44 | 0 | 29.32 | 0 | OK | Ground clear controls. | 5 | 36.34 | 438.76
263 | TIN-INTERP | Interpolated Ground | 1527.8 | 4.68 | 409.97 | 0 | 28.77 | 0 | OK | Ground clear controls. | 5 | 36.34 | 438.74
264 | TIN-INTERP | Interpolated Ground | 1527.8 | -5 | 409.43 | 0 | 18.37 | 0 | OK | Ground clear controls. | 5 | 36.34 | 427.8
265 | TIN-INTERP | Interpolated Ground | 1527.81 | 6.68 | 410.04 | 0 | 23.17 | 0 | OK | Ground clear controls. | 5 | 36.34 | 433.21
266 | TIN-INTERP | Interpolated Ground | 1527.91 | 5.18 | 410.01 | 0 | 17.77 | 0 | OK | Ground clear controls. | 5 | 36.34 | 427.78
267 | TIN-INTERP | Interpolated Ground | 1567.68 | -6.52 | 414.37 | 0 | 19.5 | 0 | OK | Ground clear controls. | 5 | 36.34 | 433.87
268 | TIN-INTERP | Interpolated Ground | 1567.71 | -4.51 | 414.69 | 0 | 24.72 | 0 | OK | Ground clear controls. | 5 | 36.34 | 439.41
269 | TIN-INTERP | Interpolated Ground | 1567.8 | 4.67 | 415.88 | 0 | 23.47 | 0 | OK | Ground clear controls. | 5 | 36.34 | 439.35
270 | TIN-INTERP | Interpolated Ground | 1567.8 | -5.02 | 414.61 | 0 | 13.86 | 0 | OK | Ground clear controls. | 5 | 36.34 | 428.47
271 | TIN-INTERP | Interpolated Ground | 1567.81 | 6.67 | 416.06 | 0 | 17.74 | 0 | OK | Ground clear controls. | 5 | 36.34 | 433.8
272 | TIN-INTERP | Interpolated Ground | 1567.91 | 5.17 | 415.95 | 0 | 12.47 | 0 | OK | Ground clear controls. | 5 | 36.34 | 428.42
273 | TIN-INTERP | Interpolated Ground | 1607.68 | -6.53 | 418.76 | 0 | 16.65 | 0 | OK | Ground clear controls. | 5 | 36.34 | 435.41
274 | TIN-INTERP | Interpolated Ground | 1607.71 | -4.53 | 418.91 | 0 | 22.04 | 0 | OK | Ground clear controls. | 5 | 36.34 | 440.95
275 | TIN-INTERP | Interpolated Ground | 1607.8 | 4.66 | 419.62 | 0 | 21.27 | 0 | OK | Ground clear controls. | 5 | 36.34 | 440.89
276 | TIN-INTERP | Interpolated Ground | 1607.8 | -5.03 | 418.88 | 0 | 11.14 | 0 | OK | Ground clear controls. | 5 | 36.34 | 430.02
277 | TIN-INTERP | Interpolated Ground | 1607.81 | 6.66 | 419.71 | 0 | 15.61 | 0 | OK | Ground clear controls. | 5 | 36.34 | 435.32
278 | TIN-INTERP | Interpolated Ground | 1607.91 | 5.16 | 419.65 | 0 | 10.32 | 0 | OK | Ground clear controls. | 5 | 36.34 | 429.97
279 | TIN-INTERP | Interpolated Ground | 1647.68 | -6.54 | 420.74 | 0 | 17.1 | 0 | OK | Ground clear controls. | 5 | 36.34 | 437.84
280 | TIN-INTERP | Interpolated Ground | 1647.71 | -4.54 | 420.95 | 0 | 22.43 | 0 | OK | Ground clear controls. | 5 | 36.34 | 443.38
281 | TIN-INTERP | Interpolated Ground | 1647.8 | 4.65 | 421.87 | 0 | 21.45 | 0 | OK | Ground clear controls. | 5 | 36.34 | 443.32
282 | TIN-INTERP | Interpolated Ground | 1647.8 | -5.04 | 420.9 | 0 | 11.56 | 0 | OK | Ground clear controls. | 5 | 36.34 | 432.46
283 | TIN-INTERP | Interpolated Ground | 1647.81 | 6.65 | 422.18 | 0 | 15.57 | 0 | OK | Ground clear controls. | 5 | 36.34 | 437.75
284 | TIN-INTERP | Interpolated Ground | 1647.91 | 5.15 | 421.97 | 0 | 10.43 | 0 | OK | Ground clear controls. | 5 | 36.34 | 432.4
285 | TIN-INTERP | Interpolated Ground | 1687.68 | -6.55 | 422.68 | 0 | 18.5 | 0 | OK | Ground clear controls. | 5 | 36.34 | 441.18
286 | TIN-INTERP | Interpolated Ground | 1687.71 | -4.55 | 422.9 | 0 | 23.81 | 0 | OK | Ground clear controls. | 5 | 36.34 | 446.71
287 | TIN-INTERP | Interpolated Ground | 1687.8 | 4.64 | 424.06 | 0 | 22.6 | 0 | OK | Ground clear controls. | 5 | 36.34 | 446.66
288 | TIN-INTERP | Interpolated Ground | 1687.8 | -5.06 | 422.85 | 0 | 12.94 | 0 | OK | Ground clear controls. | 5 | 36.34 | 435.79
289 | TIN-INTERP | Interpolated Ground | 1687.81 | 6.64 | 424.33 | 0 | 16.77 | 0 | OK | Ground clear controls. | 5 | 36.34 | 441.1
290 | TIN-INTERP | Interpolated Ground | 1687.91 | 5.14 | 424.14 | 0 | 11.6 | 0 | OK | Ground clear controls. | 5 | 36.34 | 435.74
291 | TIN-INTERP | Interpolated Ground | 1727.68 | -6.57 | 424.71 | 0 | 20.71 | 0 | OK | Ground clear controls. | 5 | 36.34 | 445.42
292 | TIN-INTERP | Interpolated Ground | 1727.71 | -4.57 | 424.87 | 0 | 26.09 | 0 | OK | Ground clear controls. | 5 | 36.34 | 450.96
293 | TIN-INTERP | Interpolated Ground | 1727.8 | 4.63 | 424.79 | 0 | 26.12 | 0 | OK | Ground clear controls. | 5 | 36.34 | 450.91
294 | TIN-INTERP | Interpolated Ground | 1727.8 | -5.07 | 424.87 | 0 | 15.14 | 0 | OK | Ground clear controls. | 5 | 36.34 | 440.01
295 | TIN-INTERP | Interpolated Ground | 1727.81 | 6.63 | 424.9 | 0 | 20.47 | 0 | OK | Ground clear controls. | 5 | 36.34 | 445.37
296 | TIN-INTERP | Interpolated Ground | 1727.91 | 5.13 | 424.82 | 0 | 15.15 | 0 | OK | Ground clear controls. | 5 | 36.34 | 439.97
297 | TIN-INTERP | Interpolated Ground | 1767.68 | -6.58 | 419.37 | 0 | 31.2 | 0 | OK | Ground clear controls. | 5 | 36.34 | 450.57
298 | TIN-INTERP | Interpolated Ground | 1767.71 | -4.58 | 419.75 | 0 | 36.34 | 0 | OK | Ground clear controls. | 5 | 36.34 | 456.09
299 | TIN-INTERP | Interpolated Ground | 1767.8 | 4.62 | 421.62 | 0 | 34.44 | 0 | OK | Ground clear controls. | 5 | 34.44 | 456.06
300 | TIN-INTERP | Interpolated Ground | 1767.8 | -5.08 | 419.64 | 0 | 25.49 | 0 | OK | Ground clear controls. | 5 | 28.8 | 445.13
301 | TIN-INTERP | Interpolated Ground | 1767.81 | 6.62 | 421.75 | 0 | 28.8 | 0 | OK | Ground clear controls. | 5 | 28.8 | 450.55
302 | TIN-INTERP | Interpolated Ground | 1767.91 | 5.12 | 421.67 | 0 | 23.44 | 0 | OK | Ground clear controls. | 5 | 23.44 | 445.11
303 | TIN-INTERP | Interpolated Ground | 1803.21 | -5.09 | 425.22 | 0 | 25.18 | 0 | OK | Ground clear controls. | 6 | 44.21 | 450.4
304 | TIN-INTERP | Interpolated Ground | 1803.22 | 5.11 | 424.9 | 0 | 25.51 | 0 | OK | Ground clear controls. | 6 | 44.21 | 450.41
305 | TIN-INTERP | Interpolated Ground | 1803.25 | 4.61 | 424.78 | 0 | 36.63 | 0 | OK | Ground clear controls. | 6 | 44.21 | 461.41
306 | TIN-INTERP | Interpolated Ground | 1803.25 | -4.59 | 425.23 | 0 | 36.18 | 0 | OK | Ground clear controls. | 6 | 44.21 | 461.41
307 | TIN-INTERP | Interpolated Ground | 1803.26 | -6.59 | 425.09 | 0 | 30.82 | 0 | OK | Ground clear controls. | 6 | 44.21 | 455.91
308 | TIN-INTERP | Interpolated Ground | 1803.26 | 6.61 | 425.19 | 0 | 30.71 | 0 | OK | Ground clear controls. | 6 | 44.21 | 455.9
309 | TIN-INTERP | Interpolated Ground | 1843.21 | -5.08 | 427.66 | 0 | 20.07 | 0 | OK | Ground clear controls. | 6 | 44.21 | 447.73
310 | TIN-INTERP | Interpolated Ground | 1843.22 | 5.12 | 427.85 | 0 | 19.85 | 0 | OK | Ground clear controls. | 6 | 44.21 | 447.7
311 | TIN-INTERP | Interpolated Ground | 1843.25 | 4.62 | 427.85 | 0 | 30.83 | 0 | OK | Ground clear controls. | 6 | 44.21 | 458.68
312 | TIN-INTERP | Interpolated Ground | 1843.25 | -4.58 | 427.75 | 0 | 30.97 | 0 | OK | Ground clear controls. | 6 | 44.21 | 458.72
313 | TIN-INTERP | Interpolated Ground | 1843.26 | -6.58 | 427.66 | 0 | 25.54 | 0 | OK | Ground clear controls. | 6 | 44.21 | 453.2
314 | TIN-INTERP | Interpolated Ground | 1843.26 | 6.62 | 427.87 | 0 | 25.28 | 0 | OK | Ground clear controls. | 6 | 44.21 | 453.15
315 | TIN-INTERP | Interpolated Ground | 1883.21 | -5.07 | 428.43 | 0 | 17.5 | 0 | OK | Ground clear controls. | 6 | 44.21 | 445.93
316 | TIN-INTERP | Interpolated Ground | 1883.22 | 5.12 | 428.74 | 0 | 17.15 | 0 | OK | Ground clear controls. | 6 | 44.21 | 445.89
317 | TIN-INTERP | Interpolated Ground | 1883.25 | 4.62 | 428.72 | 0 | 28.13 | 0 | OK | Ground clear controls. | 6 | 44.21 | 456.85
318 | TIN-INTERP | Interpolated Ground | 1883.25 | -4.57 | 428.45 | 0 | 28.46 | 0 | OK | Ground clear controls. | 6 | 44.21 | 456.91
319 | TIN-INTERP | Interpolated Ground | 1883.26 | -6.57 | 428.42 | 0 | 22.96 | 0 | OK | Ground clear controls. | 6 | 44.21 | 451.38
320 | TIN-INTERP | Interpolated Ground | 1883.26 | 6.62 | 428.85 | 0 | 22.46 | 0 | OK | Ground clear controls. | 6 | 44.21 | 451.31
321 | TIN-INTERP | Interpolated Ground | 1923.21 | -5.06 | 429.86 | 0 | 15.15 | 0 | OK | Ground clear controls. | 6 | 44.21 | 445.01
322 | TIN-INTERP | Interpolated Ground | 1923.22 | 5.13 | 430.71 | 0 | 14.24 | 0 | OK | Ground clear controls. | 6 | 44.21 | 444.95
323 | TIN-INTERP | Interpolated Ground | 1923.25 | 4.63 | 430.67 | 0 | 25.24 | 0 | OK | Ground clear controls. | 6 | 44.21 | 455.91
324 | TIN-INTERP | Interpolated Ground | 1923.25 | -4.56 | 429.9 | 0 | 26.08 | 0 | OK | Ground clear controls. | 6 | 44.21 | 455.98
325 | TIN-INTERP | Interpolated Ground | 1923.26 | -6.56 | 429.73 | 0 | 20.72 | 0 | OK | Ground clear controls. | 6 | 44.21 | 450.45
326 | TIN-INTERP | Interpolated Ground | 1923.26 | 6.63 | 430.71 | 0 | 19.64 | 0 | OK | Ground clear controls. | 6 | 44.21 | 450.35
327 | TIN-INTERP | Interpolated Ground | 1963.21 | -5.05 | 430.69 | 0 | 14.28 | 0 | OK | Ground clear controls. | 6 | 44.21 | 444.97
328 | TIN-INTERP | Interpolated Ground | 1963.22 | 5.14 | 431.82 | 0 | 13.09 | 0 | OK | Ground clear controls. | 6 | 44.21 | 444.91
329 | TIN-INTERP | Interpolated Ground | 1963.25 | 4.64 | 431.79 | 0 | 24.06 | 0 | OK | Ground clear controls. | 6 | 44.21 | 455.85
330 | TIN-INTERP | Interpolated Ground | 1963.25 | -4.55 | 430.75 | 0 | 25.19 | 0 | OK | Ground clear controls. | 6 | 44.21 | 455.94
331 | TIN-INTERP | Interpolated Ground | 1963.26 | -6.56 | 430.6 | 0 | 19.8 | 0 | OK | Ground clear controls. | 6 | 44.21 | 450.4
332 | TIN-INTERP | Interpolated Ground | 1963.26 | 6.64 | 432 | 0 | 18.29 | 0 | OK | Ground clear controls. | 6 | 44.21 | 450.29
333 | TIN-INTERP | Interpolated Ground | 2003.21 | -5.05 | 431.92 | 0 | 13.88 | 0 | OK | Ground clear controls. | 6 | 44.21 | 445.8
334 | TIN-INTERP | Interpolated Ground | 2003.22 | 5.15 | 433.36 | 0 | 12.38 | 0 | OK | Ground clear controls. | 6 | 44.21 | 445.74
335 | TIN-INTERP | Interpolated Ground | 2003.25 | 4.65 | 433.32 | 0 | 23.37 | 0 | OK | Ground clear controls. | 6 | 44.21 | 456.69
336 | TIN-INTERP | Interpolated Ground | 2003.25 | -4.55 | 431.98 | 0 | 24.8 | 0 | OK | Ground clear controls. | 6 | 44.21 | 456.78
337 | TIN-INTERP | Interpolated Ground | 2003.26 | -6.55 | 431.63 | 0 | 19.61 | 0 | OK | Ground clear controls. | 6 | 44.21 | 451.24
338 | TIN-INTERP | Interpolated Ground | 2003.26 | 6.65 | 433.54 | 0 | 17.59 | 0 | OK | Ground clear controls. | 6 | 44.21 | 451.13
339 | TIN-INTERP | Interpolated Ground | 2043.21 | -5.04 | 414.16 | 0 | 33.35 | 0 | OK | Ground clear controls. | 6 | 44.21 | 447.51
340 | TIN-INTERP | Interpolated Ground | 2043.22 | 5.16 | 415.08 | 0 | 32.38 | 0 | OK | Ground clear controls. | 6 | 44.21 | 447.46
341 | TIN-INTERP | Interpolated Ground | 2043.25 | 4.66 | 414.99 | 0 | 43.42 | 0 | OK | Ground clear controls. | 6 | 44.21 | 458.41
342 | TIN-INTERP | Interpolated Ground | 2043.25 | -4.54 | 414.27 | 0 | 44.21 | 0 | OK | Ground clear controls. | 6 | 44.21 | 458.48
343 | TIN-INTERP | Interpolated Ground | 2043.26 | -6.54 | 413.8 | 0 | 39.15 | 0 | OK | Ground clear controls. | 6 | 39.15 | 452.95
344 | TIN-INTERP | Interpolated Ground | 2043.26 | 6.66 | 415.12 | 0 | 37.75 | 0 | OK | Ground clear controls. | 6 | 37.75 | 452.87
345 | TIN-INTERP | Interpolated Ground | 2083.21 | -5.03 | 425.93 | 0 | 24.15 | 0 | OK | Ground clear controls. | 6 | 36.4 | 450.08
346 | TIN-INTERP | Interpolated Ground | 2083.22 | 5.17 | 424.56 | 0 | 25.51 | 0 | OK | Ground clear controls. | 6 | 36.4 | 450.07
347 | TIN-INTERP | Interpolated Ground | 2083.25 | 4.67 | 424.63 | 0 | 36.4 | 0 | OK | Ground clear controls. | 6 | 36.4 | 461.03
348 | TIN-INTERP | Interpolated Ground | 2083.25 | -4.53 | 425.92 | 0 | 35.15 | 0 | OK | Ground clear controls. | 6 | 35.15 | 461.07
349 | TIN-INTERP | Interpolated Ground | 2083.26 | -6.53 | 426.22 | 0 | 29.34 | 0 | OK | Ground clear controls. | 6 | 31.22 | 455.56
350 | TIN-INTERP | Interpolated Ground | 2083.26 | 6.67 | 424.28 | 0 | 31.22 | 0 | OK | Ground clear controls. | 6 | 31.22 | 455.5
351 | TIN-INTERP | Interpolated Ground | 2123.21 | -5.02 | 437.79 | 0 | 15.76 | 0 | OK | Ground clear controls. | 6 | 27.56 | 453.55
352 | TIN-INTERP | Interpolated Ground | 2123.22 | 5.18 | 436.9 | 0 | 16.66 | 0 | OK | Ground clear controls. | 6 | 27.56 | 453.56
353 | TIN-INTERP | Interpolated Ground | 2123.25 | 4.68 | 436.98 | 0 | 27.56 | 0 | OK | Ground clear controls. | 6 | 27.56 | 464.54
354 | TIN-INTERP | Interpolated Ground | 2123.25 | -4.52 | 437.78 | 0 | 26.77 | 0 | OK | Ground clear controls. | 6 | 26.77 | 464.55
355 | TIN-INTERP | Interpolated Ground | 2123.26 | -6.52 | 437.85 | 0 | 21.19 | 0 | OK | Ground clear controls. | 6 | 22.4 | 459.04
356 | TIN-INTERP | Interpolated Ground | 2123.26 | 6.68 | 436.63 | 0 | 22.4 | 0 | OK | Ground clear controls. | 6 | 22.4 | 459.03
357 | TIN-INTERP | Interpolated Ground | 2133.47 | 5.18 | 438.18 | 0 | 16.41 | 0 | OK | Ground clear controls. | 7 | 38.71 | 454.59
358 | TIN-INTERP | Interpolated Ground | 2133.62 | -5.01 | 438.5 | 0 | 16.09 | 0 | OK | Ground clear controls. | 7 | 38.71 | 454.59
359 | TIN-INTERP | Interpolated Ground | 2133.63 | 6.68 | 438.02 | 0 | 22.08 | 0 | OK | Ground clear controls. | 7 | 38.71 | 460.1
360 | TIN-INTERP | Interpolated Ground | 2133.63 | 4.68 | 438.24 | 0 | 27.36 | 0 | OK | Ground clear controls. | 7 | 38.71 | 465.6
361 | TIN-INTERP | Interpolated Ground | 2133.67 | -4.51 | 438.52 | 0 | 27.08 | 0 | OK | Ground clear controls. | 7 | 38.71 | 465.6
362 | TIN-INTERP | Interpolated Ground | 2133.67 | -6.51 | 438.44 | 0 | 21.66 | 0 | OK | Ground clear controls. | 7 | 38.71 | 460.1
363 | TIN-INTERP | Interpolated Ground | 2173.48 | 5.35 | 440.55 | 0 | 13.05 | 0 | OK | Ground clear controls. | 7 | 38.71 | 453.6
364 | TIN-INTERP | Interpolated Ground | 2173.62 | -4.85 | 439.97 | 0 | 13.67 | 0 | OK | Ground clear controls. | 7 | 38.71 | 453.64
365 | TIN-INTERP | Interpolated Ground | 2173.63 | 6.85 | 440.65 | 0 | 18.43 | 0 | OK | Ground clear controls. | 7 | 38.71 | 459.08
366 | TIN-INTERP | Interpolated Ground | 2173.63 | 4.85 | 440.54 | 0 | 24.07 | 0 | OK | Ground clear controls. | 7 | 38.71 | 464.61
367 | TIN-INTERP | Interpolated Ground | 2173.67 | -4.35 | 440 | 0 | 24.63 | 0 | OK | Ground clear controls. | 7 | 38.71 | 464.63
368 | TIN-INTERP | Interpolated Ground | 2173.67 | -6.35 | 439.89 | 0 | 19.23 | 0 | OK | Ground clear controls. | 7 | 38.71 | 459.12
369 | TIN-INTERP | Interpolated Ground | 2213.48 | 5.51 | 441.76 | 0 | 11.72 | 0 | OK | Ground clear controls. | 7 | 38.71 | 453.48
370 | TIN-INTERP | Interpolated Ground | 2213.62 | -4.68 | 441.64 | 0 | 11.9 | 0 | OK | Ground clear controls. | 7 | 38.71 | 453.54
371 | TIN-INTERP | Interpolated Ground | 2213.62 | 7.01 | 441.84 | 0 | 17.12 | 0 | OK | Ground clear controls. | 7 | 38.71 | 458.96
372 | TIN-INTERP | Interpolated Ground | 2213.63 | 5.01 | 441.75 | 0 | 22.75 | 0 | OK | Ground clear controls. | 7 | 38.71 | 464.5
373 | TIN-INTERP | Interpolated Ground | 2213.67 | -4.18 | 441.67 | 0 | 22.87 | 0 | OK | Ground clear controls. | 7 | 38.71 | 464.54
374 | TIN-INTERP | Interpolated Ground | 2213.67 | -6.18 | 441.53 | 0 | 17.49 | 0 | OK | Ground clear controls. | 7 | 38.71 | 459.02
375 | TIN-INTERP | Interpolated Ground | 2253.48 | 5.68 | 442.94 | 0 | 11.31 | 0 | OK | Ground clear controls. | 7 | 38.71 | 454.25
376 | TIN-INTERP | Interpolated Ground | 2253.62 | -4.51 | 441.59 | 0 | 12.73 | 0 | OK | Ground clear controls. | 7 | 38.71 | 454.32
377 | TIN-INTERP | Interpolated Ground | 2253.62 | 7.18 | 443.05 | 0 | 16.68 | 0 | OK | Ground clear controls. | 7 | 38.71 | 459.73
378 | TIN-INTERP | Interpolated Ground | 2253.63 | 5.18 | 442.87 | 0 | 22.4 | 0 | OK | Ground clear controls. | 7 | 38.71 | 465.27
379 | TIN-INTERP | Interpolated Ground | 2253.67 | -4.01 | 441.65 | 0 | 23.66 | 0 | OK | Ground clear controls. | 7 | 38.71 | 465.31
380 | TIN-INTERP | Interpolated Ground | 2253.67 | -6.01 | 441.24 | 0 | 18.55 | 0 | OK | Ground clear controls. | 7 | 38.71 | 459.79
381 | TIN-INTERP | Interpolated Ground | 2293.48 | 5.84 | 430.85 | 0 | 25.06 | 0 | OK | Ground clear controls. | 7 | 38.71 | 455.91
382 | TIN-INTERP | Interpolated Ground | 2293.62 | -4.35 | 428.14 | 0 | 27.83 | 0 | OK | Ground clear controls. | 7 | 38.71 | 455.97
383 | TIN-INTERP | Interpolated Ground | 2293.62 | 7.34 | 431.18 | 0 | 30.21 | 0 | OK | Ground clear controls. | 7 | 38.71 | 461.39
384 | TIN-INTERP | Interpolated Ground | 2293.63 | 5.34 | 430.68 | 0 | 36.25 | 0 | OK | Ground clear controls. | 7 | 38.71 | 466.93
385 | TIN-INTERP | Interpolated Ground | 2293.67 | -3.84 | 428.26 | 0 | 38.71 | 0 | OK | Ground clear controls. | 7 | 38.71 | 466.97
386 | TIN-INTERP | Interpolated Ground | 2293.67 | -5.84 | 427.81 | 0 | 33.62 | 0 | OK | Ground clear controls. | 7 | 33.62 | 461.43
387 | TIN-INTERP | Interpolated Ground | 2333.48 | 6.01 | 437.19 | 0 | 21.26 | 0 | OK | Ground clear controls. | 7 | 32.15 | 458.45
388 | TIN-INTERP | Interpolated Ground | 2333.62 | -4.18 | 438.34 | 0 | 20.15 | 0 | OK | Ground clear controls. | 7 | 32.15 | 458.49
389 | TIN-INTERP | Interpolated Ground | 2333.62 | 7.5 | 437.01 | 0 | 26.93 | 0 | OK | Ground clear controls. | 7 | 32.15 | 463.94
390 | TIN-INTERP | Interpolated Ground | 2333.63 | 5.51 | 437.32 | 0 | 32.15 | 0 | OK | Ground clear controls. | 7 | 32.15 | 469.47
391 | TIN-INTERP | Interpolated Ground | 2333.67 | -3.67 | 438.28 | 0 | 31.21 | 0 | OK | Ground clear controls. | 7 | 31.21 | 469.49
392 | TIN-INTERP | Interpolated Ground | 2333.67 | -5.68 | 438.78 | 0 | 25.18 | 0 | OK | Ground clear controls. | 7 | 27.74 | 463.96
393 | TIN-INTERP | Interpolated Ground | 2373.48 | 6.17 | 445.88 | 0 | 16 | 0 | OK | Ground clear controls. | 7 | 27.74 | 461.88
394 | TIN-INTERP | Interpolated Ground | 2373.62 | -4.01 | 445.07 | 0 | 16.81 | 0 | OK | Ground clear controls. | 7 | 27.74 | 461.88
395 | TIN-INTERP | Interpolated Ground | 2373.62 | 7.67 | 445.94 | 0 | 21.45 | 0 | OK | Ground clear controls. | 7 | 27.74 | 467.39
396 | TIN-INTERP | Interpolated Ground | 2373.63 | 5.67 | 445.86 | 0 | 27.04 | 0 | OK | Ground clear controls. | 7 | 27.74 | 472.9
397 | TIN-INTERP | Interpolated Ground | 2373.67 | -3.51 | 445.14 | 0 | 27.74 | 0 | OK | Ground clear controls. | 7 | 27.74 | 472.88
398 | TIN-INTERP | Interpolated Ground | 2373.67 | -5.51 | 444.97 | 0 | 22.39 | 0 | OK | Ground clear controls. | 7 | 22.39 | 467.36
399 | TIN-INTERP | Interpolated Ground | 2403.89 | -5.39 | 446.58 | 0 | 23.98 | 0 | OK | Ground clear controls. | 8 | 29.28 | 470.56
400 | TIN-INTERP | Interpolated Ground | 2403.89 | -3.89 | 446.74 | 0 | 18.31 | 0 | OK | Ground clear controls. | 8 | 29.28 | 465.05
401 | TIN-INTERP | Interpolated Ground | 2403.89 | -3.39 | 446.77 | 0 | 29.28 | 0 | OK | Ground clear controls. | 8 | 29.28 | 476.05
402 | TIN-INTERP | Interpolated Ground | 2404.28 | 5.79 | 447.28 | 0 | 28.77 | 0 | OK | Ground clear controls. | 8 | 28.77 | 476.05
403 | TIN-INTERP | Interpolated Ground | 2404.31 | 6.29 | 447.32 | 0 | 17.74 | 0 | OK | Ground clear controls. | 8 | 27.27 | 465.06
404 | TIN-INTERP | Interpolated Ground | 2404.43 | 7.78 | 447.34 | 0 | 23.21 | 0 | OK | Ground clear controls. | 8 | 27.27 | 470.55
405 | TIN-INTERP | Interpolated Ground | 2443.66 | -5.59 | 446.27 | 0 | 21.93 | 0 | OK | Ground clear controls. | 8 | 27.27 | 468.2
406 | TIN-INTERP | Interpolated Ground | 2443.66 | -4.08 | 446.38 | 0 | 16.32 | 0 | OK | Ground clear controls. | 8 | 27.27 | 462.7
407 | TIN-INTERP | Interpolated Ground | 2443.79 | -3.59 | 446.45 | 0 | 27.27 | 0 | OK | Ground clear controls. | 8 | 27.27 | 473.72
408 | TIN-INTERP | Interpolated Ground | 2444.28 | 5.59 | 447.25 | 0 | 26.43 | 0 | OK | Ground clear controls. | 8 | 26.43 | 473.68
409 | TIN-INTERP | Interpolated Ground | 2444.31 | 6.09 | 447.28 | 0 | 15.4 | 0 | OK | Ground clear controls. | 8 | 25.05 | 462.68
410 | TIN-INTERP | Interpolated Ground | 2444.42 | 7.59 | 447.43 | 0 | 20.74 | 0 | OK | Ground clear controls. | 8 | 25.05 | 468.17
411 | TIN-INTERP | Interpolated Ground | 2483.66 | -5.79 | 447.1 | 0 | 19.61 | 0 | OK | Ground clear controls. | 8 | 25.05 | 466.71
412 | TIN-INTERP | Interpolated Ground | 2483.66 | -4.29 | 447.16 | 0 | 14.05 | 0 | OK | Ground clear controls. | 8 | 25.05 | 461.21
413 | TIN-INTERP | Interpolated Ground | 2483.79 | -3.79 | 447.18 | 0 | 25.05 | 0 | OK | Ground clear controls. | 8 | 25.05 | 472.23
414 | TIN-INTERP | Interpolated Ground | 2484.28 | 5.4 | 447.75 | 0 | 24.44 | 0 | OK | Ground clear controls. | 8 | 24.44 | 472.19
415 | TIN-INTERP | Interpolated Ground | 2484.31 | 5.9 | 447.79 | 0 | 13.39 | 0 | OK | Ground clear controls. | 8 | 23.83 | 461.18
416 | TIN-INTERP | Interpolated Ground | 2484.42 | 7.39 | 447.85 | 0 | 18.81 | 0 | OK | Ground clear controls. | 8 | 23.83 | 466.66
417 | TIN-INTERP | Interpolated Ground | 2523.66 | -5.99 | 448.22 | 0 | 17.87 | 0 | OK | Ground clear controls. | 8 | 23.83 | 466.09
418 | TIN-INTERP | Interpolated Ground | 2523.66 | -4.49 | 448.34 | 0 | 12.25 | 0 | OK | Ground clear controls. | 8 | 23.83 | 460.59
419 | TIN-INTERP | Interpolated Ground | 2523.79 | -3.99 | 448.37 | 0 | 23.25 | 0 | OK | Ground clear controls. | 8 | 23.83 | 471.62
420 | TIN-INTERP | Interpolated Ground | 2524.28 | 5.2 | 448.87 | 0 | 22.7 | 0 | OK | Ground clear controls. | 8 | 23.83 | 471.57
421 | TIN-INTERP | Interpolated Ground | 2524.31 | 5.7 | 448.86 | 0 | 11.71 | 0 | OK | Ground clear controls. | 8 | 23.83 | 460.57
422 | TIN-INTERP | Interpolated Ground | 2524.42 | 7.19 | 448.84 | 0 | 17.21 | 0 | OK | Ground clear controls. | 8 | 23.83 | 466.05
423 | TIN-INTERP | Interpolated Ground | 2563.66 | -6.19 | 447.87 | 0 | 18.48 | 0 | OK | Ground clear controls. | 8 | 23.83 | 466.35
424 | TIN-INTERP | Interpolated Ground | 2563.66 | -4.69 | 447.99 | 0 | 12.86 | 0 | OK | Ground clear controls. | 8 | 23.83 | 460.85
425 | TIN-INTERP | Interpolated Ground | 2563.79 | -4.19 | 448.05 | 0 | 23.83 | 0 | OK | Ground clear controls. | 8 | 23.83 | 471.88
426 | TIN-INTERP | Interpolated Ground | 2564.28 | 5 | 448.81 | 0 | 23.02 | 0 | OK | Ground clear controls. | 8 | 23.63 | 471.83
427 | TIN-INTERP | Interpolated Ground | 2564.31 | 5.5 | 448.86 | 0 | 11.97 | 0 | OK | Ground clear controls. | 8 | 23.63 | 460.83
428 | TIN-INTERP | Interpolated Ground | 2564.42 | 7 | 449.02 | 0 | 17.3 | 0 | OK | Ground clear controls. | 8 | 23.63 | 466.32
429 | TIN-INTERP | Interpolated Ground | 2603.66 | -6.39 | 449.34 | 0 | 18.13 | 0 | OK | Ground clear controls. | 8 | 23.63 | 467.47
430 | TIN-INTERP | Interpolated Ground | 2603.66 | -4.89 | 449.34 | 0 | 12.63 | 0 | OK | Ground clear controls. | 8 | 23.63 | 461.97
431 | TIN-INTERP | Interpolated Ground | 2603.79 | -4.39 | 449.36 | 0 | 23.63 | 0 | OK | Ground clear controls. | 8 | 23.63 | 472.99
432 | TIN-INTERP | Interpolated Ground | 2604.28 | 4.81 | 449.89 | 0 | 23.09 | 0 | OK | Ground clear controls. | 8 | 23.09 | 472.98
433 | TIN-INTERP | Interpolated Ground | 2604.31 | 5.31 | 449.92 | 0 | 12.06 | 0 | OK | Ground clear controls. | 8 | 17.55 | 461.98
434 | TIN-INTERP | Interpolated Ground | 2604.42 | 6.8 | 449.93 | 0 | 17.55 | 0 | OK | Ground clear controls. | 8 | 17.55 | 467.48
435 | TIN-INTERP | Interpolated Ground | 2641.25 | -6.58 | 448.99 | 0 | 20.33 | 0 | OK | Ground clear controls. | 9 | 33.24 | 469.32
436 | TIN-INTERP | Interpolated Ground | 2641.29 | 4.62 | 449.24 | 0 | 25.58 | 0 | OK | Ground clear controls. | 9 | 33.24 | 474.82
437 | TIN-INTERP | Interpolated Ground | 2641.3 | -4.58 | 449 | 0 | 25.82 | 0 | OK | Ground clear controls. | 9 | 33.24 | 474.82
438 | TIN-INTERP | Interpolated Ground | 2641.42 | 6.62 | 449.3 | 0 | 20.02 | 0 | OK | Ground clear controls. | 9 | 33.24 | 469.32
439 | TIN-INTERP | Interpolated Ground | 2641.55 | -5.08 | 448.95 | 0 | 14.89 | 0 | OK | Ground clear controls. | 9 | 33.24 | 463.84
440 | TIN-INTERP | Interpolated Ground | 2641.58 | 5.12 | 449.26 | 0 | 14.58 | 0 | OK | Ground clear controls. | 9 | 33.24 | 463.84
441 | TIN-INTERP | Interpolated Ground | 2681.25 | -6.58 | 445.14 | 0 | 21.47 | 0 | OK | Ground clear controls. | 9 | 33.24 | 466.61
442 | TIN-INTERP | Interpolated Ground | 2681.29 | 4.63 | 444.26 | 0 | 27.83 | 0 | OK | Ground clear controls. | 9 | 33.24 | 472.09
443 | TIN-INTERP | Interpolated Ground | 2681.3 | -4.58 | 445.12 | 0 | 27.04 | 0 | OK | Ground clear controls. | 9 | 33.24 | 472.16
444 | TIN-INTERP | Interpolated Ground | 2681.42 | 6.63 | 444.06 | 0 | 22.54 | 0 | OK | Ground clear controls. | 9 | 33.24 | 466.6
445 | TIN-INTERP | Interpolated Ground | 2681.55 | -5.08 | 445.07 | 0 | 16.13 | 0 | OK | Ground clear controls. | 9 | 33.24 | 461.2
446 | TIN-INTERP | Interpolated Ground | 2681.58 | 5.13 | 444.21 | 0 | 16.95 | 0 | OK | Ground clear controls. | 9 | 33.24 | 461.16
447 | TIN-INTERP | Interpolated Ground | 2721.25 | -6.58 | 439.56 | 0 | 25.22 | 0 | OK | Ground clear controls. | 9 | 33.24 | 464.78
448 | TIN-INTERP | Interpolated Ground | 2721.29 | 4.63 | 439.72 | 0 | 30.52 | 0 | OK | Ground clear controls. | 9 | 33.24 | 470.24
449 | TIN-INTERP | Interpolated Ground | 2721.3 | -4.58 | 439.56 | 0 | 30.79 | 0 | OK | Ground clear controls. | 9 | 33.24 | 470.35
450 | TIN-INTERP | Interpolated Ground | 2721.42 | 6.63 | 439.74 | 0 | 25.01 | 0 | OK | Ground clear controls. | 9 | 33.24 | 464.75
451 | TIN-INTERP | Interpolated Ground | 2721.55 | -5.08 | 439.56 | 0 | 19.85 | 0 | OK | Ground clear controls. | 9 | 33.24 | 459.41
452 | TIN-INTERP | Interpolated Ground | 2721.58 | 5.13 | 439.71 | 0 | 19.64 | 0 | OK | Ground clear controls. | 9 | 33.24 | 459.35
453 | TIN-INTERP | Interpolated Ground | 2761.25 | -6.58 | 439.36 | 0 | 24.45 | 0 | OK | Ground clear controls. | 9 | 33.24 | 463.81
454 | TIN-INTERP | Interpolated Ground | 2761.29 | 4.64 | 439.59 | 0 | 29.67 | 0 | OK | Ground clear controls. | 9 | 33.24 | 469.26
455 | TIN-INTERP | Interpolated Ground | 2761.3 | -4.58 | 439.35 | 0 | 30.05 | 0 | OK | Ground clear controls. | 9 | 33.24 | 469.4
456 | TIN-INTERP | Interpolated Ground | 2761.42 | 6.64 | 439.57 | 0 | 24.21 | 0 | OK | Ground clear controls. | 9 | 33.24 | 463.78
457 | TIN-INTERP | Interpolated Ground | 2761.55 | -5.08 | 439.38 | 0 | 19.1 | 0 | OK | Ground clear controls. | 9 | 33.24 | 458.48
458 | TIN-INTERP | Interpolated Ground | 2761.58 | 5.14 | 439.61 | 0 | 18.79 | 0 | OK | Ground clear controls. | 9 | 33.24 | 458.4
459 | TIN-INTERP | Interpolated Ground | 2801.25 | -6.58 | 441.27 | 0 | 22.45 | 0 | OK | Ground clear controls. | 9 | 33.24 | 463.72
460 | TIN-INTERP | Interpolated Ground | 2801.29 | 4.64 | 441.54 | 0 | 27.62 | 0 | OK | Ground clear controls. | 9 | 33.24 | 469.16
461 | TIN-INTERP | Interpolated Ground | 2801.3 | -4.58 | 441.35 | 0 | 27.97 | 0 | OK | Ground clear controls. | 9 | 33.24 | 469.32
462 | TIN-INTERP | Interpolated Ground | 2801.42 | 6.65 | 441.46 | 0 | 22.22 | 0 | OK | Ground clear controls. | 9 | 33.24 | 463.68
463 | TIN-INTERP | Interpolated Ground | 2801.55 | -5.08 | 441.38 | 0 | 17.02 | 0 | OK | Ground clear controls. | 9 | 33.24 | 458.4
464 | TIN-INTERP | Interpolated Ground | 2801.58 | 5.15 | 441.56 | 0 | 16.75 | 0 | OK | Ground clear controls. | 9 | 33.24 | 458.31
465 | TIN-INTERP | Interpolated Ground | 2841.25 | -6.58 | 445.09 | 0 | 19.41 | 0 | OK | Ground clear controls. | 9 | 33.24 | 464.5
466 | TIN-INTERP | Interpolated Ground | 2841.29 | 4.65 | 446.87 | 0 | 23.06 | 0 | OK | Ground clear controls. | 9 | 33.24 | 469.93
467 | TIN-INTERP | Interpolated Ground | 2841.3 | -4.58 | 445.45 | 0 | 24.64 | 0 | OK | Ground clear controls. | 9 | 33.24 | 470.09
468 | TIN-INTERP | Interpolated Ground | 2841.42 | 6.65 | 447.02 | 0 | 17.44 | 0 | OK | Ground clear controls. | 9 | 33.24 | 464.46
469 | TIN-INTERP | Interpolated Ground | 2841.55 | -5.08 | 445.38 | 0 | 13.81 | 0 | OK | Ground clear controls. | 9 | 33.24 | 459.19
470 | TIN-INTERP | Interpolated Ground | 2841.58 | 5.15 | 446.98 | 0 | 12.12 | 0 | OK | Ground clear controls. | 9 | 33.24 | 459.1
471 | TIN-INTERP | Interpolated Ground | 2881.25 | -6.58 | 448.84 | 0 | 17.31 | 0 | OK | Ground clear controls. | 9 | 33.24 | 466.15
472 | TIN-INTERP | Interpolated Ground | 2881.29 | 4.66 | 449.12 | 0 | 22.47 | 0 | OK | Ground clear controls. | 9 | 33.24 | 471.59
473 | TIN-INTERP | Interpolated Ground | 2881.3 | -4.58 | 448.84 | 0 | 22.9 | 0 | OK | Ground clear controls. | 9 | 33.24 | 471.74
474 | TIN-INTERP | Interpolated Ground | 2881.42 | 6.66 | 449.27 | 0 | 16.84 | 0 | OK | Ground clear controls. | 9 | 33.24 | 466.11
475 | TIN-INTERP | Interpolated Ground | 2881.55 | -5.08 | 448.87 | 0 | 11.96 | 0 | OK | Ground clear controls. | 9 | 33.24 | 460.83
476 | TIN-INTERP | Interpolated Ground | 2881.58 | 5.16 | 449.16 | 0 | 11.58 | 0 | OK | Ground clear controls. | 9 | 33.24 | 460.74
477 | TIN-INTERP | Interpolated Ground | 2921.25 | -6.58 | 448.34 | 0 | 20.33 | 0 | OK | Ground clear controls. | 9 | 33.24 | 468.67
478 | TIN-INTERP | Interpolated Ground | 2921.29 | 4.66 | 449.55 | 0 | 24.58 | 0 | OK | Ground clear controls. | 9 | 33.24 | 474.13
479 | TIN-INTERP | Interpolated Ground | 2921.3 | -4.58 | 448.39 | 0 | 25.87 | 0 | OK | Ground clear controls. | 9 | 33.24 | 474.26
480 | TIN-INTERP | Interpolated Ground | 2921.42 | 6.66 | 449.79 | 0 | 18.85 | 0 | OK | Ground clear controls. | 9 | 33.24 | 468.64
481 | TIN-INTERP | Interpolated Ground | 2921.55 | -5.08 | 448.37 | 0 | 14.97 | 0 | OK | Ground clear controls. | 9 | 33.24 | 463.34
482 | TIN-INTERP | Interpolated Ground | 2921.58 | 5.16 | 449.56 | 0 | 13.7 | 0 | OK | Ground clear controls. | 9 | 33.24 | 463.26
483 | TIN-INTERP | Interpolated Ground | 2961.25 | -6.58 | 445.68 | 0 | 26.39 | 0 | OK | Ground clear controls. | 9 | 33.24 | 472.07
484 | TIN-INTERP | Interpolated Ground | 2961.29 | 4.67 | 445.97 | 0 | 31.57 | 0 | OK | Ground clear controls. | 9 | 33.24 | 477.54
485 | TIN-INTERP | Interpolated Ground | 2961.3 | -4.58 | 445.75 | 0 | 31.88 | 0 | OK | Ground clear controls. | 9 | 33.24 | 477.63
486 | TIN-INTERP | Interpolated Ground | 2961.42 | 6.67 | 446.02 | 0 | 26.04 | 0 | OK | Ground clear controls. | 9 | 33.24 | 472.06
487 | TIN-INTERP | Interpolated Ground | 2961.55 | -5.08 | 445.79 | 0 | 20.91 | 0 | OK | Ground clear controls. | 9 | 33.24 | 466.7
488 | TIN-INTERP | Interpolated Ground | 2961.58 | 5.17 | 445.98 | 0 | 20.67 | 0 | OK | Ground clear controls. | 9 | 33.24 | 466.65
489 | TIN-INTERP | Interpolated Ground | 3001.25 | -6.58 | 448.59 | 0 | 27.76 | 0 | OK | Ground clear controls. | 9 | 33.24 | 476.35
490 | TIN-INTERP | Interpolated Ground | 3001.29 | 4.67 | 448.61 | 0 | 33.23 | 0 | OK | Ground clear controls. | 9 | 33.24 | 481.84
491 | TIN-INTERP | Interpolated Ground | 3001.3 | -4.58 | 448.63 | 0 | 33.24 | 0 | OK | Ground clear controls. | 9 | 33.24 | 481.87
492 | TIN-INTERP | Interpolated Ground | 3001.42 | 6.68 | 448.56 | 0 | 27.79 | 0 | OK | Ground clear controls. | 9 | 27.79 | 476.35
493 | TIN-INTERP | Interpolated Ground | 3001.55 | -5.08 | 448.61 | 0 | 22.31 | 0 | OK | Ground clear controls. | 9 | 22.31 | 470.92
494 | TIN-INTERP | Interpolated Ground | 3001.58 | 5.18 | 448.58 | 0 | 22.31 | 0 | OK | Ground clear controls. | 9 | 22.31 | 470.89
495 | TIN-INTERP | Interpolated Ground | 3022.62 | -6.58 | 448.29 | 0 | 30.7 | 0 | OK | Ground clear controls. | 10 | 40.17 | 478.99
496 | TIN-INTERP | Interpolated Ground | 3022.64 | -5.08 | 448.42 | 0 | 25.06 | 0 | OK | Ground clear controls. | 10 | 40.17 | 473.48
497 | TIN-INTERP | Interpolated Ground | 3022.65 | -4.58 | 448.44 | 0 | 36.05 | 0 | OK | Ground clear controls. | 10 | 40.17 | 484.49
498 | TIN-INTERP | Interpolated Ground | 3022.66 | 4.67 | 448.48 | 0 | 36.01 | 0 | OK | Ground clear controls. | 10 | 40.17 | 484.49
499 | TIN-INTERP | Interpolated Ground | 3022.69 | 5.18 | 448.52 | 0 | 24.97 | 0 | OK | Ground clear controls. | 10 | 40.17 | 473.49
500 | TIN-INTERP | Interpolated Ground | 3022.71 | 6.68 | 448.63 | 0 | 30.36 | 0 | OK | Ground clear controls. | 10 | 40.17 | 478.99
501 | TIN-INTERP | Interpolated Ground | 3062.62 | -6.54 | 449.29 | 0 | 26.43 | 0 | OK | Ground clear controls. | 10 | 40.17 | 475.72
502 | TIN-INTERP | Interpolated Ground | 3062.64 | -5.03 | 449.42 | 0 | 20.85 | 0 | OK | Ground clear controls. | 10 | 40.17 | 470.27
503 | TIN-INTERP | Interpolated Ground | 3062.65 | -4.51 | 449.47 | 0 | 31.87 | 0 | OK | Ground clear controls. | 10 | 40.17 | 481.34
504 | TIN-INTERP | Interpolated Ground | 3062.66 | 4.92 | 450.22 | 0 | 31.09 | 0 | OK | Ground clear controls. | 10 | 40.17 | 481.31
505 | TIN-INTERP | Interpolated Ground | 3062.69 | 5.45 | 450.3 | 0 | 19.99 | 0 | OK | Ground clear controls. | 10 | 40.17 | 470.29
506 | TIN-INTERP | Interpolated Ground | 3062.71 | 6.94 | 450.47 | 0 | 25.3 | 0 | OK | Ground clear controls. | 10 | 40.17 | 475.77
507 | TIN-INTERP | Interpolated Ground | 3102.62 | -6.49 | 451.48 | 0 | 21.83 | 0 | OK | Ground clear controls. | 10 | 40.17 | 473.31
508 | TIN-INTERP | Interpolated Ground | 3102.64 | -4.98 | 451.62 | 0 | 16.3 | 0 | OK | Ground clear controls. | 10 | 40.17 | 467.92
509 | TIN-INTERP | Interpolated Ground | 3102.65 | -4.44 | 451.67 | 0 | 27.39 | 0 | OK | Ground clear controls. | 10 | 40.17 | 479.06
510 | TIN-INTERP | Interpolated Ground | 3102.66 | 5.17 | 452.63 | 0 | 26.37 | 0 | OK | Ground clear controls. | 10 | 40.17 | 479
511 | TIN-INTERP | Interpolated Ground | 3102.69 | 5.71 | 452.65 | 0 | 15.32 | 0 | OK | Ground clear controls. | 10 | 40.17 | 467.97
512 | TIN-INTERP | Interpolated Ground | 3102.71 | 7.21 | 452.69 | 0 | 20.73 | 0 | OK | Ground clear controls. | 10 | 40.17 | 473.42
513 | TIN-INTERP | Interpolated Ground | 3142.62 | -6.44 | 451.28 | 0 | 20.5 | 0 | OK | Ground clear controls. | 10 | 40.17 | 471.78
514 | TIN-INTERP | Interpolated Ground | 3142.64 | -4.94 | 451.55 | 0 | 14.88 | 0 | OK | Ground clear controls. | 10 | 40.17 | 466.43
515 | TIN-INTERP | Interpolated Ground | 3142.65 | -4.37 | 451.64 | 0 | 26 | 0 | OK | Ground clear controls. | 10 | 40.17 | 477.64
516 | TIN-INTERP | Interpolated Ground | 3142.65 | 5.42 | 453.77 | 0 | 23.81 | 0 | OK | Ground clear controls. | 10 | 40.17 | 477.58
517 | TIN-INTERP | Interpolated Ground | 3142.69 | 5.98 | 453.9 | 0 | 12.59 | 0 | OK | Ground clear controls. | 10 | 40.17 | 466.49
518 | TIN-INTERP | Interpolated Ground | 3142.71 | 7.47 | 454.03 | 0 | 17.93 | 0 | OK | Ground clear controls. | 10 | 40.17 | 471.96
519 | TIN-INTERP | Interpolated Ground | 3182.62 | -6.39 | 449.32 | 0 | 21.81 | 0 | OK | Ground clear controls. | 10 | 40.17 | 471.13
520 | TIN-INTERP | Interpolated Ground | 3182.64 | -4.89 | 449.54 | 0 | 16.25 | 0 | OK | Ground clear controls. | 10 | 40.17 | 465.79
521 | TIN-INTERP | Interpolated Ground | 3182.65 | -4.3 | 449.63 | 0 | 27.45 | 0 | OK | Ground clear controls. | 10 | 40.17 | 477.08
522 | TIN-INTERP | Interpolated Ground | 3182.65 | 5.67 | 451.13 | 0 | 25.9 | 0 | OK | Ground clear controls. | 10 | 40.17 | 477.03
523 | TIN-INTERP | Interpolated Ground | 3182.69 | 6.25 | 451.23 | 0 | 14.66 | 0 | OK | Ground clear controls. | 10 | 40.17 | 465.89
524 | TIN-INTERP | Interpolated Ground | 3182.71 | 7.74 | 451.46 | 0 | 19.9 | 0 | OK | Ground clear controls. | 10 | 40.17 | 471.36
525 | TIN-INTERP | Interpolated Ground | 3222.62 | -6.35 | 446.82 | 0 | 24.53 | 0 | OK | Ground clear controls. | 10 | 40.17 | 471.35
526 | TIN-INTERP | Interpolated Ground | 3222.64 | -4.84 | 447 | 0 | 19.02 | 0 | OK | Ground clear controls. | 10 | 40.17 | 466.02
527 | TIN-INTERP | Interpolated Ground | 3222.65 | -4.23 | 447.07 | 0 | 30.33 | 0 | OK | Ground clear controls. | 10 | 40.17 | 477.4
528 | TIN-INTERP | Interpolated Ground | 3222.65 | 5.91 | 448.5 | 0 | 28.86 | 0 | OK | Ground clear controls. | 10 | 40.17 | 477.36
529 | TIN-INTERP | Interpolated Ground | 3222.68 | 6.51 | 448.63 | 0 | 17.52 | 0 | OK | Ground clear controls. | 10 | 40.17 | 466.15
530 | TIN-INTERP | Interpolated Ground | 3222.71 | 8 | 448.98 | 0 | 22.66 | 0 | OK | Ground clear controls. | 10 | 40.17 | 471.64
531 | TIN-INTERP | Interpolated Ground | 3262.62 | -6.3 | 438.29 | 0 | 34.17 | 0 | OK | Ground clear controls. | 10 | 40.17 | 472.46
532 | TIN-INTERP | Interpolated Ground | 3262.64 | -4.79 | 438.32 | 0 | 28.77 | 0 | OK | Ground clear controls. | 10 | 40.17 | 467.09
533 | TIN-INTERP | Interpolated Ground | 3262.65 | -4.16 | 438.4 | 0 | 40.17 | 0 | OK | Ground clear controls. | 10 | 40.17 | 478.57
534 | TIN-INTERP | Interpolated Ground | 3262.65 | 6.16 | 439.93 | 0 | 38.64 | 0 | OK | Ground clear controls. | 10 | 38.64 | 478.57
535 | TIN-INTERP | Interpolated Ground | 3262.68 | 6.78 | 439.97 | 0 | 27.3 | 0 | OK | Ground clear controls. | 10 | 38.64 | 467.27
536 | TIN-INTERP | Interpolated Ground | 3262.7 | 8.27 | 440.29 | 0 | 32.5 | 0 | OK | Ground clear controls. | 10 | 38.64 | 472.79
537 | TIN-INTERP | Interpolated Ground | 3302.62 | -6.25 | 442.54 | 0 | 31.88 | 0 | OK | Ground clear controls. | 10 | 38.64 | 474.42
538 | TIN-INTERP | Interpolated Ground | 3302.64 | -4.74 | 442.4 | 0 | 26.63 | 0 | OK | Ground clear controls. | 10 | 38.64 | 469.03
539 | TIN-INTERP | Interpolated Ground | 3302.65 | -4.09 | 442.35 | 0 | 38.26 | 0 | OK | Ground clear controls. | 10 | 38.64 | 480.61
540 | TIN-INTERP | Interpolated Ground | 3302.65 | 6.41 | 442.02 | 0 | 38.64 | 0 | OK | Ground clear controls. | 10 | 38.64 | 480.66
541 | TIN-INTERP | Interpolated Ground | 3302.68 | 7.05 | 441.98 | 0 | 27.28 | 0 | OK | Ground clear controls. | 10 | 33.89 | 469.26
542 | TIN-INTERP | Interpolated Ground | 3302.7 | 8.53 | 441.85 | 0 | 32.96 | 0 | OK | Ground clear controls. | 10 | 33.89 | 474.81
543 | TIN-INTERP | Interpolated Ground | 3342.62 | -6.21 | 450.07 | 0 | 27.21 | 0 | OK | Ground clear controls. | 10 | 33.89 | 477.28
544 | TIN-INTERP | Interpolated Ground | 3342.64 | -4.69 | 450.04 | 0 | 21.8 | 0 | OK | Ground clear controls. | 10 | 33.89 | 471.84
545 | TIN-INTERP | Interpolated Ground | 3342.65 | -4.02 | 450.04 | 0 | 33.48 | 0 | OK | Ground clear controls. | 10 | 33.89 | 483.52
546 | TIN-INTERP | Interpolated Ground | 3342.65 | 6.66 | 449.74 | 0 | 33.89 | 0 | OK | Ground clear controls. | 10 | 33.89 | 483.63
547 | TIN-INTERP | Interpolated Ground | 3342.68 | 7.31 | 449.72 | 0 | 22.4 | 0 | OK | Ground clear controls. | 10 | 30.02 | 472.12
548 | TIN-INTERP | Interpolated Ground | 3342.7 | 8.8 | 449.68 | 0 | 28.02 | 0 | OK | Ground clear controls. | 10 | 30.02 | 477.7
549 | TIN-INTERP | Interpolated Ground | 3382.62 | -6.16 | 457.28 | 0 | 23.72 | 0 | OK | Ground clear controls. | 10 | 30.02 | 481
550 | TIN-INTERP | Interpolated Ground | 3382.64 | -4.65 | 457.24 | 0 | 18.27 | 0 | OK | Ground clear controls. | 10 | 30.02 | 475.51
551 | TIN-INTERP | Interpolated Ground | 3382.65 | -3.95 | 457.27 | 0 | 30.02 | 0 | OK | Ground clear controls. | 10 | 30.02 | 487.29
552 | TIN-INTERP | Interpolated Ground | 3382.65 | 6.91 | 457.53 | 0 | 29.95 | 0 | OK | Ground clear controls. | 10 | 29.95 | 487.48
553 | TIN-INTERP | Interpolated Ground | 3382.68 | 7.58 | 457.56 | 0 | 18.28 | 0 | OK | Ground clear controls. | 10 | 28.07 | 475.84
554 | TIN-INTERP | Interpolated Ground | 3382.7 | 9.07 | 457.66 | 0 | 23.82 | 0 | OK | Ground clear controls. | 10 | 28.07 | 481.48
555 | TIN-INTERP | Interpolated Ground | 3422.62 | -6.11 | 464.14 | 0 | 21.47 | 0 | OK | Ground clear controls. | 10 | 28.07 | 485.61
556 | TIN-INTERP | Interpolated Ground | 3422.64 | -4.6 | 464.38 | 0 | 15.66 | 0 | OK | Ground clear controls. | 10 | 28.07 | 480.04
557 | TIN-INTERP | Interpolated Ground | 3422.65 | -3.88 | 464.5 | 0 | 27.43 | 0 | OK | Ground clear controls. | 10 | 28.07 | 491.93
558 | TIN-INTERP | Interpolated Ground | 3422.65 | 7.16 | 466.25 | 0 | 25.96 | 0 | OK | Ground clear controls. | 10 | 28.07 | 492.21
559 | TIN-INTERP | Interpolated Ground | 3422.68 | 7.84 | 466.41 | 0 | 14.01 | 0 | OK | Ground clear controls. | 10 | 28.07 | 480.42
560 | TIN-INTERP | Interpolated Ground | 3422.7 | 9.33 | 466.65 | 0 | 19.48 | 0 | OK | Ground clear controls. | 10 | 28.07 | 486.13
561 | TIN-INTERP | Interpolated Ground | 3462.62 | -6.06 | 469.66 | 0 | 21.44 | 0 | OK | Ground clear controls. | 10 | 28.07 | 491.1
562 | TIN-INTERP | Interpolated Ground | 3462.64 | -4.55 | 469.66 | 0 | 15.78 | 0 | OK | Ground clear controls. | 10 | 28.07 | 485.44
563 | TIN-INTERP | Interpolated Ground | 3462.65 | -3.81 | 469.69 | 0 | 27.76 | 0 | OK | Ground clear controls. | 10 | 28.07 | 497.45
564 | TIN-INTERP | Interpolated Ground | 3462.65 | 7.4 | 469.75 | 0 | 28.07 | 0 | OK | Ground clear controls. | 10 | 28.07 | 497.82
565 | TIN-INTERP | Interpolated Ground | 3462.68 | 8.11 | 469.74 | 0 | 16.14 | 0 | OK | Ground clear controls. | 10 | 21.95 | 485.88
566 | TIN-INTERP | Interpolated Ground | 3462.7 | 9.6 | 469.71 | 0 | 21.95 | 0 | OK | Ground clear controls. | 10 | 21.95 | 491.66
567 | TIN-INTERP | Interpolated Ground | 3489.85 | -6.11 | 473.62 | 0 | 21.88 | 0 | OK | Ground clear controls. | 11 | 54.01 | 495.5
568 | TIN-INTERP | Interpolated Ground | 3489.85 | -4.59 | 473.81 | 0 | 15.92 | 0 | OK | Ground clear controls. | 11 | 54.01 | 489.73
569 | TIN-INTERP | Interpolated Ground | 3489.85 | -3.82 | 473.83 | 0 | 27.96 | 0 | OK | Ground clear controls. | 11 | 54.01 | 501.79
570 | TIN-INTERP | Interpolated Ground | 3491.22 | 7.53 | 474.14 | 0 | 27.81 | 0 | OK | Ground clear controls. | 11 | 54.01 | 501.95
571 | TIN-INTERP | Interpolated Ground | 3491.35 | 8.24 | 474.14 | 0 | 15.75 | 0 | OK | Ground clear controls. | 11 | 54.01 | 489.89
572 | TIN-INTERP | Interpolated Ground | 3491.66 | 9.7 | 474.14 | 0 | 21.54 | 0 | OK | Ground clear controls. | 11 | 54.01 | 495.68
573 | TIN-INTERP | Interpolated Ground | 3528.84 | -6.08 | 467.12 | 0 | 24.19 | 0 | OK | Ground clear controls. | 11 | 54.01 | 491.31
574 | TIN-INTERP | Interpolated Ground | 3529.18 | -4.59 | 467.36 | 0 | 18.35 | 0 | OK | Ground clear controls. | 11 | 54.01 | 485.71
575 | TIN-INTERP | Interpolated Ground | 3529.24 | -3.84 | 467.44 | 0 | 30.15 | 0 | OK | Ground clear controls. | 11 | 54.01 | 497.59
576 | TIN-INTERP | Interpolated Ground | 3531.22 | 7.27 | 469.95 | 0 | 27.75 | 0 | OK | Ground clear controls. | 11 | 54.01 | 497.7
577 | TIN-INTERP | Interpolated Ground | 3531.35 | 7.97 | 470.06 | 0 | 15.75 | 0 | OK | Ground clear controls. | 11 | 54.01 | 485.81
578 | TIN-INTERP | Interpolated Ground | 3531.66 | 9.43 | 470.33 | 0 | 21.24 | 0 | OK | Ground clear controls. | 11 | 54.01 | 491.57
579 | TIN-INTERP | Interpolated Ground | 3568.84 | -6.13 | 457.01 | 0 | 30.98 | 0 | OK | Ground clear controls. | 11 | 54.01 | 487.99
580 | TIN-INTERP | Interpolated Ground | 3569.18 | -4.64 | 457.46 | 0 | 25.07 | 0 | OK | Ground clear controls. | 11 | 54.01 | 482.53
581 | TIN-INTERP | Interpolated Ground | 3569.24 | -3.91 | 457.72 | 0 | 36.54 | 0 | OK | Ground clear controls. | 11 | 54.01 | 494.26
582 | TIN-INTERP | Interpolated Ground | 3571.22 | 7.02 | 460.85 | 0 | 33.47 | 0 | OK | Ground clear controls. | 11 | 54.01 | 494.32
583 | TIN-INTERP | Interpolated Ground | 3571.35 | 7.69 | 461.04 | 0 | 21.55 | 0 | OK | Ground clear controls. | 11 | 54.01 | 482.59
584 | TIN-INTERP | Interpolated Ground | 3571.66 | 9.16 | 461.34 | 0 | 26.98 | 0 | OK | Ground clear controls. | 11 | 54.01 | 488.32
585 | TIN-INTERP | Interpolated Ground | 3608.84 | -6.18 | 444.64 | 0 | 40.9 | 0 | OK | Ground clear controls. | 11 | 54.01 | 485.54
586 | TIN-INTERP | Interpolated Ground | 3609.18 | -4.7 | 445.11 | 0 | 35.08 | 0 | OK | Ground clear controls. | 11 | 54.01 | 480.19
587 | TIN-INTERP | Interpolated Ground | 3609.24 | -3.99 | 445.38 | 0 | 46.4 | 0 | OK | Ground clear controls. | 11 | 54.01 | 491.78
588 | TIN-INTERP | Interpolated Ground | 3611.21 | 6.76 | 448.62 | 0 | 43.18 | 0 | OK | Ground clear controls. | 11 | 54.01 | 491.8
589 | TIN-INTERP | Interpolated Ground | 3611.35 | 7.42 | 448.85 | 0 | 31.36 | 0 | OK | Ground clear controls. | 11 | 54.01 | 480.21
590 | TIN-INTERP | Interpolated Ground | 3611.66 | 8.89 | 449.31 | 0 | 36.62 | 0 | OK | Ground clear controls. | 11 | 54.01 | 485.93
591 | TIN-INTERP | Interpolated Ground | 3648.84 | -6.24 | 437.4 | 0 | 46.56 | 0 | OK | Ground clear controls. | 11 | 54.01 | 483.96
592 | TIN-INTERP | Interpolated Ground | 3649.18 | -4.75 | 437.61 | 0 | 41.09 | 0 | OK | Ground clear controls. | 11 | 54.01 | 478.7
593 | TIN-INTERP | Interpolated Ground | 3649.24 | -4.06 | 437.72 | 0 | 52.44 | 0 | OK | Ground clear controls. | 11 | 54.01 | 490.16
594 | TIN-INTERP | Interpolated Ground | 3651.21 | 6.51 | 439.54 | 0 | 50.62 | 0 | OK | Ground clear controls. | 11 | 54.01 | 490.16
595 | TIN-INTERP | Interpolated Ground | 3651.35 | 7.15 | 439.61 | 0 | 39.1 | 0 | OK | Ground clear controls. | 11 | 54.01 | 478.71
596 | TIN-INTERP | Interpolated Ground | 3651.66 | 8.62 | 439.82 | 0 | 44.57 | 0 | OK | Ground clear controls. | 11 | 54.01 | 484.39
597 | TIN-INTERP | Interpolated Ground | 3688.84 | -6.29 | 435.23 | 0 | 48.02 | 0 | OK | Ground clear controls. | 11 | 54.01 | 483.25
598 | TIN-INTERP | Interpolated Ground | 3689.18 | -4.8 | 435.32 | 0 | 42.72 | 0 | OK | Ground clear controls. | 11 | 54.01 | 478.04
599 | TIN-INTERP | Interpolated Ground | 3689.24 | -4.14 | 435.37 | 0 | 54.01 | 0 | OK | Ground clear controls. | 11 | 54.01 | 489.38
600 | TIN-INTERP | Interpolated Ground | 3691.21 | 6.25 | 435.94 | 0 | 53.45 | 0 | OK | Ground clear controls. | 11 | 53.45 | 489.39
601 | TIN-INTERP | Interpolated Ground | 3691.35 | 6.87 | 435.99 | 0 | 42.05 | 0 | OK | Ground clear controls. | 11 | 53.29 | 478.04
602 | TIN-INTERP | Interpolated Ground | 3691.66 | 8.35 | 436.12 | 0 | 47.58 | 0 | OK | Ground clear controls. | 11 | 53.29 | 483.7
603 | TIN-INTERP | Interpolated Ground | 3728.84 | -6.34 | 436.57 | 0 | 46.82 | 0 | OK | Ground clear controls. | 11 | 53.29 | 483.39
604 | TIN-INTERP | Interpolated Ground | 3729.18 | -4.85 | 436.76 | 0 | 41.46 | 0 | OK | Ground clear controls. | 11 | 53.29 | 478.22
605 | TIN-INTERP | Interpolated Ground | 3729.24 | -4.21 | 436.69 | 0 | 52.78 | 0 | OK | Ground clear controls. | 11 | 53.29 | 489.47
606 | TIN-INTERP | Interpolated Ground | 3731.21 | 6 | 436.19 | 0 | 53.29 | 0 | OK | Ground clear controls. | 11 | 53.29 | 489.48
607 | TIN-INTERP | Interpolated Ground | 3731.35 | 6.6 | 436.41 | 0 | 41.82 | 0 | OK | Ground clear controls. | 11 | 47.07 | 478.23
608 | TIN-INTERP | Interpolated Ground | 3731.66 | 8.08 | 436.81 | 0 | 47.07 | 0 | OK | Ground clear controls. | 11 | 47.07 | 483.88
609 | TIN-INTERP | Interpolated Ground | 3768.84 | -6.39 | 446.3 | 0 | 38.11 | 0 | OK | Ground clear controls. | 11 | 43.88 | 484.41
610 | TIN-INTERP | Interpolated Ground | 3769.18 | -4.9 | 446.51 | 0 | 32.74 | 0 | OK | Ground clear controls. | 11 | 43.88 | 479.25
611 | TIN-INTERP | Interpolated Ground | 3769.24 | -4.29 | 446.54 | 0 | 43.88 | 0 | OK | Ground clear controls. | 11 | 43.88 | 490.42
612 | TIN-INTERP | Interpolated Ground | 3771.21 | 5.74 | 447 | 0 | 43.45 | 0 | OK | Ground clear controls. | 11 | 43.45 | 490.45
613 | TIN-INTERP | Interpolated Ground | 3771.35 | 6.33 | 447.04 | 0 | 32.24 | 0 | OK | Ground clear controls. | 11 | 37.79 | 479.28
614 | TIN-INTERP | Interpolated Ground | 3771.66 | 7.81 | 447.11 | 0 | 37.79 | 0 | OK | Ground clear controls. | 11 | 37.79 | 484.9
615 | TIN-INTERP | Interpolated Ground | 3808.84 | -6.45 | 461.82 | 0 | 24.48 | 0 | OK | Ground clear controls. | 11 | 32.11 | 486.3
616 | TIN-INTERP | Interpolated Ground | 3809.18 | -4.95 | 462.11 | 0 | 19.01 | 0 | OK | Ground clear controls. | 11 | 32.11 | 481.12
617 | TIN-INTERP | Interpolated Ground | 3809.24 | -4.36 | 462.17 | 0 | 30.06 | 0 | OK | Ground clear controls. | 11 | 32.11 | 492.23
618 | TIN-INTERP | Interpolated Ground | 3811.21 | 5.49 | 462.58 | 0 | 29.7 | 0 | OK | Ground clear controls. | 11 | 32.11 | 492.28
619 | TIN-INTERP | Interpolated Ground | 3811.34 | 6.05 | 462.59 | 0 | 18.59 | 0 | OK | Ground clear controls. | 11 | 32.11 | 481.18
620 | TIN-INTERP | Interpolated Ground | 3811.66 | 7.54 | 462.55 | 0 | 24.23 | 0 | OK | Ground clear controls. | 11 | 32.11 | 486.78
621 | TIN-INTERP | Interpolated Ground | 3848.84 | -6.5 | 471.54 | 0 | 17.51 | 0 | OK | Ground clear controls. | 11 | 32.11 | 489.05
622 | TIN-INTERP | Interpolated Ground | 3849.18 | -5 | 471.51 | 0 | 12.31 | 0 | OK | Ground clear controls. | 11 | 32.11 | 483.82
623 | TIN-INTERP | Interpolated Ground | 3849.24 | -4.44 | 471.49 | 0 | 23.39 | 0 | OK | Ground clear controls. | 11 | 32.11 | 494.88
624 | TIN-INTERP | Interpolated Ground | 3851.21 | 5.23 | 470.64 | 0 | 24.34 | 0 | OK | Ground clear controls. | 11 | 32.11 | 494.98
625 | TIN-INTERP | Interpolated Ground | 3851.34 | 5.78 | 470.59 | 0 | 13.35 | 0 | OK | Ground clear controls. | 11 | 32.11 | 483.94
626 | TIN-INTERP | Interpolated Ground | 3851.66 | 7.27 | 470.38 | 0 | 19.14 | 0 | OK | Ground clear controls. | 11 | 32.11 | 489.52
627 | TIN-INTERP | Interpolated Ground | 3888.84 | -6.55 | 475.13 | 0 | 17.55 | 0 | OK | Ground clear controls. | 11 | 32.11 | 492.68
628 | TIN-INTERP | Interpolated Ground | 3889.18 | -5.05 | 475.08 | 0 | 12.29 | 0 | OK | Ground clear controls. | 11 | 32.11 | 487.37
629 | TIN-INTERP | Interpolated Ground | 3889.24 | -4.51 | 475.05 | 0 | 23.35 | 0 | OK | Ground clear controls. | 11 | 32.11 | 498.4
630 | TIN-INTERP | Interpolated Ground | 3891.21 | 4.98 | 473.91 | 0 | 24.64 | 0 | OK | Ground clear controls. | 11 | 32.11 | 498.55
631 | TIN-INTERP | Interpolated Ground | 3891.34 | 5.51 | 473.83 | 0 | 13.71 | 0 | OK | Ground clear controls. | 11 | 32.11 | 487.54
632 | TIN-INTERP | Interpolated Ground | 3891.66 | 7 | 473.68 | 0 | 19.43 | 0 | OK | Ground clear controls. | 11 | 32.11 | 493.11
633 | TIN-INTERP | Interpolated Ground | 3928.84 | -6.6 | 470.98 | 0 | 26.19 | 0 | OK | Ground clear controls. | 11 | 32.11 | 497.17
634 | TIN-INTERP | Interpolated Ground | 3929.18 | -5.1 | 470.88 | 0 | 20.89 | 0 | OK | Ground clear controls. | 11 | 32.11 | 491.77
635 | TIN-INTERP | Interpolated Ground | 3929.24 | -4.59 | 470.88 | 0 | 31.89 | 0 | OK | Ground clear controls. | 11 | 32.11 | 502.77
636 | TIN-INTERP | Interpolated Ground | 3931.21 | 4.72 | 470.89 | 0 | 32.11 | 0 | OK | Ground clear controls. | 11 | 32.11 | 503
637 | TIN-INTERP | Interpolated Ground | 3931.34 | 5.23 | 470.89 | 0 | 21.12 | 0 | OK | Ground clear controls. | 11 | 26.78 | 492.01
638 | TIN-INTERP | Interpolated Ground | 3931.65 | 6.73 | 470.78 | 0 | 26.78 | 0 | OK | Ground clear controls. | 11 | 26.78 | 497.56
639 | TIN-INTERP | Interpolated Ground | 3945.88 | -5.13 | 471.59 | 0 | 22.26 | 0 | OK | Ground clear controls. | 12 | 36.39 | 493.85
640 | TIN-INTERP | Interpolated Ground | 3945.9 | -4.62 | 471.55 | 0 | 33.3 | 0 | OK | Ground clear controls. | 12 | 36.39 | 504.85
641 | TIN-INTERP | Interpolated Ground | 3945.91 | 6.63 | 470 | 0 | 29.35 | 0 | OK | Ground clear controls. | 12 | 36.39 | 499.35
642 | TIN-INTERP | Interpolated Ground | 3945.92 | 4.63 | 470.34 | 0 | 34.51 | 0 | OK | Ground clear controls. | 12 | 36.39 | 504.85
643 | TIN-INTERP | Interpolated Ground | 3945.92 | -6.63 | 471.82 | 0 | 27.53 | 0 | OK | Ground clear controls. | 12 | 36.39 | 499.35
644 | TIN-INTERP | Interpolated Ground | 3945.93 | 5.13 | 470.26 | 0 | 23.59 | 0 | OK | Ground clear controls. | 12 | 36.39 | 493.85
645 | TIN-INTERP | Interpolated Ground | 3985.87 | -5.13 | 473.38 | 0 | 16.72 | 0 | OK | Ground clear controls. | 12 | 36.39 | 490.1
646 | TIN-INTERP | Interpolated Ground | 3985.9 | -4.62 | 473.3 | 0 | 27.73 | 0 | OK | Ground clear controls. | 12 | 36.39 | 501.03
647 | TIN-INTERP | Interpolated Ground | 3985.91 | 6.62 | 471.88 | 0 | 23.66 | 0 | OK | Ground clear controls. | 12 | 36.39 | 495.54
648 | TIN-INTERP | Interpolated Ground | 3985.92 | 4.62 | 472.09 | 0 | 28.9 | 0 | OK | Ground clear controls. | 12 | 36.39 | 500.99
649 | TIN-INTERP | Interpolated Ground | 3985.92 | -6.63 | 473.58 | 0 | 21.92 | 0 | OK | Ground clear controls. | 12 | 36.39 | 495.5
650 | TIN-INTERP | Interpolated Ground | 3985.93 | 5.12 | 472.02 | 0 | 18.04 | 0 | OK | Ground clear controls. | 12 | 36.39 | 490.06
651 | TIN-INTERP | Interpolated Ground | 4025.87 | -5.13 | 473.35 | 0 | 13.83 | 0 | OK | Ground clear controls. | 12 | 36.39 | 487.18
652 | TIN-INTERP | Interpolated Ground | 4025.9 | -4.63 | 473.33 | 0 | 24.74 | 0 | OK | Ground clear controls. | 12 | 36.39 | 498.07
653 | TIN-INTERP | Interpolated Ground | 4025.91 | 6.61 | 473.51 | 0 | 19.08 | 0 | OK | Ground clear controls. | 12 | 36.39 | 492.59
654 | TIN-INTERP | Interpolated Ground | 4025.92 | 4.61 | 473.54 | 0 | 24.44 | 0 | OK | Ground clear controls. | 12 | 36.39 | 497.98
655 | TIN-INTERP | Interpolated Ground | 4025.92 | -6.63 | 473.3 | 0 | 19.2 | 0 | OK | Ground clear controls. | 12 | 36.39 | 492.5
656 | TIN-INTERP | Interpolated Ground | 4025.93 | 5.11 | 473.54 | 0 | 13.58 | 0 | OK | Ground clear controls. | 12 | 36.39 | 487.12
657 | TIN-INTERP | Interpolated Ground | 4065.87 | -5.14 | 470.7 | 0 | 14.4 | 0 | OK | Ground clear controls. | 12 | 36.39 | 485.1
658 | TIN-INTERP | Interpolated Ground | 4065.9 | -4.63 | 470.76 | 0 | 25.21 | 0 | OK | Ground clear controls. | 12 | 36.39 | 495.97
659 | TIN-INTERP | Interpolated Ground | 4065.91 | 6.61 | 471.91 | 0 | 18.58 | 0 | OK | Ground clear controls. | 12 | 36.39 | 490.49
660 | TIN-INTERP | Interpolated Ground | 4065.92 | 4.6 | 471.71 | 0 | 24.14 | 0 | OK | Ground clear controls. | 12 | 36.39 | 495.85
661 | TIN-INTERP | Interpolated Ground | 4065.92 | -6.64 | 470.57 | 0 | 19.81 | 0 | OK | Ground clear controls. | 12 | 36.39 | 490.38
662 | TIN-INTERP | Interpolated Ground | 4065.93 | 5.11 | 471.75 | 0 | 13.27 | 0 | OK | Ground clear controls. | 12 | 36.39 | 485.02
663 | TIN-INTERP | Interpolated Ground | 4105.87 | -5.14 | 459.61 | 0 | 24.27 | 0 | OK | Ground clear controls. | 12 | 36.39 | 483.88
664 | TIN-INTERP | Interpolated Ground | 4105.9 | -4.63 | 459.39 | 0 | 35.32 | 0 | OK | Ground clear controls. | 12 | 36.39 | 494.71
665 | TIN-INTERP | Interpolated Ground | 4105.91 | 6.6 | 462.74 | 0 | 26.51 | 0 | OK | Ground clear controls. | 12 | 36.39 | 489.25
666 | TIN-INTERP | Interpolated Ground | 4105.92 | 4.59 | 462.01 | 0 | 32.58 | 0 | OK | Ground clear controls. | 12 | 36.39 | 494.59
667 | TIN-INTERP | Interpolated Ground | 4105.92 | -6.64 | 460.16 | 0 | 28.95 | 0 | OK | Ground clear controls. | 12 | 36.39 | 489.11
668 | TIN-INTERP | Interpolated Ground | 4105.93 | 5.1 | 462.24 | 0 | 21.54 | 0 | OK | Ground clear controls. | 12 | 36.39 | 483.78
669 | TIN-INTERP | Interpolated Ground | 4145.87 | -5.14 | 462.09 | 0 | 21.4 | 0 | OK | Ground clear controls. | 12 | 36.39 | 483.49
670 | TIN-INTERP | Interpolated Ground | 4145.9 | -4.64 | 462.16 | 0 | 32.16 | 0 | OK | Ground clear controls. | 12 | 36.39 | 494.32
671 | TIN-INTERP | Interpolated Ground | 4145.91 | 6.59 | 463.98 | 0 | 24.87 | 0 | OK | Ground clear controls. | 12 | 36.39 | 488.85
672 | TIN-INTERP | Interpolated Ground | 4145.92 | 4.59 | 463.62 | 0 | 30.56 | 0 | OK | Ground clear controls. | 12 | 36.39 | 494.18
673 | TIN-INTERP | Interpolated Ground | 4145.92 | -6.64 | 461.77 | 0 | 26.95 | 0 | OK | Ground clear controls. | 12 | 36.39 | 488.72
674 | TIN-INTERP | Interpolated Ground | 4145.93 | 5.09 | 463.7 | 0 | 19.69 | 0 | OK | Ground clear controls. | 12 | 36.39 | 483.39
675 | TIN-INTERP | Interpolated Ground | 4185.87 | -5.14 | 461 | 0 | 22.94 | 0 | OK | Ground clear controls. | 12 | 36.39 | 483.94
676 | TIN-INTERP | Interpolated Ground | 4185.9 | -4.64 | 460.79 | 0 | 33.99 | 0 | OK | Ground clear controls. | 12 | 36.39 | 494.78
677 | TIN-INTERP | Interpolated Ground | 4185.91 | 6.58 | 458.28 | 0 | 31.03 | 0 | OK | Ground clear controls. | 12 | 36.39 | 489.31
678 | TIN-INTERP | Interpolated Ground | 4185.92 | 4.58 | 458.26 | 0 | 36.39 | 0 | OK | Ground clear controls. | 12 | 36.39 | 494.65
679 | TIN-INTERP | Interpolated Ground | 4185.92 | -6.64 | 461.36 | 0 | 27.82 | 0 | OK | Ground clear controls. | 12 | 33.03 | 489.18
680 | TIN-INTERP | Interpolated Ground | 4185.93 | 5.08 | 458.27 | 0 | 25.57 | 0 | OK | Ground clear controls. | 12 | 33.03 | 483.84
681 | TIN-INTERP | Interpolated Ground | 4225.87 | -5.15 | 463.11 | 0 | 22.12 | 0 | OK | Ground clear controls. | 12 | 33.03 | 485.23
682 | TIN-INTERP | Interpolated Ground | 4225.9 | -4.65 | 463.06 | 0 | 33.03 | 0 | OK | Ground clear controls. | 12 | 33.03 | 496.09
683 | TIN-INTERP | Interpolated Ground | 4225.91 | 6.57 | 464.89 | 0 | 25.73 | 0 | OK | Ground clear controls. | 12 | 31.35 | 490.62
684 | TIN-INTERP | Interpolated Ground | 4225.92 | 4.57 | 464.63 | 0 | 31.35 | 0 | OK | Ground clear controls. | 12 | 31.35 | 495.98
685 | TIN-INTERP | Interpolated Ground | 4225.92 | -6.65 | 463.41 | 0 | 27.1 | 0 | OK | Ground clear controls. | 12 | 30.06 | 490.51
686 | TIN-INTERP | Interpolated Ground | 4225.93 | 5.07 | 464.73 | 0 | 20.42 | 0 | OK | Ground clear controls. | 12 | 30.06 | 485.15
687 | TIN-INTERP | Interpolated Ground | 4265.87 | -5.15 | 468.23 | 0 | 19.13 | 0 | OK | Ground clear controls. | 12 | 30.06 | 487.36
688 | TIN-INTERP | Interpolated Ground | 4265.9 | -4.65 | 468.2 | 0 | 30.06 | 0 | OK | Ground clear controls. | 12 | 30.06 | 498.26
689 | TIN-INTERP | Interpolated Ground | 4265.91 | 6.56 | 469.01 | 0 | 23.77 | 0 | OK | Ground clear controls. | 12 | 29.5 | 492.78
690 | TIN-INTERP | Interpolated Ground | 4265.92 | 4.56 | 468.84 | 0 | 29.34 | 0 | OK | Ground clear controls. | 12 | 29.5 | 498.18
691 | TIN-INTERP | Interpolated Ground | 4265.92 | -6.65 | 468.22 | 0 | 24.47 | 0 | OK | Ground clear controls. | 12 | 29.5 | 492.69
692 | TIN-INTERP | Interpolated Ground | 4265.93 | 5.06 | 468.87 | 0 | 18.43 | 0 | OK | Ground clear controls. | 12 | 29.5 | 487.3
693 | TIN-INTERP | Interpolated Ground | 4305.87 | -5.15 | 471.75 | 0 | 18.59 | 0 | OK | Ground clear controls. | 12 | 29.5 | 490.34
694 | TIN-INTERP | Interpolated Ground | 4305.9 | -4.65 | 471.79 | 0 | 29.5 | 0 | OK | Ground clear controls. | 12 | 29.5 | 501.29
695 | TIN-INTERP | Interpolated Ground | 4305.91 | 6.55 | 473.41 | 0 | 22.38 | 0 | OK | Ground clear controls. | 12 | 28.14 | 495.79
696 | TIN-INTERP | Interpolated Ground | 4305.92 | 4.55 | 473.1 | 0 | 28.14 | 0 | OK | Ground clear controls. | 12 | 28.14 | 501.24
697 | TIN-INTERP | Interpolated Ground | 4305.92 | -6.65 | 471.61 | 0 | 24.14 | 0 | OK | Ground clear controls. | 12 | 24.14 | 495.75
698 | TIN-INTERP | Interpolated Ground | 4305.93 | 5.05 | 473.19 | 0 | 17.12 | 0 | OK | Ground clear controls. | 12 | 17.12 | 490.31
699 | TIN-INTERP | Interpolated Ground | 4342.67 | 6.55 | 475.33 | 0 | 23.99 | 0 | OK | Ground clear controls. | 13 | 37.39 | 499.32
700 | TIN-INTERP | Interpolated Ground | 4342.69 | -4.66 | 474.04 | 0 | 30.78 | 0 | OK | Ground clear controls. | 13 | 37.39 | 504.82
701 | TIN-INTERP | Interpolated Ground | 4342.69 | 4.54 | 475 | 0 | 29.82 | 0 | OK | Ground clear controls. | 13 | 37.39 | 504.82
702 | TIN-INTERP | Interpolated Ground | 4342.71 | -6.66 | 473.7 | 0 | 25.63 | 0 | OK | Ground clear controls. | 13 | 37.39 | 499.33
703 | TIN-INTERP | Interpolated Ground | 4342.78 | 5.05 | 475.13 | 0 | 18.69 | 0 | OK | Ground clear controls. | 13 | 37.39 | 493.82
704 | TIN-INTERP | Interpolated Ground | 4342.79 | -5.16 | 473.97 | 0 | 19.85 | 0 | OK | Ground clear controls. | 13 | 37.39 | 493.82
705 | TIN-INTERP | Interpolated Ground | 4382.67 | 6.54 | 476.35 | 0 | 21.86 | 0 | OK | Ground clear controls. | 13 | 37.39 | 498.21
706 | TIN-INTERP | Interpolated Ground | 4382.69 | -4.66 | 475.34 | 0 | 28.36 | 0 | OK | Ground clear controls. | 13 | 37.39 | 503.7
707 | TIN-INTERP | Interpolated Ground | 4382.69 | 4.54 | 476.17 | 0 | 27.49 | 0 | OK | Ground clear controls. | 13 | 37.39 | 503.66
708 | TIN-INTERP | Interpolated Ground | 4382.71 | -6.66 | 475.13 | 0 | 23.04 | 0 | OK | Ground clear controls. | 13 | 37.39 | 498.17
709 | TIN-INTERP | Interpolated Ground | 4382.78 | 5.04 | 476.23 | 0 | 16.51 | 0 | OK | Ground clear controls. | 13 | 37.39 | 492.74
710 | TIN-INTERP | Interpolated Ground | 4382.79 | -5.16 | 475.27 | 0 | 17.51 | 0 | OK | Ground clear controls. | 13 | 37.39 | 492.78
711 | TIN-INTERP | Interpolated Ground | 4422.67 | 6.54 | 477.99 | 0 | 19.95 | 0 | OK | Ground clear controls. | 13 | 37.39 | 497.94
712 | TIN-INTERP | Interpolated Ground | 4422.69 | -4.66 | 477.01 | 0 | 26.42 | 0 | OK | Ground clear controls. | 13 | 37.39 | 503.43
713 | TIN-INTERP | Interpolated Ground | 4422.69 | 4.54 | 477.83 | 0 | 25.54 | 0 | OK | Ground clear controls. | 13 | 37.39 | 503.37
714 | TIN-INTERP | Interpolated Ground | 4422.71 | -6.66 | 476.81 | 0 | 21.07 | 0 | OK | Ground clear controls. | 13 | 37.39 | 497.88
715 | TIN-INTERP | Interpolated Ground | 4422.78 | 5.04 | 477.86 | 0 | 14.64 | 0 | OK | Ground clear controls. | 13 | 37.39 | 492.5
716 | TIN-INTERP | Interpolated Ground | 4422.79 | -5.16 | 476.94 | 0 | 15.63 | 0 | OK | Ground clear controls. | 13 | 37.39 | 492.57
717 | TIN-INTERP | Interpolated Ground | 4462.67 | 6.54 | 479.2 | 0 | 19.33 | 0 | OK | Ground clear controls. | 13 | 37.39 | 498.53
718 | TIN-INTERP | Interpolated Ground | 4462.69 | -4.66 | 478.25 | 0 | 25.77 | 0 | OK | Ground clear controls. | 13 | 37.39 | 504.02
719 | TIN-INTERP | Interpolated Ground | 4462.69 | 4.54 | 479.01 | 0 | 24.92 | 0 | OK | Ground clear controls. | 13 | 37.39 | 503.93
720 | TIN-INTERP | Interpolated Ground | 4462.71 | -6.66 | 478.01 | 0 | 20.45 | 0 | OK | Ground clear controls. | 13 | 37.39 | 498.46
721 | TIN-INTERP | Interpolated Ground | 4462.78 | 5.04 | 479.06 | 0 | 14.05 | 0 | OK | Ground clear controls. | 13 | 37.39 | 493.11
722 | TIN-INTERP | Interpolated Ground | 4462.79 | -5.16 | 478.2 | 0 | 14.99 | 0 | OK | Ground clear controls. | 13 | 37.39 | 493.19
723 | TIN-INTERP | Interpolated Ground | 4502.67 | 6.54 | 479.71 | 0 | 20.27 | 0 | OK | Ground clear controls. | 13 | 37.39 | 499.98
724 | TIN-INTERP | Interpolated Ground | 4502.69 | -4.66 | 478.88 | 0 | 26.58 | 0 | OK | Ground clear controls. | 13 | 37.39 | 505.46
725 | TIN-INTERP | Interpolated Ground | 4502.69 | 4.54 | 479.5 | 0 | 25.87 | 0 | OK | Ground clear controls. | 13 | 37.39 | 505.37
726 | TIN-INTERP | Interpolated Ground | 4502.71 | -6.66 | 478.65 | 0 | 21.24 | 0 | OK | Ground clear controls. | 13 | 37.39 | 499.89
727 | TIN-INTERP | Interpolated Ground | 4502.78 | 5.04 | 479.57 | 0 | 14.99 | 0 | OK | Ground clear controls. | 13 | 37.39 | 494.56
728 | TIN-INTERP | Interpolated Ground | 4502.79 | -5.16 | 478.84 | 0 | 15.81 | 0 | OK | Ground clear controls. | 13 | 37.39 | 494.65
729 | TIN-INTERP | Interpolated Ground | 4542.67 | 6.54 | 480.35 | 0 | 21.92 | 0 | OK | Ground clear controls. | 13 | 37.39 | 502.27
730 | TIN-INTERP | Interpolated Ground | 4542.69 | -4.66 | 479.68 | 0 | 28.08 | 0 | OK | Ground clear controls. | 13 | 37.39 | 507.76
731 | TIN-INTERP | Interpolated Ground | 4542.69 | 4.54 | 480.16 | 0 | 27.49 | 0 | OK | Ground clear controls. | 13 | 37.39 | 507.65
732 | TIN-INTERP | Interpolated Ground | 4542.71 | -6.66 | 479.66 | 0 | 22.53 | 0 | OK | Ground clear controls. | 13 | 37.39 | 502.19
733 | TIN-INTERP | Interpolated Ground | 4542.78 | 5.04 | 480.22 | 0 | 16.63 | 0 | OK | Ground clear controls. | 13 | 37.39 | 496.85
734 | TIN-INTERP | Interpolated Ground | 4542.79 | -5.16 | 479.68 | 0 | 17.26 | 0 | OK | Ground clear controls. | 13 | 37.39 | 496.94
735 | TIN-INTERP | Interpolated Ground | 4582.67 | 6.54 | 481.54 | 0 | 23.88 | 0 | OK | Ground clear controls. | 13 | 37.39 | 505.42
736 | TIN-INTERP | Interpolated Ground | 4582.69 | -4.66 | 481.7 | 0 | 29.2 | 0 | OK | Ground clear controls. | 13 | 37.39 | 510.9
737 | TIN-INTERP | Interpolated Ground | 4582.69 | 4.54 | 481.65 | 0 | 29.17 | 0 | OK | Ground clear controls. | 13 | 37.39 | 510.82
738 | TIN-INTERP | Interpolated Ground | 4582.71 | -6.66 | 481.73 | 0 | 23.61 | 0 | OK | Ground clear controls. | 13 | 37.39 | 505.34
739 | TIN-INTERP | Interpolated Ground | 4582.78 | 5.04 | 481.64 | 0 | 18.34 | 0 | OK | Ground clear controls. | 13 | 37.39 | 499.98
740 | TIN-INTERP | Interpolated Ground | 4582.79 | -5.16 | 481.73 | 0 | 18.34 | 0 | OK | Ground clear controls. | 13 | 37.39 | 500.07
741 | TIN-INTERP | Interpolated Ground | 4622.67 | 6.54 | 482.65 | 0 | 26.77 | 0 | OK | Ground clear controls. | 13 | 37.39 | 509.42
742 | TIN-INTERP | Interpolated Ground | 4622.69 | -4.66 | 483.18 | 0 | 31.72 | 0 | OK | Ground clear controls. | 13 | 37.39 | 514.9
743 | TIN-INTERP | Interpolated Ground | 4622.69 | 4.54 | 482.69 | 0 | 32.15 | 0 | OK | Ground clear controls. | 13 | 37.39 | 514.84
744 | TIN-INTERP | Interpolated Ground | 4622.71 | -6.66 | 483.35 | 0 | 26.01 | 0 | OK | Ground clear controls. | 13 | 37.39 | 509.36
745 | TIN-INTERP | Interpolated Ground | 4622.78 | 5.04 | 482.68 | 0 | 21.28 | 0 | OK | Ground clear controls. | 13 | 37.39 | 503.96
746 | TIN-INTERP | Interpolated Ground | 4622.79 | -5.16 | 483.22 | 0 | 20.81 | 0 | OK | Ground clear controls. | 13 | 37.39 | 504.03
747 | TIN-INTERP | Interpolated Ground | 4662.67 | 6.54 | 482.27 | 0 | 32 | 0 | OK | Ground clear controls. | 13 | 37.39 | 514.27
748 | TIN-INTERP | Interpolated Ground | 4662.69 | -4.66 | 482.89 | 0 | 36.89 | 0 | OK | Ground clear controls. | 13 | 37.39 | 519.78
749 | TIN-INTERP | Interpolated Ground | 4662.69 | 4.54 | 482.35 | 0 | 37.39 | 0 | OK | Ground clear controls. | 13 | 37.39 | 519.74
750 | TIN-INTERP | Interpolated Ground | 4662.71 | -6.66 | 482.94 | 0 | 31.31 | 0 | OK | Ground clear controls. | 13 | 31.31 | 514.25
751 | TIN-INTERP | Interpolated Ground | 4662.78 | 5.04 | 482.33 | 0 | 26.47 | 0 | OK | Ground clear controls. | 13 | 26.47 | 508.8
752 | TIN-INTERP | Interpolated Ground | 4662.79 | -5.16 | 482.91 | 0 | 25.93 | 0 | OK | Ground clear controls. | 13 | 25.93 | 508.84
753 | TIN-INTERP | Interpolated Ground | 4686.71 | -5.16 | 482.61 | 0 | 29.51 | 0 | OK | Ground clear controls. | 14 | 41.16 | 512.12
754 | TIN-INTERP | Interpolated Ground | 4686.74 | 6.54 | 481.8 | 0 | 35.81 | 0 | OK | Ground clear controls. | 14 | 41.16 | 517.61
755 | TIN-INTERP | Interpolated Ground | 4686.76 | -4.66 | 482.56 | 0 | 40.55 | 0 | OK | Ground clear controls. | 14 | 41.16 | 523.11
756 | TIN-INTERP | Interpolated Ground | 4686.78 | -6.66 | 482.74 | 0 | 34.87 | 0 | OK | Ground clear controls. | 14 | 41.16 | 517.61
757 | TIN-INTERP | Interpolated Ground | 4686.79 | 4.54 | 481.95 | 0 | 41.16 | 0 | OK | Ground clear controls. | 14 | 41.16 | 523.11
758 | TIN-INTERP | Interpolated Ground | 4686.83 | 5.04 | 481.92 | 0 | 30.19 | 0 | OK | Ground clear controls. | 14 | 37.07 | 512.11
759 | TIN-INTERP | Interpolated Ground | 4726.71 | -5.16 | 480.89 | 0 | 26.13 | 0 | OK | Ground clear controls. | 14 | 37.07 | 507.02
760 | TIN-INTERP | Interpolated Ground | 4726.74 | 6.53 | 481.36 | 0 | 31.08 | 0 | OK | Ground clear controls. | 14 | 37.07 | 512.44
761 | TIN-INTERP | Interpolated Ground | 4726.75 | -4.66 | 480.87 | 0 | 37.07 | 0 | OK | Ground clear controls. | 14 | 37.07 | 517.94
762 | TIN-INTERP | Interpolated Ground | 4726.78 | -6.66 | 480.82 | 0 | 31.59 | 0 | OK | Ground clear controls. | 14 | 36.59 | 512.41
763 | TIN-INTERP | Interpolated Ground | 4726.79 | 4.53 | 481.31 | 0 | 36.59 | 0 | OK | Ground clear controls. | 14 | 36.59 | 517.9
764 | TIN-INTERP | Interpolated Ground | 4726.83 | 5.03 | 481.31 | 0 | 25.72 | 0 | OK | Ground clear controls. | 14 | 34.11 | 507.03
765 | TIN-INTERP | Interpolated Ground | 4766.71 | -5.17 | 479.48 | 0 | 23.3 | 0 | OK | Ground clear controls. | 14 | 34.11 | 502.78
766 | TIN-INTERP | Interpolated Ground | 4766.74 | 6.53 | 480.16 | 0 | 27.98 | 0 | OK | Ground clear controls. | 14 | 34.11 | 508.14
767 | TIN-INTERP | Interpolated Ground | 4766.75 | -4.67 | 479.53 | 0 | 34.11 | 0 | OK | Ground clear controls. | 14 | 34.11 | 513.64
768 | TIN-INTERP | Interpolated Ground | 4766.78 | -6.67 | 479.29 | 0 | 28.8 | 0 | OK | Ground clear controls. | 14 | 33.72 | 508.09
769 | TIN-INTERP | Interpolated Ground | 4766.79 | 4.53 | 480.08 | 0 | 33.48 | 0 | OK | Ground clear controls. | 14 | 33.72 | 513.56
770 | TIN-INTERP | Interpolated Ground | 4766.83 | 5.03 | 480.1 | 0 | 22.71 | 0 | OK | Ground clear controls. | 14 | 33.72 | 502.81
771 | TIN-INTERP | Interpolated Ground | 4806.71 | -5.17 | 481.32 | 0 | 18.07 | 0 | OK | Ground clear controls. | 14 | 33.72 | 499.39
772 | TIN-INTERP | Interpolated Ground | 4806.74 | 6.52 | 481.48 | 0 | 23.21 | 0 | OK | Ground clear controls. | 14 | 33.72 | 504.69
773 | TIN-INTERP | Interpolated Ground | 4806.75 | -4.67 | 481.28 | 0 | 28.91 | 0 | OK | Ground clear controls. | 14 | 33.72 | 510.19
774 | TIN-INTERP | Interpolated Ground | 4806.78 | -6.67 | 481.69 | 0 | 22.95 | 0 | OK | Ground clear controls. | 14 | 33.72 | 504.64
775 | TIN-INTERP | Interpolated Ground | 4806.79 | 4.52 | 481.47 | 0 | 28.64 | 0 | OK | Ground clear controls. | 14 | 33.72 | 510.11
776 | TIN-INTERP | Interpolated Ground | 4806.83 | 5.02 | 481.47 | 0 | 17.96 | 0 | OK | Ground clear controls. | 14 | 33.72 | 499.43
777 | TIN-INTERP | Interpolated Ground | 4846.71 | -5.18 | 481.52 | 0 | 15.32 | 0 | OK | Ground clear controls. | 14 | 33.72 | 496.84
778 | TIN-INTERP | Interpolated Ground | 4846.74 | 6.51 | 481.86 | 0 | 20.25 | 0 | OK | Ground clear controls. | 14 | 33.72 | 502.11
779 | TIN-INTERP | Interpolated Ground | 4846.75 | -4.68 | 481.57 | 0 | 26.04 | 0 | OK | Ground clear controls. | 14 | 33.72 | 507.61
780 | TIN-INTERP | Interpolated Ground | 4846.78 | -6.68 | 481.4 | 0 | 20.64 | 0 | OK | Ground clear controls. | 14 | 33.72 | 502.04
781 | TIN-INTERP | Interpolated Ground | 4846.79 | 4.51 | 481.86 | 0 | 25.65 | 0 | OK | Ground clear controls. | 14 | 33.72 | 507.51
782 | TIN-INTERP | Interpolated Ground | 4846.83 | 5.01 | 481.85 | 0 | 15.03 | 0 | OK | Ground clear controls. | 14 | 33.72 | 496.88
783 | TIN-INTERP | Interpolated Ground | 4886.71 | -5.18 | 481.82 | 0 | 13.31 | 0 | OK | Ground clear controls. | 14 | 33.72 | 495.13
784 | TIN-INTERP | Interpolated Ground | 4886.74 | 6.51 | 482.72 | 0 | 17.67 | 0 | OK | Ground clear controls. | 14 | 33.72 | 500.39
785 | TIN-INTERP | Interpolated Ground | 4886.75 | -4.68 | 481.85 | 0 | 24.04 | 0 | OK | Ground clear controls. | 14 | 33.72 | 505.89
786 | TIN-INTERP | Interpolated Ground | 4886.78 | -6.68 | 481.74 | 0 | 18.57 | 0 | OK | Ground clear controls. | 14 | 33.72 | 500.31
787 | TIN-INTERP | Interpolated Ground | 4886.79 | 4.51 | 482.74 | 0 | 23.04 | 0 | OK | Ground clear controls. | 14 | 33.72 | 505.78
788 | TIN-INTERP | Interpolated Ground | 4886.83 | 5.01 | 482.75 | 0 | 12.44 | 0 | OK | Ground clear controls. | 14 | 33.72 | 495.19
789 | TIN-INTERP | Interpolated Ground | 4926.71 | -5.19 | 479.55 | 0 | 14.74 | 0 | OK | Ground clear controls. | 14 | 33.72 | 494.29
790 | TIN-INTERP | Interpolated Ground | 4926.74 | 6.5 | 480 | 0 | 19.53 | 0 | OK | Ground clear controls. | 14 | 33.72 | 499.53
791 | TIN-INTERP | Interpolated Ground | 4926.75 | -4.68 | 479.55 | 0 | 25.48 | 0 | OK | Ground clear controls. | 14 | 33.72 | 505.03
792 | TIN-INTERP | Interpolated Ground | 4926.78 | -6.68 | 479.52 | 0 | 19.94 | 0 | OK | Ground clear controls. | 14 | 33.72 | 499.46
793 | TIN-INTERP | Interpolated Ground | 4926.79 | 4.5 | 479.89 | 0 | 25.02 | 0 | OK | Ground clear controls. | 14 | 33.72 | 504.91
794 | TIN-INTERP | Interpolated Ground | 4926.83 | 5 | 479.92 | 0 | 14.42 | 0 | OK | Ground clear controls. | 14 | 33.72 | 494.34
795 | TIN-INTERP | Interpolated Ground | 4966.71 | -5.19 | 480.31 | 0 | 13.96 | 0 | OK | Ground clear controls. | 14 | 33.72 | 494.27
796 | TIN-INTERP | Interpolated Ground | 4966.74 | 6.49 | 480.63 | 0 | 18.9 | 0 | OK | Ground clear controls. | 14 | 33.72 | 499.53
797 | TIN-INTERP | Interpolated Ground | 4966.75 | -4.69 | 480.31 | 0 | 24.73 | 0 | OK | Ground clear controls. | 14 | 33.72 | 505.04
798 | TIN-INTERP | Interpolated Ground | 4966.78 | -6.69 | 480.26 | 0 | 19.2 | 0 | OK | Ground clear controls. | 14 | 33.72 | 499.46
799 | TIN-INTERP | Interpolated Ground | 4966.79 | 4.5 | 480.59 | 0 | 24.32 | 0 | OK | Ground clear controls. | 14 | 33.72 | 504.91
800 | TIN-INTERP | Interpolated Ground | 4966.83 | 4.99 | 480.61 | 0 | 13.72 | 0 | OK | Ground clear controls. | 14 | 33.72 | 494.33
801 | TIN-INTERP | Interpolated Ground | 5006.71 | -5.2 | 480.69 | 0 | 14.41 | 0 | OK | Ground clear controls. | 14 | 33.72 | 495.1
802 | TIN-INTERP | Interpolated Ground | 5006.74 | 6.49 | 480.98 | 0 | 19.41 | 0 | OK | Ground clear controls. | 14 | 33.72 | 500.39
803 | TIN-INTERP | Interpolated Ground | 5006.75 | -4.69 | 480.73 | 0 | 25.16 | 0 | OK | Ground clear controls. | 14 | 33.72 | 505.89
804 | TIN-INTERP | Interpolated Ground | 5006.78 | -6.69 | 480.68 | 0 | 19.64 | 0 | OK | Ground clear controls. | 14 | 33.72 | 500.32
805 | TIN-INTERP | Interpolated Ground | 5006.79 | 4.49 | 481 | 0 | 24.78 | 0 | OK | Ground clear controls. | 14 | 33.72 | 505.78
806 | TIN-INTERP | Interpolated Ground | 5006.83 | 4.99 | 480.99 | 0 | 14.17 | 0 | OK | Ground clear controls. | 14 | 33.72 | 495.16
807 | TIN-INTERP | Interpolated Ground | 5046.71 | -5.2 | 480.6 | 0 | 16.19 | 0 | OK | Ground clear controls. | 14 | 33.72 | 496.79
808 | TIN-INTERP | Interpolated Ground | 5046.74 | 6.48 | 481.09 | 0 | 21.01 | 0 | OK | Ground clear controls. | 14 | 33.72 | 502.1
809 | TIN-INTERP | Interpolated Ground | 5046.75 | -4.7 | 480.61 | 0 | 27 | 0 | OK | Ground clear controls. | 14 | 33.72 | 507.61
810 | TIN-INTERP | Interpolated Ground | 5046.78 | -6.7 | 480.56 | 0 | 21.5 | 0 | OK | Ground clear controls. | 14 | 33.72 | 502.06
811 | TIN-INTERP | Interpolated Ground | 5046.79 | 4.48 | 481.02 | 0 | 26.5 | 0 | OK | Ground clear controls. | 14 | 33.72 | 507.52
812 | TIN-INTERP | Interpolated Ground | 5046.83 | 4.98 | 481.05 | 0 | 15.78 | 0 | OK | Ground clear controls. | 14 | 33.72 | 496.83
813 | TIN-INTERP | Interpolated Ground | 5086.71 | -5.2 | 480.39 | 0 | 18.92 | 0 | OK | Ground clear controls. | 14 | 33.72 | 499.31
814 | TIN-INTERP | Interpolated Ground | 5086.74 | 6.48 | 480.87 | 0 | 23.81 | 0 | OK | Ground clear controls. | 14 | 33.72 | 504.68
815 | TIN-INTERP | Interpolated Ground | 5086.75 | -4.7 | 480.42 | 0 | 29.77 | 0 | OK | Ground clear controls. | 14 | 33.72 | 510.19
816 | TIN-INTERP | Interpolated Ground | 5086.78 | -6.7 | 480.34 | 0 | 24.31 | 0 | OK | Ground clear controls. | 14 | 33.72 | 504.65
817 | TIN-INTERP | Interpolated Ground | 5086.79 | 4.48 | 480.8 | 0 | 29.33 | 0 | OK | Ground clear controls. | 14 | 33.72 | 510.13
818 | TIN-INTERP | Interpolated Ground | 5086.83 | 4.97 | 480.82 | 0 | 18.52 | 0 | OK | Ground clear controls. | 14 | 33.72 | 499.34
819 | TIN-INTERP | Interpolated Ground | 5126.71 | -5.21 | 480.03 | 0 | 22.66 | 0 | OK | Ground clear controls. | 14 | 33.72 | 502.69
820 | TIN-INTERP | Interpolated Ground | 5126.74 | 6.47 | 479.78 | 0 | 28.34 | 0 | OK | Ground clear controls. | 14 | 33.72 | 508.12
821 | TIN-INTERP | Interpolated Ground | 5126.75 | -4.7 | 480.02 | 0 | 33.61 | 0 | OK | Ground clear controls. | 14 | 33.72 | 513.63
822 | TIN-INTERP | Interpolated Ground | 5126.78 | -6.7 | 480.03 | 0 | 28.09 | 0 | OK | Ground clear controls. | 14 | 33.72 | 508.12
823 | TIN-INTERP | Interpolated Ground | 5126.79 | 4.47 | 479.88 | 0 | 33.72 | 0 | OK | Ground clear controls. | 14 | 33.72 | 513.6
824 | TIN-INTERP | Interpolated Ground | 5126.83 | 4.97 | 479.85 | 0 | 22.86 | 0 | OK | Ground clear controls. | 14 | 22.86 | 502.71
825 | TIN-INTERP | Interpolated Ground | 5158.35 | -6.71 | 477.21 | 0 | 34.25 | 0 | OK | Ground clear controls. | 15 | 39.79 | 511.46
826 | TIN-INTERP | Interpolated Ground | 5158.39 | -4.71 | 477.17 | 0 | 39.79 | 0 | OK | Ground clear controls. | 15 | 39.79 | 516.96
827 | TIN-INTERP | Interpolated Ground | 5158.39 | -5.21 | 477.12 | 0 | 28.84 | 0 | OK | Ground clear controls. | 15 | 39.03 | 505.96
828 | TIN-INTERP | Interpolated Ground | 5158.4 | 4.47 | 477.93 | 0 | 39.03 | 0 | OK | Ground clear controls. | 15 | 39.03 | 516.96
829 | TIN-INTERP | Interpolated Ground | 5158.43 | 6.46 | 478.16 | 0 | 33.3 | 0 | OK | Ground clear controls. | 15 | 35.83 | 511.46
830 | TIN-INTERP | Interpolated Ground | 5158.44 | 4.96 | 477.97 | 0 | 27.99 | 0 | OK | Ground clear controls. | 15 | 35.83 | 505.96
831 | TIN-INTERP | Interpolated Ground | 5198.35 | -6.66 | 475.76 | 0 | 30.33 | 0 | OK | Ground clear controls. | 15 | 35.83 | 506.09
832 | TIN-INTERP | Interpolated Ground | 5198.39 | -4.66 | 475.89 | 0 | 35.73 | 0 | OK | Ground clear controls. | 15 | 35.83 | 511.62
833 | TIN-INTERP | Interpolated Ground | 5198.39 | -5.19 | 475.87 | 0 | 24.84 | 0 | OK | Ground clear controls. | 15 | 35.83 | 500.71
834 | TIN-INTERP | Interpolated Ground | 5198.4 | 4.4 | 476.56 | 0 | 35.02 | 0 | OK | Ground clear controls. | 15 | 35.83 | 511.58
835 | TIN-INTERP | Interpolated Ground | 5198.43 | 6.4 | 476.73 | 0 | 29.4 | 0 | OK | Ground clear controls. | 15 | 35.83 | 506.13
836 | TIN-INTERP | Interpolated Ground | 5198.44 | 4.9 | 476.62 | 0 | 24.11 | 0 | OK | Ground clear controls. | 15 | 35.83 | 500.73
837 | TIN-INTERP | Interpolated Ground | 5238.35 | -6.61 | 476.27 | 0 | 25.31 | 0 | OK | Ground clear controls. | 15 | 35.83 | 501.58
838 | TIN-INTERP | Interpolated Ground | 5238.39 | -4.6 | 476.38 | 0 | 30.78 | 0 | OK | Ground clear controls. | 15 | 35.83 | 507.16
839 | TIN-INTERP | Interpolated Ground | 5238.39 | -5.16 | 476.35 | 0 | 19.96 | 0 | OK | Ground clear controls. | 15 | 35.83 | 496.31
840 | TIN-INTERP | Interpolated Ground | 5238.4 | 4.34 | 476.8 | 0 | 30.27 | 0 | OK | Ground clear controls. | 15 | 35.83 | 507.07
841 | TIN-INTERP | Interpolated Ground | 5238.43 | 6.33 | 476.95 | 0 | 24.72 | 0 | OK | Ground clear controls. | 15 | 35.83 | 501.67
842 | TIN-INTERP | Interpolated Ground | 5238.44 | 4.83 | 476.83 | 0 | 19.52 | 0 | OK | Ground clear controls. | 15 | 35.83 | 496.35
843 | TIN-INTERP | Interpolated Ground | 5278.35 | -6.56 | 476.07 | 0 | 21.89 | 0 | OK | Ground clear controls. | 15 | 35.83 | 497.96
844 | TIN-INTERP | Interpolated Ground | 5278.39 | -4.55 | 476.09 | 0 | 27.47 | 0 | OK | Ground clear controls. | 15 | 35.83 | 503.56
845 | TIN-INTERP | Interpolated Ground | 5278.39 | -5.13 | 476.09 | 0 | 16.67 | 0 | OK | Ground clear controls. | 15 | 35.83 | 492.76
846 | TIN-INTERP | Interpolated Ground | 5278.4 | 4.28 | 476.58 | 0 | 26.87 | 0 | OK | Ground clear controls. | 15 | 35.83 | 503.45
847 | TIN-INTERP | Interpolated Ground | 5278.43 | 6.26 | 476.7 | 0 | 21.38 | 0 | OK | Ground clear controls. | 15 | 35.83 | 498.08
848 | TIN-INTERP | Interpolated Ground | 5278.44 | 4.76 | 476.61 | 0 | 16.22 | 0 | OK | Ground clear controls. | 15 | 35.83 | 492.83
849 | TIN-INTERP | Interpolated Ground | 5318.35 | -6.51 | 476.37 | 0 | 18.84 | 0 | OK | Ground clear controls. | 15 | 35.83 | 495.21
850 | TIN-INTERP | Interpolated Ground | 5318.39 | -4.5 | 476.21 | 0 | 24.62 | 0 | OK | Ground clear controls. | 15 | 35.83 | 500.83
851 | TIN-INTERP | Interpolated Ground | 5318.39 | -5.1 | 476.27 | 0 | 13.79 | 0 | OK | Ground clear controls. | 15 | 35.83 | 490.06
852 | TIN-INTERP | Interpolated Ground | 5318.4 | 4.22 | 475.68 | 0 | 25.03 | 0 | OK | Ground clear controls. | 15 | 35.83 | 500.71
853 | TIN-INTERP | Interpolated Ground | 5318.43 | 6.19 | 475.53 | 0 | 19.83 | 0 | OK | Ground clear controls. | 15 | 35.83 | 495.36
854 | TIN-INTERP | Interpolated Ground | 5318.44 | 4.7 | 475.64 | 0 | 14.51 | 0 | OK | Ground clear controls. | 15 | 35.83 | 490.15
855 | TIN-INTERP | Interpolated Ground | 5358.35 | -6.46 | 475.09 | 0 | 18.24 | 0 | OK | Ground clear controls. | 15 | 35.83 | 493.33
856 | TIN-INTERP | Interpolated Ground | 5358.39 | -4.45 | 474.87 | 0 | 24.09 | 0 | OK | Ground clear controls. | 15 | 35.83 | 498.96
857 | TIN-INTERP | Interpolated Ground | 5358.39 | -5.07 | 474.95 | 0 | 13.27 | 0 | OK | Ground clear controls. | 15 | 35.83 | 488.22
858 | TIN-INTERP | Interpolated Ground | 5358.4 | 4.16 | 474.34 | 0 | 24.5 | 0 | OK | Ground clear controls. | 15 | 35.83 | 498.84
859 | TIN-INTERP | Interpolated Ground | 5358.43 | 6.13 | 474.21 | 0 | 19.3 | 0 | OK | Ground clear controls. | 15 | 35.83 | 493.51
860 | TIN-INTERP | Interpolated Ground | 5358.44 | 4.63 | 474.29 | 0 | 14.04 | 0 | OK | Ground clear controls. | 15 | 35.83 | 488.33
861 | TIN-INTERP | Interpolated Ground | 5398.35 | -6.41 | 472.68 | 0 | 19.64 | 0 | OK | Ground clear controls. | 15 | 35.83 | 492.32
862 | TIN-INTERP | Interpolated Ground | 5398.39 | -4.4 | 472.48 | 0 | 25.48 | 0 | OK | Ground clear controls. | 15 | 35.83 | 497.96
863 | TIN-INTERP | Interpolated Ground | 5398.39 | -5.05 | 472.54 | 0 | 14.68 | 0 | OK | Ground clear controls. | 15 | 35.83 | 487.22
864 | TIN-INTERP | Interpolated Ground | 5398.4 | 4.1 | 472.62 | 0 | 25.24 | 0 | OK | Ground clear controls. | 15 | 35.83 | 497.86
865 | TIN-INTERP | Interpolated Ground | 5398.43 | 6.06 | 472.7 | 0 | 19.83 | 0 | OK | Ground clear controls. | 15 | 35.83 | 492.53
866 | TIN-INTERP | Interpolated Ground | 5398.44 | 4.57 | 472.64 | 0 | 14.71 | 0 | OK | Ground clear controls. | 15 | 35.83 | 487.35
867 | TIN-INTERP | Interpolated Ground | 5438.35 | -6.36 | 472 | 0 | 20.18 | 0 | OK | Ground clear controls. | 15 | 35.83 | 492.18
868 | TIN-INTERP | Interpolated Ground | 5438.39 | -4.34 | 472.08 | 0 | 25.74 | 0 | OK | Ground clear controls. | 15 | 35.83 | 497.82
869 | TIN-INTERP | Interpolated Ground | 5438.39 | -5.02 | 472.06 | 0 | 15.01 | 0 | OK | Ground clear controls. | 15 | 35.83 | 487.07
870 | TIN-INTERP | Interpolated Ground | 5438.4 | 4.04 | 472.69 | 0 | 25.04 | 0 | OK | Ground clear controls. | 15 | 35.83 | 497.73
871 | TIN-INTERP | Interpolated Ground | 5438.43 | 5.99 | 472.88 | 0 | 19.53 | 0 | OK | Ground clear controls. | 15 | 35.83 | 492.41
872 | TIN-INTERP | Interpolated Ground | 5438.44 | 4.5 | 472.73 | 0 | 14.49 | 0 | OK | Ground clear controls. | 15 | 35.83 | 487.22
873 | TIN-INTERP | Interpolated Ground | 5478.35 | -6.31 | 471.72 | 0 | 21.19 | 0 | OK | Ground clear controls. | 15 | 35.83 | 492.91
874 | TIN-INTERP | Interpolated Ground | 5478.39 | -4.29 | 471.61 | 0 | 26.93 | 0 | OK | Ground clear controls. | 15 | 35.83 | 498.54
875 | TIN-INTERP | Interpolated Ground | 5478.39 | -4.99 | 471.67 | 0 | 16.1 | 0 | OK | Ground clear controls. | 15 | 35.83 | 487.77
876 | TIN-INTERP | Interpolated Ground | 5478.4 | 3.97 | 471.47 | 0 | 27.04 | 0 | OK | Ground clear controls. | 15 | 35.83 | 498.51
877 | TIN-INTERP | Interpolated Ground | 5478.43 | 5.92 | 471.44 | 0 | 21.73 | 0 | OK | Ground clear controls. | 15 | 35.83 | 493.17
878 | TIN-INTERP | Interpolated Ground | 5478.44 | 4.43 | 471.47 | 0 | 16.47 | 0 | OK | Ground clear controls. | 15 | 35.83 | 487.94
879 | TIN-INTERP | Interpolated Ground | 5518.35 | -6.26 | 471.1 | 0 | 23.41 | 0 | OK | Ground clear controls. | 15 | 35.83 | 494.51
880 | TIN-INTERP | Interpolated Ground | 5518.39 | -4.24 | 471.17 | 0 | 28.96 | 0 | OK | Ground clear controls. | 15 | 35.83 | 500.13
881 | TIN-INTERP | Interpolated Ground | 5518.39 | -4.96 | 471.2 | 0 | 18.11 | 0 | OK | Ground clear controls. | 15 | 35.83 | 489.31
882 | TIN-INTERP | Interpolated Ground | 5518.4 | 3.91 | 471.18 | 0 | 28.96 | 0 | OK | Ground clear controls. | 15 | 35.83 | 500.14
883 | TIN-INTERP | Interpolated Ground | 5518.43 | 5.86 | 471.2 | 0 | 23.6 | 0 | OK | Ground clear controls. | 15 | 35.83 | 494.8
884 | TIN-INTERP | Interpolated Ground | 5518.44 | 4.37 | 471.2 | 0 | 18.32 | 0 | OK | Ground clear controls. | 15 | 35.83 | 489.52
885 | TIN-INTERP | Interpolated Ground | 5558.35 | -6.22 | 470.34 | 0 | 26.65 | 0 | OK | Ground clear controls. | 15 | 35.83 | 496.99
886 | TIN-INTERP | Interpolated Ground | 5558.39 | -4.19 | 470.24 | 0 | 32.34 | 0 | OK | Ground clear controls. | 15 | 35.83 | 502.58
887 | TIN-INTERP | Interpolated Ground | 5558.39 | -4.94 | 470.29 | 0 | 21.42 | 0 | OK | Ground clear controls. | 15 | 35.83 | 491.71
888 | TIN-INTERP | Interpolated Ground | 5558.4 | 3.85 | 470.12 | 0 | 32.53 | 0 | OK | Ground clear controls. | 15 | 35.83 | 502.65
889 | TIN-INTERP | Interpolated Ground | 5558.43 | 5.79 | 470.14 | 0 | 27.15 | 0 | OK | Ground clear controls. | 15 | 35.83 | 497.29
890 | TIN-INTERP | Interpolated Ground | 5558.44 | 4.3 | 470.13 | 0 | 21.8 | 0 | OK | Ground clear controls. | 15 | 35.83 | 491.93
891 | TIN-INTERP | Interpolated Ground | 5598.35 | -6.17 | 469.94 | 0 | 30.39 | 0 | OK | Ground clear controls. | 15 | 35.83 | 500.33
892 | TIN-INTERP | Interpolated Ground | 5598.39 | -4.13 | 470.07 | 0 | 35.83 | 0 | OK | Ground clear controls. | 15 | 35.83 | 505.9
893 | TIN-INTERP | Interpolated Ground | 5598.39 | -4.91 | 470.01 | 0 | 24.94 | 0 | OK | Ground clear controls. | 15 | 35.57 | 494.95
894 | TIN-INTERP | Interpolated Ground | 5598.4 | 3.79 | 470.48 | 0 | 35.57 | 0 | OK | Ground clear controls. | 15 | 35.57 | 506.05
895 | TIN-INTERP | Interpolated Ground | 5598.43 | 5.72 | 470.57 | 0 | 30.09 | 0 | OK | Ground clear controls. | 15 | 30.09 | 500.66
896 | TIN-INTERP | Interpolated Ground | 5598.44 | 4.23 | 470.51 | 0 | 24.69 | 0 | OK | Ground clear controls. | 15 | 24.69 | 495.2
897 | TIN-INTERP | Interpolated Ground | 5627.27 | -6.28 | 470.94 | 0 | 31.79 | 0 | OK | Ground clear controls. | 16 | 37.22 | 502.73
898 | TIN-INTERP | Interpolated Ground | 5627.51 | -4.22 | 471.02 | 0 | 37.22 | 0 | OK | Ground clear controls. | 16 | 37.22 | 508.24
899 | TIN-INTERP | Interpolated Ground | 5627.75 | -4.85 | 470.97 | 0 | 26.26 | 0 | OK | Ground clear controls. | 16 | 36.8 | 497.23
900 | TIN-INTERP | Interpolated Ground | 5629.74 | 3.78 | 471.42 | 0 | 36.8 | 0 | OK | Ground clear controls. | 16 | 36.8 | 508.22
901 | TIN-INTERP | Interpolated Ground | 5630.22 | 4.22 | 471.47 | 0 | 25.76 | 0 | OK | Ground clear controls. | 16 | 33.39 | 497.23
902 | TIN-INTERP | Interpolated Ground | 5630.51 | 5.7 | 471.59 | 0 | 31.13 | 0 | OK | Ground clear controls. | 16 | 33.39 | 502.72
903 | TIN-INTERP | Interpolated Ground | 5667.27 | -6.31 | 470.12 | 0 | 27.34 | 0 | OK | Ground clear controls. | 16 | 33.39 | 497.46
904 | TIN-INTERP | Interpolated Ground | 5667.51 | -4.26 | 469.95 | 0 | 33.09 | 0 | OK | Ground clear controls. | 16 | 33.39 | 503.04
905 | TIN-INTERP | Interpolated Ground | 5667.75 | -4.88 | 469.98 | 0 | 21.9 | 0 | OK | Ground clear controls. | 16 | 33.39 | 491.88
906 | TIN-INTERP | Interpolated Ground | 5669.74 | 3.86 | 469.55 | 0 | 33.39 | 0 | OK | Ground clear controls. | 16 | 33.39 | 502.94
907 | TIN-INTERP | Interpolated Ground | 5670.22 | 4.31 | 469.47 | 0 | 22.39 | 0 | OK | Ground clear controls. | 16 | 29.17 | 491.86
908 | TIN-INTERP | Interpolated Ground | 5670.51 | 5.79 | 469.41 | 0 | 28.04 | 0 | OK | Ground clear controls. | 16 | 29.17 | 497.45
909 | TIN-INTERP | Interpolated Ground | 5707.27 | -6.35 | 469.56 | 0 | 23.55 | 0 | OK | Ground clear controls. | 16 | 29.17 | 493.11
910 | TIN-INTERP | Interpolated Ground | 5707.51 | -4.31 | 469.59 | 0 | 29.17 | 0 | OK | Ground clear controls. | 16 | 29.17 | 498.76
911 | TIN-INTERP | Interpolated Ground | 5707.75 | -4.91 | 469.57 | 0 | 17.9 | 0 | OK | Ground clear controls. | 16 | 28.71 | 487.47
912 | TIN-INTERP | Interpolated Ground | 5709.74 | 3.94 | 469.86 | 0 | 28.71 | 0 | OK | Ground clear controls. | 16 | 28.71 | 498.57
913 | TIN-INTERP | Interpolated Ground | 5710.22 | 4.39 | 469.9 | 0 | 17.55 | 0 | OK | Ground clear controls. | 16 | 26.06 | 487.45
914 | TIN-INTERP | Interpolated Ground | 5710.51 | 5.87 | 469.91 | 0 | 23.19 | 0 | OK | Ground clear controls. | 16 | 26.06 | 493.1
915 | TIN-INTERP | Interpolated Ground | 5747.27 | -6.39 | 470.87 | 0 | 18.81 | 0 | OK | Ground clear controls. | 16 | 26.06 | 489.68
916 | TIN-INTERP | Interpolated Ground | 5747.51 | -4.35 | 470.89 | 0 | 24.48 | 0 | OK | Ground clear controls. | 16 | 26.06 | 495.37
917 | TIN-INTERP | Interpolated Ground | 5747.75 | -4.94 | 470.9 | 0 | 13.1 | 0 | OK | Ground clear controls. | 16 | 26.06 | 484
918 | TIN-INTERP | Interpolated Ground | 5749.74 | 4.02 | 471.15 | 0 | 23.99 | 0 | OK | Ground clear controls. | 16 | 26.06 | 495.14
919 | TIN-INTERP | Interpolated Ground | 5750.22 | 4.48 | 471.19 | 0 | 12.79 | 0 | OK | Ground clear controls. | 16 | 26.06 | 483.98
920 | TIN-INTERP | Interpolated Ground | 5750.51 | 5.96 | 471.22 | 0 | 18.46 | 0 | OK | Ground clear controls. | 16 | 26.06 | 489.68
921 | TIN-INTERP | Interpolated Ground | 5787.27 | -6.43 | 469.88 | 0 | 17.29 | 0 | OK | Ground clear controls. | 16 | 26.06 | 487.17
922 | TIN-INTERP | Interpolated Ground | 5787.51 | -4.4 | 469.83 | 0 | 23.06 | 0 | OK | Ground clear controls. | 16 | 26.06 | 492.89
923 | TIN-INTERP | Interpolated Ground | 5787.75 | -4.97 | 469.86 | 0 | 11.61 | 0 | OK | Ground clear controls. | 16 | 26.06 | 481.47
924 | TIN-INTERP | Interpolated Ground | 5789.74 | 4.09 | 469.57 | 0 | 23.06 | 0 | OK | Ground clear controls. | 16 | 26.06 | 492.63
925 | TIN-INTERP | Interpolated Ground | 5790.22 | 4.56 | 469.51 | 0 | 11.95 | 0 | OK | Ground clear controls. | 16 | 26.06 | 481.46
926 | TIN-INTERP | Interpolated Ground | 5790.51 | 6.05 | 469.23 | 0 | 17.96 | 0 | OK | Ground clear controls. | 16 | 26.06 | 487.19
927 | TIN-INTERP | Interpolated Ground | 5827.27 | -6.47 | 468.66 | 0 | 16.92 | 0 | OK | Ground clear controls. | 16 | 26.06 | 485.58
928 | TIN-INTERP | Interpolated Ground | 5827.51 | -4.44 | 468.69 | 0 | 22.61 | 0 | OK | Ground clear controls. | 16 | 26.06 | 491.3
929 | TIN-INTERP | Interpolated Ground | 5827.75 | -5.01 | 468.7 | 0 | 11.17 | 0 | OK | Ground clear controls. | 16 | 26.06 | 479.87
930 | TIN-INTERP | Interpolated Ground | 5829.74 | 4.17 | 468.74 | 0 | 22.32 | 0 | OK | Ground clear controls. | 16 | 26.06 | 491.06
931 | TIN-INTERP | Interpolated Ground | 5830.22 | 4.64 | 468.72 | 0 | 11.17 | 0 | OK | Ground clear controls. | 16 | 26.06 | 479.89
932 | TIN-INTERP | Interpolated Ground | 5830.51 | 6.13 | 468.59 | 0 | 17.04 | 0 | OK | Ground clear controls. | 16 | 26.06 | 485.63
933 | TIN-INTERP | Interpolated Ground | 5867.27 | -6.51 | 466.56 | 0 | 18.34 | 0 | OK | Ground clear controls. | 16 | 26.06 | 484.9
934 | TIN-INTERP | Interpolated Ground | 5867.51 | -4.48 | 466.61 | 0 | 24.01 | 0 | OK | Ground clear controls. | 16 | 26.06 | 490.62
935 | TIN-INTERP | Interpolated Ground | 5867.75 | -5.04 | 466.6 | 0 | 12.62 | 0 | OK | Ground clear controls. | 16 | 26.06 | 479.22
936 | TIN-INTERP | Interpolated Ground | 5869.74 | 4.25 | 466.99 | 0 | 23.42 | 0 | OK | Ground clear controls. | 16 | 26.06 | 490.41
937 | TIN-INTERP | Interpolated Ground | 5870.22 | 4.73 | 467.02 | 0 | 12.24 | 0 | OK | Ground clear controls. | 16 | 26.06 | 479.26
938 | TIN-INTERP | Interpolated Ground | 5870.51 | 6.22 | 467.05 | 0 | 17.93 | 0 | OK | Ground clear controls. | 16 | 26.06 | 484.98
939 | TIN-INTERP | Interpolated Ground | 5907.27 | -6.54 | 467.49 | 0 | 17.66 | 0 | OK | Ground clear controls. | 16 | 26.06 | 485.15
940 | TIN-INTERP | Interpolated Ground | 5907.51 | -4.53 | 467.61 | 0 | 23.22 | 0 | OK | Ground clear controls. | 16 | 26.06 | 490.83
941 | TIN-INTERP | Interpolated Ground | 5907.75 | -5.07 | 467.6 | 0 | 11.9 | 0 | OK | Ground clear controls. | 16 | 26.06 | 479.5
942 | TIN-INTERP | Interpolated Ground | 5909.74 | 4.33 | 468.01 | 0 | 22.68 | 0 | OK | Ground clear controls. | 16 | 26.06 | 490.69
943 | TIN-INTERP | Interpolated Ground | 5910.22 | 4.81 | 468.05 | 0 | 11.52 | 0 | OK | Ground clear controls. | 16 | 26.06 | 479.57
944 | TIN-INTERP | Interpolated Ground | 5910.51 | 6.3 | 468.19 | 0 | 17.08 | 0 | OK | Ground clear controls. | 16 | 26.06 | 485.27
945 | TIN-INTERP | Interpolated Ground | 5947.27 | -6.58 | 468.44 | 0 | 17.87 | 0 | OK | Ground clear controls. | 16 | 26.06 | 486.31
946 | TIN-INTERP | Interpolated Ground | 5947.51 | -4.57 | 468.49 | 0 | 23.45 | 0 | OK | Ground clear controls. | 16 | 26.06 | 491.94
947 | TIN-INTERP | Interpolated Ground | 5947.75 | -5.1 | 468.49 | 0 | 12.23 | 0 | OK | Ground clear controls. | 16 | 26.06 | 480.72
948 | TIN-INTERP | Interpolated Ground | 5949.74 | 4.41 | 468.86 | 0 | 23.04 | 0 | OK | Ground clear controls. | 16 | 26.06 | 491.9
949 | TIN-INTERP | Interpolated Ground | 5950.22 | 4.9 | 468.83 | 0 | 12 | 0 | OK | Ground clear controls. | 16 | 26.06 | 480.83
950 | TIN-INTERP | Interpolated Ground | 5950.51 | 6.39 | 468.88 | 0 | 17.59 | 0 | OK | Ground clear controls. | 16 | 26.06 | 486.47
951 | TIN-INTERP | Interpolated Ground | 5987.27 | -6.62 | 468.17 | 0 | 20.22 | 0 | OK | Ground clear controls. | 16 | 26.06 | 488.39
952 | TIN-INTERP | Interpolated Ground | 5987.51 | -4.62 | 468.13 | 0 | 25.83 | 0 | OK | Ground clear controls. | 16 | 26.06 | 493.96
953 | TIN-INTERP | Interpolated Ground | 5987.75 | -5.13 | 468.12 | 0 | 14.76 | 0 | OK | Ground clear controls. | 16 | 26.06 | 482.88
954 | TIN-INTERP | Interpolated Ground | 5989.74 | 4.48 | 467.98 | 0 | 26.06 | 0 | OK | Ground clear controls. | 16 | 26.06 | 494.04
955 | TIN-INTERP | Interpolated Ground | 5990.22 | 4.98 | 467.95 | 0 | 15.09 | 0 | OK | Ground clear controls. | 16 | 20.62 | 483.04
956 | TIN-INTERP | Interpolated Ground | 5990.51 | 6.48 | 467.97 | 0 | 20.62 | 0 | OK | Ground clear controls. | 16 | 20.62 | 488.59
957 | TIN-INTERP | Interpolated Ground | 6009.16 | -4.64 | 466.99 | 0 | 28.43 | 0 | OK | Ground clear controls. | 17 | 38.02 | 495.42
958 | TIN-INTERP | Interpolated Ground | 6009.23 | -5.14 | 466.98 | 0 | 17.44 | 0 | OK | Ground clear controls. | 17 | 38.02 | 484.42
959 | TIN-INTERP | Interpolated Ground | 6009.24 | -6.64 | 466.97 | 0 | 22.95 | 0 | OK | Ground clear controls. | 17 | 38.02 | 489.92
960 | TIN-INTERP | Interpolated Ground | 6009.31 | 5.02 | 466.93 | 0 | 17.49 | 0 | OK | Ground clear controls. | 17 | 38.02 | 484.42
961 | TIN-INTERP | Interpolated Ground | 6009.32 | 4.52 | 466.92 | 0 | 28.5 | 0 | OK | Ground clear controls. | 17 | 38.02 | 495.42
962 | TIN-INTERP | Interpolated Ground | 6009.33 | 6.52 | 466.84 | 0 | 23.08 | 0 | OK | Ground clear controls. | 17 | 38.02 | 489.92
963 | TIN-INTERP | Interpolated Ground | 6049.16 | -4.64 | 465.95 | 0 | 25.46 | 0 | OK | Ground clear controls. | 17 | 38.02 | 491.41
964 | TIN-INTERP | Interpolated Ground | 6049.23 | -5.15 | 465.96 | 0 | 14.29 | 0 | OK | Ground clear controls. | 17 | 38.02 | 480.25
965 | TIN-INTERP | Interpolated Ground | 6049.24 | -6.64 | 465.92 | 0 | 19.94 | 0 | OK | Ground clear controls. | 17 | 38.02 | 485.86
966 | TIN-INTERP | Interpolated Ground | 6049.31 | 5.02 | 466.09 | 0 | 14.15 | 0 | OK | Ground clear controls. | 17 | 38.02 | 480.24
967 | TIN-INTERP | Interpolated Ground | 6049.32 | 4.52 | 466.09 | 0 | 25.24 | 0 | OK | Ground clear controls. | 17 | 38.02 | 491.33
968 | TIN-INTERP | Interpolated Ground | 6049.33 | 6.52 | 466.12 | 0 | 19.73 | 0 | OK | Ground clear controls. | 17 | 38.02 | 485.85
969 | TIN-INTERP | Interpolated Ground | 6089.16 | -4.64 | 465.03 | 0 | 23.29 | 0 | OK | Ground clear controls. | 17 | 38.02 | 488.32
970 | TIN-INTERP | Interpolated Ground | 6089.23 | -5.15 | 465.01 | 0 | 12.01 | 0 | OK | Ground clear controls. | 17 | 38.02 | 477.02
971 | TIN-INTERP | Interpolated Ground | 6089.24 | -6.65 | 464.99 | 0 | 17.71 | 0 | OK | Ground clear controls. | 17 | 38.02 | 482.7
972 | TIN-INTERP | Interpolated Ground | 6089.31 | 5.02 | 465.13 | 0 | 11.87 | 0 | OK | Ground clear controls. | 17 | 38.02 | 477
973 | TIN-INTERP | Interpolated Ground | 6089.32 | 4.52 | 465.12 | 0 | 23.04 | 0 | OK | Ground clear controls. | 17 | 38.02 | 488.16
974 | TIN-INTERP | Interpolated Ground | 6089.33 | 6.52 | 465.16 | 0 | 17.54 | 0 | OK | Ground clear controls. | 17 | 38.02 | 482.7
975 | TIN-INTERP | Interpolated Ground | 6129.16 | -4.65 | 464.21 | 0 | 21.91 | 0 | OK | Ground clear controls. | 17 | 38.02 | 486.12
976 | TIN-INTERP | Interpolated Ground | 6129.23 | -5.15 | 464.22 | 0 | 10.52 | 0 | OK | Ground clear controls. | 17 | 38.02 | 474.74
977 | TIN-INTERP | Interpolated Ground | 6129.24 | -6.65 | 464.21 | 0 | 16.27 | 0 | OK | Ground clear controls. | 17 | 38.02 | 480.48
978 | TIN-INTERP | Interpolated Ground | 6129.31 | 5.02 | 464.15 | 0 | 10.58 | 0 | OK | Ground clear controls. | 17 | 38.02 | 474.73
979 | TIN-INTERP | Interpolated Ground | 6129.32 | 4.52 | 464.14 | 0 | 21.78 | 0 | OK | Ground clear controls. | 17 | 38.02 | 485.92
980 | TIN-INTERP | Interpolated Ground | 6129.33 | 6.52 | 464.12 | 0 | 16.36 | 0 | OK | Ground clear controls. | 17 | 38.02 | 480.48
981 | TIN-INTERP | Interpolated Ground | 6169.16 | -4.65 | 462.41 | 0 | 22.43 | 0 | OK | Ground clear controls. | 17 | 38.02 | 484.84
982 | TIN-INTERP | Interpolated Ground | 6169.23 | -5.15 | 462.39 | 0 | 11 | 0 | OK | Ground clear controls. | 17 | 38.02 | 473.39
983 | TIN-INTERP | Interpolated Ground | 6169.24 | -6.65 | 462.39 | 0 | 16.78 | 0 | OK | Ground clear controls. | 17 | 38.02 | 479.17
984 | TIN-INTERP | Interpolated Ground | 6169.31 | 5.02 | 462.38 | 0 | 11 | 0 | OK | Ground clear controls. | 17 | 38.02 | 473.38
985 | TIN-INTERP | Interpolated Ground | 6169.32 | 4.53 | 462.38 | 0 | 22.23 | 0 | OK | Ground clear controls. | 17 | 38.02 | 484.61
986 | TIN-INTERP | Interpolated Ground | 6169.33 | 6.52 | 462.39 | 0 | 16.77 | 0 | OK | Ground clear controls. | 17 | 38.02 | 479.16
987 | TIN-INTERP | Interpolated Ground | 6209.16 | -4.65 | 461.56 | 0 | 22.91 | 0 | OK | Ground clear controls. | 17 | 38.02 | 484.47
988 | TIN-INTERP | Interpolated Ground | 6209.23 | -5.16 | 461.56 | 0 | 11.44 | 0 | OK | Ground clear controls. | 17 | 38.02 | 473
989 | TIN-INTERP | Interpolated Ground | 6209.24 | -6.65 | 461.53 | 0 | 17.27 | 0 | OK | Ground clear controls. | 17 | 38.02 | 478.8
990 | TIN-INTERP | Interpolated Ground | 6209.31 | 5.03 | 461.69 | 0 | 11.29 | 0 | OK | Ground clear controls. | 17 | 38.02 | 472.98
991 | TIN-INTERP | Interpolated Ground | 6209.32 | 4.53 | 461.68 | 0 | 22.54 | 0 | OK | Ground clear controls. | 17 | 38.02 | 484.22
992 | TIN-INTERP | Interpolated Ground | 6209.33 | 6.52 | 461.71 | 0 | 17.07 | 0 | OK | Ground clear controls. | 17 | 38.02 | 478.78
993 | TIN-INTERP | Interpolated Ground | 6249.16 | -4.66 | 460.96 | 0 | 24.04 | 0 | OK | Ground clear controls. | 17 | 38.02 | 485
994 | TIN-INTERP | Interpolated Ground | 6249.23 | -5.16 | 460.97 | 0 | 12.56 | 0 | OK | Ground clear controls. | 17 | 38.02 | 473.53
995 | TIN-INTERP | Interpolated Ground | 6249.24 | -6.66 | 460.96 | 0 | 18.36 | 0 | OK | Ground clear controls. | 17 | 38.02 | 479.32
996 | TIN-INTERP | Interpolated Ground | 6249.31 | 5.03 | 460.99 | 0 | 12.52 | 0 | OK | Ground clear controls. | 17 | 38.02 | 473.51
997 | TIN-INTERP | Interpolated Ground | 6249.32 | 4.53 | 460.99 | 0 | 23.76 | 0 | OK | Ground clear controls. | 17 | 38.02 | 484.75
998 | TIN-INTERP | Interpolated Ground | 6249.33 | 6.53 | 461 | 0 | 18.32 | 0 | OK | Ground clear controls. | 17 | 38.02 | 479.32
999 | TIN-INTERP | Interpolated Ground | 6289.16 | -4.66 | 460.55 | 0 | 25.89 | 0 | OK | Ground clear controls. | 17 | 38.02 | 486.44
1000 | TIN-INTERP | Interpolated Ground | 6289.23 | -5.16 | 460.55 | 0 | 14.46 | 0 | OK | Ground clear controls. | 17 | 38.02 | 475.01
1001 | TIN-INTERP | Interpolated Ground | 6289.24 | -6.66 | 460.57 | 0 | 20.21 | 0 | OK | Ground clear controls. | 17 | 38.02 | 480.78
1002 | TIN-INTERP | Interpolated Ground | 6289.31 | 5.03 | 460.63 | 0 | 14.36 | 0 | OK | Ground clear controls. | 17 | 38.02 | 474.99
1003 | TIN-INTERP | Interpolated Ground | 6289.32 | 4.53 | 460.62 | 0 | 25.59 | 0 | OK | Ground clear controls. | 17 | 38.02 | 486.21
1004 | TIN-INTERP | Interpolated Ground | 6289.33 | 6.53 | 460.64 | 0 | 20.13 | 0 | OK | Ground clear controls. | 17 | 38.02 | 480.77
1005 | TIN-INTERP | Interpolated Ground | 6329.16 | -4.66 | 459.62 | 0 | 29.17 | 0 | OK | Ground clear controls. | 17 | 38.02 | 488.79
1006 | TIN-INTERP | Interpolated Ground | 6329.23 | -5.16 | 459.59 | 0 | 17.83 | 0 | OK | Ground clear controls. | 17 | 38.02 | 477.42
1007 | TIN-INTERP | Interpolated Ground | 6329.24 | -6.66 | 459.57 | 0 | 23.59 | 0 | OK | Ground clear controls. | 17 | 38.02 | 483.16
1008 | TIN-INTERP | Interpolated Ground | 6329.31 | 5.03 | 459.81 | 0 | 17.6 | 0 | OK | Ground clear controls. | 17 | 38.02 | 477.41
1009 | TIN-INTERP | Interpolated Ground | 6329.32 | 4.53 | 459.81 | 0 | 28.79 | 0 | OK | Ground clear controls. | 17 | 38.02 | 488.6
1010 | TIN-INTERP | Interpolated Ground | 6329.33 | 6.53 | 459.83 | 0 | 23.32 | 0 | OK | Ground clear controls. | 17 | 38.02 | 483.15
1011 | TIN-INTERP | Interpolated Ground | 6369.16 | -4.66 | 458.85 | 0 | 33.2 | 0 | OK | Ground clear controls. | 17 | 38.02 | 492.05
1012 | TIN-INTERP | Interpolated Ground | 6369.23 | -5.16 | 458.83 | 0 | 21.96 | 0 | OK | Ground clear controls. | 17 | 38.02 | 480.79
1013 | TIN-INTERP | Interpolated Ground | 6369.24 | -6.66 | 458.82 | 0 | 27.64 | 0 | OK | Ground clear controls. | 17 | 38.02 | 486.46
1014 | TIN-INTERP | Interpolated Ground | 6369.31 | 5.03 | 458.93 | 0 | 21.86 | 0 | OK | Ground clear controls. | 17 | 38.02 | 480.79
1015 | TIN-INTERP | Interpolated Ground | 6369.32 | 4.53 | 458.93 | 0 | 32.99 | 0 | OK | Ground clear controls. | 17 | 38.02 | 491.92
1016 | TIN-INTERP | Interpolated Ground | 6369.33 | 6.53 | 458.95 | 0 | 27.51 | 0 | OK | Ground clear controls. | 17 | 38.02 | 486.46
1017 | TIN-INTERP | Interpolated Ground | 6409.16 | -4.67 | 458.19 | 0 | 38.02 | 0 | OK | Ground clear controls. | 17 | 38.02 | 496.21
1018 | TIN-INTERP | Interpolated Ground | 6409.23 | -5.17 | 458.18 | 0 | 26.91 | 0 | OK | Ground clear controls. | 17 | 37.9 | 485.09
1019 | TIN-INTERP | Interpolated Ground | 6409.24 | -6.67 | 458.17 | 0 | 32.5 | 0 | OK | Ground clear controls. | 17 | 37.9 | 490.67
1020 | TIN-INTERP | Interpolated Ground | 6409.31 | 5.03 | 458.26 | 0 | 26.84 | 0 | OK | Ground clear controls. | 17 | 37.9 | 485.1
1021 | TIN-INTERP | Interpolated Ground | 6409.32 | 4.53 | 458.25 | 0 | 37.9 | 0 | OK | Ground clear controls. | 17 | 37.9 | 496.15
1022 | TIN-INTERP | Interpolated Ground | 6409.33 | 6.53 | 458.28 | 0 | 32.4 | 0 | OK | Ground clear controls. | 17 | 32.4 | 490.68
1023 | TIN-INTERP | Interpolated Ground | 6437.22 | -4.67 | 457.54 | 0 | 42.14 | 0 | OK | Ground clear controls. | 18 | 42.16 | 499.68
1024 | TIN-INTERP | Interpolated Ground | 6437.24 | -6.67 | 457.49 | 0 | 36.69 | 0 | OK | Ground clear controls. | 18 | 42.16 | 494.18
1025 | TIN-INTERP | Interpolated Ground | 6437.26 | 5.03 | 457.53 | 0 | 31.15 | 0 | OK | Ground clear controls. | 18 | 42.16 | 488.68
1026 | TIN-INTERP | Interpolated Ground | 6437.26 | -5.17 | 457.51 | 0 | 31.17 | 0 | OK | Ground clear controls. | 18 | 42.16 | 488.68
1027 | TIN-INTERP | Interpolated Ground | 6437.3 | 6.53 | 457.47 | 0 | 36.71 | 0 | OK | Ground clear controls. | 18 | 42.16 | 494.18
1028 | TIN-INTERP | Interpolated Ground | 6437.31 | 4.53 | 457.52 | 0 | 42.16 | 0 | OK | Ground clear controls. | 18 | 42.16 | 499.68
1029 | TIN-INTERP | Interpolated Ground | 6477.21 | -4.67 | 455.51 | 0 | 38.31 | 0 | OK | Ground clear controls. | 18 | 38.31 | 493.82
1030 | TIN-INTERP | Interpolated Ground | 6477.24 | -6.67 | 455.49 | 0 | 32.76 | 0 | OK | Ground clear controls. | 18 | 38.13 | 488.25
1031 | TIN-INTERP | Interpolated Ground | 6477.26 | 5.03 | 455.64 | 0 | 26.99 | 0 | OK | Ground clear controls. | 18 | 38.13 | 482.63
1032 | TIN-INTERP | Interpolated Ground | 6477.26 | -5.17 | 455.48 | 0 | 27.16 | 0 | OK | Ground clear controls. | 18 | 38.13 | 482.64
1033 | TIN-INTERP | Interpolated Ground | 6477.3 | 6.53 | 455.64 | 0 | 32.65 | 0 | OK | Ground clear controls. | 18 | 38.13 | 488.29
1034 | TIN-INTERP | Interpolated Ground | 6477.32 | 4.53 | 455.64 | 0 | 38.13 | 0 | OK | Ground clear controls. | 18 | 38.13 | 493.77
1035 | TIN-INTERP | Interpolated Ground | 6517.21 | -4.68 | 454.52 | 0 | 34.35 | 0 | OK | Ground clear controls. | 18 | 37.58 | 488.87
1036 | TIN-INTERP | Interpolated Ground | 6517.24 | -6.68 | 454.48 | 0 | 28.78 | 0 | OK | Ground clear controls. | 18 | 37.58 | 483.26
1037 | TIN-INTERP | Interpolated Ground | 6517.26 | 5.02 | 454.86 | 0 | 22.67 | 0 | OK | Ground clear controls. | 18 | 37.58 | 477.53
1038 | TIN-INTERP | Interpolated Ground | 6517.26 | -5.18 | 454.51 | 0 | 23.04 | 0 | OK | Ground clear controls. | 18 | 37.58 | 477.55
1039 | TIN-INTERP | Interpolated Ground | 6517.3 | 6.52 | 454.9 | 0 | 28.43 | 0 | OK | Ground clear controls. | 18 | 37.58 | 483.33
1040 | TIN-INTERP | Interpolated Ground | 6517.32 | 4.52 | 454.85 | 0 | 33.94 | 0 | OK | Ground clear controls. | 18 | 37.58 | 488.79
1041 | TIN-INTERP | Interpolated Ground | 6557.21 | -4.68 | 453.62 | 0 | 31.24 | 0 | OK | Ground clear controls. | 18 | 37.58 | 484.86
1042 | TIN-INTERP | Interpolated Ground | 6557.24 | -6.68 | 453.6 | 0 | 25.59 | 0 | OK | Ground clear controls. | 18 | 37.58 | 479.19
1043 | TIN-INTERP | Interpolated Ground | 6557.26 | 5.02 | 453.84 | 0 | 19.54 | 0 | OK | Ground clear controls. | 18 | 37.58 | 473.38
1044 | TIN-INTERP | Interpolated Ground | 6557.26 | -5.18 | 453.61 | 0 | 19.81 | 0 | OK | Ground clear controls. | 18 | 37.58 | 473.42
1045 | TIN-INTERP | Interpolated Ground | 6557.3 | 6.52 | 453.86 | 0 | 25.43 | 0 | OK | Ground clear controls. | 18 | 37.58 | 479.29
1046 | TIN-INTERP | Interpolated Ground | 6557.32 | 4.52 | 453.82 | 0 | 30.92 | 0 | OK | Ground clear controls. | 18 | 37.58 | 484.74
1047 | TIN-INTERP | Interpolated Ground | 6597.21 | -4.69 | 452.89 | 0 | 28.87 | 0 | OK | Ground clear controls. | 18 | 37.58 | 481.76
1048 | TIN-INTERP | Interpolated Ground | 6597.24 | -6.69 | 452.84 | 0 | 23.22 | 0 | OK | Ground clear controls. | 18 | 37.58 | 476.06
1049 | TIN-INTERP | Interpolated Ground | 6597.26 | 5.01 | 453.2 | 0 | 16.99 | 0 | OK | Ground clear controls. | 18 | 37.58 | 470.19
1050 | TIN-INTERP | Interpolated Ground | 6597.26 | -5.19 | 452.9 | 0 | 17.33 | 0 | OK | Ground clear controls. | 18 | 37.58 | 470.23
1051 | TIN-INTERP | Interpolated Ground | 6597.3 | 6.51 | 453.22 | 0 | 22.95 | 0 | OK | Ground clear controls. | 18 | 37.58 | 476.17
1052 | TIN-INTERP | Interpolated Ground | 6597.32 | 4.51 | 453.18 | 0 | 28.44 | 0 | OK | Ground clear controls. | 18 | 37.58 | 481.62
1053 | TIN-INTERP | Interpolated Ground | 6637.21 | -4.7 | 453.17 | 0 | 26.41 | 0 | OK | Ground clear controls. | 18 | 37.58 | 479.58
1054 | TIN-INTERP | Interpolated Ground | 6637.24 | -6.7 | 453.14 | 0 | 20.73 | 0 | OK | Ground clear controls. | 18 | 37.58 | 473.87
1055 | TIN-INTERP | Interpolated Ground | 6637.26 | 5 | 453.28 | 0 | 14.67 | 0 | OK | Ground clear controls. | 18 | 37.58 | 467.95
1056 | TIN-INTERP | Interpolated Ground | 6637.26 | -5.2 | 453.15 | 0 | 14.84 | 0 | OK | Ground clear controls. | 18 | 37.58 | 467.99
1057 | TIN-INTERP | Interpolated Ground | 6637.3 | 6.5 | 453.31 | 0 | 20.68 | 0 | OK | Ground clear controls. | 18 | 37.58 | 473.99
1058 | TIN-INTERP | Interpolated Ground | 6637.32 | 4.5 | 453.26 | 0 | 26.17 | 0 | OK | Ground clear controls. | 18 | 37.58 | 479.43
1059 | TIN-INTERP | Interpolated Ground | 6677.21 | -4.7 | 453.06 | 0 | 25.26 | 0 | OK | Ground clear controls. | 18 | 37.58 | 478.32
1060 | TIN-INTERP | Interpolated Ground | 6677.24 | -6.7 | 453.02 | 0 | 19.58 | 0 | OK | Ground clear controls. | 18 | 37.58 | 472.6
1061 | TIN-INTERP | Interpolated Ground | 6677.26 | 5 | 453.28 | 0 | 13.37 | 0 | OK | Ground clear controls. | 18 | 37.58 | 466.65
1062 | TIN-INTERP | Interpolated Ground | 6677.26 | -5.2 | 453.05 | 0 | 13.66 | 0 | OK | Ground clear controls. | 18 | 37.58 | 466.71
1063 | TIN-INTERP | Interpolated Ground | 6677.3 | 6.5 | 453.32 | 0 | 19.41 | 0 | OK | Ground clear controls. | 18 | 37.58 | 472.73
1064 | TIN-INTERP | Interpolated Ground | 6677.32 | 4.5 | 453.27 | 0 | 24.89 | 0 | OK | Ground clear controls. | 18 | 37.58 | 478.16
1065 | TIN-INTERP | Interpolated Ground | 6717.21 | -4.71 | 452.67 | 0 | 25.31 | 0 | OK | Ground clear controls. | 18 | 37.58 | 477.98
1066 | TIN-INTERP | Interpolated Ground | 6717.24 | -6.71 | 452.65 | 0 | 19.61 | 0 | OK | Ground clear controls. | 18 | 37.58 | 472.26
1067 | TIN-INTERP | Interpolated Ground | 6717.26 | 4.99 | 452.8 | 0 | 13.51 | 0 | OK | Ground clear controls. | 18 | 37.58 | 466.31
1068 | TIN-INTERP | Interpolated Ground | 6717.26 | -5.21 | 452.67 | 0 | 13.7 | 0 | OK | Ground clear controls. | 18 | 37.58 | 466.37
1069 | TIN-INTERP | Interpolated Ground | 6717.3 | 6.49 | 452.82 | 0 | 19.57 | 0 | OK | Ground clear controls. | 18 | 37.58 | 472.39
1070 | TIN-INTERP | Interpolated Ground | 6717.32 | 4.49 | 452.79 | 0 | 25.03 | 0 | OK | Ground clear controls. | 18 | 37.58 | 477.82
1071 | TIN-INTERP | Interpolated Ground | 6757.21 | -4.71 | 453.06 | 0 | 25.49 | 0 | OK | Ground clear controls. | 18 | 37.58 | 478.55
1072 | TIN-INTERP | Interpolated Ground | 6757.24 | -6.71 | 453.07 | 0 | 19.78 | 0 | OK | Ground clear controls. | 18 | 37.58 | 472.85
1073 | TIN-INTERP | Interpolated Ground | 6757.26 | 4.99 | 452.7 | 0 | 14.22 | 0 | OK | Ground clear controls. | 18 | 37.58 | 466.92
1074 | TIN-INTERP | Interpolated Ground | 6757.26 | -5.21 | 453.05 | 0 | 13.92 | 0 | OK | Ground clear controls. | 18 | 37.58 | 466.97
1075 | TIN-INTERP | Interpolated Ground | 6757.3 | 6.49 | 452.66 | 0 | 20.31 | 0 | OK | Ground clear controls. | 18 | 37.58 | 472.97
1076 | TIN-INTERP | Interpolated Ground | 6757.32 | 4.49 | 452.71 | 0 | 25.7 | 0 | OK | Ground clear controls. | 18 | 37.58 | 478.41
1077 | TIN-INTERP | Interpolated Ground | 6797.21 | -4.72 | 451.59 | 0 | 28.45 | 0 | OK | Ground clear controls. | 18 | 37.58 | 480.04
1078 | TIN-INTERP | Interpolated Ground | 6797.24 | -6.72 | 451.79 | 0 | 22.57 | 0 | OK | Ground clear controls. | 18 | 37.58 | 474.36
1079 | TIN-INTERP | Interpolated Ground | 6797.26 | 4.98 | 451.6 | 0 | 16.88 | 0 | OK | Ground clear controls. | 18 | 37.58 | 468.48
1080 | TIN-INTERP | Interpolated Ground | 6797.26 | -5.22 | 451.61 | 0 | 16.91 | 0 | OK | Ground clear controls. | 18 | 37.58 | 468.52
1081 | TIN-INTERP | Interpolated Ground | 6797.3 | 6.48 | 451.63 | 0 | 22.84 | 0 | OK | Ground clear controls. | 18 | 37.58 | 474.47
1082 | TIN-INTERP | Interpolated Ground | 6797.32 | 4.48 | 451.59 | 0 | 28.32 | 0 | OK | Ground clear controls. | 18 | 37.58 | 479.91
1083 | TIN-INTERP | Interpolated Ground | 6837.21 | -4.72 | 451.54 | 0 | 30.93 | 0 | OK | Ground clear controls. | 18 | 37.58 | 482.47
1084 | TIN-INTERP | Interpolated Ground | 6837.24 | -6.72 | 451.48 | 0 | 25.33 | 0 | OK | Ground clear controls. | 18 | 37.58 | 476.81
1085 | TIN-INTERP | Interpolated Ground | 6837.26 | 4.98 | 451.97 | 0 | 19.02 | 0 | OK | Ground clear controls. | 18 | 37.58 | 470.99
1086 | TIN-INTERP | Interpolated Ground | 6837.26 | -5.22 | 451.53 | 0 | 19.5 | 0 | OK | Ground clear controls. | 18 | 37.58 | 471.03
1087 | TIN-INTERP | Interpolated Ground | 6837.3 | 6.48 | 452.05 | 0 | 24.85 | 0 | OK | Ground clear controls. | 18 | 37.58 | 476.9
1088 | TIN-INTERP | Interpolated Ground | 6837.32 | 4.48 | 451.94 | 0 | 30.41 | 0 | OK | Ground clear controls. | 18 | 37.58 | 482.35
1089 | TIN-INTERP | Interpolated Ground | 6877.21 | -4.73 | 452.05 | 0 | 33.75 | 0 | OK | Ground clear controls. | 18 | 37.58 | 485.8
1090 | TIN-INTERP | Interpolated Ground | 6877.24 | -6.73 | 451.98 | 0 | 28.21 | 0 | OK | Ground clear controls. | 18 | 37.58 | 480.19
1091 | TIN-INTERP | Interpolated Ground | 6877.26 | 4.97 | 452.32 | 0 | 22.12 | 0 | OK | Ground clear controls. | 18 | 37.58 | 474.44
1092 | TIN-INTERP | Interpolated Ground | 6877.26 | -5.23 | 452.03 | 0 | 22.44 | 0 | OK | Ground clear controls. | 18 | 37.58 | 474.47
1093 | TIN-INTERP | Interpolated Ground | 6877.3 | 6.47 | 452.39 | 0 | 27.86 | 0 | OK | Ground clear controls. | 18 | 37.58 | 480.25
1094 | TIN-INTERP | Interpolated Ground | 6877.32 | 4.47 | 452.31 | 0 | 33.41 | 0 | OK | Ground clear controls. | 18 | 37.58 | 485.72
1095 | TIN-INTERP | Interpolated Ground | 6917.21 | -4.74 | 452.48 | 0 | 37.58 | 0 | OK | Ground clear controls. | 18 | 37.58 | 490.06
1096 | TIN-INTERP | Interpolated Ground | 6917.24 | -6.74 | 452.48 | 0 | 32.02 | 0 | OK | Ground clear controls. | 18 | 37.36 | 484.5
1097 | TIN-INTERP | Interpolated Ground | 6917.26 | 4.96 | 452.67 | 0 | 26.18 | 0 | OK | Ground clear controls. | 18 | 37.36 | 478.85
1098 | TIN-INTERP | Interpolated Ground | 6917.26 | -5.24 | 452.48 | 0 | 26.4 | 0 | OK | Ground clear controls. | 18 | 37.36 | 478.88
1099 | TIN-INTERP | Interpolated Ground | 6917.3 | 6.46 | 452.71 | 0 | 31.82 | 0 | OK | Ground clear controls. | 18 | 37.36 | 484.53
1100 | TIN-INTERP | Interpolated Ground | 6917.32 | 4.46 | 452.65 | 0 | 37.36 | 0 | OK | Ground clear controls. | 18 | 37.36 | 490.01
1101 | TIN-INTERP | Interpolated Ground | 6956.91 | -6.74 | 452.72 | 0 | 36.97 | 0 | OK | Ground clear controls. | 19 | 42.51 | 489.69
1102 | TIN-INTERP | Interpolated Ground | 6956.93 | -4.74 | 452.69 | 0 | 42.5 | 0 | OK | Ground clear controls. | 19 | 42.51 | 495.19
1103 | TIN-INTERP | Interpolated Ground | 6956.99 | -5.24 | 452.7 | 0 | 31.49 | 0 | OK | Ground clear controls. | 19 | 42.51 | 484.19
1104 | TIN-INTERP | Interpolated Ground | 6957.04 | 6.46 | 452.95 | 0 | 36.74 | 0 | OK | Ground clear controls. | 19 | 42.51 | 489.69
1105 | TIN-INTERP | Interpolated Ground | 6957.04 | 4.46 | 452.68 | 0 | 42.51 | 0 | OK | Ground clear controls. | 19 | 42.51 | 495.19
1106 | TIN-INTERP | Interpolated Ground | 6957.07 | 4.96 | 452.7 | 0 | 31.49 | 0 | OK | Ground clear controls. | 19 | 38.43 | 484.19
1107 | TIN-INTERP | Interpolated Ground | 6996.91 | -6.74 | 453.34 | 0 | 31.76 | 0 | OK | Ground clear controls. | 19 | 38.43 | 485.1
1108 | TIN-INTERP | Interpolated Ground | 6996.93 | -4.75 | 453.39 | 0 | 37.29 | 0 | OK | Ground clear controls. | 19 | 38.43 | 490.68
1109 | TIN-INTERP | Interpolated Ground | 6996.99 | -5.25 | 453.37 | 0 | 26.16 | 0 | OK | Ground clear controls. | 19 | 38.43 | 479.53
1110 | TIN-INTERP | Interpolated Ground | 6997.04 | 6.45 | 453.62 | 0 | 31.56 | 0 | OK | Ground clear controls. | 19 | 38.43 | 485.18
1111 | TIN-INTERP | Interpolated Ground | 6997.04 | 4.45 | 453.6 | 0 | 37.07 | 0 | OK | Ground clear controls. | 19 | 38.43 | 490.67
1112 | TIN-INTERP | Interpolated Ground | 6997.07 | 4.95 | 453.61 | 0 | 25.93 | 0 | OK | Ground clear controls. | 19 | 38.43 | 479.54
1113 | TIN-INTERP | Interpolated Ground | 7036.91 | -6.75 | 454.13 | 0 | 27.32 | 0 | OK | Ground clear controls. | 19 | 38.43 | 481.45
1114 | TIN-INTERP | Interpolated Ground | 7036.93 | -4.75 | 454.19 | 0 | 32.89 | 0 | OK | Ground clear controls. | 19 | 38.43 | 487.08
1115 | TIN-INTERP | Interpolated Ground | 7036.99 | -5.25 | 454.17 | 0 | 21.65 | 0 | OK | Ground clear controls. | 19 | 38.43 | 475.82
1116 | TIN-INTERP | Interpolated Ground | 7037.04 | 6.45 | 454.26 | 0 | 27.34 | 0 | OK | Ground clear controls. | 19 | 38.43 | 481.6
1117 | TIN-INTERP | Interpolated Ground | 7037.04 | 4.45 | 454.27 | 0 | 32.81 | 0 | OK | Ground clear controls. | 19 | 38.43 | 487.08
1118 | TIN-INTERP | Interpolated Ground | 7037.07 | 4.95 | 454.27 | 0 | 21.56 | 0 | OK | Ground clear controls. | 19 | 38.43 | 475.83
1119 | TIN-INTERP | Interpolated Ground | 7076.91 | -6.75 | 452.37 | 0 | 26.35 | 0 | OK | Ground clear controls. | 19 | 38.43 | 478.72
1120 | TIN-INTERP | Interpolated Ground | 7076.93 | -4.75 | 452.32 | 0 | 32.1 | 0 | OK | Ground clear controls. | 19 | 38.43 | 484.42
1121 | TIN-INTERP | Interpolated Ground | 7076.99 | -5.25 | 452.32 | 0 | 20.73 | 0 | OK | Ground clear controls. | 19 | 38.43 | 473.05
1122 | TIN-INTERP | Interpolated Ground | 7077.04 | 6.45 | 452.12 | 0 | 26.81 | 0 | OK | Ground clear controls. | 19 | 38.43 | 478.93
1123 | TIN-INTERP | Interpolated Ground | 7077.04 | 4.45 | 452.14 | 0 | 32.27 | 0 | OK | Ground clear controls. | 19 | 38.43 | 484.41
1124 | TIN-INTERP | Interpolated Ground | 7077.07 | 4.95 | 452.13 | 0 | 20.93 | 0 | OK | Ground clear controls. | 19 | 38.43 | 473.06
1125 | TIN-INTERP | Interpolated Ground | 7116.91 | -6.76 | 454.02 | 0 | 22.93 | 0 | OK | Ground clear controls. | 19 | 38.43 | 476.95
1126 | TIN-INTERP | Interpolated Ground | 7116.93 | -4.76 | 454.04 | 0 | 28.64 | 0 | OK | Ground clear controls. | 19 | 38.43 | 482.68
1127 | TIN-INTERP | Interpolated Ground | 7116.99 | -5.26 | 454.06 | 0 | 17.18 | 0 | OK | Ground clear controls. | 19 | 38.43 | 471.24
1128 | TIN-INTERP | Interpolated Ground | 7117.04 | 6.44 | 454.41 | 0 | 22.79 | 0 | OK | Ground clear controls. | 19 | 38.43 | 477.2
1129 | TIN-INTERP | Interpolated Ground | 7117.04 | 4.44 | 454.31 | 0 | 28.36 | 0 | OK | Ground clear controls. | 19 | 38.43 | 482.67
1130 | TIN-INTERP | Interpolated Ground | 7117.07 | 4.94 | 454.33 | 0 | 16.91 | 0 | OK | Ground clear controls. | 19 | 38.43 | 471.24
1131 | TIN-INTERP | Interpolated Ground | 7156.91 | -6.76 | 457.02 | 0 | 19.08 | 0 | OK | Ground clear controls. | 19 | 38.43 | 476.1
1132 | TIN-INTERP | Interpolated Ground | 7156.93 | -4.76 | 457.1 | 0 | 24.77 | 0 | OK | Ground clear controls. | 19 | 38.43 | 481.87
1133 | TIN-INTERP | Interpolated Ground | 7156.99 | -5.26 | 457.07 | 0 | 13.3 | 0 | OK | Ground clear controls. | 19 | 38.43 | 470.37
1134 | TIN-INTERP | Interpolated Ground | 7157.04 | 6.44 | 457.44 | 0 | 18.95 | 0 | OK | Ground clear controls. | 19 | 38.43 | 476.39
1135 | TIN-INTERP | Interpolated Ground | 7157.04 | 4.44 | 457.37 | 0 | 24.48 | 0 | OK | Ground clear controls. | 19 | 38.43 | 481.85
1136 | TIN-INTERP | Interpolated Ground | 7157.07 | 4.94 | 457.39 | 0 | 12.99 | 0 | OK | Ground clear controls. | 19 | 38.43 | 470.38
1137 | TIN-INTERP | Interpolated Ground | 7196.91 | -6.77 | 458.78 | 0 | 17.41 | 0 | OK | Ground clear controls. | 19 | 38.43 | 476.19
1138 | TIN-INTERP | Interpolated Ground | 7196.93 | -4.77 | 458.86 | 0 | 23.11 | 0 | OK | Ground clear controls. | 19 | 38.43 | 481.97
1139 | TIN-INTERP | Interpolated Ground | 7196.99 | -5.27 | 458.83 | 0 | 11.6 | 0 | OK | Ground clear controls. | 19 | 38.43 | 470.43
1140 | TIN-INTERP | Interpolated Ground | 7197.04 | 6.43 | 460.03 | 0 | 16.47 | 0 | OK | Ground clear controls. | 19 | 38.43 | 476.5
1141 | TIN-INTERP | Interpolated Ground | 7197.04 | 4.43 | 459.89 | 0 | 22.07 | 0 | OK | Ground clear controls. | 19 | 38.43 | 481.96
1142 | TIN-INTERP | Interpolated Ground | 7197.07 | 4.93 | 459.93 | 0 | 10.52 | 0 | OK | Ground clear controls. | 19 | 38.43 | 470.45
1143 | TIN-INTERP | Interpolated Ground | 7236.91 | -6.77 | 454.15 | 0 | 23.05 | 0 | OK | Ground clear controls. | 19 | 38.43 | 477.2
1144 | TIN-INTERP | Interpolated Ground | 7236.93 | -4.77 | 454.22 | 0 | 28.77 | 0 | OK | Ground clear controls. | 19 | 38.43 | 482.99
1145 | TIN-INTERP | Interpolated Ground | 7236.99 | -5.27 | 454.17 | 0 | 17.28 | 0 | OK | Ground clear controls. | 19 | 38.43 | 471.45
1146 | TIN-INTERP | Interpolated Ground | 7237.04 | 6.43 | 454.48 | 0 | 23.04 | 0 | OK | Ground clear controls. | 19 | 38.43 | 477.52
1147 | TIN-INTERP | Interpolated Ground | 7237.04 | 4.43 | 454.46 | 0 | 28.52 | 0 | OK | Ground clear controls. | 19 | 38.43 | 482.98
1148 | TIN-INTERP | Interpolated Ground | 7237.07 | 4.93 | 454.46 | 0 | 17.01 | 0 | OK | Ground clear controls. | 19 | 38.43 | 471.47
1149 | TIN-INTERP | Interpolated Ground | 7276.91 | -6.77 | 458.5 | 0 | 20.66 | 0 | OK | Ground clear controls. | 19 | 38.43 | 479.16
1150 | TIN-INTERP | Interpolated Ground | 7276.93 | -4.77 | 457.92 | 0 | 27.02 | 0 | OK | Ground clear controls. | 19 | 38.43 | 484.94
1151 | TIN-INTERP | Interpolated Ground | 7276.99 | -5.27 | 458.12 | 0 | 15.3 | 0 | OK | Ground clear controls. | 19 | 38.43 | 473.42
1152 | TIN-INTERP | Interpolated Ground | 7277.04 | 6.43 | 455.31 | 0 | 24.17 | 0 | OK | Ground clear controls. | 19 | 38.43 | 479.48
1153 | TIN-INTERP | Interpolated Ground | 7277.04 | 4.43 | 455.5 | 0 | 29.44 | 0 | OK | Ground clear controls. | 19 | 38.43 | 484.94
1154 | TIN-INTERP | Interpolated Ground | 7277.07 | 4.93 | 455.46 | 0 | 17.98 | 0 | OK | Ground clear controls. | 19 | 38.43 | 473.44
1155 | TIN-INTERP | Interpolated Ground | 7316.91 | -6.78 | 464.19 | 0 | 17.87 | 0 | OK | Ground clear controls. | 19 | 38.43 | 482.06
1156 | TIN-INTERP | Interpolated Ground | 7316.93 | -4.78 | 464.23 | 0 | 23.59 | 0 | OK | Ground clear controls. | 19 | 38.43 | 487.82
1157 | TIN-INTERP | Interpolated Ground | 7316.99 | -5.28 | 464.22 | 0 | 12.12 | 0 | OK | Ground clear controls. | 19 | 38.43 | 476.34
1158 | TIN-INTERP | Interpolated Ground | 7317.04 | 6.42 | 464.67 | 0 | 17.68 | 0 | OK | Ground clear controls. | 19 | 38.43 | 482.35
1159 | TIN-INTERP | Interpolated Ground | 7317.04 | 4.42 | 464.65 | 0 | 23.17 | 0 | OK | Ground clear controls. | 19 | 38.43 | 487.82
1160 | TIN-INTERP | Interpolated Ground | 7317.07 | 4.92 | 464.64 | 0 | 11.71 | 0 | OK | Ground clear controls. | 19 | 38.43 | 476.35
1161 | TIN-INTERP | Interpolated Ground | 7356.91 | -6.78 | 466.74 | 0 | 19.14 | 0 | OK | Ground clear controls. | 19 | 38.43 | 485.88
1162 | TIN-INTERP | Interpolated Ground | 7356.93 | -4.78 | 466.91 | 0 | 24.71 | 0 | OK | Ground clear controls. | 19 | 38.43 | 491.62
1163 | TIN-INTERP | Interpolated Ground | 7356.99 | -5.28 | 466.93 | 0 | 13.26 | 0 | OK | Ground clear controls. | 19 | 38.43 | 480.19
1164 | TIN-INTERP | Interpolated Ground | 7357.04 | 6.42 | 467.16 | 0 | 18.99 | 0 | OK | Ground clear controls. | 19 | 38.43 | 486.15
1165 | TIN-INTERP | Interpolated Ground | 7357.04 | 4.42 | 467.24 | 0 | 24.38 | 0 | OK | Ground clear controls. | 19 | 38.43 | 491.62
1166 | TIN-INTERP | Interpolated Ground | 7357.07 | 4.92 | 467.22 | 0 | 12.99 | 0 | OK | Ground clear controls. | 19 | 38.43 | 480.21
1167 | TIN-INTERP | Interpolated Ground | 7396.91 | -6.79 | 467.37 | 0 | 23.29 | 0 | OK | Ground clear controls. | 19 | 38.43 | 490.66
1168 | TIN-INTERP | Interpolated Ground | 7396.93 | -4.79 | 467.35 | 0 | 28.99 | 0 | OK | Ground clear controls. | 19 | 38.43 | 496.34
1169 | TIN-INTERP | Interpolated Ground | 7396.99 | -5.29 | 467.35 | 0 | 17.65 | 0 | OK | Ground clear controls. | 19 | 38.43 | 485
1170 | TIN-INTERP | Interpolated Ground | 7397.04 | 6.41 | 467.46 | 0 | 23.42 | 0 | OK | Ground clear controls. | 19 | 38.43 | 490.88
1171 | TIN-INTERP | Interpolated Ground | 7397.04 | 4.41 | 467.42 | 0 | 28.93 | 0 | OK | Ground clear controls. | 19 | 38.43 | 496.35
1172 | TIN-INTERP | Interpolated Ground | 7397.07 | 4.91 | 467.44 | 0 | 17.58 | 0 | OK | Ground clear controls. | 19 | 38.43 | 485.02
1173 | TIN-INTERP | Interpolated Ground | 7436.91 | -6.79 | 468.68 | 0 | 27.69 | 0 | OK | Ground clear controls. | 19 | 38.43 | 496.37
1174 | TIN-INTERP | Interpolated Ground | 7436.93 | -4.79 | 468.78 | 0 | 33.22 | 0 | OK | Ground clear controls. | 19 | 38.43 | 502
1175 | TIN-INTERP | Interpolated Ground | 7436.99 | -5.29 | 468.78 | 0 | 21.98 | 0 | OK | Ground clear controls. | 19 | 38.43 | 490.76
1176 | TIN-INTERP | Interpolated Ground | 7437.04 | 6.41 | 469.23 | 0 | 27.32 | 0 | OK | Ground clear controls. | 19 | 38.43 | 496.55
1177 | TIN-INTERP | Interpolated Ground | 7437.04 | 4.41 | 469.22 | 0 | 32.8 | 0 | OK | Ground clear controls. | 19 | 38.43 | 502.02
1178 | TIN-INTERP | Interpolated Ground | 7437.07 | 4.91 | 469.24 | 0 | 21.55 | 0 | OK | Ground clear controls. | 19 | 38.43 | 490.79
1179 | TIN-INTERP | Interpolated Ground | 7476.91 | -6.8 | 470.04 | 0 | 32.99 | 0 | OK | Ground clear controls. | 19 | 38.43 | 503.03
1180 | TIN-INTERP | Interpolated Ground | 7476.93 | -4.8 | 470.16 | 0 | 38.43 | 0 | OK | Ground clear controls. | 19 | 38.43 | 508.59
1181 | TIN-INTERP | Interpolated Ground | 7476.99 | -5.3 | 470.12 | 0 | 27.36 | 0 | OK | Ground clear controls. | 19 | 38.08 | 497.48
1182 | TIN-INTERP | Interpolated Ground | 7477.04 | 6.4 | 470.59 | 0 | 32.54 | 0 | OK | Ground clear controls. | 19 | 38.08 | 503.13
1183 | TIN-INTERP | Interpolated Ground | 7477.04 | 4.4 | 470.54 | 0 | 38.08 | 0 | OK | Ground clear controls. | 19 | 38.08 | 508.62
1184 | TIN-INTERP | Interpolated Ground | 7477.07 | 4.9 | 470.55 | 0 | 26.96 | 0 | OK | Ground clear controls. | 19 | 26.96 | 497.51
1185 | TIN-INTERP | Interpolated Ground | 7506.04 | 6.4 | 471.94 | 0 | 36.55 | 0 | OK | Ground clear controls. | 20 | 42.51 | 508.49
1186 | TIN-INTERP | Interpolated Ground | 7506.06 | 4.4 | 471.66 | 0 | 42.33 | 0 | OK | Ground clear controls. | 20 | 42.51 | 513.99
1187 | TIN-INTERP | Interpolated Ground | 7506.14 | -4.8 | 471.48 | 0 | 42.51 | 0 | OK | Ground clear controls. | 20 | 42.51 | 513.99
1188 | TIN-INTERP | Interpolated Ground | 7506.14 | 4.9 | 471.79 | 0 | 31.21 | 0 | OK | Ground clear controls. | 20 | 41.73 | 503
1189 | TIN-INTERP | Interpolated Ground | 7506.19 | -6.8 | 471.4 | 0 | 37.09 | 0 | OK | Ground clear controls. | 20 | 41.73 | 508.49
1190 | TIN-INTERP | Interpolated Ground | 7506.2 | -5.3 | 471.46 | 0 | 31.54 | 0 | OK | Ground clear controls. | 20 | 41.73 | 503
1191 | TIN-INTERP | Interpolated Ground | 7546.04 | 6.4 | 474.35 | 0 | 30.07 | 0 | OK | Ground clear controls. | 20 | 41.73 | 504.42
1192 | TIN-INTERP | Interpolated Ground | 7546.06 | 4.4 | 474.25 | 0 | 35.65 | 0 | OK | Ground clear controls. | 20 | 41.73 | 509.9
1193 | TIN-INTERP | Interpolated Ground | 7546.14 | -4.8 | 473.99 | 0 | 35.92 | 0 | OK | Ground clear controls. | 20 | 41.73 | 509.91
1194 | TIN-INTERP | Interpolated Ground | 7546.14 | 4.9 | 474.28 | 0 | 24.57 | 0 | OK | Ground clear controls. | 20 | 41.73 | 498.85
1195 | TIN-INTERP | Interpolated Ground | 7546.19 | -6.8 | 474.02 | 0 | 30.35 | 0 | OK | Ground clear controls. | 20 | 41.73 | 504.37
1196 | TIN-INTERP | Interpolated Ground | 7546.2 | -5.3 | 474 | 0 | 24.82 | 0 | OK | Ground clear controls. | 20 | 41.73 | 498.82
1197 | TIN-INTERP | Interpolated Ground | 7586.04 | 6.39 | 475.44 | 0 | 25.82 | 0 | OK | Ground clear controls. | 20 | 41.73 | 501.26
1198 | TIN-INTERP | Interpolated Ground | 7586.06 | 4.39 | 475.37 | 0 | 31.36 | 0 | OK | Ground clear controls. | 20 | 41.73 | 506.73
1199 | TIN-INTERP | Interpolated Ground | 7586.14 | -4.81 | 475.16 | 0 | 31.59 | 0 | OK | Ground clear controls. | 20 | 41.73 | 506.75
1200 | TIN-INTERP | Interpolated Ground | 7586.14 | 4.89 | 475.39 | 0 | 20.22 | 0 | OK | Ground clear controls. | 20 | 41.73 | 495.61
1201 | TIN-INTERP | Interpolated Ground | 7586.19 | -6.81 | 475.09 | 0 | 26.07 | 0 | OK | Ground clear controls. | 20 | 41.73 | 501.16
1202 | TIN-INTERP | Interpolated Ground | 7586.2 | -5.31 | 475.11 | 0 | 20.46 | 0 | OK | Ground clear controls. | 20 | 41.73 | 495.57
1203 | TIN-INTERP | Interpolated Ground | 7626.04 | 6.39 | 475.96 | 0 | 23.06 | 0 | OK | Ground clear controls. | 20 | 41.73 | 499.02
1204 | TIN-INTERP | Interpolated Ground | 7626.06 | 4.39 | 475.91 | 0 | 28.58 | 0 | OK | Ground clear controls. | 20 | 41.73 | 504.49
1205 | TIN-INTERP | Interpolated Ground | 7626.14 | -4.81 | 475.83 | 0 | 28.68 | 0 | OK | Ground clear controls. | 20 | 41.73 | 504.51
1206 | TIN-INTERP | Interpolated Ground | 7626.14 | 4.89 | 475.93 | 0 | 17.4 | 0 | OK | Ground clear controls. | 20 | 41.73 | 493.33
1207 | TIN-INTERP | Interpolated Ground | 7626.19 | -6.81 | 475.88 | 0 | 23.02 | 0 | OK | Ground clear controls. | 20 | 41.73 | 498.9
1208 | TIN-INTERP | Interpolated Ground | 7626.2 | -5.31 | 475.85 | 0 | 17.42 | 0 | OK | Ground clear controls. | 20 | 41.73 | 493.27
1209 | TIN-INTERP | Interpolated Ground | 7666.04 | 6.39 | 477.06 | 0 | 20.63 | 0 | OK | Ground clear controls. | 20 | 41.73 | 497.69
1210 | TIN-INTERP | Interpolated Ground | 7666.06 | 4.39 | 477.01 | 0 | 26.13 | 0 | OK | Ground clear controls. | 20 | 41.73 | 503.14
1211 | TIN-INTERP | Interpolated Ground | 7666.14 | -4.81 | 477 | 0 | 26.17 | 0 | OK | Ground clear controls. | 20 | 41.73 | 503.17
1212 | TIN-INTERP | Interpolated Ground | 7666.14 | 4.89 | 477.01 | 0 | 14.95 | 0 | OK | Ground clear controls. | 20 | 41.73 | 491.96
1213 | TIN-INTERP | Interpolated Ground | 7666.19 | -6.81 | 477.02 | 0 | 20.52 | 0 | OK | Ground clear controls. | 20 | 41.73 | 497.54
1214 | TIN-INTERP | Interpolated Ground | 7666.2 | -5.31 | 477 | 0 | 14.89 | 0 | OK | Ground clear controls. | 20 | 41.73 | 491.89
1215 | TIN-INTERP | Interpolated Ground | 7706.04 | 6.38 | 479.61 | 0 | 17.67 | 0 | OK | Ground clear controls. | 20 | 41.73 | 497.28
1216 | TIN-INTERP | Interpolated Ground | 7706.06 | 4.38 | 479.57 | 0 | 23.16 | 0 | OK | Ground clear controls. | 20 | 41.73 | 502.73
1217 | TIN-INTERP | Interpolated Ground | 7706.14 | -4.82 | 479.4 | 0 | 23.37 | 0 | OK | Ground clear controls. | 20 | 41.73 | 502.77
1218 | TIN-INTERP | Interpolated Ground | 7706.14 | 4.88 | 479.54 | 0 | 11.98 | 0 | OK | Ground clear controls. | 20 | 41.73 | 491.52
1219 | TIN-INTERP | Interpolated Ground | 7706.19 | -6.82 | 479.55 | 0 | 17.57 | 0 | OK | Ground clear controls. | 20 | 41.73 | 497.12
1220 | TIN-INTERP | Interpolated Ground | 7706.2 | -5.32 | 479.44 | 0 | 12.01 | 0 | OK | Ground clear controls. | 20 | 41.73 | 491.45
1221 | TIN-INTERP | Interpolated Ground | 7746.04 | 6.38 | 480.34 | 0 | 17.45 | 0 | OK | Ground clear controls. | 20 | 41.73 | 497.79
1222 | TIN-INTERP | Interpolated Ground | 7746.06 | 4.38 | 480.36 | 0 | 22.87 | 0 | OK | Ground clear controls. | 20 | 41.73 | 503.23
1223 | TIN-INTERP | Interpolated Ground | 7746.14 | -4.82 | 480.74 | 0 | 22.53 | 0 | OK | Ground clear controls. | 20 | 41.73 | 503.27
1224 | TIN-INTERP | Interpolated Ground | 7746.14 | 4.88 | 480.35 | 0 | 11.66 | 0 | OK | Ground clear controls. | 20 | 41.73 | 492.01
1225 | TIN-INTERP | Interpolated Ground | 7746.19 | -6.82 | 480.73 | 0 | 16.87 | 0 | OK | Ground clear controls. | 20 | 41.73 | 497.6
1226 | TIN-INTERP | Interpolated Ground | 7746.2 | -5.32 | 480.72 | 0 | 11.21 | 0 | OK | Ground clear controls. | 20 | 41.73 | 491.93
1227 | TIN-INTERP | Interpolated Ground | 7786.04 | 6.37 | 481.04 | 0 | 18.16 | 0 | OK | Ground clear controls. | 20 | 41.73 | 499.2
1228 | TIN-INTERP | Interpolated Ground | 7786.06 | 4.37 | 480.94 | 0 | 23.7 | 0 | OK | Ground clear controls. | 20 | 41.73 | 504.64
1229 | TIN-INTERP | Interpolated Ground | 7786.14 | -4.82 | 480.76 | 0 | 23.93 | 0 | OK | Ground clear controls. | 20 | 41.73 | 504.69
1230 | TIN-INTERP | Interpolated Ground | 7786.14 | 4.87 | 480.97 | 0 | 12.45 | 0 | OK | Ground clear controls. | 20 | 41.73 | 493.42
1231 | TIN-INTERP | Interpolated Ground | 7786.19 | -6.82 | 480.65 | 0 | 18.37 | 0 | OK | Ground clear controls. | 20 | 41.73 | 499.02
1232 | TIN-INTERP | Interpolated Ground | 7786.2 | -5.32 | 480.75 | 0 | 12.6 | 0 | OK | Ground clear controls. | 20 | 41.73 | 493.35
1233 | TIN-INTERP | Interpolated Ground | 7826.04 | 6.37 | 482.33 | 0 | 19.21 | 0 | OK | Ground clear controls. | 20 | 41.73 | 501.54
1234 | TIN-INTERP | Interpolated Ground | 7826.06 | 4.37 | 482.29 | 0 | 24.69 | 0 | OK | Ground clear controls. | 20 | 41.73 | 506.98
1235 | TIN-INTERP | Interpolated Ground | 7826.14 | -4.83 | 482.14 | 0 | 24.88 | 0 | OK | Ground clear controls. | 20 | 41.73 | 507.02
1236 | TIN-INTERP | Interpolated Ground | 7826.14 | 4.87 | 482.29 | 0 | 13.48 | 0 | OK | Ground clear controls. | 20 | 41.73 | 495.77
1237 | TIN-INTERP | Interpolated Ground | 7826.19 | -6.83 | 482.12 | 0 | 19.25 | 0 | OK | Ground clear controls. | 20 | 41.73 | 501.37
1238 | TIN-INTERP | Interpolated Ground | 7826.2 | -5.33 | 482.12 | 0 | 13.57 | 0 | OK | Ground clear controls. | 20 | 41.73 | 495.69
1239 | TIN-INTERP | Interpolated Ground | 7866.04 | 6.37 | 484.11 | 0 | 20.67 | 0 | OK | Ground clear controls. | 20 | 41.73 | 504.78
1240 | TIN-INTERP | Interpolated Ground | 7866.06 | 4.37 | 484.15 | 0 | 26.08 | 0 | OK | Ground clear controls. | 20 | 41.73 | 510.23
1241 | TIN-INTERP | Interpolated Ground | 7866.14 | -4.83 | 484.11 | 0 | 26.16 | 0 | OK | Ground clear controls. | 20 | 41.73 | 510.27
1242 | TIN-INTERP | Interpolated Ground | 7866.14 | 4.87 | 484.14 | 0 | 14.9 | 0 | OK | Ground clear controls. | 20 | 41.73 | 499.04
1243 | TIN-INTERP | Interpolated Ground | 7866.19 | -6.83 | 484.13 | 0 | 20.51 | 0 | OK | Ground clear controls. | 20 | 41.73 | 504.64
1244 | TIN-INTERP | Interpolated Ground | 7866.2 | -5.33 | 484.11 | 0 | 14.87 | 0 | OK | Ground clear controls. | 20 | 41.73 | 498.98
1245 | TIN-INTERP | Interpolated Ground | 7906.04 | 6.36 | 485.3 | 0 | 23.65 | 0 | OK | Ground clear controls. | 20 | 41.73 | 508.95
1246 | TIN-INTERP | Interpolated Ground | 7906.06 | 4.36 | 485.29 | 0 | 29.12 | 0 | OK | Ground clear controls. | 20 | 41.73 | 514.41
1247 | TIN-INTERP | Interpolated Ground | 7906.14 | -4.84 | 485.07 | 0 | 29.38 | 0 | OK | Ground clear controls. | 20 | 41.73 | 514.45
1248 | TIN-INTERP | Interpolated Ground | 7906.14 | 4.86 | 485.3 | 0 | 17.95 | 0 | OK | Ground clear controls. | 20 | 41.73 | 503.25
1249 | TIN-INTERP | Interpolated Ground | 7906.19 | -6.84 | 485.06 | 0 | 23.76 | 0 | OK | Ground clear controls. | 20 | 41.73 | 508.82
1250 | TIN-INTERP | Interpolated Ground | 7906.2 | -5.34 | 485.07 | 0 | 18.12 | 0 | OK | Ground clear controls. | 20 | 41.73 | 503.19
1251 | TIN-INTERP | Interpolated Ground | 7946.04 | 6.36 | 486.55 | 0 | 27.48 | 0 | OK | Ground clear controls. | 20 | 41.73 | 514.03
1252 | TIN-INTERP | Interpolated Ground | 7946.06 | 4.36 | 486.5 | 0 | 33 | 0 | OK | Ground clear controls. | 20 | 41.73 | 519.5
1253 | TIN-INTERP | Interpolated Ground | 7946.14 | -4.84 | 486.26 | 0 | 33.28 | 0 | OK | Ground clear controls. | 20 | 41.73 | 519.54
1254 | TIN-INTERP | Interpolated Ground | 7946.14 | 4.86 | 486.51 | 0 | 21.87 | 0 | OK | Ground clear controls. | 20 | 41.73 | 508.38
1255 | TIN-INTERP | Interpolated Ground | 7946.19 | -6.84 | 486.22 | 0 | 27.73 | 0 | OK | Ground clear controls. | 20 | 41.73 | 513.95
1256 | TIN-INTERP | Interpolated Ground | 7946.2 | -5.34 | 486.29 | 0 | 22.06 | 0 | OK | Ground clear controls. | 20 | 41.73 | 508.35
1257 | TIN-INTERP | Interpolated Ground | 7986.04 | 6.36 | 488.11 | 0 | 31.94 | 0 | OK | Ground clear controls. | 20 | 41.73 | 520.05
1258 | TIN-INTERP | Interpolated Ground | 7986.06 | 4.36 | 488.09 | 0 | 37.44 | 0 | OK | Ground clear controls. | 20 | 41.73 | 525.53
1259 | TIN-INTERP | Interpolated Ground | 7986.14 | -4.84 | 488.22 | 0 | 37.33 | 0 | OK | Ground clear controls. | 20 | 41.73 | 525.55
1260 | TIN-INTERP | Interpolated Ground | 7986.14 | 4.86 | 488.09 | 0 | 26.37 | 0 | OK | Ground clear controls. | 20 | 41.73 | 514.46
1261 | TIN-INTERP | Interpolated Ground | 7986.19 | -6.84 | 488.3 | 0 | 31.7 | 0 | OK | Ground clear controls. | 20 | 41.73 | 520
1262 | TIN-INTERP | Interpolated Ground | 7986.2 | -5.34 | 488.25 | 0 | 26.2 | 0 | OK | Ground clear controls. | 20 | 41.73 | 514.45
1263 | TIN-INTERP | Interpolated Ground | 8026.04 | 6.35 | 490.66 | 0 | 36.32 | 0 | OK | Ground clear controls. | 20 | 41.73 | 526.98
1264 | TIN-INTERP | Interpolated Ground | 8026.06 | 4.35 | 490.75 | 0 | 41.73 | 0 | OK | Ground clear controls. | 20 | 41.73 | 532.48
1265 | TIN-INTERP | Interpolated Ground | 8026.14 | -4.85 | 491.15 | 0 | 41.35 | 0 | OK | Ground clear controls. | 20 | 41.35 | 532.5
1266 | TIN-INTERP | Interpolated Ground | 8026.14 | 4.85 | 490.75 | 0 | 30.72 | 0 | OK | Ground clear controls. | 20 | 35.74 | 521.47
1267 | TIN-INTERP | Interpolated Ground | 8026.19 | -6.85 | 491.25 | 0 | 35.74 | 0 | OK | Ground clear controls. | 20 | 35.74 | 526.99
1268 | TIN-INTERP | Interpolated Ground | 8026.2 | -5.35 | 491.18 | 0 | 30.3 | 0 | OK | Ground clear controls. | 20 | 30.3 | 521.48
1269 | TIN-INTERP | Interpolated Ground | 8033.42 | 6.35 | 491.16 | 0 | 37.2 | 0 | OK | Ground clear controls. | 21 | 42.72 | 528.36
1270 | TIN-INTERP | Interpolated Ground | 8033.44 | -4.85 | 491.66 | 0 | 42.2 | 0 | OK | Ground clear controls. | 21 | 42.72 | 533.86
1271 | TIN-INTERP | Interpolated Ground | 8033.45 | 4.35 | 491.14 | 0 | 42.72 | 0 | OK | Ground clear controls. | 21 | 42.72 | 533.86
1272 | TIN-INTERP | Interpolated Ground | 8033.46 | -6.85 | 491.79 | 0 | 36.57 | 0 | OK | Ground clear controls. | 21 | 36.57 | 528.36
1273 | TIN-INTERP | Interpolated Ground | 8033.48 | -5.35 | 491.69 | 0 | 31.17 | 0 | OK | Ground clear controls. | 21 | 36.23 | 522.86
1274 | TIN-INTERP | Interpolated Ground | 8033.52 | 4.85 | 491.14 | 0 | 31.72 | 0 | OK | Ground clear controls. | 21 | 36.23 | 522.86
1275 | TIN-INTERP | Interpolated Ground | 8073.42 | 6.35 | 494.51 | 0 | 29.75 | 0 | OK | Ground clear controls. | 21 | 36.23 | 524.26
1276 | TIN-INTERP | Interpolated Ground | 8073.44 | -4.85 | 494 | 0 | 35.77 | 0 | OK | Ground clear controls. | 21 | 36.23 | 529.77
1277 | TIN-INTERP | Interpolated Ground | 8073.45 | 4.35 | 494.38 | 0 | 35.38 | 0 | OK | Ground clear controls. | 21 | 36.23 | 529.76
1278 | TIN-INTERP | Interpolated Ground | 8073.46 | -6.85 | 493.89 | 0 | 30.34 | 0 | OK | Ground clear controls. | 21 | 36.23 | 524.23
1279 | TIN-INTERP | Interpolated Ground | 8073.48 | -5.35 | 493.99 | 0 | 24.73 | 0 | OK | Ground clear controls. | 21 | 36.23 | 518.72
1280 | TIN-INTERP | Interpolated Ground | 8073.52 | 4.85 | 494.4 | 0 | 24.35 | 0 | OK | Ground clear controls. | 21 | 36.23 | 518.75
1281 | TIN-INTERP | Interpolated Ground | 8113.42 | 6.36 | 491.05 | 0 | 30.01 | 0 | OK | Ground clear controls. | 21 | 36.23 | 521.06
1282 | TIN-INTERP | Interpolated Ground | 8113.44 | -4.84 | 490.35 | 0 | 36.23 | 0 | OK | Ground clear controls. | 21 | 36.23 | 526.58
1283 | TIN-INTERP | Interpolated Ground | 8113.45 | 4.36 | 490.93 | 0 | 35.64 | 0 | OK | Ground clear controls. | 21 | 35.64 | 526.57
1284 | TIN-INTERP | Interpolated Ground | 8113.46 | -6.84 | 490.29 | 0 | 30.73 | 0 | OK | Ground clear controls. | 21 | 34.45 | 521.02
1285 | TIN-INTERP | Interpolated Ground | 8113.48 | -5.34 | 490.32 | 0 | 25.16 | 0 | OK | Ground clear controls. | 21 | 34.45 | 515.48
1286 | TIN-INTERP | Interpolated Ground | 8113.52 | 4.86 | 490.96 | 0 | 24.58 | 0 | OK | Ground clear controls. | 21 | 34.45 | 515.54
1287 | TIN-INTERP | Interpolated Ground | 8153.42 | 6.36 | 492.04 | 0 | 26.73 | 0 | OK | Ground clear controls. | 21 | 34.45 | 518.77
1288 | TIN-INTERP | Interpolated Ground | 8153.44 | -4.84 | 492.12 | 0 | 32.18 | 0 | OK | Ground clear controls. | 21 | 34.45 | 524.3
1289 | TIN-INTERP | Interpolated Ground | 8153.45 | 4.36 | 492.09 | 0 | 32.19 | 0 | OK | Ground clear controls. | 21 | 34.45 | 524.28
1290 | TIN-INTERP | Interpolated Ground | 8153.46 | -6.84 | 492.2 | 0 | 26.52 | 0 | OK | Ground clear controls. | 21 | 34.45 | 518.72
1291 | TIN-INTERP | Interpolated Ground | 8153.48 | -5.34 | 492.16 | 0 | 21 | 0 | OK | Ground clear controls. | 21 | 34.45 | 513.16
1292 | TIN-INTERP | Interpolated Ground | 8153.52 | 4.86 | 492.1 | 0 | 21.15 | 0 | OK | Ground clear controls. | 21 | 34.45 | 513.25
1293 | TIN-INTERP | Interpolated Ground | 8193.42 | 6.36 | 493.65 | 0 | 23.75 | 0 | OK | Ground clear controls. | 21 | 34.45 | 517.4
1294 | TIN-INTERP | Interpolated Ground | 8193.44 | -4.84 | 495.15 | 0 | 27.78 | 0 | OK | Ground clear controls. | 21 | 34.45 | 522.93
1295 | TIN-INTERP | Interpolated Ground | 8193.45 | 4.36 | 494.64 | 0 | 28.26 | 0 | OK | Ground clear controls. | 21 | 34.45 | 522.9
1296 | TIN-INTERP | Interpolated Ground | 8193.46 | -6.84 | 495.28 | 0 | 22.06 | 0 | OK | Ground clear controls. | 21 | 34.45 | 517.34
1297 | TIN-INTERP | Interpolated Ground | 8193.48 | -5.34 | 495.2 | 0 | 16.57 | 0 | OK | Ground clear controls. | 21 | 34.45 | 511.77
1298 | TIN-INTERP | Interpolated Ground | 8193.52 | 4.86 | 494.48 | 0 | 17.38 | 0 | OK | Ground clear controls. | 21 | 34.45 | 511.86
1299 | TIN-INTERP | Interpolated Ground | 8233.42 | 6.36 | 496.15 | 0 | 20.78 | 0 | OK | Ground clear controls. | 21 | 34.45 | 516.93
1300 | TIN-INTERP | Interpolated Ground | 8233.44 | -4.84 | 496.89 | 0 | 25.57 | 0 | OK | Ground clear controls. | 21 | 34.45 | 522.46
1301 | TIN-INTERP | Interpolated Ground | 8233.45 | 4.36 | 496.31 | 0 | 26.12 | 0 | OK | Ground clear controls. | 21 | 34.45 | 522.43
1302 | TIN-INTERP | Interpolated Ground | 8233.46 | -6.84 | 496.99 | 0 | 19.87 | 0 | OK | Ground clear controls. | 21 | 34.45 | 516.86
1303 | TIN-INTERP | Interpolated Ground | 8233.48 | -5.34 | 496.93 | 0 | 14.36 | 0 | OK | Ground clear controls. | 21 | 34.45 | 511.29
1304 | TIN-INTERP | Interpolated Ground | 8233.52 | 4.86 | 496.3 | 0 | 15.1 | 0 | OK | Ground clear controls. | 21 | 34.45 | 511.4
1305 | TIN-INTERP | Interpolated Ground | 8273.42 | 6.36 | 498.05 | 0 | 19.32 | 0 | OK | Ground clear controls. | 21 | 34.45 | 517.37
1306 | TIN-INTERP | Interpolated Ground | 8273.44 | -4.84 | 497.82 | 0 | 25.08 | 0 | OK | Ground clear controls. | 21 | 34.45 | 522.9
1307 | TIN-INTERP | Interpolated Ground | 8273.45 | 4.36 | 498.1 | 0 | 24.78 | 0 | OK | Ground clear controls. | 21 | 34.45 | 522.88
1308 | TIN-INTERP | Interpolated Ground | 8273.46 | -6.84 | 497.73 | 0 | 19.57 | 0 | OK | Ground clear controls. | 21 | 34.45 | 517.3
1309 | TIN-INTERP | Interpolated Ground | 8273.48 | -5.34 | 497.8 | 0 | 13.94 | 0 | OK | Ground clear controls. | 21 | 34.45 | 511.74
1310 | TIN-INTERP | Interpolated Ground | 8273.52 | 4.86 | 498.11 | 0 | 13.73 | 0 | OK | Ground clear controls. | 21 | 34.45 | 511.84
1311 | TIN-INTERP | Interpolated Ground | 8313.42 | 6.36 | 498.88 | 0 | 19.84 | 0 | OK | Ground clear controls. | 21 | 34.45 | 518.72
1312 | TIN-INTERP | Interpolated Ground | 8313.44 | -4.84 | 498.4 | 0 | 25.85 | 0 | OK | Ground clear controls. | 21 | 34.45 | 524.25
1313 | TIN-INTERP | Interpolated Ground | 8313.45 | 4.36 | 498.95 | 0 | 25.27 | 0 | OK | Ground clear controls. | 21 | 34.45 | 524.22
1314 | TIN-INTERP | Interpolated Ground | 8313.46 | -6.84 | 498.22 | 0 | 20.43 | 0 | OK | Ground clear controls. | 21 | 34.45 | 518.65
1315 | TIN-INTERP | Interpolated Ground | 8313.48 | -5.34 | 498.38 | 0 | 14.71 | 0 | OK | Ground clear controls. | 21 | 34.45 | 513.09
1316 | TIN-INTERP | Interpolated Ground | 8313.52 | 4.86 | 498.94 | 0 | 14.26 | 0 | OK | Ground clear controls. | 21 | 34.45 | 513.2
1317 | TIN-INTERP | Interpolated Ground | 8353.42 | 6.36 | 498.39 | 0 | 22.6 | 0 | OK | Ground clear controls. | 21 | 34.45 | 520.99
1318 | TIN-INTERP | Interpolated Ground | 8353.44 | -4.83 | 499.18 | 0 | 27.32 | 0 | OK | Ground clear controls. | 21 | 34.45 | 526.5
1319 | TIN-INTERP | Interpolated Ground | 8353.45 | 4.36 | 497.95 | 0 | 28.53 | 0 | OK | Ground clear controls. | 21 | 34.45 | 526.48
1320 | TIN-INTERP | Interpolated Ground | 8353.46 | -6.83 | 499.36 | 0 | 21.57 | 0 | OK | Ground clear controls. | 21 | 34.45 | 520.93
1321 | TIN-INTERP | Interpolated Ground | 8353.48 | -5.33 | 499.24 | 0 | 16.13 | 0 | OK | Ground clear controls. | 21 | 34.45 | 515.37
1322 | TIN-INTERP | Interpolated Ground | 8353.52 | 4.86 | 498.02 | 0 | 17.44 | 0 | OK | Ground clear controls. | 21 | 34.45 | 515.46
1323 | TIN-INTERP | Interpolated Ground | 8393.42 | 6.37 | 502.27 | 0 | 21.87 | 0 | OK | Ground clear controls. | 21 | 34.45 | 524.14
1324 | TIN-INTERP | Interpolated Ground | 8393.44 | -4.83 | 501.78 | 0 | 27.89 | 0 | OK | Ground clear controls. | 21 | 34.45 | 529.67
1325 | TIN-INTERP | Interpolated Ground | 8393.45 | 4.37 | 502.3 | 0 | 27.35 | 0 | OK | Ground clear controls. | 21 | 34.45 | 529.65
1326 | TIN-INTERP | Interpolated Ground | 8393.46 | -6.83 | 501.68 | 0 | 22.43 | 0 | OK | Ground clear controls. | 21 | 34.45 | 524.11
1327 | TIN-INTERP | Interpolated Ground | 8393.48 | -5.33 | 501.73 | 0 | 16.83 | 0 | OK | Ground clear controls. | 21 | 34.45 | 518.56
1328 | TIN-INTERP | Interpolated Ground | 8393.52 | 4.87 | 502.31 | 0 | 16.32 | 0 | OK | Ground clear controls. | 21 | 34.45 | 518.63
1329 | TIN-INTERP | Interpolated Ground | 8433.42 | 6.37 | 503.65 | 0 | 24.58 | 0 | OK | Ground clear controls. | 21 | 34.45 | 528.23
1330 | TIN-INTERP | Interpolated Ground | 8433.44 | -4.83 | 502.72 | 0 | 31.02 | 0 | OK | Ground clear controls. | 21 | 34.45 | 533.74
1331 | TIN-INTERP | Interpolated Ground | 8433.45 | 4.37 | 503.45 | 0 | 30.28 | 0 | OK | Ground clear controls. | 21 | 34.45 | 533.73
1332 | TIN-INTERP | Interpolated Ground | 8433.46 | -6.83 | 502.68 | 0 | 25.54 | 0 | OK | Ground clear controls. | 21 | 34.45 | 528.22
1333 | TIN-INTERP | Interpolated Ground | 8433.48 | -5.33 | 502.71 | 0 | 19.98 | 0 | OK | Ground clear controls. | 21 | 34.45 | 522.69
1334 | TIN-INTERP | Interpolated Ground | 8433.52 | 4.87 | 503.51 | 0 | 19.22 | 0 | OK | Ground clear controls. | 21 | 34.45 | 522.73
1335 | TIN-INTERP | Interpolated Ground | 8473.42 | 6.37 | 504.56 | 0 | 28.66 | 0 | OK | Ground clear controls. | 21 | 34.45 | 533.22
1336 | TIN-INTERP | Interpolated Ground | 8473.44 | -4.83 | 504.29 | 0 | 34.45 | 0 | OK | Ground clear controls. | 21 | 34.45 | 538.74
1337 | TIN-INTERP | Interpolated Ground | 8473.45 | 4.37 | 504.7 | 0 | 34.02 | 0 | OK | Ground clear controls. | 21 | 34.02 | 538.72
1338 | TIN-INTERP | Interpolated Ground | 8473.46 | -6.83 | 503.96 | 0 | 29.27 | 0 | OK | Ground clear controls. | 21 | 29.27 | 533.23
1339 | TIN-INTERP | Interpolated Ground | 8473.48 | -5.33 | 504.19 | 0 | 23.54 | 0 | OK | Ground clear controls. | 21 | 23.54 | 527.73
1340 | TIN-INTERP | Interpolated Ground | 8473.52 | 4.87 | 504.69 | 0 | 23.05 | 0 | OK | Ground clear controls. | 21 | 23.05 | 527.74
1341 | TIN-INTERP | Interpolated Ground | 8476.79 | -4.83 | 504.23 | 0 | 34.96 | 0 | OK | Ground clear controls. | 22 | 38.95 | 539.19
1342 | TIN-INTERP | Interpolated Ground | 8476.8 | -6.83 | 503.98 | 0 | 29.71 | 0 | OK | Ground clear controls. | 22 | 38.95 | 533.69
1343 | TIN-INTERP | Interpolated Ground | 8476.81 | -5.33 | 504.17 | 0 | 24.03 | 0 | OK | Ground clear controls. | 22 | 38.95 | 528.2
1344 | TIN-INTERP | Interpolated Ground | 8476.84 | 6.37 | 504.72 | 0 | 28.97 | 0 | OK | Ground clear controls. | 22 | 38.95 | 533.69
1345 | TIN-INTERP | Interpolated Ground | 8476.85 | 4.87 | 504.69 | 0 | 23.5 | 0 | OK | Ground clear controls. | 22 | 38.95 | 528.19
1346 | TIN-INTERP | Interpolated Ground | 8476.9 | 4.37 | 504.39 | 0 | 34.8 | 0 | OK | Ground clear controls. | 22 | 38.95 | 539.19
1347 | TIN-INTERP | Interpolated Ground | 8516.79 | -4.82 | 499.34 | 0 | 37.38 | 0 | OK | Ground clear controls. | 22 | 38.95 | 536.72
1348 | TIN-INTERP | Interpolated Ground | 8516.8 | -6.82 | 497.82 | 0 | 33.38 | 0 | OK | Ground clear controls. | 22 | 38.95 | 531.2
1349 | TIN-INTERP | Interpolated Ground | 8516.81 | -5.32 | 498.95 | 0 | 26.73 | 0 | OK | Ground clear controls. | 22 | 38.95 | 525.68
1350 | TIN-INTERP | Interpolated Ground | 8516.84 | 6.38 | 504.84 | 0 | 26.36 | 0 | OK | Ground clear controls. | 22 | 38.95 | 531.2
1351 | TIN-INTERP | Interpolated Ground | 8516.85 | 4.88 | 504.81 | 0 | 20.88 | 0 | OK | Ground clear controls. | 22 | 38.95 | 525.69
1352 | TIN-INTERP | Interpolated Ground | 8516.9 | 4.38 | 504.91 | 0 | 31.82 | 0 | OK | Ground clear controls. | 22 | 38.95 | 536.73
1353 | TIN-INTERP | Interpolated Ground | 8556.79 | -4.81 | 496.22 | 0 | 38.95 | 0 | OK | Ground clear controls. | 22 | 38.95 | 535.17
1354 | TIN-INTERP | Interpolated Ground | 8556.8 | -6.81 | 496.22 | 0 | 33.4 | 0 | OK | Ground clear controls. | 22 | 36.8 | 529.62
1355 | TIN-INTERP | Interpolated Ground | 8556.81 | -5.31 | 496.22 | 0 | 27.86 | 0 | OK | Ground clear controls. | 22 | 36.8 | 524.08
1356 | TIN-INTERP | Interpolated Ground | 8556.84 | 6.39 | 499.79 | 0 | 29.82 | 0 | OK | Ground clear controls. | 22 | 36.8 | 529.61
1357 | TIN-INTERP | Interpolated Ground | 8556.85 | 4.89 | 498.73 | 0 | 25.37 | 0 | OK | Ground clear controls. | 22 | 36.8 | 524.1
1358 | TIN-INTERP | Interpolated Ground | 8556.9 | 4.39 | 498.37 | 0 | 36.8 | 0 | OK | Ground clear controls. | 22 | 36.8 | 535.17
1359 | TIN-INTERP | Interpolated Ground | 8596.79 | -4.8 | 497.72 | 0 | 36.79 | 0 | OK | Ground clear controls. | 22 | 36.79 | 534.51
1360 | TIN-INTERP | Interpolated Ground | 8596.8 | -6.8 | 497.67 | 0 | 31.28 | 0 | OK | Ground clear controls. | 22 | 36.52 | 528.95
1361 | TIN-INTERP | Interpolated Ground | 8596.81 | -5.3 | 497.7 | 0 | 25.69 | 0 | OK | Ground clear controls. | 22 | 36.52 | 523.39
1362 | TIN-INTERP | Interpolated Ground | 8596.84 | 6.4 | 498.07 | 0 | 30.87 | 0 | OK | Ground clear controls. | 22 | 36.52 | 528.94
1363 | TIN-INTERP | Interpolated Ground | 8596.85 | 4.9 | 498.01 | 0 | 25.41 | 0 | OK | Ground clear controls. | 22 | 36.52 | 523.42
1364 | TIN-INTERP | Interpolated Ground | 8596.9 | 4.4 | 498.01 | 0 | 36.52 | 0 | OK | Ground clear controls. | 22 | 36.52 | 534.53
1365 | TIN-INTERP | Interpolated Ground | 8636.79 | -4.79 | 505.81 | 0 | 28.93 | 0 | OK | Ground clear controls. | 22 | 31.54 | 534.74
1366 | TIN-INTERP | Interpolated Ground | 8636.8 | -6.79 | 505.99 | 0 | 23.19 | 0 | OK | Ground clear controls. | 22 | 31.54 | 529.18
1367 | TIN-INTERP | Interpolated Ground | 8636.81 | -5.29 | 505.85 | 0 | 17.76 | 0 | OK | Ground clear controls. | 22 | 31.54 | 523.61
1368 | TIN-INTERP | Interpolated Ground | 8636.84 | 6.41 | 502.85 | 0 | 26.32 | 0 | OK | Ground clear controls. | 22 | 31.54 | 529.17
1369 | TIN-INTERP | Interpolated Ground | 8636.85 | 4.91 | 503.07 | 0 | 20.58 | 0 | OK | Ground clear controls. | 22 | 31.54 | 523.65
1370 | TIN-INTERP | Interpolated Ground | 8636.9 | 4.41 | 503.23 | 0 | 31.54 | 0 | OK | Ground clear controls. | 22 | 31.54 | 534.77
1371 | TIN-INTERP | Interpolated Ground | 8676.79 | -4.78 | 510.54 | 0 | 25.35 | 0 | OK | Ground clear controls. | 22 | 30.26 | 535.89
1372 | TIN-INTERP | Interpolated Ground | 8676.8 | -6.78 | 510.26 | 0 | 20.06 | 0 | OK | Ground clear controls. | 22 | 30.26 | 530.32
1373 | TIN-INTERP | Interpolated Ground | 8676.81 | -5.28 | 510.48 | 0 | 14.25 | 0 | OK | Ground clear controls. | 22 | 30.26 | 524.73
1374 | TIN-INTERP | Interpolated Ground | 8676.84 | 6.42 | 511.03 | 0 | 19.27 | 0 | OK | Ground clear controls. | 22 | 30.26 | 530.3
1375 | TIN-INTERP | Interpolated Ground | 8676.85 | 4.92 | 511.14 | 0 | 13.64 | 0 | OK | Ground clear controls. | 22 | 30.26 | 524.78
1376 | TIN-INTERP | Interpolated Ground | 8676.9 | 4.42 | 511.14 | 0 | 24.77 | 0 | OK | Ground clear controls. | 22 | 30.26 | 535.91
1377 | TIN-INTERP | Interpolated Ground | 8716.79 | -4.77 | 508.88 | 0 | 29.05 | 0 | OK | Ground clear controls. | 22 | 30.26 | 537.93
1378 | TIN-INTERP | Interpolated Ground | 8716.8 | -6.77 | 508.9 | 0 | 23.45 | 0 | OK | Ground clear controls. | 22 | 30.26 | 532.35
1379 | TIN-INTERP | Interpolated Ground | 8716.81 | -5.27 | 508.9 | 0 | 17.88 | 0 | OK | Ground clear controls. | 22 | 30.26 | 526.78
1380 | TIN-INTERP | Interpolated Ground | 8716.84 | 6.43 | 509.35 | 0 | 22.99 | 0 | OK | Ground clear controls. | 22 | 30.26 | 532.34
1381 | TIN-INTERP | Interpolated Ground | 8716.85 | 4.93 | 509.18 | 0 | 17.64 | 0 | OK | Ground clear controls. | 22 | 30.26 | 526.82
1382 | TIN-INTERP | Interpolated Ground | 8716.9 | 4.43 | 509.16 | 0 | 28.79 | 0 | OK | Ground clear controls. | 22 | 30.26 | 537.95
1383 | TIN-INTERP | Interpolated Ground | 8756.79 | -4.76 | 514.64 | 0 | 26.24 | 0 | OK | Ground clear controls. | 22 | 30.26 | 540.88
1384 | TIN-INTERP | Interpolated Ground | 8756.8 | -6.76 | 514.75 | 0 | 20.56 | 0 | OK | Ground clear controls. | 22 | 30.26 | 535.31
1385 | TIN-INTERP | Interpolated Ground | 8756.81 | -5.26 | 514.67 | 0 | 15.06 | 0 | OK | Ground clear controls. | 22 | 30.26 | 529.73
1386 | TIN-INTERP | Interpolated Ground | 8756.84 | 6.44 | 514.69 | 0 | 20.59 | 0 | OK | Ground clear controls. | 22 | 30.26 | 535.28
1387 | TIN-INTERP | Interpolated Ground | 8756.85 | 4.94 | 514.59 | 0 | 15.18 | 0 | OK | Ground clear controls. | 22 | 30.26 | 529.77
1388 | TIN-INTERP | Interpolated Ground | 8756.9 | 4.44 | 514.46 | 0 | 26.44 | 0 | OK | Ground clear controls. | 22 | 30.26 | 540.9
1389 | TIN-INTERP | Interpolated Ground | 8796.79 | -4.75 | 519.55 | 0 | 25.18 | 0 | OK | Ground clear controls. | 22 | 30.26 | 544.73
1390 | TIN-INTERP | Interpolated Ground | 8796.8 | -6.75 | 519.44 | 0 | 19.72 | 0 | OK | Ground clear controls. | 22 | 30.26 | 539.16
1391 | TIN-INTERP | Interpolated Ground | 8796.81 | -5.25 | 519.52 | 0 | 14.07 | 0 | OK | Ground clear controls. | 22 | 30.26 | 533.59
1392 | TIN-INTERP | Interpolated Ground | 8796.84 | 6.45 | 519.99 | 0 | 19.16 | 0 | OK | Ground clear controls. | 22 | 30.26 | 539.15
1393 | TIN-INTERP | Interpolated Ground | 8796.85 | 4.95 | 519.9 | 0 | 13.73 | 0 | OK | Ground clear controls. | 22 | 30.26 | 533.63
1394 | TIN-INTERP | Interpolated Ground | 8796.9 | 4.45 | 519.86 | 0 | 24.89 | 0 | OK | Ground clear controls. | 22 | 30.26 | 544.75
1395 | TIN-INTERP | Interpolated Ground | 8836.79 | -4.74 | 525.27 | 0 | 24.22 | 0 | OK | Ground clear controls. | 22 | 30.26 | 549.49
1396 | TIN-INTERP | Interpolated Ground | 8836.8 | -6.74 | 525.09 | 0 | 18.85 | 0 | OK | Ground clear controls. | 22 | 30.26 | 543.94
1397 | TIN-INTERP | Interpolated Ground | 8836.81 | -5.24 | 525.22 | 0 | 13.15 | 0 | OK | Ground clear controls. | 22 | 30.26 | 538.37
1398 | TIN-INTERP | Interpolated Ground | 8836.84 | 6.46 | 526.22 | 0 | 17.7 | 0 | OK | Ground clear controls. | 22 | 30.26 | 543.92
1399 | TIN-INTERP | Interpolated Ground | 8836.85 | 4.96 | 526.2 | 0 | 12.2 | 0 | OK | Ground clear controls. | 22 | 30.26 | 538.4
1400 | TIN-INTERP | Interpolated Ground | 8836.9 | 4.46 | 526.19 | 0 | 23.32 | 0 | OK | Ground clear controls. | 22 | 30.26 | 549.51
1401 | TIN-INTERP | Interpolated Ground | 8876.79 | -4.73 | 529.17 | 0 | 25.99 | 0 | OK | Ground clear controls. | 22 | 30.26 | 555.16
1402 | TIN-INTERP | Interpolated Ground | 8876.8 | -6.73 | 528.41 | 0 | 21.21 | 0 | OK | Ground clear controls. | 22 | 30.26 | 549.62
1403 | TIN-INTERP | Interpolated Ground | 8876.81 | -5.23 | 529.01 | 0 | 15.06 | 0 | OK | Ground clear controls. | 22 | 30.26 | 544.07
1404 | TIN-INTERP | Interpolated Ground | 8876.84 | 6.47 | 531.19 | 0 | 18.41 | 0 | OK | Ground clear controls. | 22 | 30.26 | 549.6
1405 | TIN-INTERP | Interpolated Ground | 8876.85 | 4.97 | 531.06 | 0 | 13.04 | 0 | OK | Ground clear controls. | 22 | 30.26 | 544.1
1406 | TIN-INTERP | Interpolated Ground | 8876.9 | 4.47 | 531.01 | 0 | 24.17 | 0 | OK | Ground clear controls. | 22 | 30.26 | 555.18
1407 | TIN-INTERP | Interpolated Ground | 8916.79 | -4.72 | 534.37 | 0 | 27.37 | 0 | OK | Ground clear controls. | 22 | 30.26 | 561.74
1408 | TIN-INTERP | Interpolated Ground | 8916.8 | -6.72 | 534.67 | 0 | 21.55 | 0 | OK | Ground clear controls. | 22 | 30.26 | 556.22
1409 | TIN-INTERP | Interpolated Ground | 8916.81 | -5.22 | 534.45 | 0 | 16.25 | 0 | OK | Ground clear controls. | 22 | 30.26 | 550.7
1410 | TIN-INTERP | Interpolated Ground | 8916.84 | 6.48 | 534.18 | 0 | 22.03 | 0 | OK | Ground clear controls. | 22 | 30.26 | 556.21
1411 | TIN-INTERP | Interpolated Ground | 8916.85 | 4.98 | 533.94 | 0 | 16.76 | 0 | OK | Ground clear controls. | 22 | 30.26 | 550.7
1412 | TIN-INTERP | Interpolated Ground | 8916.9 | 4.48 | 533.81 | 0 | 27.94 | 0 | OK | Ground clear controls. | 22 | 30.26 | 561.75
1413 | TIN-INTERP | Interpolated Ground | 8956.79 | -4.71 | 538.98 | 0 | 30.26 | 0 | OK | Ground clear controls. | 22 | 30.26 | 569.24
1414 | TIN-INTERP | Interpolated Ground | 8956.8 | -6.71 | 538.95 | 0 | 24.79 | 0 | OK | Ground clear controls. | 22 | 29.65 | 563.74
1415 | TIN-INTERP | Interpolated Ground | 8956.81 | -5.21 | 539.01 | 0 | 19.23 | 0 | OK | Ground clear controls. | 22 | 29.65 | 558.24
1416 | TIN-INTERP | Interpolated Ground | 8956.84 | 6.49 | 539.72 | 0 | 24.01 | 0 | OK | Ground clear controls. | 22 | 29.65 | 563.73
1417 | TIN-INTERP | Interpolated Ground | 8956.85 | 4.99 | 539.65 | 0 | 18.58 | 0 | OK | Ground clear controls. | 22 | 29.65 | 558.23
1418 | TIN-INTERP | Interpolated Ground | 8956.9 | 4.49 | 539.59 | 0 | 29.65 | 0 | OK | Ground clear controls. | 22 | 29.65 | 569.24
1419 | TIN-INTERP | Interpolated Ground | 8959.06 | -6.71 | 539.3 | 0 | 24.89 | 0 | OK | Ground clear controls. | 23 | 31.74 | 564.19
1420 | TIN-INTERP | Interpolated Ground | 8959.07 | -4.71 | 539.39 | 0 | 30.29 | 0 | OK | Ground clear controls. | 23 | 31.74 | 569.68
1421 | TIN-INTERP | Interpolated Ground | 8959.07 | -5.21 | 539.38 | 0 | 19.31 | 0 | OK | Ground clear controls. | 23 | 31.74 | 558.69
1422 | TIN-INTERP | Interpolated Ground | 8959.15 | 6.49 | 539.88 | 0 | 24.31 | 0 | OK | Ground clear controls. | 23 | 31.74 | 564.19
1423 | TIN-INTERP | Interpolated Ground | 8959.15 | 4.49 | 539.71 | 0 | 29.98 | 0 | OK | Ground clear controls. | 23 | 31.74 | 569.69
1424 | TIN-INTERP | Interpolated Ground | 8959.18 | 4.99 | 539.8 | 0 | 18.89 | 0 | OK | Ground clear controls. | 23 | 31.74 | 558.69
1425 | TIN-INTERP | Interpolated Ground | 8999.06 | -6.7 | 542.07 | 0 | 22.11 | 0 | OK | Ground clear controls. | 23 | 31.74 | 564.18
1426 | TIN-INTERP | Interpolated Ground | 8999.07 | -4.7 | 541.9 | 0 | 27.8 | 0 | OK | Ground clear controls. | 23 | 31.74 | 569.7
1427 | TIN-INTERP | Interpolated Ground | 8999.07 | -5.2 | 541.97 | 0 | 16.69 | 0 | OK | Ground clear controls. | 23 | 31.74 | 558.66
1428 | TIN-INTERP | Interpolated Ground | 8999.15 | 6.5 | 541.23 | 0 | 22.94 | 0 | OK | Ground clear controls. | 23 | 31.74 | 564.17
1429 | TIN-INTERP | Interpolated Ground | 8999.15 | 4.5 | 540.62 | 0 | 29.09 | 0 | OK | Ground clear controls. | 23 | 31.74 | 569.71
1430 | TIN-INTERP | Interpolated Ground | 8999.18 | 5 | 540.75 | 0 | 17.94 | 0 | OK | Ground clear controls. | 23 | 31.74 | 558.69
1431 | TIN-INTERP | Interpolated Ground | 9039.06 | -6.69 | 543.54 | 0 | 21.52 | 0 | OK | Ground clear controls. | 23 | 31.74 | 565.06
1432 | TIN-INTERP | Interpolated Ground | 9039.07 | -4.69 | 544.49 | 0 | 26.1 | 0 | OK | Ground clear controls. | 23 | 31.74 | 570.59
1433 | TIN-INTERP | Interpolated Ground | 9039.07 | -5.19 | 544.31 | 0 | 15.21 | 0 | OK | Ground clear controls. | 23 | 31.74 | 559.52
1434 | TIN-INTERP | Interpolated Ground | 9039.15 | 6.51 | 545.93 | 0 | 19.11 | 0 | OK | Ground clear controls. | 23 | 31.74 | 565.04
1435 | TIN-INTERP | Interpolated Ground | 9039.15 | 4.51 | 545.71 | 0 | 24.89 | 0 | OK | Ground clear controls. | 23 | 31.74 | 570.6
1436 | TIN-INTERP | Interpolated Ground | 9039.18 | 5.01 | 545.77 | 0 | 13.8 | 0 | OK | Ground clear controls. | 23 | 31.74 | 559.57
1437 | TIN-INTERP | Interpolated Ground | 9079.06 | -6.68 | 547.88 | 0 | 18.95 | 0 | OK | Ground clear controls. | 23 | 31.74 | 566.83
1438 | TIN-INTERP | Interpolated Ground | 9079.07 | -4.68 | 548.22 | 0 | 24.16 | 0 | OK | Ground clear controls. | 23 | 31.74 | 572.38
1439 | TIN-INTERP | Interpolated Ground | 9079.07 | -5.18 | 548.15 | 0 | 13.13 | 0 | OK | Ground clear controls. | 23 | 31.74 | 561.28
1440 | TIN-INTERP | Interpolated Ground | 9079.15 | 6.52 | 549.36 | 0 | 17.45 | 0 | OK | Ground clear controls. | 23 | 31.74 | 566.81
1441 | TIN-INTERP | Interpolated Ground | 9079.15 | 4.52 | 549.27 | 0 | 23.12 | 0 | OK | Ground clear controls. | 23 | 31.74 | 572.39
1442 | TIN-INTERP | Interpolated Ground | 9079.18 | 5.02 | 549.29 | 0 | 12.05 | 0 | OK | Ground clear controls. | 23 | 31.74 | 561.34
1443 | TIN-INTERP | Interpolated Ground | 9119.06 | -6.68 | 541.88 | 0 | 27.62 | 0 | OK | Ground clear controls. | 23 | 31.74 | 569.5
1444 | TIN-INTERP | Interpolated Ground | 9119.07 | -4.68 | 543.3 | 0 | 31.74 | 0 | OK | Ground clear controls. | 23 | 31.74 | 575.04
1445 | TIN-INTERP | Interpolated Ground | 9119.07 | -5.18 | 542.91 | 0 | 21.02 | 0 | OK | Ground clear controls. | 23 | 29.84 | 563.93
1446 | TIN-INTERP | Interpolated Ground | 9119.15 | 6.52 | 550.14 | 0 | 19.32 | 0 | OK | Ground clear controls. | 23 | 29.84 | 569.46
1447 | TIN-INTERP | Interpolated Ground | 9119.15 | 4.52 | 548.88 | 0 | 26.18 | 0 | OK | Ground clear controls. | 23 | 29.84 | 575.06
1448 | TIN-INTERP | Interpolated Ground | 9119.18 | 5.02 | 549.23 | 0 | 14.77 | 0 | OK | Ground clear controls. | 23 | 29.84 | 564
1449 | TIN-INTERP | Interpolated Ground | 9159.06 | -6.67 | 551.64 | 0 | 21.4 | 0 | OK | Ground clear controls. | 23 | 29.84 | 573.04
1450 | TIN-INTERP | Interpolated Ground | 9159.07 | -4.67 | 551.78 | 0 | 26.82 | 0 | OK | Ground clear controls. | 23 | 29.84 | 578.6
1451 | TIN-INTERP | Interpolated Ground | 9159.07 | -5.17 | 551.73 | 0 | 15.74 | 0 | OK | Ground clear controls. | 23 | 29.84 | 567.47
1452 | TIN-INTERP | Interpolated Ground | 9159.15 | 6.53 | 547.31 | 0 | 25.71 | 0 | OK | Ground clear controls. | 23 | 29.84 | 573.02
1453 | TIN-INTERP | Interpolated Ground | 9159.15 | 4.53 | 548.79 | 0 | 29.84 | 0 | OK | Ground clear controls. | 23 | 29.84 | 578.63
1454 | TIN-INTERP | Interpolated Ground | 9159.18 | 5.03 | 548.46 | 0 | 19.1 | 0 | OK | Ground clear controls. | 23 | 28.03 | 567.56
1455 | TIN-INTERP | Interpolated Ground | 9199.06 | -6.66 | 555.42 | 0 | 22.07 | 0 | OK | Ground clear controls. | 23 | 28.03 | 577.49
1456 | TIN-INTERP | Interpolated Ground | 9199.07 | -4.66 | 555.57 | 0 | 27.48 | 0 | OK | Ground clear controls. | 23 | 28.03 | 583.05
1457 | TIN-INTERP | Interpolated Ground | 9199.07 | -5.16 | 555.5 | 0 | 16.43 | 0 | OK | Ground clear controls. | 23 | 28.03 | 571.93
1458 | TIN-INTERP | Interpolated Ground | 9199.15 | 6.54 | 556.42 | 0 | 21.05 | 0 | OK | Ground clear controls. | 23 | 28.03 | 577.47
1459 | TIN-INTERP | Interpolated Ground | 9199.15 | 4.54 | 556.23 | 0 | 26.85 | 0 | OK | Ground clear controls. | 23 | 28.03 | 583.08
1460 | TIN-INTERP | Interpolated Ground | 9199.18 | 5.04 | 556.3 | 0 | 15.72 | 0 | OK | Ground clear controls. | 23 | 28.03 | 572.02
1461 | TIN-INTERP | Interpolated Ground | 9239.06 | -6.65 | 565.22 | 0 | 17.62 | 0 | OK | Ground clear controls. | 23 | 28.03 | 582.84
1462 | TIN-INTERP | Interpolated Ground | 9239.07 | -4.65 | 565.01 | 0 | 23.38 | 0 | OK | Ground clear controls. | 23 | 28.03 | 588.39
1463 | TIN-INTERP | Interpolated Ground | 9239.07 | -5.15 | 565.1 | 0 | 12.17 | 0 | OK | Ground clear controls. | 23 | 28.03 | 577.27
1464 | TIN-INTERP | Interpolated Ground | 9239.15 | 6.55 | 564.17 | 0 | 18.65 | 0 | OK | Ground clear controls. | 23 | 28.03 | 582.82
1465 | TIN-INTERP | Interpolated Ground | 9239.15 | 4.55 | 564.41 | 0 | 24.01 | 0 | OK | Ground clear controls. | 23 | 28.03 | 588.42
1466 | TIN-INTERP | Interpolated Ground | 9239.18 | 5.05 | 564.38 | 0 | 12.98 | 0 | OK | Ground clear controls. | 23 | 28.03 | 577.36
1467 | TIN-INTERP | Interpolated Ground | 9279.06 | -6.64 | 571.85 | 0 | 17.23 | 0 | OK | Ground clear controls. | 23 | 28.03 | 589.08
1468 | TIN-INTERP | Interpolated Ground | 9279.07 | -4.64 | 571.86 | 0 | 22.76 | 0 | OK | Ground clear controls. | 23 | 28.03 | 594.62
1469 | TIN-INTERP | Interpolated Ground | 9279.07 | -5.14 | 571.88 | 0 | 11.65 | 0 | OK | Ground clear controls. | 23 | 28.03 | 583.53
1470 | TIN-INTERP | Interpolated Ground | 9279.15 | 6.56 | 571 | 0 | 18.07 | 0 | OK | Ground clear controls. | 23 | 28.03 | 589.07
1471 | TIN-INTERP | Interpolated Ground | 9279.15 | 4.56 | 571.28 | 0 | 23.37 | 0 | OK | Ground clear controls. | 23 | 28.03 | 594.65
1472 | TIN-INTERP | Interpolated Ground | 9279.18 | 5.06 | 571.2 | 0 | 12.41 | 0 | OK | Ground clear controls. | 23 | 28.03 | 583.61
1473 | TIN-INTERP | Interpolated Ground | 9319.06 | -6.63 | 575.89 | 0 | 20.33 | 0 | OK | Ground clear controls. | 23 | 28.03 | 596.22
1474 | TIN-INTERP | Interpolated Ground | 9319.07 | -4.63 | 575.99 | 0 | 25.77 | 0 | OK | Ground clear controls. | 23 | 28.03 | 601.76
1475 | TIN-INTERP | Interpolated Ground | 9319.07 | -5.13 | 575.96 | 0 | 14.72 | 0 | OK | Ground clear controls. | 23 | 28.03 | 590.68
1476 | TIN-INTERP | Interpolated Ground | 9319.15 | 6.57 | 576.76 | 0 | 19.46 | 0 | OK | Ground clear controls. | 23 | 28.03 | 596.22
1477 | TIN-INTERP | Interpolated Ground | 9319.15 | 4.57 | 576.7 | 0 | 25.08 | 0 | OK | Ground clear controls. | 23 | 28.03 | 601.78
1478 | TIN-INTERP | Interpolated Ground | 9319.18 | 5.07 | 576.73 | 0 | 14.02 | 0 | OK | Ground clear controls. | 23 | 28.03 | 590.75
1479 | TIN-INTERP | Interpolated Ground | 9359.06 | -6.62 | 581.5 | 0 | 22.78 | 0 | OK | Ground clear controls. | 23 | 28.03 | 604.28
1480 | TIN-INTERP | Interpolated Ground | 9359.07 | -4.62 | 581.77 | 0 | 28.03 | 0 | OK | Ground clear controls. | 23 | 28.03 | 609.8
1481 | TIN-INTERP | Interpolated Ground | 9359.07 | -5.12 | 581.7 | 0 | 17.06 | 0 | OK | Ground clear controls. | 23 | 27.69 | 598.76
1482 | TIN-INTERP | Interpolated Ground | 9359.15 | 6.58 | 582.18 | 0 | 22.11 | 0 | OK | Ground clear controls. | 23 | 27.69 | 604.29
1483 | TIN-INTERP | Interpolated Ground | 9359.15 | 4.58 | 582.13 | 0 | 27.69 | 0 | OK | Ground clear controls. | 23 | 27.69 | 609.82
1484 | TIN-INTERP | Interpolated Ground | 9359.18 | 5.08 | 582.15 | 0 | 16.66 | 0 | OK | Ground clear controls. | 23 | 16.66 | 598.81
1485 | TIN-INTERP | Interpolated Ground | 9392.61 | 5.08 | 585.69 | 0 | 20.55 | 0 | OK | Ground clear controls. | 24 | 56.56 | 606.24
1486 | TIN-INTERP | Interpolated Ground | 9392.63 | 4.58 | 585.6 | 0 | 31.64 | 0 | OK | Ground clear controls. | 24 | 56.56 | 617.24
1487 | TIN-INTERP | Interpolated Ground | 9392.63 | -4.62 | 585.35 | 0 | 31.88 | 0 | OK | Ground clear controls. | 24 | 56.56 | 617.23
1488 | TIN-INTERP | Interpolated Ground | 9392.66 | -6.62 | 585.21 | 0 | 26.53 | 0 | OK | Ground clear controls. | 24 | 56.56 | 611.74
1489 | TIN-INTERP | Interpolated Ground | 9392.66 | 6.58 | 585.86 | 0 | 25.88 | 0 | OK | Ground clear controls. | 24 | 56.56 | 611.74
1490 | TIN-INTERP | Interpolated Ground | 9392.72 | -5.12 | 585.32 | 0 | 20.92 | 0 | OK | Ground clear controls. | 24 | 56.56 | 606.24
1491 | TIN-INTERP | Interpolated Ground | 9432.61 | 5.08 | 584.25 | 0 | 22.87 | 0 | OK | Ground clear controls. | 24 | 56.56 | 607.12
1492 | TIN-INTERP | Interpolated Ground | 9432.63 | 4.58 | 584.08 | 0 | 34.06 | 0 | OK | Ground clear controls. | 24 | 56.56 | 618.14
1493 | TIN-INTERP | Interpolated Ground | 9432.63 | -4.62 | 580.74 | 0 | 37.4 | 0 | OK | Ground clear controls. | 24 | 56.56 | 618.14
1494 | TIN-INTERP | Interpolated Ground | 9432.66 | -6.62 | 579.91 | 0 | 32.73 | 0 | OK | Ground clear controls. | 24 | 56.56 | 612.64
1495 | TIN-INTERP | Interpolated Ground | 9432.66 | 6.58 | 584.88 | 0 | 27.75 | 0 | OK | Ground clear controls. | 24 | 56.56 | 612.63
1496 | TIN-INTERP | Interpolated Ground | 9432.72 | -5.12 | 580.48 | 0 | 26.67 | 0 | OK | Ground clear controls. | 24 | 56.56 | 607.15
1497 | TIN-INTERP | Interpolated Ground | 9472.61 | 5.07 | 567.31 | 0 | 41.56 | 0 | OK | Ground clear controls. | 24 | 56.56 | 608.87
1498 | TIN-INTERP | Interpolated Ground | 9472.63 | 4.57 | 567.05 | 0 | 52.87 | 0 | OK | Ground clear controls. | 24 | 56.56 | 619.92
1499 | TIN-INTERP | Interpolated Ground | 9472.63 | -4.63 | 563.35 | 0 | 56.56 | 0 | OK | Ground clear controls. | 24 | 56.56 | 619.91
1500 | TIN-INTERP | Interpolated Ground | 9472.66 | -6.63 | 563.28 | 0 | 51.12 | 0 | OK | Ground clear controls. | 24 | 51.12 | 614.4
1501 | TIN-INTERP | Interpolated Ground | 9472.66 | 6.57 | 568.25 | 0 | 46.14 | 0 | OK | Ground clear controls. | 24 | 49.19 | 614.39
1502 | TIN-INTERP | Interpolated Ground | 9472.72 | -5.13 | 563.36 | 0 | 45.56 | 0 | OK | Ground clear controls. | 24 | 49.19 | 608.92
1503 | TIN-INTERP | Interpolated Ground | 9512.61 | 5.06 | 573.06 | 0 | 38.44 | 0 | OK | Ground clear controls. | 24 | 49.19 | 611.5
1504 | TIN-INTERP | Interpolated Ground | 9512.63 | 4.56 | 573.37 | 0 | 49.19 | 0 | OK | Ground clear controls. | 24 | 49.19 | 622.56
1505 | TIN-INTERP | Interpolated Ground | 9512.63 | -4.64 | 579.42 | 0 | 43.15 | 0 | OK | Ground clear controls. | 24 | 44.69 | 622.57
1506 | TIN-INTERP | Interpolated Ground | 9512.66 | -6.64 | 580.85 | 0 | 36.2 | 0 | OK | Ground clear controls. | 24 | 44.69 | 617.05
1507 | TIN-INTERP | Interpolated Ground | 9512.66 | 6.56 | 572.33 | 0 | 44.69 | 0 | OK | Ground clear controls. | 24 | 44.69 | 617.02
1508 | TIN-INTERP | Interpolated Ground | 9512.72 | -5.14 | 579.95 | 0 | 31.61 | 0 | OK | Ground clear controls. | 24 | 39.3 | 611.56
1509 | TIN-INTERP | Interpolated Ground | 9552.61 | 5.06 | 586.38 | 0 | 28.63 | 0 | OK | Ground clear controls. | 24 | 39.3 | 615.01
1510 | TIN-INTERP | Interpolated Ground | 9552.63 | 4.56 | 586.78 | 0 | 39.3 | 0 | OK | Ground clear controls. | 24 | 39.3 | 626.08
1511 | TIN-INTERP | Interpolated Ground | 9552.63 | -4.64 | 591.02 | 0 | 35.06 | 0 | OK | Ground clear controls. | 24 | 35.23 | 626.08
1512 | TIN-INTERP | Interpolated Ground | 9552.66 | -6.64 | 592.08 | 0 | 28.48 | 0 | OK | Ground clear controls. | 24 | 35.23 | 620.56
1513 | TIN-INTERP | Interpolated Ground | 9552.66 | 6.56 | 585.3 | 0 | 35.23 | 0 | OK | Ground clear controls. | 24 | 35.23 | 620.53
1514 | TIN-INTERP | Interpolated Ground | 9552.72 | -5.14 | 591.31 | 0 | 23.77 | 0 | OK | Ground clear controls. | 24 | 35.23 | 615.08
1515 | TIN-INTERP | Interpolated Ground | 9592.61 | 5.05 | 600.05 | 0 | 19.34 | 0 | OK | Ground clear controls. | 24 | 35.23 | 619.39
1516 | TIN-INTERP | Interpolated Ground | 9592.63 | 4.55 | 600.2 | 0 | 30.27 | 0 | OK | Ground clear controls. | 24 | 35.23 | 630.47
1517 | TIN-INTERP | Interpolated Ground | 9592.63 | -4.65 | 604.02 | 0 | 26.45 | 0 | OK | Ground clear controls. | 24 | 35.23 | 630.47
1518 | TIN-INTERP | Interpolated Ground | 9592.66 | -6.65 | 604.99 | 0 | 19.97 | 0 | OK | Ground clear controls. | 24 | 35.23 | 624.96
1519 | TIN-INTERP | Interpolated Ground | 9592.66 | 6.55 | 599.32 | 0 | 25.6 | 0 | OK | Ground clear controls. | 24 | 35.23 | 624.92
1520 | TIN-INTERP | Interpolated Ground | 9592.72 | -5.15 | 604.28 | 0 | 15.19 | 0 | OK | Ground clear controls. | 24 | 35.23 | 619.47
1521 | TIN-INTERP | Interpolated Ground | 9632.61 | 5.04 | 607.2 | 0 | 17.46 | 0 | OK | Ground clear controls. | 24 | 35.23 | 624.66
1522 | TIN-INTERP | Interpolated Ground | 9632.63 | 4.54 | 607.47 | 0 | 28.26 | 0 | OK | Ground clear controls. | 24 | 35.23 | 635.73
1523 | TIN-INTERP | Interpolated Ground | 9632.63 | -4.66 | 612.87 | 0 | 22.87 | 0 | OK | Ground clear controls. | 24 | 35.23 | 635.74
1524 | TIN-INTERP | Interpolated Ground | 9632.66 | -6.66 | 613.87 | 0 | 16.35 | 0 | OK | Ground clear controls. | 24 | 35.23 | 630.22
1525 | TIN-INTERP | Interpolated Ground | 9632.66 | 6.54 | 605.53 | 0 | 24.66 | 0 | OK | Ground clear controls. | 24 | 35.23 | 630.19
1526 | TIN-INTERP | Interpolated Ground | 9632.72 | -5.16 | 613.18 | 0 | 11.56 | 0 | OK | Ground clear controls. | 24 | 35.23 | 624.74
1527 | TIN-INTERP | Interpolated Ground | 9672.61 | 5.04 | 608.4 | 0 | 22.42 | 0 | OK | Ground clear controls. | 24 | 35.23 | 630.82
1528 | TIN-INTERP | Interpolated Ground | 9672.63 | 4.54 | 608.86 | 0 | 33.02 | 0 | OK | Ground clear controls. | 24 | 35.23 | 641.88
1529 | TIN-INTERP | Interpolated Ground | 9672.63 | -4.66 | 614.99 | 0 | 26.89 | 0 | OK | Ground clear controls. | 24 | 35.23 | 641.88
1530 | TIN-INTERP | Interpolated Ground | 9672.66 | -6.66 | 615.97 | 0 | 20.41 | 0 | OK | Ground clear controls. | 24 | 35.23 | 636.38
1531 | TIN-INTERP | Interpolated Ground | 9672.66 | 6.54 | 607.11 | 0 | 29.22 | 0 | OK | Ground clear controls. | 24 | 35.23 | 636.33
1532 | TIN-INTERP | Interpolated Ground | 9672.72 | -5.16 | 615.26 | 0 | 15.62 | 0 | OK | Ground clear controls. | 24 | 35.23 | 630.88
1533 | TIN-INTERP | Interpolated Ground | 9712.61 | 5.03 | 615.22 | 0 | 22.64 | 0 | OK | Ground clear controls. | 24 | 35.23 | 637.86
1534 | TIN-INTERP | Interpolated Ground | 9712.63 | 4.53 | 614.93 | 0 | 33.97 | 0 | OK | Ground clear controls. | 24 | 35.23 | 648.9
1535 | TIN-INTERP | Interpolated Ground | 9712.63 | -4.67 | 613.68 | 0 | 35.23 | 0 | OK | Ground clear controls. | 24 | 35.23 | 648.91
1536 | TIN-INTERP | Interpolated Ground | 9712.66 | -6.67 | 615.36 | 0 | 28.04 | 0 | OK | Ground clear controls. | 24 | 28.4 | 643.4
1537 | TIN-INTERP | Interpolated Ground | 9712.66 | 6.53 | 616.23 | 0 | 27.13 | 0 | OK | Ground clear controls. | 24 | 28.4 | 643.36
1538 | TIN-INTERP | Interpolated Ground | 9712.72 | -5.17 | 614.04 | 0 | 23.88 | 0 | OK | Ground clear controls. | 24 | 28.4 | 637.92
1539 | TIN-INTERP | Interpolated Ground | 9752.61 | 5.02 | 628.4 | 0 | 17.38 | 0 | OK | Ground clear controls. | 24 | 28.4 | 645.78
1540 | TIN-INTERP | Interpolated Ground | 9752.63 | 4.52 | 628.4 | 0 | 28.4 | 0 | OK | Ground clear controls. | 24 | 28.4 | 656.8
1541 | TIN-INTERP | Interpolated Ground | 9752.63 | -4.67 | 630.14 | 0 | 26.68 | 0 | OK | Ground clear controls. | 24 | 26.68 | 656.82
1542 | TIN-INTERP | Interpolated Ground | 9752.66 | -6.67 | 630.46 | 0 | 20.86 | 0 | OK | Ground clear controls. | 24 | 23.09 | 651.32
1543 | TIN-INTERP | Interpolated Ground | 9752.66 | 6.52 | 628.2 | 0 | 23.09 | 0 | OK | Ground clear controls. | 24 | 23.09 | 651.29
1544 | TIN-INTERP | Interpolated Ground | 9752.72 | -5.17 | 630.2 | 0 | 15.64 | 0 | OK | Ground clear controls. | 24 | 15.64 | 645.84
1545 | TIN-INTERP | Interpolated Ground | 9778.22 | -5.18 | 635.24 | 0 | 16.1 | 0 | OK | Ground clear controls. | 25 | 31.41 | 651.34
1546 | TIN-INTERP | Interpolated Ground | 9778.24 | -6.68 | 635.22 | 0 | 21.63 | 0 | OK | Ground clear controls. | 25 | 31.41 | 656.85
1547 | TIN-INTERP | Interpolated Ground | 9778.26 | 5.02 | 635.13 | 0 | 16.22 | 0 | OK | Ground clear controls. | 25 | 31.41 | 651.35
1548 | TIN-INTERP | Interpolated Ground | 9778.26 | -4.68 | 635.27 | 0 | 27.08 | 0 | OK | Ground clear controls. | 25 | 31.41 | 662.35
1549 | TIN-INTERP | Interpolated Ground | 9778.31 | 4.52 | 635.24 | 0 | 27.11 | 0 | OK | Ground clear controls. | 25 | 31.41 | 662.35
1550 | TIN-INTERP | Interpolated Ground | 9778.34 | 6.52 | 634.7 | 0 | 22.15 | 0 | OK | Ground clear controls. | 25 | 31.41 | 656.85
1551 | TIN-INTERP | Interpolated Ground | 9818.22 | -5.13 | 638.21 | 0 | 15.13 | 0 | OK | Ground clear controls. | 25 | 31.41 | 653.34
1552 | TIN-INTERP | Interpolated Ground | 9818.24 | -6.63 | 637.96 | 0 | 20.88 | 0 | OK | Ground clear controls. | 25 | 31.41 | 658.84
1553 | TIN-INTERP | Interpolated Ground | 9818.26 | 5.07 | 639.19 | 0 | 14.13 | 0 | OK | Ground clear controls. | 25 | 31.41 | 653.32
1554 | TIN-INTERP | Interpolated Ground | 9818.26 | -4.63 | 638.29 | 0 | 26.06 | 0 | OK | Ground clear controls. | 25 | 31.41 | 664.35
1555 | TIN-INTERP | Interpolated Ground | 9818.31 | 4.57 | 639.17 | 0 | 25.18 | 0 | OK | Ground clear controls. | 25 | 31.41 | 664.35
1556 | TIN-INTERP | Interpolated Ground | 9818.34 | 6.57 | 639.36 | 0 | 19.48 | 0 | OK | Ground clear controls. | 25 | 31.41 | 658.84
1557 | TIN-INTERP | Interpolated Ground | 9858.22 | -5.08 | 639.4 | 0 | 16.79 | 0 | OK | Ground clear controls. | 25 | 31.41 | 656.19
1558 | TIN-INTERP | Interpolated Ground | 9858.24 | -6.58 | 639.16 | 0 | 22.55 | 0 | OK | Ground clear controls. | 25 | 31.41 | 661.71
1559 | TIN-INTERP | Interpolated Ground | 9858.26 | 5.12 | 641.84 | 0 | 14.33 | 0 | OK | Ground clear controls. | 25 | 31.41 | 656.17
1560 | TIN-INTERP | Interpolated Ground | 9858.26 | -4.58 | 639.51 | 0 | 27.69 | 0 | OK | Ground clear controls. | 25 | 31.41 | 667.2
1561 | TIN-INTERP | Interpolated Ground | 9858.31 | 4.62 | 641.8 | 0 | 25.4 | 0 | OK | Ground clear controls. | 25 | 31.41 | 667.2
1562 | TIN-INTERP | Interpolated Ground | 9858.34 | 6.62 | 642.04 | 0 | 19.65 | 0 | OK | Ground clear controls. | 25 | 31.41 | 661.69
1563 | TIN-INTERP | Interpolated Ground | 9898.22 | -5.03 | 642.05 | 0 | 17.86 | 0 | OK | Ground clear controls. | 25 | 31.41 | 659.91
1564 | TIN-INTERP | Interpolated Ground | 9898.24 | -6.53 | 641.41 | 0 | 24.01 | 0 | OK | Ground clear controls. | 25 | 31.41 | 665.42
1565 | TIN-INTERP | Interpolated Ground | 9898.26 | 5.16 | 645.06 | 0 | 14.82 | 0 | OK | Ground clear controls. | 25 | 31.41 | 659.88
1566 | TIN-INTERP | Interpolated Ground | 9898.26 | -4.53 | 642.16 | 0 | 28.76 | 0 | OK | Ground clear controls. | 25 | 31.41 | 670.92
1567 | TIN-INTERP | Interpolated Ground | 9898.31 | 4.67 | 644.97 | 0 | 25.95 | 0 | OK | Ground clear controls. | 25 | 31.41 | 670.92
1568 | TIN-INTERP | Interpolated Ground | 9898.34 | 6.66 | 645.24 | 0 | 20.17 | 0 | OK | Ground clear controls. | 25 | 31.41 | 665.41
1569 | TIN-INTERP | Interpolated Ground | 9938.22 | -4.99 | 646.27 | 0 | 18.22 | 0 | OK | Ground clear controls. | 25 | 31.41 | 664.49
1570 | TIN-INTERP | Interpolated Ground | 9938.24 | -6.49 | 646.72 | 0 | 23.28 | 0 | OK | Ground clear controls. | 25 | 31.41 | 670
1571 | TIN-INTERP | Interpolated Ground | 9938.26 | 5.21 | 644.35 | 0 | 20.13 | 0 | OK | Ground clear controls. | 25 | 31.41 | 664.48
1572 | TIN-INTERP | Interpolated Ground | 9938.26 | -4.49 | 646.17 | 0 | 29.33 | 0 | OK | Ground clear controls. | 25 | 31.41 | 675.5
1573 | TIN-INTERP | Interpolated Ground | 9938.31 | 4.71 | 644.09 | 0 | 31.41 | 0 | OK | Ground clear controls. | 25 | 31.41 | 675.5
1574 | TIN-INTERP | Interpolated Ground | 9938.34 | 6.71 | 645.09 | 0 | 24.9 | 0 | OK | Ground clear controls. | 25 | 24.9 | 669.99
1575 | TIN-INTERP | Interpolated Ground | 9962.17 | -6.46 | 652.39 | 0 | 20.76 | 0 | OK | Ground clear controls. | 26 | 43.05 | 673.15
1576 | TIN-INTERP | Interpolated Ground | 9962.2 | -4.46 | 652.79 | 0 | 25.87 | 0 | OK | Ground clear controls. | 26 | 43.05 | 678.66
1577 | TIN-INTERP | Interpolated Ground | 9962.28 | 4.74 | 653.81 | 0 | 24.85 | 0 | OK | Ground clear controls. | 26 | 43.05 | 678.66
1578 | TIN-INTERP | Interpolated Ground | 9962.34 | 6.74 | 653.82 | 0 | 19.34 | 0 | OK | Ground clear controls. | 26 | 43.05 | 673.16
1579 | TIN-INTERP | Interpolated Ground | 9962.48 | -4.96 | 652.75 | 0 | 14.94 | 0 | OK | Ground clear controls. | 26 | 43.05 | 667.69
1580 | TIN-INTERP | Interpolated Ground | 9962.6 | 5.24 | 653.89 | 0 | 13.8 | 0 | OK | Ground clear controls. | 26 | 43.05 | 667.69
1581 | TIN-INTERP | Interpolated Ground | 10002.17 | -6.48 | 657.9 | 0 | 16.86 | 0 | OK | Ground clear controls. | 26 | 43.05 | 674.76
1582 | TIN-INTERP | Interpolated Ground | 10002.2 | -4.48 | 657.97 | 0 | 22.3 | 0 | OK | Ground clear controls. | 26 | 43.05 | 680.27
1583 | TIN-INTERP | Interpolated Ground | 10002.28 | 4.72 | 659.02 | 0 | 21.24 | 0 | OK | Ground clear controls. | 26 | 43.05 | 680.26
1584 | TIN-INTERP | Interpolated Ground | 10002.34 | 6.72 | 659.32 | 0 | 15.44 | 0 | OK | Ground clear controls. | 26 | 43.05 | 674.76
1585 | TIN-INTERP | Interpolated Ground | 10002.48 | -4.98 | 657.96 | 0 | 11.36 | 0 | OK | Ground clear controls. | 26 | 43.05 | 669.32
1586 | TIN-INTERP | Interpolated Ground | 10002.6 | 5.22 | 659.13 | 0 | 10.17 | 0 | OK | Ground clear controls. | 26 | 43.05 | 669.3
1587 | TIN-INTERP | Interpolated Ground | 10042.17 | -6.5 | 659.71 | 0 | 17.51 | 0 | OK | Ground clear controls. | 26 | 43.05 | 677.22
1588 | TIN-INTERP | Interpolated Ground | 10042.2 | -4.5 | 659.89 | 0 | 22.84 | 0 | OK | Ground clear controls. | 26 | 43.05 | 682.73
1589 | TIN-INTERP | Interpolated Ground | 10042.28 | 4.7 | 660.78 | 0 | 21.95 | 0 | OK | Ground clear controls. | 26 | 43.05 | 682.73
1590 | TIN-INTERP | Interpolated Ground | 10042.34 | 6.7 | 660.88 | 0 | 16.34 | 0 | OK | Ground clear controls. | 26 | 43.05 | 677.22
1591 | TIN-INTERP | Interpolated Ground | 10042.48 | -5 | 659.87 | 0 | 11.91 | 0 | OK | Ground clear controls. | 26 | 43.05 | 671.78
1592 | TIN-INTERP | Interpolated Ground | 10042.6 | 5.2 | 660.85 | 0 | 10.92 | 0 | OK | Ground clear controls. | 26 | 43.05 | 671.77
1593 | TIN-INTERP | Interpolated Ground | 10082.17 | -6.52 | 643.32 | 0 | 37.22 | 0 | OK | Ground clear controls. | 26 | 43.05 | 680.54
1594 | TIN-INTERP | Interpolated Ground | 10082.2 | -4.52 | 643 | 0 | 43.05 | 0 | OK | Ground clear controls. | 26 | 43.05 | 686.05
1595 | TIN-INTERP | Interpolated Ground | 10082.28 | 4.68 | 644 | 0 | 42.05 | 0 | OK | Ground clear controls. | 26 | 42.05 | 686.05
1596 | TIN-INTERP | Interpolated Ground | 10082.34 | 6.68 | 644.78 | 0 | 35.76 | 0 | OK | Ground clear controls. | 26 | 37.68 | 680.54
1597 | TIN-INTERP | Interpolated Ground | 10082.48 | -5.02 | 642.86 | 0 | 32.25 | 0 | OK | Ground clear controls. | 26 | 37.68 | 675.11
1598 | TIN-INTERP | Interpolated Ground | 10082.6 | 5.17 | 644.02 | 0 | 31.07 | 0 | OK | Ground clear controls. | 26 | 37.68 | 675.09
1599 | TIN-INTERP | Interpolated Ground | 10122.17 | -6.55 | 651.02 | 0 | 33.7 | 0 | OK | Ground clear controls. | 26 | 37.68 | 684.72
1600 | TIN-INTERP | Interpolated Ground | 10122.2 | -4.55 | 652.54 | 0 | 37.68 | 0 | OK | Ground clear controls. | 26 | 37.68 | 690.22
1601 | TIN-INTERP | Interpolated Ground | 10122.28 | 4.65 | 656.69 | 0 | 33.54 | 0 | OK | Ground clear controls. | 26 | 33.54 | 690.23
1602 | TIN-INTERP | Interpolated Ground | 10122.34 | 6.65 | 656.79 | 0 | 27.93 | 0 | OK | Ground clear controls. | 26 | 27.93 | 684.72
1603 | TIN-INTERP | Interpolated Ground | 10122.48 | -5.05 | 652.26 | 0 | 27.01 | 0 | OK | Ground clear controls. | 26 | 27.01 | 679.27
1604 | TIN-INTERP | Interpolated Ground | 10122.6 | 5.15 | 657.29 | 0 | 21.97 | 0 | OK | Ground clear controls. | 26 | 21.97 | 679.26
1605 | TIN-INTERP | Interpolated Ground | 10152.15 | -6.56 | 666.38 | 0 | 22.03 | 0 | OK | Ground clear controls. | 27 | 28.45 | 688.41
1606 | TIN-INTERP | Interpolated Ground | 10152.16 | -4.56 | 666.85 | 0 | 27.06 | 0 | OK | Ground clear controls. | 27 | 28.45 | 693.91
1607 | TIN-INTERP | Interpolated Ground | 10152.18 | -5.06 | 666.7 | 0 | 16.21 | 0 | OK | Ground clear controls. | 27 | 28.45 | 682.91
1608 | TIN-INTERP | Interpolated Ground | 10152.23 | 4.64 | 668.63 | 0 | 25.28 | 0 | OK | Ground clear controls. | 27 | 28.45 | 693.91
1609 | TIN-INTERP | Interpolated Ground | 10152.27 | 6.64 | 669.11 | 0 | 19.3 | 0 | OK | Ground clear controls. | 27 | 28.45 | 688.41
1610 | TIN-INTERP | Interpolated Ground | 10152.29 | 5.14 | 668.73 | 0 | 14.18 | 0 | OK | Ground clear controls. | 27 | 28.45 | 682.91
1611 | TIN-INTERP | Interpolated Ground | 10192.13 | -6.58 | 665.71 | 0 | 21.73 | 0 | OK | Ground clear controls. | 27 | 28.45 | 687.44
1612 | TIN-INTERP | Interpolated Ground | 10192.16 | -4.58 | 665.94 | 0 | 27.01 | 0 | OK | Ground clear controls. | 27 | 28.45 | 692.95
1613 | TIN-INTERP | Interpolated Ground | 10192.18 | -5.08 | 665.84 | 0 | 16.13 | 0 | OK | Ground clear controls. | 27 | 28.45 | 681.97
1614 | TIN-INTERP | Interpolated Ground | 10192.23 | 4.62 | 667.74 | 0 | 25.2 | 0 | OK | Ground clear controls. | 27 | 28.45 | 692.94
1615 | TIN-INTERP | Interpolated Ground | 10192.27 | 6.62 | 667.47 | 0 | 19.97 | 0 | OK | Ground clear controls. | 27 | 28.45 | 687.44
1616 | TIN-INTERP | Interpolated Ground | 10192.29 | 5.12 | 667.68 | 0 | 14.27 | 0 | OK | Ground clear controls. | 27 | 28.45 | 681.95
1617 | TIN-INTERP | Interpolated Ground | 10232.13 | -6.6 | 669.6 | 0 | 17.72 | 0 | OK | Ground clear controls. | 27 | 28.45 | 687.32
1618 | TIN-INTERP | Interpolated Ground | 10232.16 | -4.6 | 669.87 | 0 | 22.96 | 0 | OK | Ground clear controls. | 27 | 28.45 | 692.83
1619 | TIN-INTERP | Interpolated Ground | 10232.18 | -5.1 | 669.81 | 0 | 12.06 | 0 | OK | Ground clear controls. | 27 | 28.45 | 681.87
1620 | TIN-INTERP | Interpolated Ground | 10232.23 | 4.6 | 669.91 | 0 | 22.92 | 0 | OK | Ground clear controls. | 27 | 28.45 | 692.83
1621 | TIN-INTERP | Interpolated Ground | 10232.27 | 6.6 | 670.03 | 0 | 17.29 | 0 | OK | Ground clear controls. | 27 | 28.45 | 687.32
1622 | TIN-INTERP | Interpolated Ground | 10232.29 | 5.1 | 669.93 | 0 | 11.91 | 0 | OK | Ground clear controls. | 27 | 28.45 | 681.84
1623 | TIN-INTERP | Interpolated Ground | 10272.13 | -6.62 | 665.63 | 0 | 22.42 | 0 | OK | Ground clear controls. | 27 | 28.45 | 688.05
1624 | TIN-INTERP | Interpolated Ground | 10272.16 | -4.62 | 666.03 | 0 | 27.54 | 0 | OK | Ground clear controls. | 27 | 28.45 | 693.57
1625 | TIN-INTERP | Interpolated Ground | 10272.18 | -5.12 | 665.97 | 0 | 16.63 | 0 | OK | Ground clear controls. | 27 | 28.45 | 682.6
1626 | TIN-INTERP | Interpolated Ground | 10272.23 | 4.58 | 667.52 | 0 | 26.05 | 0 | OK | Ground clear controls. | 27 | 28.45 | 693.57
1627 | TIN-INTERP | Interpolated Ground | 10272.27 | 6.58 | 668.2 | 0 | 19.85 | 0 | OK | Ground clear controls. | 27 | 28.45 | 688.05
1628 | TIN-INTERP | Interpolated Ground | 10272.29 | 5.08 | 667.63 | 0 | 14.95 | 0 | OK | Ground clear controls. | 27 | 28.45 | 682.58
1629 | TIN-INTERP | Interpolated Ground | 10312.13 | -6.64 | 666.17 | 0 | 23.47 | 0 | OK | Ground clear controls. | 27 | 28.45 | 689.64
1630 | TIN-INTERP | Interpolated Ground | 10312.16 | -4.64 | 666.7 | 0 | 28.45 | 0 | OK | Ground clear controls. | 27 | 28.45 | 695.15
1631 | TIN-INTERP | Interpolated Ground | 10312.18 | -5.14 | 666.56 | 0 | 17.61 | 0 | OK | Ground clear controls. | 27 | 28.08 | 684.17
1632 | TIN-INTERP | Interpolated Ground | 10312.23 | 4.56 | 669.2 | 0 | 25.94 | 0 | OK | Ground clear controls. | 27 | 28.08 | 695.14
1633 | TIN-INTERP | Interpolated Ground | 10312.27 | 6.56 | 669.7 | 0 | 19.94 | 0 | OK | Ground clear controls. | 27 | 28.08 | 689.64
1634 | TIN-INTERP | Interpolated Ground | 10312.29 | 5.06 | 669.32 | 0 | 14.84 | 0 | OK | Ground clear controls. | 27 | 28.08 | 684.16
1635 | TIN-INTERP | Interpolated Ground | 10352.13 | -6.66 | 669.37 | 0 | 22.71 | 0 | OK | Ground clear controls. | 27 | 28.08 | 692.08
1636 | TIN-INTERP | Interpolated Ground | 10352.16 | -4.66 | 669.5 | 0 | 28.08 | 0 | OK | Ground clear controls. | 27 | 28.08 | 697.58
1637 | TIN-INTERP | Interpolated Ground | 10352.18 | -5.16 | 669.47 | 0 | 17.12 | 0 | OK | Ground clear controls. | 27 | 26.48 | 686.59
1638 | TIN-INTERP | Interpolated Ground | 10352.23 | 4.54 | 671.1 | 0 | 26.48 | 0 | OK | Ground clear controls. | 27 | 26.48 | 697.58
1639 | TIN-INTERP | Interpolated Ground | 10352.27 | 6.54 | 671.48 | 0 | 20.6 | 0 | OK | Ground clear controls. | 27 | 20.6 | 692.08
1640 | TIN-INTERP | Interpolated Ground | 10352.29 | 5.04 | 671.16 | 0 | 15.44 | 0 | OK | Ground clear controls. | 27 | 15.44 | 686.6
1641 | TIN-INTERP | Interpolated Ground | 10361.99 | -5.16 | 669.11 | 0 | 18.2 | 0 | OK | Ground clear controls. | 28 | 70.17 | 687.31
1642 | TIN-INTERP | Interpolated Ground | 10362.01 | 5.04 | 671.08 | 0 | 16.23 | 0 | OK | Ground clear controls. | 28 | 70.17 | 687.31
1643 | TIN-INTERP | Interpolated Ground | 10362.06 | -4.66 | 669.23 | 0 | 29.08 | 0 | OK | Ground clear controls. | 28 | 70.17 | 698.31
1644 | TIN-INTERP | Interpolated Ground | 10362.06 | 4.54 | 670.85 | 0 | 27.46 | 0 | OK | Ground clear controls. | 28 | 70.17 | 698.31
1645 | TIN-INTERP | Interpolated Ground | 10362.08 | -6.66 | 668.83 | 0 | 23.99 | 0 | OK | Ground clear controls. | 28 | 70.17 | 692.82
1646 | TIN-INTERP | Interpolated Ground | 10362.08 | 6.54 | 671.82 | 0 | 20.99 | 0 | OK | Ground clear controls. | 28 | 70.17 | 692.81
1647 | TIN-INTERP | Interpolated Ground | 10401.99 | -5.15 | 664.83 | 0 | 16.46 | 0 | OK | Ground clear controls. | 28 | 70.17 | 681.29
1648 | TIN-INTERP | Interpolated Ground | 10402.01 | 5.05 | 667.02 | 0 | 14.25 | 0 | OK | Ground clear controls. | 28 | 70.17 | 681.27
1649 | TIN-INTERP | Interpolated Ground | 10402.06 | -4.65 | 664.99 | 0 | 27.29 | 0 | OK | Ground clear controls. | 28 | 70.17 | 692.28
1650 | TIN-INTERP | Interpolated Ground | 10402.06 | 4.55 | 666.95 | 0 | 25.31 | 0 | OK | Ground clear controls. | 28 | 70.17 | 692.26
1651 | TIN-INTERP | Interpolated Ground | 10402.08 | -6.65 | 664.34 | 0 | 22.43 | 0 | OK | Ground clear controls. | 28 | 70.17 | 686.77
1652 | TIN-INTERP | Interpolated Ground | 10402.08 | 6.55 | 667.05 | 0 | 19.72 | 0 | OK | Ground clear controls. | 28 | 70.17 | 686.77
1653 | TIN-INTERP | Interpolated Ground | 10441.99 | -5.14 | 660.33 | 0 | 15.79 | 0 | OK | Ground clear controls. | 28 | 70.17 | 676.12
1654 | TIN-INTERP | Interpolated Ground | 10442.01 | 5.06 | 662.07 | 0 | 14.02 | 0 | OK | Ground clear controls. | 28 | 70.17 | 676.09
1655 | TIN-INTERP | Interpolated Ground | 10442.06 | -4.64 | 660.4 | 0 | 26.71 | 0 | OK | Ground clear controls. | 28 | 70.17 | 687.11
1656 | TIN-INTERP | Interpolated Ground | 10442.06 | 4.56 | 661.87 | 0 | 25.22 | 0 | OK | Ground clear controls. | 28 | 70.17 | 687.09
1657 | TIN-INTERP | Interpolated Ground | 10442.08 | -6.64 | 659.99 | 0 | 21.61 | 0 | OK | Ground clear controls. | 28 | 70.17 | 681.6
1658 | TIN-INTERP | Interpolated Ground | 10442.08 | 6.56 | 662.63 | 0 | 18.97 | 0 | OK | Ground clear controls. | 28 | 70.17 | 681.6
1659 | TIN-INTERP | Interpolated Ground | 10481.99 | -5.13 | 643.15 | 0 | 28.67 | 0 | OK | Ground clear controls. | 28 | 70.17 | 671.82
1660 | TIN-INTERP | Interpolated Ground | 10482.01 | 5.07 | 634.91 | 0 | 36.87 | 0 | OK | Ground clear controls. | 28 | 70.17 | 671.78
1661 | TIN-INTERP | Interpolated Ground | 10482.06 | -4.63 | 642.82 | 0 | 39.99 | 0 | OK | Ground clear controls. | 28 | 70.17 | 682.81
1662 | TIN-INTERP | Interpolated Ground | 10482.06 | 4.57 | 635.35 | 0 | 47.43 | 0 | OK | Ground clear controls. | 28 | 70.17 | 682.78
1663 | TIN-INTERP | Interpolated Ground | 10482.08 | -6.63 | 643.88 | 0 | 33.41 | 0 | OK | Ground clear controls. | 28 | 70.17 | 677.29
1664 | TIN-INTERP | Interpolated Ground | 10482.08 | 6.57 | 633.61 | 0 | 43.67 | 0 | OK | Ground clear controls. | 28 | 70.17 | 677.28
1665 | TIN-INTERP | Interpolated Ground | 10521.99 | -5.11 | 609.35 | 0 | 59.03 | 0 | OK | Ground clear controls. | 28 | 70.17 | 668.38
1666 | TIN-INTERP | Interpolated Ground | 10522.01 | 5.09 | 610.24 | 0 | 58.09 | 0 | OK | Ground clear controls. | 28 | 70.17 | 668.33
1667 | TIN-INTERP | Interpolated Ground | 10522.06 | -4.61 | 609.19 | 0 | 70.17 | 0 | OK | Ground clear controls. | 28 | 70.17 | 679.36
1668 | TIN-INTERP | Interpolated Ground | 10522.06 | 4.59 | 609.91 | 0 | 69.42 | 0 | OK | Ground clear controls. | 28 | 69.42 | 679.33
1669 | TIN-INTERP | Interpolated Ground | 10522.08 | -6.61 | 609.72 | 0 | 64.12 | 0 | OK | Ground clear controls. | 28 | 64.12 | 673.84
1670 | TIN-INTERP | Interpolated Ground | 10522.08 | 6.59 | 611.34 | 0 | 62.49 | 0 | OK | Ground clear controls. | 28 | 62.49 | 673.83
1671 | TIN-INTERP | Interpolated Ground | 10561.99 | -5.1 | 620.39 | 0 | 45.4 | 0 | OK | Ground clear controls. | 28 | 55.77 | 665.79
1672 | TIN-INTERP | Interpolated Ground | 10562.01 | 5.1 | 631.86 | 0 | 33.89 | 0 | OK | Ground clear controls. | 28 | 55.77 | 665.75
1673 | TIN-INTERP | Interpolated Ground | 10562.06 | -4.6 | 621 | 0 | 55.77 | 0 | OK | Ground clear controls. | 28 | 55.77 | 676.77
1674 | TIN-INTERP | Interpolated Ground | 10562.06 | 4.6 | 631.29 | 0 | 45.46 | 0 | OK | Ground clear controls. | 28 | 52.59 | 676.75
1675 | TIN-INTERP | Interpolated Ground | 10562.08 | -6.6 | 618.67 | 0 | 52.59 | 0 | OK | Ground clear controls. | 28 | 52.59 | 671.26
1676 | TIN-INTERP | Interpolated Ground | 10562.08 | 6.6 | 633.73 | 0 | 37.52 | 0 | OK | Ground clear controls. | 28 | 45.07 | 671.25
1677 | TIN-INTERP | Interpolated Ground | 10601.99 | -5.09 | 636.32 | 0 | 27.75 | 0 | OK | Ground clear controls. | 28 | 45.07 | 664.07
1678 | TIN-INTERP | Interpolated Ground | 10602.01 | 5.11 | 638.08 | 0 | 25.94 | 0 | OK | Ground clear controls. | 28 | 45.07 | 664.02
1679 | TIN-INTERP | Interpolated Ground | 10602.06 | -4.59 | 636.32 | 0 | 38.73 | 0 | OK | Ground clear controls. | 28 | 45.07 | 675.05
1680 | TIN-INTERP | Interpolated Ground | 10602.06 | 4.61 | 637.96 | 0 | 37.06 | 0 | OK | Ground clear controls. | 28 | 45.07 | 675.02
1681 | TIN-INTERP | Interpolated Ground | 10602.08 | -6.59 | 635.82 | 0 | 33.71 | 0 | OK | Ground clear controls. | 28 | 45.07 | 669.53
1682 | TIN-INTERP | Interpolated Ground | 10602.08 | 6.61 | 638.28 | 0 | 31.24 | 0 | OK | Ground clear controls. | 28 | 45.07 | 669.52
1683 | TIN-INTERP | Interpolated Ground | 10641.99 | -5.08 | 633.03 | 0 | 30.17 | 0 | OK | Ground clear controls. | 28 | 45.07 | 663.2
1684 | TIN-INTERP | Interpolated Ground | 10642.01 | 5.12 | 634.35 | 0 | 28.81 | 0 | OK | Ground clear controls. | 28 | 45.07 | 663.16
1685 | TIN-INTERP | Interpolated Ground | 10642.06 | -4.58 | 633.17 | 0 | 41.01 | 0 | OK | Ground clear controls. | 28 | 45.07 | 674.18
1686 | TIN-INTERP | Interpolated Ground | 10642.06 | 4.62 | 634.58 | 0 | 39.58 | 0 | OK | Ground clear controls. | 28 | 45.07 | 674.16
1687 | TIN-INTERP | Interpolated Ground | 10642.08 | -6.58 | 632.66 | 0 | 36.01 | 0 | OK | Ground clear controls. | 28 | 45.07 | 668.67
1688 | TIN-INTERP | Interpolated Ground | 10642.08 | 6.62 | 633.92 | 0 | 34.74 | 0 | OK | Ground clear controls. | 28 | 45.07 | 668.66
1689 | TIN-INTERP | Interpolated Ground | 10681.99 | -5.07 | 628.91 | 0 | 34.27 | 0 | OK | Ground clear controls. | 28 | 45.07 | 663.18
1690 | TIN-INTERP | Interpolated Ground | 10682.01 | 5.13 | 631.5 | 0 | 31.65 | 0 | OK | Ground clear controls. | 28 | 45.07 | 663.15
1691 | TIN-INTERP | Interpolated Ground | 10682.06 | -4.57 | 629.1 | 0 | 45.07 | 0 | OK | Ground clear controls. | 28 | 45.07 | 674.17
1692 | TIN-INTERP | Interpolated Ground | 10682.06 | 4.63 | 631.46 | 0 | 42.7 | 0 | OK | Ground clear controls. | 28 | 42.7 | 674.16
1693 | TIN-INTERP | Interpolated Ground | 10682.08 | -6.57 | 628.66 | 0 | 40 | 0 | OK | Ground clear controls. | 28 | 40 | 668.66
1694 | TIN-INTERP | Interpolated Ground | 10682.08 | 6.63 | 631.78 | 0 | 36.88 | 0 | OK | Ground clear controls. | 28 | 38.15 | 668.66
1695 | TIN-INTERP | Interpolated Ground | 10721.99 | -5.05 | 636.87 | 0 | 27.15 | 0 | OK | Ground clear controls. | 28 | 38.15 | 664.02
1696 | TIN-INTERP | Interpolated Ground | 10722.01 | 5.15 | 638.49 | 0 | 25.52 | 0 | OK | Ground clear controls. | 28 | 38.15 | 664.01
1697 | TIN-INTERP | Interpolated Ground | 10722.06 | -4.55 | 636.87 | 0 | 38.15 | 0 | OK | Ground clear controls. | 28 | 38.15 | 675.02
1698 | TIN-INTERP | Interpolated Ground | 10722.06 | 4.65 | 638.36 | 0 | 36.65 | 0 | OK | Ground clear controls. | 28 | 36.65 | 675.01
1699 | TIN-INTERP | Interpolated Ground | 10722.08 | -6.55 | 636.95 | 0 | 32.56 | 0 | OK | Ground clear controls. | 28 | 32.56 | 669.51
1700 | TIN-INTERP | Interpolated Ground | 10722.08 | 6.65 | 638.94 | 0 | 30.58 | 0 | OK | Ground clear controls. | 28 | 30.58 | 669.52
1701 | TIN-INTERP | Interpolated Ground | 10742.4 | 6.65 | 644.31 | 0 | 25.97 | 0 | OK | Ground clear controls. | 29 | 53.72 | 670.28
1702 | TIN-INTERP | Interpolated Ground | 10742.4 | -4.55 | 642.41 | 0 | 33.38 | 0 | OK | Ground clear controls. | 29 | 53.72 | 675.79
1703 | TIN-INTERP | Interpolated Ground | 10742.42 | 4.65 | 644.41 | 0 | 31.37 | 0 | OK | Ground clear controls. | 29 | 53.72 | 675.78
1704 | TIN-INTERP | Interpolated Ground | 10742.43 | -6.55 | 641.26 | 0 | 29.03 | 0 | OK | Ground clear controls. | 29 | 53.72 | 670.29
1705 | TIN-INTERP | Interpolated Ground | 10742.43 | 5.15 | 644.38 | 0 | 20.4 | 0 | OK | Ground clear controls. | 29 | 53.72 | 664.78
1706 | TIN-INTERP | Interpolated Ground | 10742.44 | -5.05 | 642.11 | 0 | 22.67 | 0 | OK | Ground clear controls. | 29 | 53.72 | 664.78
1707 | TIN-INTERP | Interpolated Ground | 10782.37 | -4.56 | 635.47 | 0 | 33.5 | 0 | OK | Ground clear controls. | 29 | 53.72 | 668.97
1708 | TIN-INTERP | Interpolated Ground | 10782.4 | -6.56 | 635.77 | 0 | 27.7 | 0 | OK | Ground clear controls. | 29 | 53.72 | 663.47
1709 | TIN-INTERP | Interpolated Ground | 10782.41 | -5.06 | 635.54 | 0 | 22.46 | 0 | OK | Ground clear controls. | 29 | 53.72 | 658
1710 | TIN-INTERP | Interpolated Ground | 10782.43 | 6.64 | 636.24 | 0 | 27.23 | 0 | OK | Ground clear controls. | 29 | 53.72 | 663.47
1711 | TIN-INTERP | Interpolated Ground | 10782.44 | 4.64 | 635.68 | 0 | 33.29 | 0 | OK | Ground clear controls. | 29 | 53.72 | 668.97
1712 | TIN-INTERP | Interpolated Ground | 10782.46 | 5.14 | 635.82 | 0 | 22.16 | 0 | OK | Ground clear controls. | 29 | 53.72 | 657.98
1713 | TIN-INTERP | Interpolated Ground | 10822.37 | -4.57 | 630.78 | 0 | 32.26 | 0 | OK | Ground clear controls. | 29 | 53.72 | 663.04
1714 | TIN-INTERP | Interpolated Ground | 10822.4 | -6.57 | 630.31 | 0 | 27.24 | 0 | OK | Ground clear controls. | 29 | 53.72 | 657.55
1715 | TIN-INTERP | Interpolated Ground | 10822.41 | -5.07 | 630.65 | 0 | 21.44 | 0 | OK | Ground clear controls. | 29 | 53.72 | 652.09
1716 | TIN-INTERP | Interpolated Ground | 10822.43 | 6.63 | 630.47 | 0 | 27.06 | 0 | OK | Ground clear controls. | 29 | 53.72 | 657.53
1717 | TIN-INTERP | Interpolated Ground | 10822.44 | 4.63 | 630.54 | 0 | 32.51 | 0 | OK | Ground clear controls. | 29 | 53.72 | 663.05
1718 | TIN-INTERP | Interpolated Ground | 10822.46 | 5.13 | 630.51 | 0 | 21.55 | 0 | OK | Ground clear controls. | 29 | 53.72 | 652.06
1719 | TIN-INTERP | Interpolated Ground | 10862.37 | -4.57 | 624.37 | 0 | 33.63 | 0 | OK | Ground clear controls. | 29 | 53.72 | 658
1720 | TIN-INTERP | Interpolated Ground | 10862.4 | -6.57 | 624.01 | 0 | 28.5 | 0 | OK | Ground clear controls. | 29 | 53.72 | 652.51
1721 | TIN-INTERP | Interpolated Ground | 10862.41 | -5.07 | 624.29 | 0 | 22.78 | 0 | OK | Ground clear controls. | 29 | 53.72 | 647.07
1722 | TIN-INTERP | Interpolated Ground | 10862.43 | 6.63 | 625.29 | 0 | 27.21 | 0 | OK | Ground clear controls. | 29 | 53.72 | 652.5
1723 | TIN-INTERP | Interpolated Ground | 10862.44 | 4.63 | 625.24 | 0 | 32.77 | 0 | OK | Ground clear controls. | 29 | 53.72 | 658.01
1724 | TIN-INTERP | Interpolated Ground | 10862.46 | 5.13 | 625.21 | 0 | 21.82 | 0 | OK | Ground clear controls. | 29 | 53.72 | 647.03
1725 | TIN-INTERP | Interpolated Ground | 10902.37 | -4.58 | 619.92 | 0 | 33.91 | 0 | OK | Ground clear controls. | 29 | 53.72 | 653.83
1726 | TIN-INTERP | Interpolated Ground | 10902.4 | -6.58 | 619.16 | 0 | 29.19 | 0 | OK | Ground clear controls. | 29 | 53.72 | 648.35
1727 | TIN-INTERP | Interpolated Ground | 10902.41 | -5.08 | 619.74 | 0 | 23.18 | 0 | OK | Ground clear controls. | 29 | 53.72 | 642.92
1728 | TIN-INTERP | Interpolated Ground | 10902.43 | 6.62 | 622.72 | 0 | 25.62 | 0 | OK | Ground clear controls. | 29 | 53.72 | 648.34
1729 | TIN-INTERP | Interpolated Ground | 10902.44 | 4.62 | 622.29 | 0 | 31.56 | 0 | OK | Ground clear controls. | 29 | 53.72 | 653.85
1730 | TIN-INTERP | Interpolated Ground | 10902.46 | 5.12 | 622.41 | 0 | 20.47 | 0 | OK | Ground clear controls. | 29 | 53.72 | 642.88
1731 | TIN-INTERP | Interpolated Ground | 10942.37 | -4.59 | 599.23 | 0 | 51.32 | 0 | OK | Ground clear controls. | 29 | 53.72 | 650.55
1732 | TIN-INTERP | Interpolated Ground | 10942.4 | -6.59 | 598.84 | 0 | 46.24 | 0 | OK | Ground clear controls. | 29 | 53.72 | 645.08
1733 | TIN-INTERP | Interpolated Ground | 10942.41 | -5.09 | 599.16 | 0 | 40.48 | 0 | OK | Ground clear controls. | 29 | 53.72 | 639.64
1734 | TIN-INTERP | Interpolated Ground | 10942.43 | 6.61 | 599.3 | 0 | 45.76 | 0 | OK | Ground clear controls. | 29 | 53.72 | 645.06
1735 | TIN-INTERP | Interpolated Ground | 10942.44 | 4.61 | 599.07 | 0 | 51.51 | 0 | OK | Ground clear controls. | 29 | 53.72 | 650.58
1736 | TIN-INTERP | Interpolated Ground | 10942.46 | 5.11 | 599.13 | 0 | 40.48 | 0 | OK | Ground clear controls. | 29 | 53.72 | 639.61
1737 | TIN-INTERP | Interpolated Ground | 10982.37 | -4.6 | 617.69 | 0 | 30.47 | 0 | OK | Ground clear controls. | 29 | 53.72 | 648.16
1738 | TIN-INTERP | Interpolated Ground | 10982.4 | -6.6 | 616.95 | 0 | 25.73 | 0 | OK | Ground clear controls. | 29 | 53.72 | 642.68
1739 | TIN-INTERP | Interpolated Ground | 10982.41 | -5.1 | 617.52 | 0 | 19.73 | 0 | OK | Ground clear controls. | 29 | 53.72 | 637.25
1740 | TIN-INTERP | Interpolated Ground | 10982.43 | 6.6 | 620.76 | 0 | 21.91 | 0 | OK | Ground clear controls. | 29 | 53.72 | 642.67
1741 | TIN-INTERP | Interpolated Ground | 10982.44 | 4.6 | 620.34 | 0 | 27.85 | 0 | OK | Ground clear controls. | 29 | 53.72 | 648.19
1742 | TIN-INTERP | Interpolated Ground | 10982.46 | 5.1 | 620.45 | 0 | 16.77 | 0 | OK | Ground clear controls. | 29 | 53.72 | 637.22
1743 | TIN-INTERP | Interpolated Ground | 11022.37 | -4.61 | 618.4 | 0 | 28.24 | 0 | OK | Ground clear controls. | 29 | 53.72 | 646.64
1744 | TIN-INTERP | Interpolated Ground | 11022.4 | -6.61 | 618 | 0 | 23.16 | 0 | OK | Ground clear controls. | 29 | 53.72 | 641.16
1745 | TIN-INTERP | Interpolated Ground | 11022.41 | -5.11 | 618.29 | 0 | 17.44 | 0 | OK | Ground clear controls. | 29 | 53.72 | 635.73
1746 | TIN-INTERP | Interpolated Ground | 11022.43 | 6.59 | 620.19 | 0 | 20.96 | 0 | OK | Ground clear controls. | 29 | 53.72 | 641.15
1747 | TIN-INTERP | Interpolated Ground | 11022.44 | 4.59 | 620 | 0 | 26.67 | 0 | OK | Ground clear controls. | 29 | 53.72 | 646.67
1748 | TIN-INTERP | Interpolated Ground | 11022.46 | 5.09 | 620.07 | 0 | 15.63 | 0 | OK | Ground clear controls. | 29 | 53.72 | 635.7
1749 | TIN-INTERP | Interpolated Ground | 11062.37 | -4.62 | 613.78 | 0 | 32.23 | 0 | OK | Ground clear controls. | 29 | 53.72 | 646.01
1750 | TIN-INTERP | Interpolated Ground | 11062.4 | -6.62 | 613.35 | 0 | 27.17 | 0 | OK | Ground clear controls. | 29 | 53.72 | 640.52
1751 | TIN-INTERP | Interpolated Ground | 11062.41 | -5.12 | 613.7 | 0 | 21.38 | 0 | OK | Ground clear controls. | 29 | 53.72 | 635.08
1752 | TIN-INTERP | Interpolated Ground | 11062.43 | 6.58 | 615.39 | 0 | 25.12 | 0 | OK | Ground clear controls. | 29 | 53.72 | 640.51
1753 | TIN-INTERP | Interpolated Ground | 11062.44 | 4.58 | 615.23 | 0 | 30.8 | 0 | OK | Ground clear controls. | 29 | 53.72 | 646.03
1754 | TIN-INTERP | Interpolated Ground | 11062.46 | 5.08 | 615.38 | 0 | 19.68 | 0 | OK | Ground clear controls. | 29 | 53.72 | 635.06
1755 | TIN-INTERP | Interpolated Ground | 11102.37 | -4.63 | 594.05 | 0 | 52.19 | 0 | OK | Ground clear controls. | 29 | 53.72 | 646.24
1756 | TIN-INTERP | Interpolated Ground | 11102.4 | -6.63 | 594.39 | 0 | 46.36 | 0 | OK | Ground clear controls. | 29 | 53.72 | 640.75
1757 | TIN-INTERP | Interpolated Ground | 11102.41 | -5.13 | 594.11 | 0 | 41.2 | 0 | OK | Ground clear controls. | 29 | 53.72 | 635.31
1758 | TIN-INTERP | Interpolated Ground | 11102.43 | 6.57 | 593.16 | 0 | 47.59 | 0 | OK | Ground clear controls. | 29 | 53.72 | 640.75
1759 | TIN-INTERP | Interpolated Ground | 11102.44 | 4.57 | 592.55 | 0 | 53.72 | 0 | OK | Ground clear controls. | 29 | 53.72 | 646.27
1760 | TIN-INTERP | Interpolated Ground | 11102.46 | 5.07 | 592.71 | 0 | 42.57 | 0 | OK | Ground clear controls. | 29 | 42.57 | 635.28
1761 | TIN-INTERP | Interpolated Ground | 11142.37 | -4.64 | 605.45 | 0 | 41.9 | 0 | OK | Ground clear controls. | 29 | 41.9 | 647.35
1762 | TIN-INTERP | Interpolated Ground | 11142.4 | -6.64 | 605.12 | 0 | 36.74 | 0 | OK | Ground clear controls. | 29 | 38.57 | 641.86
1763 | TIN-INTERP | Interpolated Ground | 11142.41 | -5.14 | 605.33 | 0 | 31.07 | 0 | OK | Ground clear controls. | 29 | 38.57 | 636.4
1764 | TIN-INTERP | Interpolated Ground | 11142.43 | 6.56 | 610.62 | 0 | 31.24 | 0 | OK | Ground clear controls. | 29 | 38.57 | 641.86
1765 | TIN-INTERP | Interpolated Ground | 11142.44 | 4.56 | 609.85 | 0 | 37.53 | 0 | OK | Ground clear controls. | 29 | 38.57 | 647.38
1766 | TIN-INTERP | Interpolated Ground | 11142.46 | 5.06 | 610.05 | 0 | 26.34 | 0 | OK | Ground clear controls. | 29 | 38.57 | 636.39
1767 | TIN-INTERP | Interpolated Ground | 11182.37 | -4.65 | 610.78 | 0 | 38.57 | 0 | OK | Ground clear controls. | 29 | 38.57 | 649.35
1768 | TIN-INTERP | Interpolated Ground | 11182.4 | -6.65 | 610.37 | 0 | 33.48 | 0 | OK | Ground clear controls. | 29 | 37.01 | 643.85
1769 | TIN-INTERP | Interpolated Ground | 11182.41 | -5.15 | 610.7 | 0 | 27.67 | 0 | OK | Ground clear controls. | 29 | 37.01 | 638.37
1770 | TIN-INTERP | Interpolated Ground | 11182.43 | 6.55 | 612.56 | 0 | 31.3 | 0 | OK | Ground clear controls. | 29 | 37.01 | 643.86
1771 | TIN-INTERP | Interpolated Ground | 11182.44 | 4.55 | 612.35 | 0 | 37.01 | 0 | OK | Ground clear controls. | 29 | 37.01 | 649.36
1772 | TIN-INTERP | Interpolated Ground | 11182.46 | 5.05 | 612.35 | 0 | 26.03 | 0 | OK | Ground clear controls. | 29 | 26.03 | 638.38
1773 | TIN-INTERP | Interpolated Ground | 11196.52 | 5.05 | 611.48 | 0 | 27.8 | 0 | OK | Ground clear controls. | 30 | 54.14 | 639.28
1774 | TIN-INTERP | Interpolated Ground | 11196.56 | 4.55 | 611.48 | 0 | 38.8 | 0 | OK | Ground clear controls. | 30 | 54.14 | 650.28
1775 | TIN-INTERP | Interpolated Ground | 11196.56 | 6.55 | 611.5 | 0 | 33.28 | 0 | OK | Ground clear controls. | 30 | 54.14 | 644.78
1776 | TIN-INTERP | Interpolated Ground | 11196.59 | -5.15 | 609.74 | 0 | 29.54 | 0 | OK | Ground clear controls. | 30 | 54.14 | 639.28
1777 | TIN-INTERP | Interpolated Ground | 11196.59 | -4.65 | 609.83 | 0 | 40.44 | 0 | OK | Ground clear controls. | 30 | 54.14 | 650.27
1778 | TIN-INTERP | Interpolated Ground | 11196.6 | -6.65 | 609.42 | 0 | 35.36 | 0 | OK | Ground clear controls. | 30 | 54.14 | 644.78
1779 | TIN-INTERP | Interpolated Ground | 11236.52 | 5.06 | 608.24 | 0 | 21.32 | 0 | OK | Ground clear controls. | 30 | 54.14 | 629.56
1780 | TIN-INTERP | Interpolated Ground | 11236.55 | 4.56 | 608.13 | 0 | 32.44 | 0 | OK | Ground clear controls. | 30 | 54.14 | 640.57
1781 | TIN-INTERP | Interpolated Ground | 11236.56 | 6.56 | 608.57 | 0 | 26.49 | 0 | OK | Ground clear controls. | 30 | 54.14 | 635.06
1782 | TIN-INTERP | Interpolated Ground | 11236.59 | -5.14 | 607.01 | 0 | 22.61 | 0 | OK | Ground clear controls. | 30 | 54.14 | 629.62
1783 | TIN-INTERP | Interpolated Ground | 11236.6 | -4.64 | 607.04 | 0 | 33.55 | 0 | OK | Ground clear controls. | 30 | 54.14 | 640.59
1784 | TIN-INTERP | Interpolated Ground | 11236.6 | -6.64 | 606.94 | 0 | 28.16 | 0 | OK | Ground clear controls. | 30 | 54.14 | 635.1
1785 | TIN-INTERP | Interpolated Ground | 11276.52 | 5.08 | 604.89 | 0 | 15.87 | 0 | OK | Ground clear controls. | 30 | 54.14 | 620.76
1786 | TIN-INTERP | Interpolated Ground | 11276.55 | 4.58 | 604.85 | 0 | 26.94 | 0 | OK | Ground clear controls. | 30 | 54.14 | 631.79
1787 | TIN-INTERP | Interpolated Ground | 11276.56 | 6.58 | 605.13 | 0 | 21.15 | 0 | OK | Ground clear controls. | 30 | 54.14 | 626.28
1788 | TIN-INTERP | Interpolated Ground | 11276.59 | -5.13 | 603.85 | 0 | 17.04 | 0 | OK | Ground clear controls. | 30 | 54.14 | 620.89
1789 | TIN-INTERP | Interpolated Ground | 11276.6 | -4.63 | 604.01 | 0 | 27.82 | 0 | OK | Ground clear controls. | 30 | 54.14 | 631.83
1790 | TIN-INTERP | Interpolated Ground | 11276.6 | -6.63 | 603.39 | 0 | 22.96 | 0 | OK | Ground clear controls. | 30 | 54.14 | 626.35
1791 | TIN-INTERP | Interpolated Ground | 11316.52 | 5.09 | 599.73 | 0 | 13.17 | 0 | OK | Ground clear controls. | 30 | 54.14 | 612.9
1792 | TIN-INTERP | Interpolated Ground | 11316.55 | 4.59 | 599.74 | 0 | 24.2 | 0 | OK | Ground clear controls. | 30 | 54.14 | 623.94
1793 | TIN-INTERP | Interpolated Ground | 11316.56 | 6.59 | 599.68 | 0 | 18.74 | 0 | OK | Ground clear controls. | 30 | 54.14 | 618.42
1794 | TIN-INTERP | Interpolated Ground | 11316.59 | -5.11 | 599.98 | 0 | 13.1 | 0 | OK | Ground clear controls. | 30 | 54.14 | 613.08
1795 | TIN-INTERP | Interpolated Ground | 11316.6 | -4.61 | 599.97 | 0 | 24.01 | 0 | OK | Ground clear controls. | 30 | 54.14 | 623.98
1796 | TIN-INTERP | Interpolated Ground | 11316.6 | -6.61 | 599.94 | 0 | 18.59 | 0 | OK | Ground clear controls. | 30 | 54.14 | 618.53
1797 | TIN-INTERP | Interpolated Ground | 11356.52 | 5.11 | 584.06 | 0 | 21.92 | 0 | OK | Ground clear controls. | 30 | 54.14 | 605.98
1798 | TIN-INTERP | Interpolated Ground | 11356.55 | 4.61 | 584.09 | 0 | 32.93 | 0 | OK | Ground clear controls. | 30 | 54.14 | 617.02
1799 | TIN-INTERP | Interpolated Ground | 11356.56 | 6.61 | 583.17 | 0 | 28.33 | 0 | OK | Ground clear controls. | 30 | 54.14 | 611.5
1800 | TIN-INTERP | Interpolated Ground | 11356.59 | -5.1 | 585.3 | 0 | 20.89 | 0 | OK | Ground clear controls. | 30 | 54.14 | 606.19
1801 | TIN-INTERP | Interpolated Ground | 11356.6 | -4.6 | 585.29 | 0 | 31.79 | 0 | OK | Ground clear controls. | 30 | 54.14 | 617.08
1802 | TIN-INTERP | Interpolated Ground | 11356.6 | -6.6 | 585.76 | 0 | 25.87 | 0 | OK | Ground clear controls. | 30 | 54.14 | 611.63
1803 | TIN-INTERP | Interpolated Ground | 11396.52 | 5.12 | 567.77 | 0 | 32.21 | 0 | OK | Ground clear controls. | 30 | 54.14 | 599.98
1804 | TIN-INTERP | Interpolated Ground | 11396.55 | 4.63 | 567.68 | 0 | 43.35 | 0 | OK | Ground clear controls. | 30 | 54.14 | 611.03
1805 | TIN-INTERP | Interpolated Ground | 11396.56 | 6.62 | 567.94 | 0 | 37.56 | 0 | OK | Ground clear controls. | 30 | 54.14 | 605.5
1806 | TIN-INTERP | Interpolated Ground | 11396.59 | -5.09 | 565.75 | 0 | 34.48 | 0 | OK | Ground clear controls. | 30 | 54.14 | 600.23
1807 | TIN-INTERP | Interpolated Ground | 11396.6 | -4.59 | 565.83 | 0 | 45.26 | 0 | OK | Ground clear controls. | 30 | 54.14 | 611.09
1808 | TIN-INTERP | Interpolated Ground | 11396.6 | -6.59 | 565.4 | 0 | 40.24 | 0 | OK | Ground clear controls. | 30 | 54.14 | 605.64
1809 | TIN-INTERP | Interpolated Ground | 11436.52 | 5.14 | 571.06 | 0 | 23.84 | 0 | OK | Ground clear controls. | 30 | 54.14 | 594.9
1810 | TIN-INTERP | Interpolated Ground | 11436.55 | 4.64 | 570.99 | 0 | 34.96 | 0 | OK | Ground clear controls. | 30 | 54.14 | 605.95
1811 | TIN-INTERP | Interpolated Ground | 11436.56 | 6.64 | 571.29 | 0 | 29.13 | 0 | OK | Ground clear controls. | 30 | 54.14 | 600.42
1812 | TIN-INTERP | Interpolated Ground | 11436.59 | -5.08 | 568.64 | 0 | 26.52 | 0 | OK | Ground clear controls. | 30 | 54.14 | 595.16
1813 | TIN-INTERP | Interpolated Ground | 11436.6 | -4.58 | 568.77 | 0 | 37.25 | 0 | OK | Ground clear controls. | 30 | 54.14 | 606.02
1814 | TIN-INTERP | Interpolated Ground | 11436.6 | -6.58 | 568.06 | 0 | 32.52 | 0 | OK | Ground clear controls. | 30 | 54.14 | 600.58
1815 | TIN-INTERP | Interpolated Ground | 11476.52 | 5.15 | 561.06 | 0 | 29.68 | 0 | OK | Ground clear controls. | 30 | 54.14 | 590.74
1816 | TIN-INTERP | Interpolated Ground | 11476.55 | 4.66 | 561.04 | 0 | 40.76 | 0 | OK | Ground clear controls. | 30 | 54.14 | 601.8
1817 | TIN-INTERP | Interpolated Ground | 11476.56 | 6.65 | 561.28 | 0 | 34.99 | 0 | OK | Ground clear controls. | 30 | 54.14 | 596.27
1818 | TIN-INTERP | Interpolated Ground | 11476.59 | -5.06 | 560.64 | 0 | 30.37 | 0 | OK | Ground clear controls. | 30 | 54.14 | 591.01
1819 | TIN-INTERP | Interpolated Ground | 11476.6 | -4.57 | 560.63 | 0 | 41.24 | 0 | OK | Ground clear controls. | 30 | 54.14 | 601.87
1820 | TIN-INTERP | Interpolated Ground | 11476.6 | -6.56 | 560.74 | 0 | 35.69 | 0 | OK | Ground clear controls. | 30 | 54.14 | 596.43
1821 | TIN-INTERP | Interpolated Ground | 11516.52 | 5.17 | 567.85 | 0 | 19.66 | 0 | OK | Ground clear controls. | 30 | 54.14 | 587.51
1822 | TIN-INTERP | Interpolated Ground | 11516.55 | 4.67 | 567.84 | 0 | 30.73 | 0 | OK | Ground clear controls. | 30 | 54.14 | 598.57
1823 | TIN-INTERP | Interpolated Ground | 11516.56 | 6.67 | 567.76 | 0 | 25.27 | 0 | OK | Ground clear controls. | 30 | 54.14 | 593.03
1824 | TIN-INTERP | Interpolated Ground | 11516.59 | -5.05 | 567.1 | 0 | 20.67 | 0 | OK | Ground clear controls. | 30 | 54.14 | 587.77
1825 | TIN-INTERP | Interpolated Ground | 11516.6 | -4.55 | 567.22 | 0 | 31.42 | 0 | OK | Ground clear controls. | 30 | 54.14 | 598.64
1826 | TIN-INTERP | Interpolated Ground | 11516.6 | -6.55 | 566.75 | 0 | 26.44 | 0 | OK | Ground clear controls. | 30 | 54.14 | 593.19
1827 | TIN-INTERP | Interpolated Ground | 11556.52 | 5.18 | 557.97 | 0 | 27.22 | 0 | OK | Ground clear controls. | 30 | 54.14 | 585.19
1828 | TIN-INTERP | Interpolated Ground | 11556.55 | 4.69 | 557.66 | 0 | 38.58 | 0 | OK | Ground clear controls. | 30 | 54.14 | 596.24
1829 | TIN-INTERP | Interpolated Ground | 11556.56 | 6.68 | 558.6 | 0 | 32.11 | 0 | OK | Ground clear controls. | 30 | 54.14 | 590.71
1830 | TIN-INTERP | Interpolated Ground | 11556.59 | -5.04 | 555.13 | 0 | 30.31 | 0 | OK | Ground clear controls. | 30 | 54.14 | 585.44
1831 | TIN-INTERP | Interpolated Ground | 11556.6 | -4.54 | 554.96 | 0 | 41.35 | 0 | OK | Ground clear controls. | 30 | 54.14 | 596.31
1832 | TIN-INTERP | Interpolated Ground | 11556.6 | -6.54 | 555.73 | 0 | 35.13 | 0 | OK | Ground clear controls. | 30 | 54.14 | 590.86
1833 | TIN-INTERP | Interpolated Ground | 11596.52 | 5.2 | 543.76 | 0 | 40.02 | 0 | OK | Ground clear controls. | 30 | 54.14 | 583.78
1834 | TIN-INTERP | Interpolated Ground | 11596.55 | 4.7 | 543.82 | 0 | 51 | 0 | OK | Ground clear controls. | 30 | 54.14 | 594.82
1835 | TIN-INTERP | Interpolated Ground | 11596.56 | 6.7 | 543.68 | 0 | 45.62 | 0 | OK | Ground clear controls. | 30 | 54.14 | 589.3
1836 | TIN-INTERP | Interpolated Ground | 11596.59 | -5.03 | 546.31 | 0 | 37.69 | 0 | OK | Ground clear controls. | 30 | 54.14 | 584
1837 | TIN-INTERP | Interpolated Ground | 11596.6 | -4.53 | 546.11 | 0 | 48.78 | 0 | OK | Ground clear controls. | 30 | 54.14 | 594.89
1838 | TIN-INTERP | Interpolated Ground | 11596.6 | -6.52 | 546.54 | 0 | 42.89 | 0 | OK | Ground clear controls. | 30 | 54.14 | 589.43
1839 | TIN-INTERP | Interpolated Ground | 11636.52 | 5.21 | 540.59 | 0 | 42.7 | 0 | OK | Ground clear controls. | 30 | 54.14 | 583.29
1840 | TIN-INTERP | Interpolated Ground | 11636.55 | 4.72 | 540.5 | 0 | 53.83 | 0 | OK | Ground clear controls. | 30 | 54.14 | 594.33
1841 | TIN-INTERP | Interpolated Ground | 11636.56 | 6.71 | 540.82 | 0 | 47.99 | 0 | OK | Ground clear controls. | 30 | 54.14 | 588.81
1842 | TIN-INTERP | Interpolated Ground | 11636.59 | -5.01 | 540.42 | 0 | 43.06 | 0 | OK | Ground clear controls. | 30 | 54.14 | 583.48
1843 | TIN-INTERP | Interpolated Ground | 11636.6 | -4.52 | 540.25 | 0 | 54.14 | 0 | OK | Ground clear controls. | 30 | 54.14 | 594.39
1844 | TIN-INTERP | Interpolated Ground | 11636.6 | -6.51 | 541 | 0 | 47.92 | 0 | OK | Ground clear controls. | 30 | 52.93 | 588.92
1845 | TIN-INTERP | Interpolated Ground | 11676.52 | 5.23 | 546.97 | 0 | 36.75 | 0 | OK | Ground clear controls. | 30 | 52.93 | 583.72
1846 | TIN-INTERP | Interpolated Ground | 11676.55 | 4.73 | 546.92 | 0 | 47.82 | 0 | OK | Ground clear controls. | 30 | 52.93 | 594.74
1847 | TIN-INTERP | Interpolated Ground | 11676.56 | 6.73 | 547.08 | 0 | 42.15 | 0 | OK | Ground clear controls. | 30 | 52.93 | 589.23
1848 | TIN-INTERP | Interpolated Ground | 11676.59 | -5 | 541.58 | 0 | 42.27 | 0 | OK | Ground clear controls. | 30 | 52.93 | 583.85
1849 | TIN-INTERP | Interpolated Ground | 11676.6 | -4.5 | 541.86 | 0 | 52.93 | 0 | OK | Ground clear controls. | 30 | 52.93 | 594.79
1850 | TIN-INTERP | Interpolated Ground | 11676.6 | -6.5 | 540.75 | 0 | 48.57 | 0 | OK | Ground clear controls. | 30 | 48.57 | 589.32
1851 | TIN-INTERP | Interpolated Ground | 11716.52 | 5.24 | 557.64 | 0 | 27.42 | 0 | OK | Ground clear controls. | 30 | 41.11 | 585.06
1852 | TIN-INTERP | Interpolated Ground | 11716.55 | 4.75 | 557.71 | 0 | 38.36 | 0 | OK | Ground clear controls. | 30 | 41.11 | 596.07
1853 | TIN-INTERP | Interpolated Ground | 11716.56 | 6.74 | 557.49 | 0 | 33.07 | 0 | OK | Ground clear controls. | 30 | 41.11 | 590.56
1854 | TIN-INTERP | Interpolated Ground | 11716.59 | -4.99 | 555 | 0 | 30.13 | 0 | OK | Ground clear controls. | 30 | 41.11 | 585.13
1855 | TIN-INTERP | Interpolated Ground | 11716.6 | -4.49 | 554.99 | 0 | 41.11 | 0 | OK | Ground clear controls. | 30 | 41.11 | 596.1
1856 | TIN-INTERP | Interpolated Ground | 11716.6 | -6.49 | 554.98 | 0 | 35.64 | 0 | OK | Ground clear controls. | 30 | 35.64 | 590.62
1857 | TIN-INTERP | Interpolated Ground | 11747.87 | -6.48 | 561.78 | 0 | 30.48 | 0 | OK | Ground clear controls. | 31 | 41.32 | 592.26
1858 | TIN-INTERP | Interpolated Ground | 11747.94 | -4.98 | 562.4 | 0 | 24.36 | 0 | OK | Ground clear controls. | 31 | 41.32 | 586.76
1859 | TIN-INTERP | Interpolated Ground | 11747.95 | -4.48 | 562.61 | 0 | 35.16 | 0 | OK | Ground clear controls. | 31 | 41.32 | 597.77
1860 | TIN-INTERP | Interpolated Ground | 11748.12 | 5.25 | 564.86 | 0 | 21.9 | 0 | OK | Ground clear controls. | 31 | 41.32 | 586.76
1861 | TIN-INTERP | Interpolated Ground | 11748.14 | 4.76 | 564.7 | 0 | 33.06 | 0 | OK | Ground clear controls. | 31 | 41.32 | 597.76
1862 | TIN-INTERP | Interpolated Ground | 11748.14 | 6.75 | 564.98 | 0 | 27.28 | 0 | OK | Ground clear controls. | 31 | 41.32 | 592.26
1863 | TIN-INTERP | Interpolated Ground | 11787.87 | -6.56 | 555.18 | 0 | 33.04 | 0 | OK | Ground clear controls. | 31 | 41.32 | 588.22
1864 | TIN-INTERP | Interpolated Ground | 11787.94 | -5.06 | 555.16 | 0 | 27.57 | 0 | OK | Ground clear controls. | 31 | 41.32 | 582.73
1865 | TIN-INTERP | Interpolated Ground | 11787.95 | -4.58 | 555.16 | 0 | 38.61 | 0 | OK | Ground clear controls. | 31 | 41.32 | 593.77
1866 | TIN-INTERP | Interpolated Ground | 11788.12 | 5.26 | 555.34 | 0 | 27.36 | 0 | OK | Ground clear controls. | 31 | 41.32 | 582.7
1867 | TIN-INTERP | Interpolated Ground | 11788.14 | 4.78 | 555.35 | 0 | 38.42 | 0 | OK | Ground clear controls. | 31 | 41.32 | 593.77
1868 | TIN-INTERP | Interpolated Ground | 11788.14 | 6.76 | 555.3 | 0 | 32.9 | 0 | OK | Ground clear controls. | 31 | 41.32 | 588.2
1869 | TIN-INTERP | Interpolated Ground | 11827.87 | -6.64 | 549.33 | 0 | 35.74 | 0 | OK | Ground clear controls. | 31 | 41.32 | 585.07
1870 | TIN-INTERP | Interpolated Ground | 11827.94 | -5.14 | 549.35 | 0 | 30.25 | 0 | OK | Ground clear controls. | 31 | 41.32 | 579.6
1871 | TIN-INTERP | Interpolated Ground | 11827.95 | -4.68 | 549.37 | 0 | 41.32 | 0 | OK | Ground clear controls. | 31 | 41.32 | 590.69
1872 | TIN-INTERP | Interpolated Ground | 11828.12 | 5.27 | 549.66 | 0 | 29.9 | 0 | OK | Ground clear controls. | 31 | 41.02 | 579.56
1873 | TIN-INTERP | Interpolated Ground | 11828.14 | 4.8 | 549.66 | 0 | 41.02 | 0 | OK | Ground clear controls. | 31 | 41.02 | 590.68
1874 | TIN-INTERP | Interpolated Ground | 11828.14 | 6.77 | 549.63 | 0 | 35.43 | 0 | OK | Ground clear controls. | 31 | 37.56 | 585.06
1875 | TIN-INTERP | Interpolated Ground | 11867.87 | -6.73 | 550.61 | 0 | 32.26 | 0 | OK | Ground clear controls. | 31 | 37.56 | 582.87
1876 | TIN-INTERP | Interpolated Ground | 11867.94 | -5.23 | 550.94 | 0 | 26.45 | 0 | OK | Ground clear controls. | 31 | 37.56 | 577.39
1877 | TIN-INTERP | Interpolated Ground | 11867.95 | -4.78 | 550.96 | 0 | 37.56 | 0 | OK | Ground clear controls. | 31 | 37.56 | 588.52
1878 | TIN-INTERP | Interpolated Ground | 11868.12 | 5.28 | 552.54 | 0 | 24.8 | 0 | OK | Ground clear controls. | 31 | 36.08 | 577.34
1879 | TIN-INTERP | Interpolated Ground | 11868.14 | 4.83 | 552.44 | 0 | 36.08 | 0 | OK | Ground clear controls. | 31 | 36.08 | 588.52
1880 | TIN-INTERP | Interpolated Ground | 11868.14 | 6.78 | 552.72 | 0 | 30.12 | 0 | OK | Ground clear controls. | 31 | 33.5 | 582.84
1881 | TIN-INTERP | Interpolated Ground | 11907.87 | -6.81 | 553.08 | 0 | 28.47 | 0 | OK | Ground clear controls. | 31 | 33.5 | 581.55
1882 | TIN-INTERP | Interpolated Ground | 11907.94 | -5.31 | 553.62 | 0 | 22.46 | 0 | OK | Ground clear controls. | 31 | 33.5 | 576.08
1883 | TIN-INTERP | Interpolated Ground | 11907.95 | -4.88 | 553.85 | 0 | 33.42 | 0 | OK | Ground clear controls. | 31 | 33.5 | 587.27
1884 | TIN-INTERP | Interpolated Ground | 11908.12 | 5.28 | 558.2 | 0 | 17.84 | 0 | OK | Ground clear controls. | 31 | 33.5 | 576.04
1885 | TIN-INTERP | Interpolated Ground | 11908.14 | 4.85 | 558.03 | 0 | 29.24 | 0 | OK | Ground clear controls. | 31 | 33.5 | 587.27
1886 | TIN-INTERP | Interpolated Ground | 11908.14 | 6.78 | 558.75 | 0 | 22.79 | 0 | OK | Ground clear controls. | 31 | 33.5 | 581.54
1887 | TIN-INTERP | Interpolated Ground | 11947.87 | -6.9 | 554.93 | 0 | 26.24 | 0 | OK | Ground clear controls. | 31 | 33.5 | 581.17
1888 | TIN-INTERP | Interpolated Ground | 11947.94 | -5.4 | 554.45 | 0 | 21.23 | 0 | OK | Ground clear controls. | 31 | 33.5 | 575.68
1889 | TIN-INTERP | Interpolated Ground | 11947.95 | -4.98 | 554.33 | 0 | 32.6 | 0 | OK | Ground clear controls. | 31 | 33.5 | 586.93
1890 | TIN-INTERP | Interpolated Ground | 11948.12 | 5.29 | 553.38 | 0 | 22.28 | 0 | OK | Ground clear controls. | 31 | 33.5 | 575.66
1891 | TIN-INTERP | Interpolated Ground | 11948.14 | 4.87 | 553.43 | 0 | 33.5 | 0 | OK | Ground clear controls. | 31 | 33.5 | 586.93
1892 | TIN-INTERP | Interpolated Ground | 11948.14 | 6.79 | 553.21 | 0 | 27.95 | 0 | OK | Ground clear controls. | 31 | 27.95 | 581.16
1893 | TIN-INTERP | Interpolated Ground | 11972.77 | -5.45 | 557.56 | 0 | 18.32 | 0 | OK | Ground clear controls. | 32 | 50.09 | 575.88
1894 | TIN-INTERP | Interpolated Ground | 11972.8 | -6.95 | 557.29 | 0 | 24.1 | 0 | OK | Ground clear controls. | 32 | 50.09 | 581.39
1895 | TIN-INTERP | Interpolated Ground | 11972.83 | 5.3 | 558.61 | 0 | 17.27 | 0 | OK | Ground clear controls. | 32 | 50.09 | 575.88
1896 | TIN-INTERP | Interpolated Ground | 11972.84 | 6.8 | 558.56 | 0 | 22.83 | 0 | OK | Ground clear controls. | 32 | 50.09 | 581.39
1897 | TIN-INTERP | Interpolated Ground | 11972.85 | -5.04 | 557.62 | 0 | 29.56 | 0 | OK | Ground clear controls. | 32 | 50.09 | 587.18
1898 | TIN-INTERP | Interpolated Ground | 11972.86 | 4.89 | 558.62 | 0 | 28.56 | 0 | OK | Ground clear controls. | 32 | 50.09 | 587.18
1899 | TIN-INTERP | Interpolated Ground | 12012.76 | -5.43 | 551.39 | 0 | 19.94 | 0 | OK | Ground clear controls. | 32 | 50.09 | 571.33
1900 | TIN-INTERP | Interpolated Ground | 12012.79 | -6.93 | 551.19 | 0 | 25.61 | 0 | OK | Ground clear controls. | 32 | 50.09 | 576.8
1901 | TIN-INTERP | Interpolated Ground | 12012.83 | 5.27 | 553.2 | 0 | 18.06 | 0 | OK | Ground clear controls. | 32 | 50.09 | 571.26
1902 | TIN-INTERP | Interpolated Ground | 12012.84 | -5.02 | 551.42 | 0 | 31.17 | 0 | OK | Ground clear controls. | 32 | 50.09 | 582.59
1903 | TIN-INTERP | Interpolated Ground | 12012.85 | 6.77 | 553.69 | 0 | 23.09 | 0 | OK | Ground clear controls. | 32 | 50.09 | 576.78
1904 | TIN-INTERP | Interpolated Ground | 12012.86 | 4.86 | 553.11 | 0 | 29.48 | 0 | OK | Ground clear controls. | 32 | 50.09 | 582.59
1905 | TIN-INTERP | Interpolated Ground | 12052.76 | -5.42 | 543.11 | 0 | 24.59 | 0 | OK | Ground clear controls. | 32 | 50.09 | 567.7
1906 | TIN-INTERP | Interpolated Ground | 12052.79 | -6.92 | 542.97 | 0 | 30.16 | 0 | OK | Ground clear controls. | 32 | 50.09 | 573.13
1907 | TIN-INTERP | Interpolated Ground | 12052.83 | 5.25 | 544.22 | 0 | 23.36 | 0 | OK | Ground clear controls. | 32 | 50.09 | 567.58
1908 | TIN-INTERP | Interpolated Ground | 12052.84 | -5 | 543.18 | 0 | 35.76 | 0 | OK | Ground clear controls. | 32 | 50.09 | 578.94
1909 | TIN-INTERP | Interpolated Ground | 12052.85 | 6.75 | 544.46 | 0 | 28.66 | 0 | OK | Ground clear controls. | 32 | 50.09 | 573.12
1910 | TIN-INTERP | Interpolated Ground | 12052.86 | 4.83 | 544.17 | 0 | 34.76 | 0 | OK | Ground clear controls. | 32 | 50.09 | 578.93
1911 | TIN-INTERP | Interpolated Ground | 12092.76 | -5.4 | 533.12 | 0 | 31.86 | 0 | OK | Ground clear controls. | 32 | 50.09 | 564.98
1912 | TIN-INTERP | Interpolated Ground | 12092.79 | -6.9 | 533.11 | 0 | 37.29 | 0 | OK | Ground clear controls. | 32 | 50.09 | 570.4
1913 | TIN-INTERP | Interpolated Ground | 12092.83 | 5.23 | 533.08 | 0 | 31.74 | 0 | OK | Ground clear controls. | 32 | 50.09 | 564.82
1914 | TIN-INTERP | Interpolated Ground | 12092.84 | -4.98 | 533.08 | 0 | 43.11 | 0 | OK | Ground clear controls. | 32 | 50.09 | 576.19
1915 | TIN-INTERP | Interpolated Ground | 12092.85 | 6.73 | 533.1 | 0 | 37.27 | 0 | OK | Ground clear controls. | 32 | 50.09 | 570.37
1916 | TIN-INTERP | Interpolated Ground | 12092.86 | 4.8 | 533.1 | 0 | 43.09 | 0 | OK | Ground clear controls. | 32 | 50.09 | 576.19
1917 | TIN-INTERP | Interpolated Ground | 12132.76 | -5.39 | 529.94 | 0 | 33.25 | 0 | OK | Ground clear controls. | 32 | 50.09 | 563.19
1918 | TIN-INTERP | Interpolated Ground | 12132.79 | -6.89 | 529.67 | 0 | 38.91 | 0 | OK | Ground clear controls. | 32 | 50.09 | 568.58
1919 | TIN-INTERP | Interpolated Ground | 12132.83 | 5.21 | 530.72 | 0 | 32.27 | 0 | OK | Ground clear controls. | 32 | 50.09 | 562.99
1920 | TIN-INTERP | Interpolated Ground | 12132.84 | -4.96 | 530.06 | 0 | 44.31 | 0 | OK | Ground clear controls. | 32 | 50.09 | 574.37
1921 | TIN-INTERP | Interpolated Ground | 12132.85 | 6.71 | 530.77 | 0 | 37.78 | 0 | OK | Ground clear controls. | 32 | 50.09 | 568.55
1922 | TIN-INTERP | Interpolated Ground | 12132.86 | 4.77 | 530.71 | 0 | 43.65 | 0 | OK | Ground clear controls. | 32 | 50.09 | 574.36
1923 | TIN-INTERP | Interpolated Ground | 12172.76 | -5.37 | 529.68 | 0 | 32.62 | 0 | OK | Ground clear controls. | 32 | 50.09 | 562.3
1924 | TIN-INTERP | Interpolated Ground | 12172.79 | -6.87 | 529.2 | 0 | 38.49 | 0 | OK | Ground clear controls. | 32 | 50.09 | 567.69
1925 | TIN-INTERP | Interpolated Ground | 12172.83 | 5.18 | 533.35 | 0 | 28.73 | 0 | OK | Ground clear controls. | 32 | 50.09 | 562.08
1926 | TIN-INTERP | Interpolated Ground | 12172.84 | -4.94 | 529.9 | 0 | 43.56 | 0 | OK | Ground clear controls. | 32 | 50.09 | 573.46
1927 | TIN-INTERP | Interpolated Ground | 12172.85 | 6.68 | 533.67 | 0 | 33.97 | 0 | OK | Ground clear controls. | 32 | 50.09 | 567.64
1928 | TIN-INTERP | Interpolated Ground | 12172.86 | 4.75 | 533.26 | 0 | 40.19 | 0 | OK | Ground clear controls. | 32 | 50.09 | 573.45
1929 | TIN-INTERP | Interpolated Ground | 12212.76 | -5.36 | 532.37 | 0 | 29.96 | 0 | OK | Ground clear controls. | 32 | 50.09 | 562.33
1930 | TIN-INTERP | Interpolated Ground | 12212.79 | -6.86 | 531.91 | 0 | 35.8 | 0 | OK | Ground clear controls. | 32 | 50.09 | 567.71
1931 | TIN-INTERP | Interpolated Ground | 12212.83 | 5.16 | 535.79 | 0 | 26.31 | 0 | OK | Ground clear controls. | 32 | 50.09 | 562.1
1932 | TIN-INTERP | Interpolated Ground | 12212.84 | -4.92 | 532.52 | 0 | 40.95 | 0 | OK | Ground clear controls. | 32 | 50.09 | 573.47
1933 | TIN-INTERP | Interpolated Ground | 12212.85 | 6.66 | 536.36 | 0 | 31.3 | 0 | OK | Ground clear controls. | 32 | 50.09 | 567.66
1934 | TIN-INTERP | Interpolated Ground | 12212.86 | 4.72 | 535.63 | 0 | 37.84 | 0 | OK | Ground clear controls. | 32 | 50.09 | 573.47
1935 | TIN-INTERP | Interpolated Ground | 12252.76 | -5.35 | 526.68 | 0 | 36.61 | 0 | OK | Ground clear controls. | 32 | 50.09 | 563.29
1936 | TIN-INTERP | Interpolated Ground | 12252.79 | -6.85 | 526.52 | 0 | 42.15 | 0 | OK | Ground clear controls. | 32 | 50.09 | 568.67
1937 | TIN-INTERP | Interpolated Ground | 12252.83 | 5.14 | 529.35 | 0 | 33.7 | 0 | OK | Ground clear controls. | 32 | 50.09 | 563.05
1938 | TIN-INTERP | Interpolated Ground | 12252.84 | -4.9 | 526.78 | 0 | 47.63 | 0 | OK | Ground clear controls. | 32 | 50.09 | 574.41
1939 | TIN-INTERP | Interpolated Ground | 12252.85 | 6.64 | 530.23 | 0 | 38.39 | 0 | OK | Ground clear controls. | 32 | 50.09 | 568.62
1940 | TIN-INTERP | Interpolated Ground | 12252.86 | 4.69 | 529.27 | 0 | 45.13 | 0 | OK | Ground clear controls. | 32 | 50.09 | 574.4
1941 | TIN-INTERP | Interpolated Ground | 12292.76 | -5.33 | 526.61 | 0 | 38.56 | 0 | OK | Ground clear controls. | 32 | 50.09 | 565.17
1942 | TIN-INTERP | Interpolated Ground | 12292.79 | -6.83 | 526.58 | 0 | 43.96 | 0 | OK | Ground clear controls. | 32 | 50.09 | 570.54
1943 | TIN-INTERP | Interpolated Ground | 12292.83 | 5.12 | 526.83 | 0 | 38.09 | 0 | OK | Ground clear controls. | 32 | 50.09 | 564.92
1944 | TIN-INTERP | Interpolated Ground | 12292.84 | -4.88 | 526.62 | 0 | 49.65 | 0 | OK | Ground clear controls. | 32 | 50.09 | 576.27
1945 | TIN-INTERP | Interpolated Ground | 12292.85 | 6.62 | 526.85 | 0 | 43.64 | 0 | OK | Ground clear controls. | 32 | 50.09 | 570.49
1946 | TIN-INTERP | Interpolated Ground | 12292.86 | 4.66 | 526.83 | 0 | 49.43 | 0 | OK | Ground clear controls. | 32 | 50.09 | 576.26
1947 | TIN-INTERP | Interpolated Ground | 12332.76 | -5.32 | 529.01 | 0 | 38.95 | 0 | OK | Ground clear controls. | 32 | 50.09 | 567.96
1948 | TIN-INTERP | Interpolated Ground | 12332.79 | -6.82 | 529.36 | 0 | 43.98 | 0 | OK | Ground clear controls. | 32 | 50.09 | 573.34
1949 | TIN-INTERP | Interpolated Ground | 12332.83 | 5.1 | 528.95 | 0 | 38.76 | 0 | OK | Ground clear controls. | 32 | 50.09 | 567.71
1950 | TIN-INTERP | Interpolated Ground | 12332.84 | -4.86 | 528.98 | 0 | 50.06 | 0 | OK | Ground clear controls. | 32 | 50.09 | 579.04
1951 | TIN-INTERP | Interpolated Ground | 12332.85 | 6.59 | 529.02 | 0 | 44.27 | 0 | OK | Ground clear controls. | 32 | 50.09 | 573.29
1952 | TIN-INTERP | Interpolated Ground | 12332.86 | 4.63 | 528.94 | 0 | 50.09 | 0 | OK | Ground clear controls. | 32 | 50.09 | 579.03
1953 | TIN-INTERP | Interpolated Ground | 12372.76 | -5.3 | 538.36 | 0 | 33.31 | 0 | OK | Ground clear controls. | 32 | 46.17 | 571.67
1954 | TIN-INTERP | Interpolated Ground | 12372.79 | -6.8 | 538.66 | 0 | 38.39 | 0 | OK | Ground clear controls. | 32 | 46.17 | 577.05
1955 | TIN-INTERP | Interpolated Ground | 12372.83 | 5.07 | 536.56 | 0 | 34.88 | 0 | OK | Ground clear controls. | 32 | 46.17 | 571.44
1956 | TIN-INTERP | Interpolated Ground | 12372.84 | -4.84 | 538.3 | 0 | 44.44 | 0 | OK | Ground clear controls. | 32 | 46.17 | 582.74
1957 | TIN-INTERP | Interpolated Ground | 12372.85 | 6.57 | 536.58 | 0 | 40.42 | 0 | OK | Ground clear controls. | 32 | 46.17 | 577
1958 | TIN-INTERP | Interpolated Ground | 12372.86 | 4.6 | 536.56 | 0 | 46.17 | 0 | OK | Ground clear controls. | 32 | 46.17 | 582.73
1959 | TIN-INTERP | Interpolated Ground | 12412.76 | -5.29 | 552.62 | 0 | 23.68 | 0 | OK | Ground clear controls. | 32 | 38.44 | 576.3
1960 | TIN-INTERP | Interpolated Ground | 12412.79 | -6.79 | 552.6 | 0 | 29.1 | 0 | OK | Ground clear controls. | 32 | 38.44 | 581.7
1961 | TIN-INTERP | Interpolated Ground | 12412.83 | 5.05 | 552.66 | 0 | 23.44 | 0 | OK | Ground clear controls. | 32 | 38.44 | 576.1
1962 | TIN-INTERP | Interpolated Ground | 12412.84 | -4.81 | 552.68 | 0 | 34.68 | 0 | OK | Ground clear controls. | 32 | 38.44 | 587.36
1963 | TIN-INTERP | Interpolated Ground | 12412.85 | 6.55 | 551.97 | 0 | 29.68 | 0 | OK | Ground clear controls. | 32 | 38.44 | 581.65
1964 | TIN-INTERP | Interpolated Ground | 12412.86 | 4.58 | 552.89 | 0 | 34.45 | 0 | OK | Ground clear controls. | 32 | 38.44 | 587.34
1965 | TIN-INTERP | Interpolated Ground | 12452.76 | -5.27 | 565.16 | 0 | 16.7 | 0 | OK | Ground clear controls. | 32 | 38.44 | 581.86
1966 | TIN-INTERP | Interpolated Ground | 12452.79 | -6.77 | 565.34 | 0 | 21.94 | 0 | OK | Ground clear controls. | 32 | 38.44 | 587.28
1967 | TIN-INTERP | Interpolated Ground | 12452.83 | 5.03 | 564.07 | 0 | 17.61 | 0 | OK | Ground clear controls. | 32 | 38.44 | 581.68
1968 | TIN-INTERP | Interpolated Ground | 12452.84 | -4.79 | 565.17 | 0 | 27.74 | 0 | OK | Ground clear controls. | 32 | 38.44 | 592.91
1969 | TIN-INTERP | Interpolated Ground | 12452.85 | 6.53 | 564.08 | 0 | 23.16 | 0 | OK | Ground clear controls. | 32 | 38.44 | 587.24
1970 | TIN-INTERP | Interpolated Ground | 12452.86 | 4.55 | 564.06 | 0 | 28.83 | 0 | OK | Ground clear controls. | 32 | 38.44 | 592.89
1971 | TIN-INTERP | Interpolated Ground | 12492.76 | -5.26 | 576.1 | 0 | 12.25 | 0 | OK | Ground clear controls. | 32 | 38.44 | 588.35
1972 | TIN-INTERP | Interpolated Ground | 12492.79 | -6.76 | 576.06 | 0 | 17.73 | 0 | OK | Ground clear controls. | 32 | 38.44 | 593.79
1973 | TIN-INTERP | Interpolated Ground | 12492.83 | 5.01 | 575.51 | 0 | 12.71 | 0 | OK | Ground clear controls. | 32 | 38.44 | 588.22
1974 | TIN-INTERP | Interpolated Ground | 12492.84 | -4.77 | 576.12 | 0 | 23.27 | 0 | OK | Ground clear controls. | 32 | 38.44 | 599.39
1975 | TIN-INTERP | Interpolated Ground | 12492.85 | 6.51 | 575.92 | 0 | 17.83 | 0 | OK | Ground clear controls. | 32 | 38.44 | 593.75
1976 | TIN-INTERP | Interpolated Ground | 12492.86 | 4.52 | 575.39 | 0 | 23.98 | 0 | OK | Ground clear controls. | 32 | 38.44 | 599.37
1977 | TIN-INTERP | Interpolated Ground | 12532.76 | -5.24 | 572.66 | 0 | 23.11 | 0 | OK | Ground clear controls. | 32 | 38.44 | 595.77
1978 | TIN-INTERP | Interpolated Ground | 12532.79 | -6.74 | 572.12 | 0 | 29.12 | 0 | OK | Ground clear controls. | 32 | 38.44 | 601.24
1979 | TIN-INTERP | Interpolated Ground | 12532.83 | 4.98 | 574.65 | 0 | 21.03 | 0 | OK | Ground clear controls. | 32 | 38.44 | 595.68
1980 | TIN-INTERP | Interpolated Ground | 12532.84 | -4.75 | 572.8 | 0 | 34 | 0 | OK | Ground clear controls. | 32 | 38.44 | 606.8
1981 | TIN-INTERP | Interpolated Ground | 12532.85 | 6.48 | 574.64 | 0 | 26.56 | 0 | OK | Ground clear controls. | 32 | 38.44 | 601.2
1982 | TIN-INTERP | Interpolated Ground | 12532.86 | 4.49 | 574.62 | 0 | 32.16 | 0 | OK | Ground clear controls. | 32 | 38.44 | 606.78
1983 | TIN-INTERP | Interpolated Ground | 12572.76 | -5.23 | 576.68 | 0 | 27.44 | 0 | OK | Ground clear controls. | 32 | 38.44 | 604.12
1984 | TIN-INTERP | Interpolated Ground | 12572.79 | -6.73 | 576.7 | 0 | 32.92 | 0 | OK | Ground clear controls. | 32 | 38.44 | 609.62
1985 | TIN-INTERP | Interpolated Ground | 12572.83 | 4.96 | 577.1 | 0 | 26.99 | 0 | OK | Ground clear controls. | 32 | 38.44 | 604.09
1986 | TIN-INTERP | Interpolated Ground | 12572.84 | -4.73 | 576.7 | 0 | 38.44 | 0 | OK | Ground clear controls. | 32 | 38.44 | 615.14
1987 | TIN-INTERP | Interpolated Ground | 12572.85 | 6.46 | 577.19 | 0 | 32.4 | 0 | OK | Ground clear controls. | 32 | 38.05 | 609.59
1988 | TIN-INTERP | Interpolated Ground | 12572.86 | 4.46 | 577.07 | 0 | 38.05 | 0 | OK | Ground clear controls. | 32 | 38.05 | 615.12
1989 | TIN-INTERP | Interpolated Ground | 12588.85 | -6.72 | 579.73 | 0 | 33.51 | 0 | OK | Ground clear controls. | 33 | 47.99 | 613.24
1990 | TIN-INTERP | Interpolated Ground | 12588.86 | -4.73 | 580.13 | 0 | 38.61 | 0 | OK | Ground clear controls. | 33 | 47.99 | 618.74
1991 | TIN-INTERP | Interpolated Ground | 12588.89 | -5.22 | 580.01 | 0 | 27.73 | 0 | OK | Ground clear controls. | 33 | 47.99 | 607.74
1992 | TIN-INTERP | Interpolated Ground | 12588.97 | 4.95 | 581.13 | 0 | 26.62 | 0 | OK | Ground clear controls. | 33 | 47.99 | 607.75
1993 | TIN-INTERP | Interpolated Ground | 12588.97 | 4.45 | 581.03 | 0 | 37.71 | 0 | OK | Ground clear controls. | 33 | 47.99 | 618.74
1994 | TIN-INTERP | Interpolated Ground | 12589.03 | 6.45 | 581.2 | 0 | 32.05 | 0 | OK | Ground clear controls. | 33 | 47.99 | 613.25
1995 | TIN-INTERP | Interpolated Ground | 12628.85 | -6.6 | 574.07 | 0 | 37.22 | 0 | OK | Ground clear controls. | 33 | 47.99 | 611.29
1996 | TIN-INTERP | Interpolated Ground | 12628.86 | -4.61 | 574.74 | 0 | 42.04 | 0 | OK | Ground clear controls. | 33 | 47.99 | 616.78
1997 | TIN-INTERP | Interpolated Ground | 12628.89 | -5.1 | 574.5 | 0 | 31.3 | 0 | OK | Ground clear controls. | 33 | 47.99 | 605.8
1998 | TIN-INTERP | Interpolated Ground | 12628.97 | 4.93 | 577.15 | 0 | 28.6 | 0 | OK | Ground clear controls. | 33 | 47.99 | 605.75
1999 | TIN-INTERP | Interpolated Ground | 12628.97 | 4.42 | 576.97 | 0 | 39.8 | 0 | OK | Ground clear controls. | 33 | 47.99 | 616.77
2000 | TIN-INTERP | Interpolated Ground | 12629.03 | 6.42 | 577.65 | 0 | 33.62 | 0 | OK | Ground clear controls. | 33 | 47.99 | 611.27
2001 | TIN-INTERP | Interpolated Ground | 12668.85 | -6.48 | 569.71 | 0 | 40.51 | 0 | OK | Ground clear controls. | 33 | 47.99 | 610.22
2002 | TIN-INTERP | Interpolated Ground | 12668.86 | -4.5 | 568.96 | 0 | 46.75 | 0 | OK | Ground clear controls. | 33 | 47.99 | 615.71
2003 | TIN-INTERP | Interpolated Ground | 12668.89 | -4.98 | 569.18 | 0 | 35.58 | 0 | OK | Ground clear controls. | 33 | 47.99 | 604.76
2004 | TIN-INTERP | Interpolated Ground | 12668.97 | 4.91 | 567.43 | 0 | 37.23 | 0 | OK | Ground clear controls. | 33 | 47.99 | 604.66
2005 | TIN-INTERP | Interpolated Ground | 12668.97 | 4.38 | 567.7 | 0 | 47.99 | 0 | OK | Ground clear controls. | 33 | 47.99 | 615.69
2006 | TIN-INTERP | Interpolated Ground | 12669.03 | 6.39 | 566.93 | 0 | 43.25 | 0 | OK | Ground clear controls. | 33 | 43.25 | 610.18
2007 | TIN-INTERP | Interpolated Ground | 12708.85 | -6.36 | 584.36 | 0 | 25.7 | 0 | OK | Ground clear controls. | 33 | 31.19 | 610.06
2008 | TIN-INTERP | Interpolated Ground | 12708.86 | -4.38 | 584.35 | 0 | 31.19 | 0 | OK | Ground clear controls. | 33 | 31.19 | 615.54
2009 | TIN-INTERP | Interpolated Ground | 12708.89 | -4.86 | 584.36 | 0 | 20.24 | 0 | OK | Ground clear controls. | 33 | 31.03 | 604.6
2010 | TIN-INTERP | Interpolated Ground | 12708.97 | 4.89 | 584.59 | 0 | 19.87 | 0 | OK | Ground clear controls. | 33 | 31.03 | 604.46
2011 | TIN-INTERP | Interpolated Ground | 12708.97 | 4.35 | 584.46 | 0 | 31.03 | 0 | OK | Ground clear controls. | 33 | 31.03 | 615.49
2012 | TIN-INTERP | Interpolated Ground | 12709.03 | 6.36 | 584.91 | 0 | 25.08 | 0 | OK | Ground clear controls. | 33 | 27.81 | 609.99
2013 | TIN-INTERP | Interpolated Ground | 12748.85 | -6.24 | 588.87 | 0 | 21.92 | 0 | OK | Ground clear controls. | 33 | 27.81 | 610.79
2014 | TIN-INTERP | Interpolated Ground | 12748.86 | -4.27 | 588.92 | 0 | 27.34 | 0 | OK | Ground clear controls. | 33 | 27.81 | 616.26
2015 | TIN-INTERP | Interpolated Ground | 12748.89 | -4.74 | 588.89 | 0 | 16.44 | 0 | OK | Ground clear controls. | 33 | 27.81 | 605.33
2016 | TIN-INTERP | Interpolated Ground | 12748.97 | 4.87 | 589.13 | 0 | 16.02 | 0 | OK | Ground clear controls. | 33 | 27.81 | 605.15
2017 | TIN-INTERP | Interpolated Ground | 12748.97 | 4.31 | 589.1 | 0 | 27.08 | 0 | OK | Ground clear controls. | 33 | 27.81 | 616.18
2018 | TIN-INTERP | Interpolated Ground | 12749.03 | 6.33 | 589.15 | 0 | 21.53 | 0 | OK | Ground clear controls. | 33 | 27.81 | 610.68
2019 | TIN-INTERP | Interpolated Ground | 12788.85 | -6.12 | 592.85 | 0 | 19.57 | 0 | OK | Ground clear controls. | 33 | 27.81 | 612.42
2020 | TIN-INTERP | Interpolated Ground | 12788.86 | -4.15 | 592.94 | 0 | 24.94 | 0 | OK | Ground clear controls. | 33 | 27.81 | 617.88
2021 | TIN-INTERP | Interpolated Ground | 12788.89 | -4.62 | 592.92 | 0 | 14.03 | 0 | OK | Ground clear controls. | 33 | 27.81 | 606.95
2022 | TIN-INTERP | Interpolated Ground | 12788.97 | 4.85 | 593 | 0 | 13.75 | 0 | OK | Ground clear controls. | 33 | 27.81 | 606.75
2023 | TIN-INTERP | Interpolated Ground | 12788.97 | 4.28 | 593.01 | 0 | 24.76 | 0 | OK | Ground clear controls. | 33 | 27.81 | 617.77
2024 | TIN-INTERP | Interpolated Ground | 12789.03 | 6.3 | 593 | 0 | 19.26 | 0 | OK | Ground clear controls. | 33 | 27.81 | 612.26
2025 | TIN-INTERP | Interpolated Ground | 12828.85 | -6 | 593.91 | 0 | 21.03 | 0 | OK | Ground clear controls. | 33 | 27.81 | 614.94
2026 | TIN-INTERP | Interpolated Ground | 12828.86 | -4.04 | 593.98 | 0 | 26.42 | 0 | OK | Ground clear controls. | 33 | 27.81 | 620.4
2027 | TIN-INTERP | Interpolated Ground | 12828.89 | -4.5 | 593.95 | 0 | 15.5 | 0 | OK | Ground clear controls. | 33 | 27.81 | 609.45
2028 | TIN-INTERP | Interpolated Ground | 12828.97 | 4.83 | 594.26 | 0 | 14.98 | 0 | OK | Ground clear controls. | 33 | 27.81 | 609.24
2029 | TIN-INTERP | Interpolated Ground | 12828.97 | 4.24 | 594.24 | 0 | 26.01 | 0 | OK | Ground clear controls. | 33 | 27.81 | 620.25
2030 | TIN-INTERP | Interpolated Ground | 12829.03 | 6.27 | 594.33 | 0 | 20.41 | 0 | OK | Ground clear controls. | 33 | 27.81 | 614.74
2031 | TIN-INTERP | Interpolated Ground | 12868.85 | -5.88 | 595.98 | 0 | 22.38 | 0 | OK | Ground clear controls. | 33 | 27.81 | 618.36
2032 | TIN-INTERP | Interpolated Ground | 12868.86 | -3.92 | 595.98 | 0 | 27.81 | 0 | OK | Ground clear controls. | 33 | 27.81 | 623.79
2033 | TIN-INTERP | Interpolated Ground | 12868.89 | -4.39 | 595.99 | 0 | 16.86 | 0 | OK | Ground clear controls. | 33 | 27.22 | 612.85
2034 | TIN-INTERP | Interpolated Ground | 12868.97 | 4.81 | 596.44 | 0 | 16.19 | 0 | OK | Ground clear controls. | 33 | 27.22 | 612.63
2035 | TIN-INTERP | Interpolated Ground | 12868.97 | 4.21 | 596.41 | 0 | 27.22 | 0 | OK | Ground clear controls. | 33 | 27.22 | 623.63
2036 | TIN-INTERP | Interpolated Ground | 12869.03 | 6.24 | 596.51 | 0 | 21.59 | 0 | OK | Ground clear controls. | 33 | 21.59 | 618.1
2037 | TIN-INTERP | Interpolated Ground | 12886.6 | 6.21 | 597.38 | 0 | 22.04 | 0 | OK | Ground clear controls. | 34 | 58.31 | 619.42
2038 | TIN-INTERP | Interpolated Ground | 12886.94 | 4.18 | 597.21 | 0 | 27.7 | 0 | OK | Ground clear controls. | 34 | 58.31 | 624.91
2039 | TIN-INTERP | Interpolated Ground | 12887 | 4.77 | 597.3 | 0 | 16.63 | 0 | OK | Ground clear controls. | 34 | 58.31 | 613.93
2040 | TIN-INTERP | Interpolated Ground | 12888.95 | -3.88 | 597.04 | 0 | 27.88 | 0 | OK | Ground clear controls. | 34 | 58.31 | 624.92
2041 | TIN-INTERP | Interpolated Ground | 12889.37 | -4.34 | 597.08 | 0 | 16.85 | 0 | OK | Ground clear controls. | 34 | 58.31 | 613.93
2042 | TIN-INTERP | Interpolated Ground | 12889.63 | -5.82 | 597.15 | 0 | 22.27 | 0 | OK | Ground clear controls. | 34 | 58.31 | 619.42
2043 | TIN-INTERP | Interpolated Ground | 12926.6 | 6.25 | 590.81 | 0 | 25.51 | 0 | OK | Ground clear controls. | 34 | 58.31 | 616.32
2044 | TIN-INTERP | Interpolated Ground | 12926.94 | 4.23 | 590.83 | 0 | 30.99 | 0 | OK | Ground clear controls. | 34 | 58.31 | 621.82
2045 | TIN-INTERP | Interpolated Ground | 12927 | 4.8 | 590.81 | 0 | 20.1 | 0 | OK | Ground clear controls. | 34 | 58.31 | 610.91
2046 | TIN-INTERP | Interpolated Ground | 12928.95 | -4 | 590.94 | 0 | 30.84 | 0 | OK | Ground clear controls. | 34 | 58.31 | 621.78
2047 | TIN-INTERP | Interpolated Ground | 12929.37 | -4.47 | 590.86 | 0 | 20.03 | 0 | OK | Ground clear controls. | 34 | 58.31 | 610.89
2048 | TIN-INTERP | Interpolated Ground | 12929.63 | -5.95 | 590.87 | 0 | 25.44 | 0 | OK | Ground clear controls. | 34 | 58.31 | 616.31
2049 | TIN-INTERP | Interpolated Ground | 12966.6 | 6.29 | 580.13 | 0 | 34 | 0 | OK | Ground clear controls. | 34 | 58.31 | 614.13
2050 | TIN-INTERP | Interpolated Ground | 12966.94 | 4.28 | 580.33 | 0 | 39.32 | 0 | OK | Ground clear controls. | 34 | 58.31 | 619.65
2051 | TIN-INTERP | Interpolated Ground | 12967 | 4.83 | 580.24 | 0 | 28.55 | 0 | OK | Ground clear controls. | 34 | 58.31 | 608.79
2052 | TIN-INTERP | Interpolated Ground | 12968.95 | -4.12 | 580.39 | 0 | 39.21 | 0 | OK | Ground clear controls. | 34 | 58.31 | 619.6
2053 | TIN-INTERP | Interpolated Ground | 12969.37 | -4.59 | 580.27 | 0 | 28.48 | 0 | OK | Ground clear controls. | 34 | 58.31 | 608.75
2054 | TIN-INTERP | Interpolated Ground | 12969.63 | -6.08 | 580.2 | 0 | 33.93 | 0 | OK | Ground clear controls. | 34 | 58.31 | 614.13
2055 | TIN-INTERP | Interpolated Ground | 13006.6 | 6.34 | 574.93 | 0 | 37.94 | 0 | OK | Ground clear controls. | 34 | 58.31 | 612.87
2056 | TIN-INTERP | Interpolated Ground | 13006.94 | 4.32 | 573.21 | 0 | 45.18 | 0 | OK | Ground clear controls. | 34 | 58.31 | 618.39
2057 | TIN-INTERP | Interpolated Ground | 13007 | 4.87 | 573.88 | 0 | 33.67 | 0 | OK | Ground clear controls. | 34 | 58.31 | 607.55
2058 | TIN-INTERP | Interpolated Ground | 13008.95 | -4.24 | 567.73 | 0 | 50.61 | 0 | OK | Ground clear controls. | 34 | 58.31 | 618.34
2059 | TIN-INTERP | Interpolated Ground | 13009.37 | -4.72 | 567.56 | 0 | 39.97 | 0 | OK | Ground clear controls. | 34 | 58.31 | 607.53
2060 | TIN-INTERP | Interpolated Ground | 13009.63 | -6.21 | 566.38 | 0 | 46.51 | 0 | OK | Ground clear controls. | 34 | 58.31 | 612.89
2061 | TIN-INTERP | Interpolated Ground | 13046.6 | 6.38 | 560.55 | 0 | 51.97 | 0 | OK | Ground clear controls. | 34 | 58.31 | 612.52
2062 | TIN-INTERP | Interpolated Ground | 13046.94 | 4.37 | 560.11 | 0 | 57.94 | 0 | OK | Ground clear controls. | 34 | 58.31 | 618.05
2063 | TIN-INTERP | Interpolated Ground | 13047 | 4.9 | 560.12 | 0 | 47.08 | 0 | OK | Ground clear controls. | 34 | 58.31 | 607.2
2064 | TIN-INTERP | Interpolated Ground | 13048.95 | -4.36 | 559.71 | 0 | 58.31 | 0 | OK | Ground clear controls. | 34 | 58.31 | 618.02
2065 | TIN-INTERP | Interpolated Ground | 13049.37 | -4.85 | 559.84 | 0 | 47.36 | 0 | OK | Ground clear controls. | 34 | 52.67 | 607.2
2066 | TIN-INTERP | Interpolated Ground | 13049.63 | -6.34 | 559.9 | 0 | 52.67 | 0 | OK | Ground clear controls. | 34 | 52.67 | 612.57
2067 | TIN-INTERP | Interpolated Ground | 13086.6 | 6.42 | 579.45 | 0 | 33.64 | 0 | OK | Ground clear controls. | 34 | 39.57 | 613.09
2068 | TIN-INTERP | Interpolated Ground | 13086.94 | 4.41 | 579.37 | 0 | 39.24 | 0 | OK | Ground clear controls. | 34 | 39.57 | 618.61
2069 | TIN-INTERP | Interpolated Ground | 13087 | 4.93 | 579.37 | 0 | 28.37 | 0 | OK | Ground clear controls. | 34 | 39.57 | 607.74
2070 | TIN-INTERP | Interpolated Ground | 13088.95 | -4.48 | 579.07 | 0 | 39.57 | 0 | OK | Ground clear controls. | 34 | 39.57 | 618.64
2071 | TIN-INTERP | Interpolated Ground | 13089.37 | -4.97 | 579.32 | 0 | 28.45 | 0 | OK | Ground clear controls. | 34 | 33.63 | 607.77
2072 | TIN-INTERP | Interpolated Ground | 13089.63 | -6.47 | 579.55 | 0 | 33.63 | 0 | OK | Ground clear controls. | 34 | 33.63 | 613.18
2073 | TIN-INTERP | Interpolated Ground | 13126.6 | 6.46 | 592.87 | 0 | 21.71 | 0 | OK | Ground clear controls. | 34 | 27.1 | 614.58
2074 | TIN-INTERP | Interpolated Ground | 13126.94 | 4.46 | 593 | 0 | 27.1 | 0 | OK | Ground clear controls. | 34 | 27.1 | 620.1
2075 | TIN-INTERP | Interpolated Ground | 13127 | 4.97 | 593 | 0 | 16.17 | 0 | OK | Ground clear controls. | 34 | 26.93 | 609.17
2076 | TIN-INTERP | Interpolated Ground | 13128.95 | -4.6 | 593.26 | 0 | 26.93 | 0 | OK | Ground clear controls. | 34 | 26.93 | 620.19
2077 | TIN-INTERP | Interpolated Ground | 13129.37 | -5.1 | 593.32 | 0 | 15.93 | 0 | OK | Ground clear controls. | 34 | 21.3 | 609.25
2078 | TIN-INTERP | Interpolated Ground | 13129.63 | -6.6 | 593.43 | 0 | 21.3 | 0 | OK | Ground clear controls. | 34 | 21.3 | 614.73
2079 | TIN-INTERP | Interpolated Ground | 13146.84 | 4.98 | 595.78 | 0 | 14.43 | 0 | OK | Ground clear controls. | 35 | 45.93 | 610.21
2080 | TIN-INTERP | Interpolated Ground | 13147.01 | -4.66 | 595.7 | 0 | 25.49 | 0 | OK | Ground clear controls. | 35 | 45.93 | 621.19
2081 | TIN-INTERP | Interpolated Ground | 13147.03 | 6.48 | 595.78 | 0 | 19.91 | 0 | OK | Ground clear controls. | 35 | 45.93 | 615.69
2082 | TIN-INTERP | Interpolated Ground | 13147.03 | 4.48 | 595.78 | 0 | 25.41 | 0 | OK | Ground clear controls. | 35 | 45.93 | 621.19
2083 | TIN-INTERP | Interpolated Ground | 13147.04 | -6.65 | 595.64 | 0 | 20.05 | 0 | OK | Ground clear controls. | 35 | 45.93 | 615.69
2084 | TIN-INTERP | Interpolated Ground | 13147.05 | -5.15 | 595.68 | 0 | 14.51 | 0 | OK | Ground clear controls. | 35 | 45.93 | 610.19
2085 | TIN-INTERP | Interpolated Ground | 13186.84 | 4.98 | 585.57 | 0 | 21.22 | 0 | OK | Ground clear controls. | 35 | 45.93 | 606.79
2086 | TIN-INTERP | Interpolated Ground | 13187.01 | -4.67 | 585.69 | 0 | 31.96 | 0 | OK | Ground clear controls. | 35 | 45.93 | 617.65
2087 | TIN-INTERP | Interpolated Ground | 13187.03 | 6.47 | 585.45 | 0 | 26.75 | 0 | OK | Ground clear controls. | 35 | 45.93 | 612.2
2088 | TIN-INTERP | Interpolated Ground | 13187.03 | 4.47 | 585.54 | 0 | 32.18 | 0 | OK | Ground clear controls. | 35 | 45.93 | 617.72
2089 | TIN-INTERP | Interpolated Ground | 13187.04 | -6.67 | 585.85 | 0 | 26.33 | 0 | OK | Ground clear controls. | 35 | 45.93 | 612.18
2090 | TIN-INTERP | Interpolated Ground | 13187.05 | -5.17 | 585.71 | 0 | 21.07 | 0 | OK | Ground clear controls. | 35 | 45.93 | 606.78
2091 | TIN-INTERP | Interpolated Ground | 13226.84 | 4.97 | 573.12 | 0 | 31.14 | 0 | OK | Ground clear controls. | 35 | 45.93 | 604.26
2092 | TIN-INTERP | Interpolated Ground | 13227.01 | -4.69 | 569.13 | 0 | 45.93 | 0 | OK | Ground clear controls. | 35 | 45.93 | 615.06
2093 | TIN-INTERP | Interpolated Ground | 13227.03 | 6.47 | 573.26 | 0 | 36.38 | 0 | OK | Ground clear controls. | 35 | 42.17 | 609.64
2094 | TIN-INTERP | Interpolated Ground | 13227.03 | 4.47 | 572.98 | 0 | 42.17 | 0 | OK | Ground clear controls. | 35 | 42.17 | 615.15
2095 | TIN-INTERP | Interpolated Ground | 13227.04 | -6.68 | 569 | 0 | 40.61 | 0 | OK | Ground clear controls. | 35 | 40.61 | 609.61
2096 | TIN-INTERP | Interpolated Ground | 13227.05 | -5.18 | 568.92 | 0 | 35.35 | 0 | OK | Ground clear controls. | 35 | 36.78 | 604.27
2097 | TIN-INTERP | Interpolated Ground | 13266.84 | 4.96 | 579.06 | 0 | 23.59 | 0 | OK | Ground clear controls. | 35 | 36.78 | 602.65
2098 | TIN-INTERP | Interpolated Ground | 13267.01 | -4.7 | 577.5 | 0 | 35.9 | 0 | OK | Ground clear controls. | 35 | 36.78 | 613.4
2099 | TIN-INTERP | Interpolated Ground | 13267.03 | 6.46 | 579.19 | 0 | 28.8 | 0 | OK | Ground clear controls. | 35 | 36.78 | 607.99
2100 | TIN-INTERP | Interpolated Ground | 13267.03 | 4.46 | 578.97 | 0 | 34.55 | 0 | OK | Ground clear controls. | 35 | 36.78 | 613.52
2101 | TIN-INTERP | Interpolated Ground | 13267.04 | -6.7 | 577.22 | 0 | 30.74 | 0 | OK | Ground clear controls. | 35 | 36.78 | 607.96
2102 | TIN-INTERP | Interpolated Ground | 13267.05 | -5.2 | 577.44 | 0 | 25.22 | 0 | OK | Ground clear controls. | 35 | 36.78 | 602.66
2103 | TIN-INTERP | Interpolated Ground | 13306.84 | 4.95 | 589.39 | 0 | 12.55 | 0 | OK | Ground clear controls. | 35 | 36.78 | 601.94
2104 | TIN-INTERP | Interpolated Ground | 13307.01 | -4.72 | 587.86 | 0 | 24.82 | 0 | OK | Ground clear controls. | 35 | 36.78 | 612.68
2105 | TIN-INTERP | Interpolated Ground | 13307.03 | 6.45 | 589.59 | 0 | 17.69 | 0 | OK | Ground clear controls. | 35 | 36.78 | 607.28
2106 | TIN-INTERP | Interpolated Ground | 13307.03 | 4.45 | 589.29 | 0 | 23.52 | 0 | OK | Ground clear controls. | 35 | 36.78 | 612.81
2107 | TIN-INTERP | Interpolated Ground | 13307.04 | -6.72 | 587.54 | 0 | 19.7 | 0 | OK | Ground clear controls. | 35 | 36.78 | 607.24
2108 | TIN-INTERP | Interpolated Ground | 13307.05 | -5.22 | 587.78 | 0 | 14.18 | 0 | OK | Ground clear controls. | 35 | 36.78 | 601.96
2109 | TIN-INTERP | Interpolated Ground | 13346.84 | 4.94 | 581.2 | 0 | 20.94 | 0 | OK | Ground clear controls. | 35 | 36.78 | 602.14
2110 | TIN-INTERP | Interpolated Ground | 13347.01 | -4.73 | 581.58 | 0 | 31.32 | 0 | OK | Ground clear controls. | 35 | 36.78 | 612.9
2111 | TIN-INTERP | Interpolated Ground | 13347.03 | 6.44 | 581.61 | 0 | 25.89 | 0 | OK | Ground clear controls. | 35 | 36.78 | 607.5
2112 | TIN-INTERP | Interpolated Ground | 13347.03 | 4.44 | 581.18 | 0 | 31.84 | 0 | OK | Ground clear controls. | 35 | 36.78 | 613.02
2113 | TIN-INTERP | Interpolated Ground | 13347.04 | -6.73 | 580.96 | 0 | 26.5 | 0 | OK | Ground clear controls. | 35 | 36.78 | 607.46
2114 | TIN-INTERP | Interpolated Ground | 13347.05 | -5.23 | 581.41 | 0 | 20.75 | 0 | OK | Ground clear controls. | 35 | 36.78 | 602.16
2115 | TIN-INTERP | Interpolated Ground | 13386.84 | 4.94 | 577.31 | 0 | 25.92 | 0 | OK | Ground clear controls. | 35 | 36.78 | 603.23
2116 | TIN-INTERP | Interpolated Ground | 13387.01 | -4.75 | 578.61 | 0 | 35.44 | 0 | OK | Ground clear controls. | 35 | 36.78 | 614.05
2117 | TIN-INTERP | Interpolated Ground | 13387.03 | 6.44 | 577.77 | 0 | 30.85 | 0 | OK | Ground clear controls. | 35 | 36.78 | 608.62
2118 | TIN-INTERP | Interpolated Ground | 13387.03 | 4.44 | 577.37 | 0 | 36.78 | 0 | OK | Ground clear controls. | 35 | 36.78 | 614.15
2119 | TIN-INTERP | Interpolated Ground | 13387.04 | -6.75 | 579.29 | 0 | 29.3 | 0 | OK | Ground clear controls. | 35 | 29.3 | 608.59
2120 | TIN-INTERP | Interpolated Ground | 13387.05 | -5.25 | 578.75 | 0 | 24.51 | 0 | OK | Ground clear controls. | 35 | 24.51 | 603.26
2121 | TIN-INTERP | Interpolated Ground | 13426.84 | 4.93 | 591.97 | 0 | 13.27 | 0 | OK | Ground clear controls. | 35 | 24.49 | 605.24
2122 | TIN-INTERP | Interpolated Ground | 13427.01 | -4.76 | 591.65 | 0 | 24.49 | 0 | OK | Ground clear controls. | 35 | 24.49 | 616.14
2123 | TIN-INTERP | Interpolated Ground | 13427.03 | 6.43 | 591.99 | 0 | 18.69 | 0 | OK | Ground clear controls. | 35 | 24.2 | 610.68
2124 | TIN-INTERP | Interpolated Ground | 13427.03 | 4.43 | 591.99 | 0 | 24.2 | 0 | OK | Ground clear controls. | 35 | 24.2 | 616.19
2125 | TIN-INTERP | Interpolated Ground | 13427.04 | -6.76 | 591.67 | 0 | 19 | 0 | OK | Ground clear controls. | 35 | 19 | 610.67
2126 | TIN-INTERP | Interpolated Ground | 13427.05 | -5.26 | 591.68 | 0 | 13.58 | 0 | OK | Ground clear controls. | 35 | 13.58 | 605.26
2127 | TIN-INTERP | Interpolated Ground | 13462.02 | -5.28 | 593.41 | 0 | 14.35 | 0 | OK | Ground clear controls. | 36 | 62.41 | 607.76
2128 | TIN-INTERP | Interpolated Ground | 13462.08 | 6.42 | 593.5 | 0 | 19.75 | 0 | OK | Ground clear controls. | 36 | 62.41 | 613.25
2129 | TIN-INTERP | Interpolated Ground | 13462.08 | 4.42 | 593.44 | 0 | 25.31 | 0 | OK | Ground clear controls. | 36 | 62.41 | 618.75
2130 | TIN-INTERP | Interpolated Ground | 13462.08 | 4.92 | 593.4 | 0 | 14.35 | 0 | OK | Ground clear controls. | 36 | 62.41 | 607.75
2131 | TIN-INTERP | Interpolated Ground | 13462.12 | -4.78 | 593.46 | 0 | 25.29 | 0 | OK | Ground clear controls. | 36 | 62.41 | 618.75
2132 | TIN-INTERP | Interpolated Ground | 13462.17 | -6.78 | 593.33 | 0 | 19.92 | 0 | OK | Ground clear controls. | 36 | 62.41 | 613.25
2133 | TIN-INTERP | Interpolated Ground | 13502.02 | -5.25 | 590.63 | 0 | 13.24 | 0 | OK | Ground clear controls. | 36 | 62.41 | 603.87
2134 | TIN-INTERP | Interpolated Ground | 13502.07 | 6.45 | 591.56 | 0 | 17.74 | 0 | OK | Ground clear controls. | 36 | 62.41 | 609.3
2135 | TIN-INTERP | Interpolated Ground | 13502.07 | 4.45 | 591.47 | 0 | 23.34 | 0 | OK | Ground clear controls. | 36 | 62.41 | 614.81
2136 | TIN-INTERP | Interpolated Ground | 13502.08 | 4.95 | 591.53 | 0 | 12.34 | 0 | OK | Ground clear controls. | 36 | 62.41 | 603.87
2137 | TIN-INTERP | Interpolated Ground | 13502.12 | -4.75 | 590.64 | 0 | 24.13 | 0 | OK | Ground clear controls. | 36 | 62.41 | 614.77
2138 | TIN-INTERP | Interpolated Ground | 13502.17 | -6.75 | 590.54 | 0 | 18.76 | 0 | OK | Ground clear controls. | 36 | 62.41 | 609.3
2139 | TIN-INTERP | Interpolated Ground | 13542.02 | -5.23 | 573.69 | 0 | 27.2 | 0 | OK | Ground clear controls. | 36 | 62.41 | 600.89
2140 | TIN-INTERP | Interpolated Ground | 13542.07 | 6.48 | 573.32 | 0 | 32.97 | 0 | OK | Ground clear controls. | 36 | 62.41 | 606.29
2141 | TIN-INTERP | Interpolated Ground | 13542.07 | 4.48 | 573.62 | 0 | 38.18 | 0 | OK | Ground clear controls. | 36 | 62.41 | 611.8
2142 | TIN-INTERP | Interpolated Ground | 13542.08 | 4.98 | 573.5 | 0 | 27.4 | 0 | OK | Ground clear controls. | 36 | 62.41 | 600.9
2143 | TIN-INTERP | Interpolated Ground | 13542.12 | -4.73 | 573.74 | 0 | 37.99 | 0 | OK | Ground clear controls. | 36 | 62.41 | 611.73
2144 | TIN-INTERP | Interpolated Ground | 13542.17 | -6.73 | 573.22 | 0 | 33.08 | 0 | OK | Ground clear controls. | 36 | 62.41 | 606.3
2145 | TIN-INTERP | Interpolated Ground | 13582.02 | -5.2 | 559.08 | 0 | 39.75 | 0 | OK | Ground clear controls. | 36 | 62.41 | 598.83
2146 | TIN-INTERP | Interpolated Ground | 13582.07 | 6.5 | 557.48 | 0 | 46.72 | 0 | OK | Ground clear controls. | 36 | 62.41 | 604.2
2147 | TIN-INTERP | Interpolated Ground | 13582.07 | 4.5 | 557.75 | 0 | 51.98 | 0 | OK | Ground clear controls. | 36 | 62.41 | 609.73
2148 | TIN-INTERP | Interpolated Ground | 13582.08 | 5 | 557.68 | 0 | 41.16 | 0 | OK | Ground clear controls. | 36 | 62.41 | 598.84
2149 | TIN-INTERP | Interpolated Ground | 13582.12 | -4.7 | 558.98 | 0 | 50.66 | 0 | OK | Ground clear controls. | 36 | 62.41 | 609.64
2150 | TIN-INTERP | Interpolated Ground | 13582.17 | -6.7 | 559.25 | 0 | 44.97 | 0 | OK | Ground clear controls. | 36 | 62.41 | 604.22
2151 | TIN-INTERP | Interpolated Ground | 13622.02 | -5.18 | 546.05 | 0 | 51.63 | 0 | OK | Ground clear controls. | 36 | 62.41 | 597.68
2152 | TIN-INTERP | Interpolated Ground | 13622.07 | 6.53 | 546.73 | 0 | 56.32 | 0 | OK | Ground clear controls. | 36 | 62.41 | 603.05
2153 | TIN-INTERP | Interpolated Ground | 13622.07 | 4.53 | 546.82 | 0 | 61.75 | 0 | OK | Ground clear controls. | 36 | 62.41 | 608.57
2154 | TIN-INTERP | Interpolated Ground | 13622.08 | 5.03 | 546.79 | 0 | 50.89 | 0 | OK | Ground clear controls. | 36 | 62.41 | 597.68
2155 | TIN-INTERP | Interpolated Ground | 13622.12 | -4.68 | 546.07 | 0 | 62.41 | 0 | OK | Ground clear controls. | 36 | 62.41 | 608.48
2156 | TIN-INTERP | Interpolated Ground | 13622.17 | -6.68 | 546.03 | 0 | 57.03 | 0 | OK | Ground clear controls. | 36 | 58.43 | 603.06
2157 | TIN-INTERP | Interpolated Ground | 13662.02 | -5.15 | 549.75 | 0 | 47.68 | 0 | OK | Ground clear controls. | 36 | 58.43 | 597.43
2158 | TIN-INTERP | Interpolated Ground | 13662.07 | 6.56 | 550.72 | 0 | 52.1 | 0 | OK | Ground clear controls. | 36 | 58.43 | 602.82
2159 | TIN-INTERP | Interpolated Ground | 13662.07 | 4.56 | 550.58 | 0 | 57.76 | 0 | OK | Ground clear controls. | 36 | 58.43 | 608.34
2160 | TIN-INTERP | Interpolated Ground | 13662.08 | 5.06 | 550.62 | 0 | 46.82 | 0 | OK | Ground clear controls. | 36 | 58.43 | 597.44
2161 | TIN-INTERP | Interpolated Ground | 13662.12 | -4.65 | 549.83 | 0 | 58.43 | 0 | OK | Ground clear controls. | 36 | 58.43 | 608.26
2162 | TIN-INTERP | Interpolated Ground | 13662.17 | -6.65 | 549.59 | 0 | 53.25 | 0 | OK | Ground clear controls. | 36 | 53.25 | 602.84
2163 | TIN-INTERP | Interpolated Ground | 13702.02 | -5.13 | 567.83 | 0 | 30.27 | 0 | OK | Ground clear controls. | 36 | 42.48 | 598.1
2164 | TIN-INTERP | Interpolated Ground | 13702.07 | 6.58 | 565.94 | 0 | 37.58 | 0 | OK | Ground clear controls. | 36 | 42.48 | 603.52
2165 | TIN-INTERP | Interpolated Ground | 13702.07 | 4.59 | 566.56 | 0 | 42.48 | 0 | OK | Ground clear controls. | 36 | 42.48 | 609.04
2166 | TIN-INTERP | Interpolated Ground | 13702.08 | 5.09 | 566.4 | 0 | 31.71 | 0 | OK | Ground clear controls. | 36 | 41.08 | 598.11
2167 | TIN-INTERP | Interpolated Ground | 13702.12 | -4.63 | 567.91 | 0 | 41.08 | 0 | OK | Ground clear controls. | 36 | 41.08 | 608.99
2168 | TIN-INTERP | Interpolated Ground | 13702.17 | -6.63 | 567.79 | 0 | 35.75 | 0 | OK | Ground clear controls. | 36 | 35.75 | 603.54
2169 | TIN-INTERP | Interpolated Ground | 13742.02 | -5.1 | 581.89 | 0 | 17.78 | 0 | OK | Ground clear controls. | 36 | 28.61 | 599.67
2170 | TIN-INTERP | Interpolated Ground | 13742.07 | 6.61 | 582.26 | 0 | 22.89 | 0 | OK | Ground clear controls. | 36 | 28.61 | 605.15
2171 | TIN-INTERP | Interpolated Ground | 13742.07 | 4.61 | 582.78 | 0 | 27.88 | 0 | OK | Ground clear controls. | 36 | 28.61 | 610.66
2172 | TIN-INTERP | Interpolated Ground | 13742.08 | 5.11 | 582.7 | 0 | 16.98 | 0 | OK | Ground clear controls. | 36 | 28.61 | 599.68
2173 | TIN-INTERP | Interpolated Ground | 13742.12 | -4.6 | 582.04 | 0 | 28.61 | 0 | OK | Ground clear controls. | 36 | 28.61 | 610.65
2174 | TIN-INTERP | Interpolated Ground | 13742.17 | -6.6 | 581.57 | 0 | 23.59 | 0 | OK | Ground clear controls. | 36 | 23.59 | 605.16
2175 | TIN-INTERP | Interpolated Ground | 13755.66 | -4.6 | 582.33 | 0 | 29.09 | 0 | OK | Ground clear controls. | 37 | 43.39 | 611.42
2176 | TIN-INTERP | Interpolated Ground | 13755.67 | -5.09 | 582.2 | 0 | 18.22 | 0 | OK | Ground clear controls. | 37 | 43.39 | 600.42
2177 | TIN-INTERP | Interpolated Ground | 13755.69 | 4.62 | 585.26 | 0 | 26.16 | 0 | OK | Ground clear controls. | 37 | 43.39 | 611.42
2178 | TIN-INTERP | Interpolated Ground | 13755.69 | 6.62 | 585.56 | 0 | 20.36 | 0 | OK | Ground clear controls. | 37 | 43.39 | 605.92
2179 | TIN-INTERP | Interpolated Ground | 13755.7 | 5.12 | 585.49 | 0 | 14.93 | 0 | OK | Ground clear controls. | 37 | 43.39 | 600.42
2180 | TIN-INTERP | Interpolated Ground | 13755.71 | -6.59 | 581.81 | 0 | 24.12 | 0 | OK | Ground clear controls. | 37 | 43.39 | 605.93
2181 | TIN-INTERP | Interpolated Ground | 13795.65 | -4.63 | 575.8 | 0 | 31.22 | 0 | OK | Ground clear controls. | 37 | 43.39 | 607.02
2182 | TIN-INTERP | Interpolated Ground | 13795.66 | -5.12 | 575.6 | 0 | 20.57 | 0 | OK | Ground clear controls. | 37 | 43.39 | 596.17
2183 | TIN-INTERP | Interpolated Ground | 13795.7 | 4.65 | 580 | 0 | 27.08 | 0 | OK | Ground clear controls. | 37 | 43.39 | 607.08
2184 | TIN-INTERP | Interpolated Ground | 13795.7 | -6.62 | 575 | 0 | 26.59 | 0 | OK | Ground clear controls. | 37 | 43.39 | 601.59
2185 | TIN-INTERP | Interpolated Ground | 13795.71 | 6.64 | 580.96 | 0 | 20.57 | 0 | OK | Ground clear controls. | 37 | 43.39 | 601.53
2186 | TIN-INTERP | Interpolated Ground | 13795.71 | 5.14 | 580.26 | 0 | 15.9 | 0 | OK | Ground clear controls. | 37 | 43.39 | 596.16
2187 | TIN-INTERP | Interpolated Ground | 13835.65 | -4.66 | 565.76 | 0 | 37.81 | 0 | OK | Ground clear controls. | 37 | 43.39 | 603.57
2188 | TIN-INTERP | Interpolated Ground | 13835.66 | -5.14 | 565.62 | 0 | 27.2 | 0 | OK | Ground clear controls. | 37 | 43.39 | 592.82
2189 | TIN-INTERP | Interpolated Ground | 13835.7 | 4.68 | 569.89 | 0 | 33.79 | 0 | OK | Ground clear controls. | 37 | 43.39 | 603.68
2190 | TIN-INTERP | Interpolated Ground | 13835.7 | -6.64 | 565.2 | 0 | 32.99 | 0 | OK | Ground clear controls. | 37 | 43.39 | 598.19
2191 | TIN-INTERP | Interpolated Ground | 13835.71 | 6.66 | 570.53 | 0 | 27.55 | 0 | OK | Ground clear controls. | 37 | 43.39 | 598.08
2192 | TIN-INTERP | Interpolated Ground | 13835.71 | 5.17 | 570.04 | 0 | 22.77 | 0 | OK | Ground clear controls. | 37 | 43.39 | 592.81
2193 | TIN-INTERP | Interpolated Ground | 13875.65 | -4.69 | 566.23 | 0 | 34.82 | 0 | OK | Ground clear controls. | 37 | 43.39 | 601.05
2194 | TIN-INTERP | Interpolated Ground | 13875.66 | -5.16 | 566.05 | 0 | 24.34 | 0 | OK | Ground clear controls. | 37 | 43.39 | 590.39
2195 | TIN-INTERP | Interpolated Ground | 13875.7 | 4.71 | 568.06 | 0 | 33.14 | 0 | OK | Ground clear controls. | 37 | 43.39 | 601.2
2196 | TIN-INTERP | Interpolated Ground | 13875.7 | -6.66 | 565.47 | 0 | 30.24 | 0 | OK | Ground clear controls. | 37 | 43.39 | 595.71
2197 | TIN-INTERP | Interpolated Ground | 13875.71 | 6.69 | 568.46 | 0 | 27.1 | 0 | OK | Ground clear controls. | 37 | 43.39 | 595.56
2198 | TIN-INTERP | Interpolated Ground | 13875.71 | 5.19 | 568.15 | 0 | 22.22 | 0 | OK | Ground clear controls. | 37 | 43.39 | 590.37
2199 | TIN-INTERP | Interpolated Ground | 13915.65 | -4.72 | 562.77 | 0 | 36.72 | 0 | OK | Ground clear controls. | 37 | 43.39 | 599.49
2200 | TIN-INTERP | Interpolated Ground | 13915.66 | -5.19 | 562.66 | 0 | 26.22 | 0 | OK | Ground clear controls. | 37 | 43.39 | 588.88
2201 | TIN-INTERP | Interpolated Ground | 13915.7 | 4.74 | 564.52 | 0 | 35.13 | 0 | OK | Ground clear controls. | 37 | 43.39 | 599.65
2202 | TIN-INTERP | Interpolated Ground | 13915.7 | -6.69 | 562.33 | 0 | 31.83 | 0 | OK | Ground clear controls. | 37 | 43.39 | 594.16
2203 | TIN-INTERP | Interpolated Ground | 13915.71 | 6.71 | 565 | 0 | 28.98 | 0 | OK | Ground clear controls. | 37 | 43.39 | 593.98
2204 | TIN-INTERP | Interpolated Ground | 13915.71 | 5.21 | 564.57 | 0 | 24.28 | 0 | OK | Ground clear controls. | 37 | 43.39 | 588.85
2205 | TIN-INTERP | Interpolated Ground | 13955.65 | -4.75 | 561.25 | 0 | 37.6 | 0 | OK | Ground clear controls. | 37 | 43.39 | 598.85
2206 | TIN-INTERP | Interpolated Ground | 13955.66 | -5.21 | 561.21 | 0 | 27.06 | 0 | OK | Ground clear controls. | 37 | 43.39 | 588.27
2207 | TIN-INTERP | Interpolated Ground | 13955.7 | 4.77 | 562.36 | 0 | 36.68 | 0 | OK | Ground clear controls. | 37 | 43.39 | 599.04
2208 | TIN-INTERP | Interpolated Ground | 13955.7 | -6.71 | 561.05 | 0 | 32.48 | 0 | OK | Ground clear controls. | 37 | 43.39 | 593.53
2209 | TIN-INTERP | Interpolated Ground | 13955.71 | 6.73 | 563.76 | 0 | 29.57 | 0 | OK | Ground clear controls. | 37 | 43.39 | 593.33
2210 | TIN-INTERP | Interpolated Ground | 13955.71 | 5.23 | 562.69 | 0 | 25.55 | 0 | OK | Ground clear controls. | 37 | 43.39 | 588.24
2211 | TIN-INTERP | Interpolated Ground | 13995.65 | -4.78 | 562.74 | 0 | 36.42 | 0 | OK | Ground clear controls. | 37 | 43.39 | 599.16
2212 | TIN-INTERP | Interpolated Ground | 13995.66 | -5.23 | 562.71 | 0 | 25.86 | 0 | OK | Ground clear controls. | 37 | 43.39 | 588.57
2213 | TIN-INTERP | Interpolated Ground | 13995.7 | 4.8 | 563.9 | 0 | 35.45 | 0 | OK | Ground clear controls. | 37 | 43.39 | 599.35
2214 | TIN-INTERP | Interpolated Ground | 13995.7 | -6.73 | 562.64 | 0 | 31.19 | 0 | OK | Ground clear controls. | 37 | 43.39 | 593.83
2215 | TIN-INTERP | Interpolated Ground | 13995.71 | 6.75 | 564.06 | 0 | 29.56 | 0 | OK | Ground clear controls. | 37 | 43.39 | 593.62
2216 | TIN-INTERP | Interpolated Ground | 13995.71 | 5.25 | 563.94 | 0 | 24.6 | 0 | OK | Ground clear controls. | 37 | 43.39 | 588.54
2217 | TIN-INTERP | Interpolated Ground | 14035.65 | -4.81 | 570.89 | 0 | 29.52 | 0 | OK | Ground clear controls. | 37 | 43.39 | 600.41
2218 | TIN-INTERP | Interpolated Ground | 14035.66 | -5.26 | 571.08 | 0 | 18.71 | 0 | OK | Ground clear controls. | 37 | 43.39 | 589.79
2219 | TIN-INTERP | Interpolated Ground | 14035.7 | 4.83 | 565.21 | 0 | 35.38 | 0 | OK | Ground clear controls. | 37 | 43.39 | 600.59
2220 | TIN-INTERP | Interpolated Ground | 14035.7 | -6.76 | 571.7 | 0 | 23.34 | 0 | OK | Ground clear controls. | 37 | 43.39 | 595.04
2221 | TIN-INTERP | Interpolated Ground | 14035.71 | 6.77 | 564.83 | 0 | 30.01 | 0 | OK | Ground clear controls. | 37 | 43.39 | 594.84
2222 | TIN-INTERP | Interpolated Ground | 14035.71 | 5.27 | 565.19 | 0 | 24.55 | 0 | OK | Ground clear controls. | 37 | 43.39 | 589.74
2223 | TIN-INTERP | Interpolated Ground | 14075.65 | -4.84 | 573.92 | 0 | 28.68 | 0 | OK | Ground clear controls. | 37 | 43.39 | 602.6
2224 | TIN-INTERP | Interpolated Ground | 14075.66 | -5.28 | 573.95 | 0 | 17.96 | 0 | OK | Ground clear controls. | 37 | 43.39 | 591.91
2225 | TIN-INTERP | Interpolated Ground | 14075.7 | 4.86 | 570.21 | 0 | 32.56 | 0 | OK | Ground clear controls. | 37 | 43.39 | 602.77
2226 | TIN-INTERP | Interpolated Ground | 14075.7 | -6.78 | 574.07 | 0 | 23.12 | 0 | OK | Ground clear controls. | 37 | 43.39 | 597.19
2227 | TIN-INTERP | Interpolated Ground | 14075.71 | 6.8 | 569.55 | 0 | 27.44 | 0 | OK | Ground clear controls. | 37 | 43.39 | 596.99
2228 | TIN-INTERP | Interpolated Ground | 14075.71 | 5.3 | 570.04 | 0 | 21.83 | 0 | OK | Ground clear controls. | 37 | 43.39 | 591.87
2229 | TIN-INTERP | Interpolated Ground | 14115.65 | -4.87 | 572.1 | 0 | 33.64 | 0 | OK | Ground clear controls. | 37 | 43.39 | 605.74
2230 | TIN-INTERP | Interpolated Ground | 14115.66 | -5.3 | 571.99 | 0 | 22.95 | 0 | OK | Ground clear controls. | 37 | 43.39 | 594.94
2231 | TIN-INTERP | Interpolated Ground | 14115.7 | 4.89 | 575.48 | 0 | 30.4 | 0 | OK | Ground clear controls. | 37 | 43.39 | 605.88
2232 | TIN-INTERP | Interpolated Ground | 14115.7 | -6.8 | 571.73 | 0 | 28.53 | 0 | OK | Ground clear controls. | 37 | 43.39 | 600.26
2233 | TIN-INTERP | Interpolated Ground | 14115.71 | 6.82 | 575.67 | 0 | 24.42 | 0 | OK | Ground clear controls. | 37 | 43.39 | 600.09
2234 | TIN-INTERP | Interpolated Ground | 14115.71 | 5.32 | 575.53 | 0 | 19.38 | 0 | OK | Ground clear controls. | 37 | 43.39 | 594.91
2235 | TIN-INTERP | Interpolated Ground | 14155.65 | -4.91 | 572.91 | 0 | 36.91 | 0 | OK | Ground clear controls. | 37 | 43.39 | 609.82
2236 | TIN-INTERP | Interpolated Ground | 14155.66 | -5.33 | 572.88 | 0 | 26.02 | 0 | OK | Ground clear controls. | 37 | 43.39 | 598.9
2237 | TIN-INTERP | Interpolated Ground | 14155.7 | 4.92 | 573.14 | 0 | 36.78 | 0 | OK | Ground clear controls. | 37 | 43.39 | 609.92
2238 | TIN-INTERP | Interpolated Ground | 14155.7 | -6.83 | 572.75 | 0 | 31.51 | 0 | OK | Ground clear controls. | 37 | 43.39 | 604.26
2239 | TIN-INTERP | Interpolated Ground | 14155.71 | 6.84 | 572.55 | 0 | 31.57 | 0 | OK | Ground clear controls. | 37 | 43.39 | 604.12
2240 | TIN-INTERP | Interpolated Ground | 14155.71 | 5.34 | 573.03 | 0 | 25.84 | 0 | OK | Ground clear controls. | 37 | 43.39 | 598.87
2241 | TIN-INTERP | Interpolated Ground | 14195.65 | -4.94 | 575.54 | 0 | 39.31 | 0 | OK | Ground clear controls. | 37 | 43.39 | 614.85
2242 | TIN-INTERP | Interpolated Ground | 14195.66 | -5.35 | 575.52 | 0 | 28.24 | 0 | OK | Ground clear controls. | 37 | 43.39 | 603.76
2243 | TIN-INTERP | Interpolated Ground | 14195.7 | 4.95 | 576.02 | 0 | 38.88 | 0 | OK | Ground clear controls. | 37 | 43.39 | 614.9
2244 | TIN-INTERP | Interpolated Ground | 14195.7 | -6.85 | 575.57 | 0 | 33.62 | 0 | OK | Ground clear controls. | 37 | 43.39 | 609.19
2245 | TIN-INTERP | Interpolated Ground | 14195.71 | 6.86 | 575.87 | 0 | 33.22 | 0 | OK | Ground clear controls. | 37 | 43.39 | 609.09
2246 | TIN-INTERP | Interpolated Ground | 14195.71 | 5.36 | 575.99 | 0 | 27.74 | 0 | OK | Ground clear controls. | 37 | 43.39 | 603.73
2247 | TIN-INTERP | Interpolated Ground | 14235.65 | -4.97 | 577.81 | 0 | 43.01 | 0 | OK | Ground clear controls. | 37 | 43.39 | 620.82
2248 | TIN-INTERP | Interpolated Ground | 14235.66 | -5.37 | 577.89 | 0 | 31.66 | 0 | OK | Ground clear controls. | 37 | 43.39 | 609.55
2249 | TIN-INTERP | Interpolated Ground | 14235.7 | 4.98 | 577.42 | 0 | 43.39 | 0 | OK | Ground clear controls. | 37 | 43.39 | 620.81
2250 | TIN-INTERP | Interpolated Ground | 14235.7 | -6.87 | 578.04 | 0 | 37 | 0 | OK | Ground clear controls. | 37 | 37.54 | 615.04
2251 | TIN-INTERP | Interpolated Ground | 14235.71 | 6.88 | 577.46 | 0 | 37.54 | 0 | OK | Ground clear controls. | 37 | 37.54 | 615
2252 | TIN-INTERP | Interpolated Ground | 14235.71 | 5.38 | 577.44 | 0 | 32.09 | 0 | OK | Ground clear controls. | 37 | 32.09 | 609.53
2253 | TIN-INTERP | Interpolated Ground | 14241.1 | -4.97 | 577.83 | 0 | 43.87 | 0 | OK | Ground clear controls. | 38 | 44.32 | 621.7
2254 | TIN-INTERP | Interpolated Ground | 14241.13 | -6.88 | 577.91 | 0 | 38 | 0 | OK | Ground clear controls. | 38 | 44.32 | 615.91
2255 | TIN-INTERP | Interpolated Ground | 14241.15 | -5.38 | 577.85 | 0 | 32.55 | 0 | OK | Ground clear controls. | 38 | 44.32 | 610.4
2256 | TIN-INTERP | Interpolated Ground | 14241.26 | 4.98 | 577.38 | 0 | 44.32 | 0 | OK | Ground clear controls. | 38 | 44.32 | 621.7
2257 | TIN-INTERP | Interpolated Ground | 14241.32 | 6.89 | 577.64 | 0 | 38.27 | 0 | OK | Ground clear controls. | 38 | 42.89 | 615.91
2258 | TIN-INTERP | Interpolated Ground | 14241.33 | 5.39 | 577.47 | 0 | 32.94 | 0 | OK | Ground clear controls. | 38 | 42.89 | 610.41
2259 | TIN-INTERP | Interpolated Ground | 14281.1 | -4.96 | 579.59 | 0 | 41.64 | 0 | OK | Ground clear controls. | 38 | 42.89 | 621.23
2260 | TIN-INTERP | Interpolated Ground | 14281.13 | -6.87 | 579.63 | 0 | 35.93 | 0 | OK | Ground clear controls. | 38 | 42.89 | 615.56
2261 | TIN-INTERP | Interpolated Ground | 14281.15 | -5.37 | 579.58 | 0 | 30.55 | 0 | OK | Ground clear controls. | 38 | 42.89 | 610.13
2262 | TIN-INTERP | Interpolated Ground | 14281.26 | 4.93 | 578.88 | 0 | 42.39 | 0 | OK | Ground clear controls. | 38 | 42.89 | 621.27
2263 | TIN-INTERP | Interpolated Ground | 14281.32 | 6.84 | 578.76 | 0 | 36.73 | 0 | OK | Ground clear controls. | 38 | 42.89 | 615.49
2264 | TIN-INTERP | Interpolated Ground | 14281.33 | 5.34 | 578.84 | 0 | 31.27 | 0 | OK | Ground clear controls. | 38 | 42.89 | 610.11
2265 | TIN-INTERP | Interpolated Ground | 14321.1 | -4.94 | 584.23 | 0 | 37.47 | 0 | OK | Ground clear controls. | 38 | 42.89 | 621.7
2266 | TIN-INTERP | Interpolated Ground | 14321.13 | -6.86 | 584.6 | 0 | 31.53 | 0 | OK | Ground clear controls. | 38 | 42.89 | 616.13
2267 | TIN-INTERP | Interpolated Ground | 14321.15 | -5.36 | 584.32 | 0 | 26.42 | 0 | OK | Ground clear controls. | 38 | 42.89 | 610.74
2268 | TIN-INTERP | Interpolated Ground | 14321.26 | 4.87 | 581.74 | 0 | 40.03 | 0 | OK | Ground clear controls. | 38 | 42.89 | 621.77
2269 | TIN-INTERP | Interpolated Ground | 14321.32 | 6.79 | 581.64 | 0 | 34.36 | 0 | OK | Ground clear controls. | 38 | 42.89 | 616
2270 | TIN-INTERP | Interpolated Ground | 14321.33 | 5.29 | 581.72 | 0 | 29 | 0 | OK | Ground clear controls. | 38 | 42.89 | 610.72
2271 | TIN-INTERP | Interpolated Ground | 14361.1 | -4.93 | 591.63 | 0 | 31.45 | 0 | OK | Ground clear controls. | 38 | 42.89 | 623.08
2272 | TIN-INTERP | Interpolated Ground | 14361.13 | -6.86 | 591.77 | 0 | 25.83 | 0 | OK | Ground clear controls. | 38 | 42.89 | 617.6
2273 | TIN-INTERP | Interpolated Ground | 14361.15 | -5.36 | 591.68 | 0 | 20.56 | 0 | OK | Ground clear controls. | 38 | 42.89 | 612.24
2274 | TIN-INTERP | Interpolated Ground | 14361.26 | 4.81 | 589.12 | 0 | 34.06 | 0 | OK | Ground clear controls. | 38 | 42.89 | 623.18
2275 | TIN-INTERP | Interpolated Ground | 14361.32 | 6.74 | 588.7 | 0 | 28.74 | 0 | OK | Ground clear controls. | 38 | 42.89 | 617.44
2276 | TIN-INTERP | Interpolated Ground | 14361.33 | 5.24 | 589.02 | 0 | 23.19 | 0 | OK | Ground clear controls. | 38 | 42.89 | 612.21
2277 | TIN-INTERP | Interpolated Ground | 14401.1 | -4.91 | 596.51 | 0 | 28.89 | 0 | OK | Ground clear controls. | 38 | 42.89 | 625.4
2278 | TIN-INTERP | Interpolated Ground | 14401.13 | -6.85 | 597.34 | 0 | 22.65 | 0 | OK | Ground clear controls. | 38 | 42.89 | 619.99
2279 | TIN-INTERP | Interpolated Ground | 14401.15 | -5.35 | 596.72 | 0 | 17.93 | 0 | OK | Ground clear controls. | 38 | 42.89 | 614.65
2280 | TIN-INTERP | Interpolated Ground | 14401.26 | 4.75 | 594.15 | 0 | 31.37 | 0 | OK | Ground clear controls. | 38 | 42.89 | 625.52
2281 | TIN-INTERP | Interpolated Ground | 14401.32 | 6.69 | 593.75 | 0 | 26.05 | 0 | OK | Ground clear controls. | 38 | 42.89 | 619.8
2282 | TIN-INTERP | Interpolated Ground | 14401.33 | 5.19 | 594.07 | 0 | 20.55 | 0 | OK | Ground clear controls. | 38 | 42.89 | 614.62
2283 | TIN-INTERP | Interpolated Ground | 14441.1 | -4.9 | 603.31 | 0 | 25.34 | 0 | OK | Ground clear controls. | 38 | 42.89 | 628.65
2284 | TIN-INTERP | Interpolated Ground | 14441.13 | -6.85 | 604.08 | 0 | 19.2 | 0 | OK | Ground clear controls. | 38 | 42.89 | 623.28
2285 | TIN-INTERP | Interpolated Ground | 14441.15 | -5.35 | 603.44 | 0 | 14.52 | 0 | OK | Ground clear controls. | 38 | 42.89 | 617.96
2286 | TIN-INTERP | Interpolated Ground | 14441.26 | 4.7 | 599.66 | 0 | 29.11 | 0 | OK | Ground clear controls. | 38 | 42.89 | 628.77
2287 | TIN-INTERP | Interpolated Ground | 14441.32 | 6.65 | 598.85 | 0 | 24.23 | 0 | OK | Ground clear controls. | 38 | 42.89 | 623.08
2288 | TIN-INTERP | Interpolated Ground | 14441.33 | 5.15 | 599.46 | 0 | 18.46 | 0 | OK | Ground clear controls. | 38 | 42.89 | 617.92
2289 | TIN-INTERP | Interpolated Ground | 14481.1 | -4.88 | 610.81 | 0 | 22.03 | 0 | OK | Ground clear controls. | 38 | 42.89 | 632.84
2290 | TIN-INTERP | Interpolated Ground | 14481.13 | -6.84 | 610.91 | 0 | 16.58 | 0 | OK | Ground clear controls. | 38 | 42.89 | 627.49
2291 | TIN-INTERP | Interpolated Ground | 14481.15 | -5.34 | 610.83 | 0 | 11.33 | 0 | OK | Ground clear controls. | 38 | 42.89 | 622.16
2292 | TIN-INTERP | Interpolated Ground | 14481.26 | 4.64 | 605.81 | 0 | 27.15 | 0 | OK | Ground clear controls. | 38 | 42.89 | 632.96
2293 | TIN-INTERP | Interpolated Ground | 14481.32 | 6.6 | 604.91 | 0 | 22.38 | 0 | OK | Ground clear controls. | 38 | 42.89 | 627.29
2294 | TIN-INTERP | Interpolated Ground | 14481.33 | 5.1 | 605.62 | 0 | 16.5 | 0 | OK | Ground clear controls. | 38 | 42.89 | 622.12
2295 | TIN-INTERP | Interpolated Ground | 14521.1 | -4.87 | 611.86 | 0 | 26.1 | 0 | OK | Ground clear controls. | 38 | 42.89 | 637.96
2296 | TIN-INTERP | Interpolated Ground | 14521.13 | -6.84 | 611.88 | 0 | 20.73 | 0 | OK | Ground clear controls. | 38 | 42.89 | 632.61
2297 | TIN-INTERP | Interpolated Ground | 14521.15 | -5.34 | 611.87 | 0 | 15.4 | 0 | OK | Ground clear controls. | 38 | 42.89 | 627.27
2298 | TIN-INTERP | Interpolated Ground | 14521.26 | 4.58 | 611.66 | 0 | 26.4 | 0 | OK | Ground clear controls. | 38 | 42.89 | 638.06
2299 | TIN-INTERP | Interpolated Ground | 14521.32 | 6.55 | 611.51 | 0 | 20.92 | 0 | OK | Ground clear controls. | 38 | 42.89 | 632.43
2300 | TIN-INTERP | Interpolated Ground | 14521.33 | 5.05 | 611.58 | 0 | 15.65 | 0 | OK | Ground clear controls. | 38 | 42.89 | 627.23
2301 | TIN-INTERP | Interpolated Ground | 14561.1 | -4.85 | 612.69 | 0 | 31.33 | 0 | OK | Ground clear controls. | 38 | 42.89 | 644.02
2302 | TIN-INTERP | Interpolated Ground | 14561.13 | -6.83 | 612.75 | 0 | 25.91 | 0 | OK | Ground clear controls. | 38 | 42.89 | 638.66
2303 | TIN-INTERP | Interpolated Ground | 14561.15 | -5.33 | 612.72 | 0 | 20.57 | 0 | OK | Ground clear controls. | 38 | 42.89 | 633.29
2304 | TIN-INTERP | Interpolated Ground | 14561.26 | 4.52 | 612.87 | 0 | 31.23 | 0 | OK | Ground clear controls. | 38 | 42.89 | 644.1
2305 | TIN-INTERP | Interpolated Ground | 14561.32 | 6.5 | 613.06 | 0 | 25.45 | 0 | OK | Ground clear controls. | 38 | 42.89 | 638.51
2306 | TIN-INTERP | Interpolated Ground | 14561.33 | 5 | 612.92 | 0 | 20.33 | 0 | OK | Ground clear controls. | 38 | 42.89 | 633.25
2307 | TIN-INTERP | Interpolated Ground | 14601.1 | -4.84 | 615.03 | 0 | 36 | 0 | OK | Ground clear controls. | 38 | 42.89 | 651.03
2308 | TIN-INTERP | Interpolated Ground | 14601.13 | -6.82 | 615.11 | 0 | 30.51 | 0 | OK | Ground clear controls. | 38 | 42.89 | 645.62
2309 | TIN-INTERP | Interpolated Ground | 14601.15 | -5.32 | 615.08 | 0 | 25.13 | 0 | OK | Ground clear controls. | 38 | 42.89 | 640.21
2310 | TIN-INTERP | Interpolated Ground | 14601.26 | 4.47 | 613.9 | 0 | 37.18 | 0 | OK | Ground clear controls. | 38 | 42.89 | 651.08
2311 | TIN-INTERP | Interpolated Ground | 14601.32 | 6.45 | 613 | 0 | 32.52 | 0 | OK | Ground clear controls. | 38 | 42.89 | 645.52
2312 | TIN-INTERP | Interpolated Ground | 14601.33 | 4.95 | 613.67 | 0 | 26.51 | 0 | OK | Ground clear controls. | 38 | 42.89 | 640.18
2313 | TIN-INTERP | Interpolated Ground | 14641.1 | -4.82 | 617.13 | 0 | 41.84 | 0 | OK | Ground clear controls. | 38 | 42.89 | 658.97
2314 | TIN-INTERP | Interpolated Ground | 14641.13 | -6.82 | 617.32 | 0 | 36.19 | 0 | OK | Ground clear controls. | 38 | 42.89 | 653.51
2315 | TIN-INTERP | Interpolated Ground | 14641.15 | -5.32 | 617.2 | 0 | 30.85 | 0 | OK | Ground clear controls. | 38 | 42.89 | 648.05
2316 | TIN-INTERP | Interpolated Ground | 14641.26 | 4.41 | 616.09 | 0 | 42.89 | 0 | OK | Ground clear controls. | 38 | 42.89 | 658.98
2317 | TIN-INTERP | Interpolated Ground | 14641.32 | 6.41 | 615.8 | 0 | 37.67 | 0 | OK | Ground clear controls. | 38 | 37.67 | 653.47
2318 | TIN-INTERP | Interpolated Ground | 14641.33 | 4.91 | 615.94 | 0 | 32.09 | 0 | OK | Ground clear controls. | 38 | 32.09 | 648.03
2319 | TIN-INTERP | Interpolated Ground | 14652.53 | -5.32 | 617.98 | 0 | 32.46 | 0 | OK | Ground clear controls. | 39 | 44.22 | 650.44
2320 | TIN-INTERP | Interpolated Ground | 14652.59 | -6.82 | 617.95 | 0 | 37.99 | 0 | OK | Ground clear controls. | 39 | 44.22 | 655.94
2321 | TIN-INTERP | Interpolated Ground | 14652.63 | -4.82 | 618.01 | 0 | 43.43 | 0 | OK | Ground clear controls. | 39 | 44.22 | 661.44
2322 | TIN-INTERP | Interpolated Ground | 14652.78 | 4.89 | 617.22 | 0 | 33.22 | 0 | OK | Ground clear controls. | 39 | 44.22 | 650.44
2323 | TIN-INTERP | Interpolated Ground | 14652.79 | 4.39 | 617.22 | 0 | 44.22 | 0 | OK | Ground clear controls. | 39 | 44.22 | 661.44
2324 | TIN-INTERP | Interpolated Ground | 14652.87 | 6.39 | 617.01 | 0 | 38.93 | 0 | OK | Ground clear controls. | 39 | 39 | 655.94
2325 | TIN-INTERP | Interpolated Ground | 14692.55 | -5.3 | 618.34 | 0 | 27.34 | 0 | OK | Ground clear controls. | 39 | 39 | 645.68
2326 | TIN-INTERP | Interpolated Ground | 14692.62 | -6.8 | 618.41 | 0 | 32.75 | 0 | OK | Ground clear controls. | 39 | 39 | 651.16
2327 | TIN-INTERP | Interpolated Ground | 14692.65 | -4.8 | 618.3 | 0 | 38.24 | 0 | OK | Ground clear controls. | 39 | 39 | 656.54
2328 | TIN-INTERP | Interpolated Ground | 14692.78 | 4.91 | 617.58 | 0 | 28.13 | 0 | OK | Ground clear controls. | 39 | 39 | 645.71
2329 | TIN-INTERP | Interpolated Ground | 14692.79 | 4.41 | 617.6 | 0 | 39 | 0 | OK | Ground clear controls. | 39 | 39 | 656.6
2330 | TIN-INTERP | Interpolated Ground | 14692.87 | 6.41 | 617.56 | 0 | 33.56 | 0 | OK | Ground clear controls. | 39 | 36.64 | 651.12
2331 | TIN-INTERP | Interpolated Ground | 14732.55 | -5.28 | 619.86 | 0 | 21.96 | 0 | OK | Ground clear controls. | 39 | 36.64 | 641.82
2332 | TIN-INTERP | Interpolated Ground | 14732.62 | -6.78 | 619.82 | 0 | 27.48 | 0 | OK | Ground clear controls. | 39 | 36.64 | 647.3
2333 | TIN-INTERP | Interpolated Ground | 14732.65 | -4.78 | 619.87 | 0 | 32.69 | 0 | OK | Ground clear controls. | 39 | 36.64 | 652.56
2334 | TIN-INTERP | Interpolated Ground | 14732.78 | 4.93 | 619.41 | 0 | 22.48 | 0 | OK | Ground clear controls. | 39 | 36.64 | 641.89
2335 | TIN-INTERP | Interpolated Ground | 14732.79 | 4.43 | 619.49 | 0 | 33.19 | 0 | OK | Ground clear controls. | 39 | 36.64 | 652.68
2336 | TIN-INTERP | Interpolated Ground | 14732.87 | 6.43 | 619.22 | 0 | 28 | 0 | OK | Ground clear controls. | 39 | 36.64 | 647.22
2337 | TIN-INTERP | Interpolated Ground | 14772.55 | -5.26 | 619.19 | 0 | 19.67 | 0 | OK | Ground clear controls. | 39 | 36.64 | 638.86
2338 | TIN-INTERP | Interpolated Ground | 14772.62 | -6.76 | 619.2 | 0 | 25.14 | 0 | OK | Ground clear controls. | 39 | 36.64 | 644.34
2339 | TIN-INTERP | Interpolated Ground | 14772.65 | -4.76 | 619.2 | 0 | 30.33 | 0 | OK | Ground clear controls. | 39 | 36.64 | 649.53
2340 | TIN-INTERP | Interpolated Ground | 14772.78 | 4.94 | 619.67 | 0 | 19.29 | 0 | OK | Ground clear controls. | 39 | 36.64 | 638.96
2341 | TIN-INTERP | Interpolated Ground | 14772.79 | 4.44 | 619.64 | 0 | 30.04 | 0 | OK | Ground clear controls. | 39 | 36.64 | 649.68
2342 | TIN-INTERP | Interpolated Ground | 14772.87 | 6.44 | 619.7 | 0 | 24.53 | 0 | OK | Ground clear controls. | 39 | 36.64 | 644.23
2343 | TIN-INTERP | Interpolated Ground | 14812.55 | -5.25 | 620.67 | 0 | 16.15 | 0 | OK | Ground clear controls. | 39 | 36.64 | 636.82
2344 | TIN-INTERP | Interpolated Ground | 14812.62 | -6.75 | 620.7 | 0 | 21.59 | 0 | OK | Ground clear controls. | 39 | 36.64 | 642.29
2345 | TIN-INTERP | Interpolated Ground | 14812.65 | -4.75 | 620.67 | 0 | 26.75 | 0 | OK | Ground clear controls. | 39 | 36.64 | 647.42
2346 | TIN-INTERP | Interpolated Ground | 14812.78 | 4.96 | 620.76 | 0 | 16.18 | 0 | OK | Ground clear controls. | 39 | 36.64 | 636.94
2347 | TIN-INTERP | Interpolated Ground | 14812.79 | 4.46 | 620.78 | 0 | 26.82 | 0 | OK | Ground clear controls. | 39 | 36.64 | 647.6
2348 | TIN-INTERP | Interpolated Ground | 14812.87 | 6.46 | 620.69 | 0 | 21.48 | 0 | OK | Ground clear controls. | 39 | 36.64 | 642.17
2349 | TIN-INTERP | Interpolated Ground | 14852.55 | -5.23 | 621.79 | 0 | 13.88 | 0 | OK | Ground clear controls. | 39 | 36.64 | 635.67
2350 | TIN-INTERP | Interpolated Ground | 14852.62 | -6.73 | 621.69 | 0 | 19.46 | 0 | OK | Ground clear controls. | 39 | 36.64 | 641.15
2351 | TIN-INTERP | Interpolated Ground | 14852.65 | -4.73 | 621.8 | 0 | 24.44 | 0 | OK | Ground clear controls. | 39 | 36.64 | 646.24
2352 | TIN-INTERP | Interpolated Ground | 14852.78 | 4.98 | 622.04 | 0 | 13.78 | 0 | OK | Ground clear controls. | 39 | 36.64 | 635.82
2353 | TIN-INTERP | Interpolated Ground | 14852.79 | 4.48 | 622.01 | 0 | 24.43 | 0 | OK | Ground clear controls. | 39 | 36.64 | 646.44
2354 | TIN-INTERP | Interpolated Ground | 14852.87 | 6.48 | 622.04 | 0 | 18.97 | 0 | OK | Ground clear controls. | 39 | 36.64 | 641.01
2355 | TIN-INTERP | Interpolated Ground | 14892.55 | -5.21 | 622.57 | 0 | 12.88 | 0 | OK | Ground clear controls. | 39 | 36.64 | 635.45
2356 | TIN-INTERP | Interpolated Ground | 14892.62 | -6.71 | 622.54 | 0 | 18.39 | 0 | OK | Ground clear controls. | 39 | 36.64 | 640.93
2357 | TIN-INTERP | Interpolated Ground | 14892.65 | -4.71 | 622.61 | 0 | 23.39 | 0 | OK | Ground clear controls. | 39 | 36.64 | 646
2358 | TIN-INTERP | Interpolated Ground | 14892.78 | 4.99 | 623.22 | 0 | 12.38 | 0 | OK | Ground clear controls. | 39 | 36.64 | 635.6
2359 | TIN-INTERP | Interpolated Ground | 14892.79 | 4.49 | 623.22 | 0 | 22.99 | 0 | OK | Ground clear controls. | 39 | 36.64 | 646.21
2360 | TIN-INTERP | Interpolated Ground | 14892.87 | 6.49 | 623.22 | 0 | 17.56 | 0 | OK | Ground clear controls. | 39 | 36.64 | 640.78
2361 | TIN-INTERP | Interpolated Ground | 14932.55 | -5.19 | 623.14 | 0 | 12.98 | 0 | OK | Ground clear controls. | 39 | 36.64 | 636.12
2362 | TIN-INTERP | Interpolated Ground | 14932.62 | -6.69 | 623.08 | 0 | 18.52 | 0 | OK | Ground clear controls. | 39 | 36.64 | 641.6
2363 | TIN-INTERP | Interpolated Ground | 14932.65 | -4.69 | 623.17 | 0 | 23.5 | 0 | OK | Ground clear controls. | 39 | 36.64 | 646.67
2364 | TIN-INTERP | Interpolated Ground | 14932.78 | 5.01 | 623.72 | 0 | 12.56 | 0 | OK | Ground clear controls. | 39 | 36.64 | 636.28
2365 | TIN-INTERP | Interpolated Ground | 14932.79 | 4.51 | 623.68 | 0 | 23.2 | 0 | OK | Ground clear controls. | 39 | 36.64 | 646.88
2366 | TIN-INTERP | Interpolated Ground | 14932.87 | 6.51 | 623.7 | 0 | 17.76 | 0 | OK | Ground clear controls. | 39 | 36.64 | 641.46
2367 | TIN-INTERP | Interpolated Ground | 14972.55 | -5.18 | 623.64 | 0 | 14.07 | 0 | OK | Ground clear controls. | 39 | 36.64 | 637.71
2368 | TIN-INTERP | Interpolated Ground | 14972.62 | -6.68 | 623.59 | 0 | 19.6 | 0 | OK | Ground clear controls. | 39 | 36.64 | 643.19
2369 | TIN-INTERP | Interpolated Ground | 14972.65 | -4.68 | 623.65 | 0 | 24.63 | 0 | OK | Ground clear controls. | 39 | 36.64 | 648.28
2370 | TIN-INTERP | Interpolated Ground | 14972.78 | 5.03 | 624.56 | 0 | 13.3 | 0 | OK | Ground clear controls. | 39 | 36.64 | 637.86
2371 | TIN-INTERP | Interpolated Ground | 14972.79 | 4.53 | 624.53 | 0 | 23.96 | 0 | OK | Ground clear controls. | 39 | 36.64 | 648.49
2372 | TIN-INTERP | Interpolated Ground | 14972.87 | 6.53 | 624.58 | 0 | 18.48 | 0 | OK | Ground clear controls. | 39 | 36.64 | 643.06
2373 | TIN-INTERP | Interpolated Ground | 15012.55 | -5.16 | 624.69 | 0 | 15.51 | 0 | OK | Ground clear controls. | 39 | 36.64 | 640.2
2374 | TIN-INTERP | Interpolated Ground | 15012.62 | -6.66 | 624.61 | 0 | 21.07 | 0 | OK | Ground clear controls. | 39 | 36.64 | 645.68
2375 | TIN-INTERP | Interpolated Ground | 15012.65 | -4.66 | 624.7 | 0 | 26.11 | 0 | OK | Ground clear controls. | 39 | 36.64 | 650.81
2376 | TIN-INTERP | Interpolated Ground | 15012.78 | 5.05 | 625.03 | 0 | 15.31 | 0 | OK | Ground clear controls. | 39 | 36.64 | 640.34
2377 | TIN-INTERP | Interpolated Ground | 15012.79 | 4.55 | 625.02 | 0 | 25.98 | 0 | OK | Ground clear controls. | 39 | 36.64 | 651
2378 | TIN-INTERP | Interpolated Ground | 15012.87 | 6.55 | 625.03 | 0 | 20.55 | 0 | OK | Ground clear controls. | 39 | 36.64 | 645.58
2379 | TIN-INTERP | Interpolated Ground | 15052.55 | -5.14 | 624.97 | 0 | 18.62 | 0 | OK | Ground clear controls. | 39 | 36.64 | 643.59
2380 | TIN-INTERP | Interpolated Ground | 15052.62 | -6.64 | 624.87 | 0 | 24.21 | 0 | OK | Ground clear controls. | 39 | 36.64 | 649.08
2381 | TIN-INTERP | Interpolated Ground | 15052.65 | -4.64 | 625.02 | 0 | 29.26 | 0 | OK | Ground clear controls. | 39 | 36.64 | 654.28
2382 | TIN-INTERP | Interpolated Ground | 15052.78 | 5.06 | 625.78 | 0 | 17.94 | 0 | OK | Ground clear controls. | 39 | 36.64 | 643.72
2383 | TIN-INTERP | Interpolated Ground | 15052.79 | 4.56 | 625.74 | 0 | 28.71 | 0 | OK | Ground clear controls. | 39 | 36.64 | 654.45
2384 | TIN-INTERP | Interpolated Ground | 15052.87 | 6.56 | 625.92 | 0 | 23.08 | 0 | OK | Ground clear controls. | 39 | 36.64 | 649
2385 | TIN-INTERP | Interpolated Ground | 15092.55 | -5.12 | 626.09 | 0 | 21.82 | 0 | OK | Ground clear controls. | 39 | 36.64 | 647.91
2386 | TIN-INTERP | Interpolated Ground | 15092.62 | -6.62 | 625.92 | 0 | 27.47 | 0 | OK | Ground clear controls. | 39 | 36.64 | 653.39
2387 | TIN-INTERP | Interpolated Ground | 15092.65 | -4.62 | 626.12 | 0 | 32.56 | 0 | OK | Ground clear controls. | 39 | 36.64 | 658.68
2388 | TIN-INTERP | Interpolated Ground | 15092.78 | 5.08 | 626.65 | 0 | 21.36 | 0 | OK | Ground clear controls. | 39 | 36.64 | 648.01
2389 | TIN-INTERP | Interpolated Ground | 15092.79 | 4.58 | 626.62 | 0 | 32.19 | 0 | OK | Ground clear controls. | 39 | 36.64 | 658.81
2390 | TIN-INTERP | Interpolated Ground | 15092.87 | 6.58 | 626.74 | 0 | 26.61 | 0 | OK | Ground clear controls. | 39 | 36.64 | 653.35
2391 | TIN-INTERP | Interpolated Ground | 15132.55 | -5.1 | 627.33 | 0 | 25.79 | 0 | OK | Ground clear controls. | 39 | 36.64 | 653.12
2392 | TIN-INTERP | Interpolated Ground | 15132.62 | -6.6 | 627.23 | 0 | 31.39 | 0 | OK | Ground clear controls. | 39 | 36.64 | 658.62
2393 | TIN-INTERP | Interpolated Ground | 15132.65 | -4.61 | 627.37 | 0 | 36.64 | 0 | OK | Ground clear controls. | 39 | 36.64 | 664.01
2394 | TIN-INTERP | Interpolated Ground | 15132.78 | 5.1 | 627.89 | 0 | 25.31 | 0 | OK | Ground clear controls. | 39 | 36.23 | 653.2
2395 | TIN-INTERP | Interpolated Ground | 15132.79 | 4.6 | 627.87 | 0 | 36.23 | 0 | OK | Ground clear controls. | 39 | 36.23 | 664.1
2396 | TIN-INTERP | Interpolated Ground | 15132.87 | 6.6 | 627.94 | 0 | 30.68 | 0 | OK | Ground clear controls. | 39 | 30.68 | 658.62
2397 | TIN-INTERP | Interpolated Ground | 15167.73 | 5.11 | 628.68 | 0 | 29.8 | 0 | OK | Ground clear controls. | 40 | 40.99 | 658.48
2398 | TIN-INTERP | Interpolated Ground | 15167.74 | 4.61 | 628.66 | 0 | 40.82 | 0 | OK | Ground clear controls. | 40 | 40.99 | 669.48
2399 | TIN-INTERP | Interpolated Ground | 15167.79 | 6.61 | 628.75 | 0 | 35.23 | 0 | OK | Ground clear controls. | 40 | 40.99 | 663.98
2400 | TIN-INTERP | Interpolated Ground | 15167.82 | -6.59 | 628.59 | 0 | 35.4 | 0 | OK | Ground clear controls. | 40 | 40.99 | 663.99
2401 | TIN-INTERP | Interpolated Ground | 15167.82 | -5.09 | 628.71 | 0 | 29.77 | 0 | OK | Ground clear controls. | 40 | 40.99 | 658.48
2402 | TIN-INTERP | Interpolated Ground | 15167.82 | -4.59 | 628.75 | 0 | 40.73 | 0 | OK | Ground clear controls. | 40 | 40.99 | 669.48
2403 | TIN-INTERP | Interpolated Ground | 15207.77 | 5.1 | 628.56 | 0 | 24.5 | 0 | OK | Ground clear controls. | 40 | 40.99 | 653.06
2404 | TIN-INTERP | Interpolated Ground | 15207.77 | 4.6 | 628.54 | 0 | 35.38 | 0 | OK | Ground clear controls. | 40 | 40.99 | 663.92
2405 | TIN-INTERP | Interpolated Ground | 15207.78 | -6.6 | 627.68 | 0 | 30.86 | 0 | OK | Ground clear controls. | 40 | 40.99 | 658.54
2406 | TIN-INTERP | Interpolated Ground | 15207.79 | -5.1 | 627.84 | 0 | 25.22 | 0 | OK | Ground clear controls. | 40 | 40.99 | 653.06
2407 | TIN-INTERP | Interpolated Ground | 15207.82 | -4.6 | 627.89 | 0 | 36.04 | 0 | OK | Ground clear controls. | 40 | 40.99 | 663.93
2408 | TIN-INTERP | Interpolated Ground | 15207.83 | 6.6 | 628.61 | 0 | 29.88 | 0 | OK | Ground clear controls. | 40 | 40.99 | 658.49
2409 | TIN-INTERP | Interpolated Ground | 15247.77 | 5.09 | 626.81 | 0 | 21.73 | 0 | OK | Ground clear controls. | 40 | 40.99 | 648.54
2410 | TIN-INTERP | Interpolated Ground | 15247.77 | 4.59 | 626.81 | 0 | 32.49 | 0 | OK | Ground clear controls. | 40 | 40.99 | 659.3
2411 | TIN-INTERP | Interpolated Ground | 15247.78 | -6.61 | 627.08 | 0 | 26.92 | 0 | OK | Ground clear controls. | 40 | 40.99 | 654
2412 | TIN-INTERP | Interpolated Ground | 15247.79 | -5.11 | 627.06 | 0 | 21.48 | 0 | OK | Ground clear controls. | 40 | 40.99 | 648.54
2413 | TIN-INTERP | Interpolated Ground | 15247.82 | -4.61 | 627.04 | 0 | 32.26 | 0 | OK | Ground clear controls. | 40 | 40.99 | 659.3
2414 | TIN-INTERP | Interpolated Ground | 15247.83 | 6.59 | 626.8 | 0 | 27.13 | 0 | OK | Ground clear controls. | 40 | 40.99 | 653.93
2415 | TIN-INTERP | Interpolated Ground | 15287.77 | 5.08 | 623.05 | 0 | 21.88 | 0 | OK | Ground clear controls. | 40 | 40.99 | 644.93
2416 | TIN-INTERP | Interpolated Ground | 15287.77 | 4.58 | 622.99 | 0 | 32.61 | 0 | OK | Ground clear controls. | 40 | 40.99 | 655.6
2417 | TIN-INTERP | Interpolated Ground | 15287.78 | -6.62 | 621.92 | 0 | 28.46 | 0 | OK | Ground clear controls. | 40 | 40.99 | 650.38
2418 | TIN-INTERP | Interpolated Ground | 15287.79 | -5.12 | 622.08 | 0 | 22.85 | 0 | OK | Ground clear controls. | 40 | 40.99 | 644.93
2419 | TIN-INTERP | Interpolated Ground | 15287.82 | -4.62 | 622.14 | 0 | 33.47 | 0 | OK | Ground clear controls. | 40 | 40.99 | 655.61
2420 | TIN-INTERP | Interpolated Ground | 15287.83 | 6.58 | 623.2 | 0 | 27.09 | 0 | OK | Ground clear controls. | 40 | 40.99 | 650.29
2421 | TIN-INTERP | Interpolated Ground | 15327.77 | 5.06 | 619.24 | 0 | 23 | 0 | OK | Ground clear controls. | 40 | 40.99 | 642.24
2422 | TIN-INTERP | Interpolated Ground | 15327.77 | 4.56 | 619.05 | 0 | 33.78 | 0 | OK | Ground clear controls. | 40 | 40.99 | 652.83
2423 | TIN-INTERP | Interpolated Ground | 15327.78 | -6.64 | 617.01 | 0 | 30.67 | 0 | OK | Ground clear controls. | 40 | 40.99 | 647.68
2424 | TIN-INTERP | Interpolated Ground | 15327.79 | -5.14 | 617.02 | 0 | 25.22 | 0 | OK | Ground clear controls. | 40 | 40.99 | 642.24
2425 | TIN-INTERP | Interpolated Ground | 15327.82 | -4.64 | 617.06 | 0 | 35.79 | 0 | OK | Ground clear controls. | 40 | 40.99 | 652.85
2426 | TIN-INTERP | Interpolated Ground | 15327.83 | 6.56 | 619.76 | 0 | 27.8 | 0 | OK | Ground clear controls. | 40 | 40.99 | 647.56
2427 | TIN-INTERP | Interpolated Ground | 15367.77 | 5.05 | 620.37 | 0 | 20.08 | 0 | OK | Ground clear controls. | 40 | 40.99 | 640.45
2428 | TIN-INTERP | Interpolated Ground | 15367.77 | 4.55 | 620.28 | 0 | 30.71 | 0 | OK | Ground clear controls. | 40 | 40.99 | 650.99
2429 | TIN-INTERP | Interpolated Ground | 15367.78 | -6.65 | 617.78 | 0 | 28.11 | 0 | OK | Ground clear controls. | 40 | 40.99 | 645.89
2430 | TIN-INTERP | Interpolated Ground | 15367.79 | -5.15 | 618.12 | 0 | 22.33 | 0 | OK | Ground clear controls. | 40 | 40.99 | 640.45
2431 | TIN-INTERP | Interpolated Ground | 15367.82 | -4.65 | 618.21 | 0 | 32.8 | 0 | OK | Ground clear controls. | 40 | 40.99 | 651.01
2432 | TIN-INTERP | Interpolated Ground | 15367.83 | 6.55 | 620.7 | 0 | 25.05 | 0 | OK | Ground clear controls. | 40 | 40.99 | 645.75
2433 | TIN-INTERP | Interpolated Ground | 15407.77 | 5.04 | 617.9 | 0 | 21.67 | 0 | OK | Ground clear controls. | 40 | 40.99 | 639.57
2434 | TIN-INTERP | Interpolated Ground | 15407.77 | 4.54 | 617.81 | 0 | 32.28 | 0 | OK | Ground clear controls. | 40 | 40.99 | 650.09
2435 | TIN-INTERP | Interpolated Ground | 15407.78 | -6.66 | 615.88 | 0 | 29.13 | 0 | OK | Ground clear controls. | 40 | 40.99 | 645.01
2436 | TIN-INTERP | Interpolated Ground | 15407.79 | -5.16 | 616.09 | 0 | 23.48 | 0 | OK | Ground clear controls. | 40 | 40.99 | 639.57
2437 | TIN-INTERP | Interpolated Ground | 15407.82 | -4.66 | 616.15 | 0 | 33.95 | 0 | OK | Ground clear controls. | 40 | 40.99 | 650.1
2438 | TIN-INTERP | Interpolated Ground | 15407.83 | 6.54 | 618.21 | 0 | 26.65 | 0 | OK | Ground clear controls. | 40 | 40.99 | 644.86
2439 | TIN-INTERP | Interpolated Ground | 15447.77 | 5.03 | 619.56 | 0 | 20.04 | 0 | OK | Ground clear controls. | 40 | 40.99 | 639.6
2440 | TIN-INTERP | Interpolated Ground | 15447.77 | 4.53 | 619.58 | 0 | 30.52 | 0 | OK | Ground clear controls. | 40 | 40.99 | 650.1
2441 | TIN-INTERP | Interpolated Ground | 15447.78 | -6.67 | 620.06 | 0 | 24.97 | 0 | OK | Ground clear controls. | 40 | 40.99 | 645.03
2442 | TIN-INTERP | Interpolated Ground | 15447.79 | -5.17 | 620.1 | 0 | 19.51 | 0 | OK | Ground clear controls. | 40 | 40.99 | 639.61
2443 | TIN-INTERP | Interpolated Ground | 15447.82 | -4.67 | 620.09 | 0 | 30.03 | 0 | OK | Ground clear controls. | 40 | 40.99 | 650.12
2444 | TIN-INTERP | Interpolated Ground | 15447.83 | 6.53 | 619.54 | 0 | 25.34 | 0 | OK | Ground clear controls. | 40 | 40.99 | 644.88
2445 | TIN-INTERP | Interpolated Ground | 15487.77 | 5.02 | 627.61 | 0 | 12.93 | 0 | OK | Ground clear controls. | 40 | 40.99 | 640.54
2446 | TIN-INTERP | Interpolated Ground | 15487.77 | 4.52 | 627.63 | 0 | 23.41 | 0 | OK | Ground clear controls. | 40 | 40.99 | 651.04
2447 | TIN-INTERP | Interpolated Ground | 15487.78 | -6.68 | 627.17 | 0 | 18.8 | 0 | OK | Ground clear controls. | 40 | 40.99 | 645.97
2448 | TIN-INTERP | Interpolated Ground | 15487.79 | -5.18 | 627.29 | 0 | 13.25 | 0 | OK | Ground clear controls. | 40 | 40.99 | 640.54
2449 | TIN-INTERP | Interpolated Ground | 15487.82 | -4.68 | 627.31 | 0 | 23.75 | 0 | OK | Ground clear controls. | 40 | 40.99 | 651.06
2450 | TIN-INTERP | Interpolated Ground | 15487.83 | 6.52 | 627.43 | 0 | 18.4 | 0 | OK | Ground clear controls. | 40 | 40.99 | 645.83
2451 | TIN-INTERP | Interpolated Ground | 15527.77 | 5.01 | 629.96 | 0 | 12.42 | 0 | OK | Ground clear controls. | 40 | 40.99 | 642.38
2452 | TIN-INTERP | Interpolated Ground | 15527.77 | 4.51 | 629.93 | 0 | 22.99 | 0 | OK | Ground clear controls. | 40 | 40.99 | 652.92
2453 | TIN-INTERP | Interpolated Ground | 15527.78 | -6.69 | 629.1 | 0 | 18.71 | 0 | OK | Ground clear controls. | 40 | 40.99 | 647.81
2454 | TIN-INTERP | Interpolated Ground | 15527.79 | -5.19 | 629.21 | 0 | 13.17 | 0 | OK | Ground clear controls. | 40 | 40.99 | 642.38
2455 | TIN-INTERP | Interpolated Ground | 15527.82 | -4.69 | 629.23 | 0 | 23.69 | 0 | OK | Ground clear controls. | 40 | 40.99 | 652.92
2456 | TIN-INTERP | Interpolated Ground | 15527.83 | 6.51 | 630.03 | 0 | 17.65 | 0 | OK | Ground clear controls. | 40 | 40.99 | 647.68
2457 | TIN-INTERP | Interpolated Ground | 15567.77 | 4.99 | 632.28 | 0 | 12.86 | 0 | OK | Ground clear controls. | 40 | 40.99 | 645.14
2458 | TIN-INTERP | Interpolated Ground | 15567.77 | 4.49 | 632.27 | 0 | 23.44 | 0 | OK | Ground clear controls. | 40 | 40.99 | 655.71
2459 | TIN-INTERP | Interpolated Ground | 15567.78 | -6.71 | 631.71 | 0 | 18.87 | 0 | OK | Ground clear controls. | 40 | 40.99 | 650.58
2460 | TIN-INTERP | Interpolated Ground | 15567.79 | -5.21 | 631.84 | 0 | 13.3 | 0 | OK | Ground clear controls. | 40 | 40.99 | 645.14
2461 | TIN-INTERP | Interpolated Ground | 15567.82 | -4.71 | 631.89 | 0 | 23.83 | 0 | OK | Ground clear controls. | 40 | 40.99 | 655.72
2462 | TIN-INTERP | Interpolated Ground | 15567.83 | 6.49 | 632.32 | 0 | 18.14 | 0 | OK | Ground clear controls. | 40 | 40.99 | 650.46
2463 | TIN-INTERP | Interpolated Ground | 15607.77 | 4.98 | 633.88 | 0 | 14.93 | 0 | OK | Ground clear controls. | 40 | 40.99 | 648.81
2464 | TIN-INTERP | Interpolated Ground | 15607.77 | 4.48 | 633.86 | 0 | 25.59 | 0 | OK | Ground clear controls. | 40 | 40.99 | 659.45
2465 | TIN-INTERP | Interpolated Ground | 15607.78 | -6.72 | 632.95 | 0 | 21.3 | 0 | OK | Ground clear controls. | 40 | 40.99 | 654.25
2466 | TIN-INTERP | Interpolated Ground | 15607.79 | -5.22 | 633.13 | 0 | 15.67 | 0 | OK | Ground clear controls. | 40 | 40.99 | 648.8
2467 | TIN-INTERP | Interpolated Ground | 15607.82 | -4.72 | 633.18 | 0 | 26.27 | 0 | OK | Ground clear controls. | 40 | 40.99 | 659.45
2468 | TIN-INTERP | Interpolated Ground | 15607.83 | 6.48 | 634 | 0 | 20.15 | 0 | OK | Ground clear controls. | 40 | 40.99 | 654.15
2469 | TIN-INTERP | Interpolated Ground | 15647.77 | 4.97 | 635.34 | 0 | 18.04 | 0 | OK | Ground clear controls. | 40 | 40.99 | 653.38
2470 | TIN-INTERP | Interpolated Ground | 15647.77 | 4.47 | 635.29 | 0 | 28.82 | 0 | OK | Ground clear controls. | 40 | 40.99 | 664.11
2471 | TIN-INTERP | Interpolated Ground | 15647.78 | -6.73 | 634.19 | 0 | 24.65 | 0 | OK | Ground clear controls. | 40 | 40.99 | 658.84
2472 | TIN-INTERP | Interpolated Ground | 15647.79 | -5.23 | 634.33 | 0 | 19.05 | 0 | OK | Ground clear controls. | 40 | 40.99 | 653.38
2473 | TIN-INTERP | Interpolated Ground | 15647.82 | -4.73 | 634.37 | 0 | 29.74 | 0 | OK | Ground clear controls. | 40 | 40.99 | 664.11
2474 | TIN-INTERP | Interpolated Ground | 15647.83 | 6.47 | 635.43 | 0 | 23.34 | 0 | OK | Ground clear controls. | 40 | 40.99 | 658.77
2475 | TIN-INTERP | Interpolated Ground | 15687.77 | 4.96 | 635.84 | 0 | 23.03 | 0 | OK | Ground clear controls. | 40 | 40.99 | 658.87
2476 | TIN-INTERP | Interpolated Ground | 15687.77 | 4.46 | 635.81 | 0 | 33.9 | 0 | OK | Ground clear controls. | 40 | 40.99 | 669.71
2477 | TIN-INTERP | Interpolated Ground | 15687.78 | -6.74 | 634.91 | 0 | 29.43 | 0 | OK | Ground clear controls. | 40 | 40.99 | 664.34
2478 | TIN-INTERP | Interpolated Ground | 15687.79 | -5.24 | 635.03 | 0 | 23.84 | 0 | OK | Ground clear controls. | 40 | 40.99 | 658.87
2479 | TIN-INTERP | Interpolated Ground | 15687.82 | -4.74 | 635.06 | 0 | 34.64 | 0 | OK | Ground clear controls. | 40 | 40.99 | 669.7
2480 | TIN-INTERP | Interpolated Ground | 15687.83 | 6.46 | 635.98 | 0 | 28.33 | 0 | OK | Ground clear controls. | 40 | 40.99 | 664.31
2481 | TIN-INTERP | Interpolated Ground | 15727.77 | 4.95 | 636.19 | 0 | 29.1 | 0 | OK | Ground clear controls. | 40 | 40.99 | 665.29
2482 | TIN-INTERP | Interpolated Ground | 15727.77 | 4.45 | 636.13 | 0 | 40.11 | 0 | OK | Ground clear controls. | 40 | 40.99 | 676.24
2483 | TIN-INTERP | Interpolated Ground | 15727.78 | -6.75 | 635.09 | 0 | 35.68 | 0 | OK | Ground clear controls. | 40 | 40.99 | 670.77
2484 | TIN-INTERP | Interpolated Ground | 15727.79 | -5.25 | 635.2 | 0 | 30.07 | 0 | OK | Ground clear controls. | 40 | 40.99 | 665.27
2485 | TIN-INTERP | Interpolated Ground | 15727.82 | -4.75 | 635.24 | 0 | 40.99 | 0 | OK | Ground clear controls. | 40 | 40.99 | 676.23
2486 | TIN-INTERP | Interpolated Ground | 15727.83 | 6.45 | 636.31 | 0 | 34.47 | 0 | OK | Ground clear controls. | 40 | 34.47 | 670.78
2487 | TIN-INTERP | Interpolated Ground | 15742.29 | 6.44 | 636.13 | 0 | 37.21 | 0 | OK | Ground clear controls. | 41 | 43.63 | 673.34
2488 | TIN-INTERP | Interpolated Ground | 15742.3 | 4.94 | 635.94 | 0 | 31.9 | 0 | OK | Ground clear controls. | 41 | 43.63 | 667.84
2489 | TIN-INTERP | Interpolated Ground | 15742.3 | 4.44 | 635.89 | 0 | 42.95 | 0 | OK | Ground clear controls. | 41 | 43.63 | 678.84
2490 | TIN-INTERP | Interpolated Ground | 15742.39 | -6.76 | 634.92 | 0 | 38.42 | 0 | OK | Ground clear controls. | 41 | 43.63 | 673.34
2491 | TIN-INTERP | Interpolated Ground | 15742.4 | -4.76 | 635.21 | 0 | 43.63 | 0 | OK | Ground clear controls. | 41 | 43.63 | 678.84
2492 | TIN-INTERP | Interpolated Ground | 15742.41 | -5.26 | 635.16 | 0 | 32.68 | 0 | OK | Ground clear controls. | 41 | 42.34 | 667.84
2493 | TIN-INTERP | Interpolated Ground | 15782.29 | 6.45 | 636.52 | 0 | 32.46 | 0 | OK | Ground clear controls. | 41 | 42.34 | 668.98
2494 | TIN-INTERP | Interpolated Ground | 15782.3 | 4.95 | 636.36 | 0 | 27.2 | 0 | OK | Ground clear controls. | 41 | 42.34 | 663.56
2495 | TIN-INTERP | Interpolated Ground | 15782.3 | 4.45 | 636.3 | 0 | 38.12 | 0 | OK | Ground clear controls. | 41 | 42.34 | 674.42
2496 | TIN-INTERP | Interpolated Ground | 15782.39 | -6.75 | 635.28 | 0 | 33.73 | 0 | OK | Ground clear controls. | 41 | 42.34 | 669.01
2497 | TIN-INTERP | Interpolated Ground | 15782.4 | -4.75 | 635.51 | 0 | 38.9 | 0 | OK | Ground clear controls. | 41 | 42.34 | 674.41
2498 | TIN-INTERP | Interpolated Ground | 15782.41 | -5.25 | 635.47 | 0 | 28.07 | 0 | OK | Ground clear controls. | 41 | 42.34 | 663.54
2499 | TIN-INTERP | Interpolated Ground | 15822.29 | 6.45 | 636.88 | 0 | 28.68 | 0 | OK | Ground clear controls. | 41 | 42.34 | 665.56
2500 | TIN-INTERP | Interpolated Ground | 15822.3 | 4.95 | 636.73 | 0 | 23.47 | 0 | OK | Ground clear controls. | 41 | 42.34 | 660.2
2501 | TIN-INTERP | Interpolated Ground | 15822.3 | 4.45 | 636.68 | 0 | 34.26 | 0 | OK | Ground clear controls. | 41 | 42.34 | 670.94
2502 | TIN-INTERP | Interpolated Ground | 15822.39 | -6.75 | 635.62 | 0 | 29.98 | 0 | OK | Ground clear controls. | 41 | 42.34 | 665.6
2503 | TIN-INTERP | Interpolated Ground | 15822.4 | -4.75 | 635.91 | 0 | 35.01 | 0 | OK | Ground clear controls. | 41 | 42.34 | 670.92
2504 | TIN-INTERP | Interpolated Ground | 15822.41 | -5.25 | 635.84 | 0 | 24.33 | 0 | OK | Ground clear controls. | 41 | 42.34 | 660.17
2505 | TIN-INTERP | Interpolated Ground | 15862.29 | 6.46 | 637.31 | 0 | 25.74 | 0 | OK | Ground clear controls. | 41 | 42.34 | 663.05
2506 | TIN-INTERP | Interpolated Ground | 15862.3 | 4.96 | 637.25 | 0 | 20.49 | 0 | OK | Ground clear controls. | 41 | 42.34 | 657.74
2507 | TIN-INTERP | Interpolated Ground | 15862.3 | 4.46 | 637.22 | 0 | 31.17 | 0 | OK | Ground clear controls. | 41 | 42.34 | 668.39
2508 | TIN-INTERP | Interpolated Ground | 15862.39 | -6.75 | 636.49 | 0 | 26.63 | 0 | OK | Ground clear controls. | 41 | 42.34 | 663.12
2509 | TIN-INTERP | Interpolated Ground | 15862.4 | -4.75 | 636.65 | 0 | 31.71 | 0 | OK | Ground clear controls. | 41 | 42.34 | 668.36
2510 | TIN-INTERP | Interpolated Ground | 15862.41 | -5.25 | 636.61 | 0 | 21.09 | 0 | OK | Ground clear controls. | 41 | 42.34 | 657.7
2511 | TIN-INTERP | Interpolated Ground | 15902.29 | 6.46 | 638.72 | 0 | 22.75 | 0 | OK | Ground clear controls. | 41 | 42.34 | 661.47
2512 | TIN-INTERP | Interpolated Ground | 15902.3 | 4.96 | 638.67 | 0 | 17.54 | 0 | OK | Ground clear controls. | 41 | 42.34 | 656.21
2513 | TIN-INTERP | Interpolated Ground | 15902.3 | 4.46 | 638.6 | 0 | 28.18 | 0 | OK | Ground clear controls. | 41 | 42.34 | 666.78
2514 | TIN-INTERP | Interpolated Ground | 15902.39 | -6.74 | 638.06 | 0 | 23.49 | 0 | OK | Ground clear controls. | 41 | 42.34 | 661.55
2515 | TIN-INTERP | Interpolated Ground | 15902.4 | -4.74 | 638.18 | 0 | 28.55 | 0 | OK | Ground clear controls. | 41 | 42.34 | 666.73
2516 | TIN-INTERP | Interpolated Ground | 15902.41 | -5.24 | 638.13 | 0 | 18.01 | 0 | OK | Ground clear controls. | 41 | 42.34 | 656.14
2517 | TIN-INTERP | Interpolated Ground | 15942.29 | 6.47 | 640.26 | 0 | 20.55 | 0 | OK | Ground clear controls. | 41 | 42.34 | 660.81
2518 | TIN-INTERP | Interpolated Ground | 15942.3 | 4.97 | 640.13 | 0 | 15.45 | 0 | OK | Ground clear controls. | 41 | 42.34 | 655.58
2519 | TIN-INTERP | Interpolated Ground | 15942.3 | 4.47 | 640.13 | 0 | 25.96 | 0 | OK | Ground clear controls. | 41 | 42.34 | 666.09
2520 | TIN-INTERP | Interpolated Ground | 15942.39 | -6.74 | 639.44 | 0 | 21.45 | 0 | OK | Ground clear controls. | 41 | 42.34 | 660.89
2521 | TIN-INTERP | Interpolated Ground | 15942.4 | -4.74 | 639.58 | 0 | 26.45 | 0 | OK | Ground clear controls. | 41 | 42.34 | 666.03
2522 | TIN-INTERP | Interpolated Ground | 15942.41 | -5.24 | 639.55 | 0 | 15.95 | 0 | OK | Ground clear controls. | 41 | 42.34 | 655.5
2523 | TIN-INTERP | Interpolated Ground | 15982.29 | 6.47 | 641.28 | 0 | 19.77 | 0 | OK | Ground clear controls. | 41 | 42.34 | 661.05
2524 | TIN-INTERP | Interpolated Ground | 15982.3 | 4.97 | 641.24 | 0 | 14.63 | 0 | OK | Ground clear controls. | 41 | 42.34 | 655.87
2525 | TIN-INTERP | Interpolated Ground | 15982.3 | 4.47 | 641.22 | 0 | 25.13 | 0 | OK | Ground clear controls. | 41 | 42.34 | 666.35
2526 | TIN-INTERP | Interpolated Ground | 15982.39 | -6.73 | 640.75 | 0 | 20.39 | 0 | OK | Ground clear controls. | 41 | 42.34 | 661.14
2527 | TIN-INTERP | Interpolated Ground | 15982.4 | -4.73 | 640.74 | 0 | 25.52 | 0 | OK | Ground clear controls. | 41 | 42.34 | 666.26
2528 | TIN-INTERP | Interpolated Ground | 15982.41 | -5.23 | 640.72 | 0 | 15.04 | 0 | OK | Ground clear controls. | 41 | 42.34 | 655.76
2529 | TIN-INTERP | Interpolated Ground | 16022.29 | 6.48 | 642.61 | 0 | 19.62 | 0 | OK | Ground clear controls. | 41 | 42.34 | 662.23
2530 | TIN-INTERP | Interpolated Ground | 16022.3 | 4.98 | 642.5 | 0 | 14.57 | 0 | OK | Ground clear controls. | 41 | 42.34 | 657.07
2531 | TIN-INTERP | Interpolated Ground | 16022.3 | 4.48 | 642.5 | 0 | 25.02 | 0 | OK | Ground clear controls. | 41 | 42.34 | 667.52
2532 | TIN-INTERP | Interpolated Ground | 16022.39 | -6.73 | 642.15 | 0 | 20.17 | 0 | OK | Ground clear controls. | 41 | 42.34 | 662.32
2533 | TIN-INTERP | Interpolated Ground | 16022.4 | -4.73 | 642.28 | 0 | 25.14 | 0 | OK | Ground clear controls. | 41 | 42.34 | 667.42
2534 | TIN-INTERP | Interpolated Ground | 16022.41 | -5.23 | 642.29 | 0 | 14.64 | 0 | OK | Ground clear controls. | 41 | 42.34 | 656.93
2535 | TIN-INTERP | Interpolated Ground | 16062.29 | 6.48 | 644.26 | 0 | 20.08 | 0 | OK | Ground clear controls. | 41 | 42.34 | 664.34
2536 | TIN-INTERP | Interpolated Ground | 16062.3 | 4.98 | 644.18 | 0 | 15.01 | 0 | OK | Ground clear controls. | 41 | 42.34 | 659.19
2537 | TIN-INTERP | Interpolated Ground | 16062.3 | 4.48 | 644.1 | 0 | 25.54 | 0 | OK | Ground clear controls. | 41 | 42.34 | 669.64
2538 | TIN-INTERP | Interpolated Ground | 16062.39 | -6.72 | 643.35 | 0 | 21.06 | 0 | OK | Ground clear controls. | 41 | 42.34 | 664.41
2539 | TIN-INTERP | Interpolated Ground | 16062.4 | -4.73 | 643.45 | 0 | 26.05 | 0 | OK | Ground clear controls. | 41 | 42.34 | 669.5
2540 | TIN-INTERP | Interpolated Ground | 16062.41 | -5.22 | 643.38 | 0 | 15.63 | 0 | OK | Ground clear controls. | 41 | 42.34 | 659.01
2541 | TIN-INTERP | Interpolated Ground | 16102.29 | 6.49 | 644.89 | 0 | 22.46 | 0 | OK | Ground clear controls. | 41 | 42.34 | 667.35
2542 | TIN-INTERP | Interpolated Ground | 16102.3 | 4.99 | 644.7 | 0 | 17.51 | 0 | OK | Ground clear controls. | 41 | 42.34 | 662.21
2543 | TIN-INTERP | Interpolated Ground | 16102.3 | 4.49 | 644.68 | 0 | 28.01 | 0 | OK | Ground clear controls. | 41 | 42.34 | 672.69
2544 | TIN-INTERP | Interpolated Ground | 16102.39 | -6.72 | 643.7 | 0 | 23.72 | 0 | OK | Ground clear controls. | 41 | 42.34 | 667.42
2545 | TIN-INTERP | Interpolated Ground | 16102.4 | -4.72 | 643.95 | 0 | 28.58 | 0 | OK | Ground clear controls. | 41 | 42.34 | 672.53
2546 | TIN-INTERP | Interpolated Ground | 16102.41 | -5.22 | 643.88 | 0 | 18.13 | 0 | OK | Ground clear controls. | 41 | 42.34 | 662.01
2547 | TIN-INTERP | Interpolated Ground | 16142.29 | 6.49 | 645.88 | 0 | 25.42 | 0 | OK | Ground clear controls. | 41 | 42.34 | 671.3
2548 | TIN-INTERP | Interpolated Ground | 16142.3 | 4.99 | 645.7 | 0 | 20.46 | 0 | OK | Ground clear controls. | 41 | 42.34 | 666.16
2549 | TIN-INTERP | Interpolated Ground | 16142.3 | 4.49 | 645.66 | 0 | 31.01 | 0 | OK | Ground clear controls. | 41 | 42.34 | 676.67
2550 | TIN-INTERP | Interpolated Ground | 16142.39 | -6.72 | 644.54 | 0 | 26.82 | 0 | OK | Ground clear controls. | 41 | 42.34 | 671.36
2551 | TIN-INTERP | Interpolated Ground | 16142.4 | -4.72 | 644.76 | 0 | 31.72 | 0 | OK | Ground clear controls. | 41 | 42.34 | 676.48
2552 | TIN-INTERP | Interpolated Ground | 16142.41 | -5.22 | 644.71 | 0 | 21.22 | 0 | OK | Ground clear controls. | 41 | 42.34 | 665.93
2553 | TIN-INTERP | Interpolated Ground | 16182.29 | 6.49 | 646.14 | 0 | 30.03 | 0 | OK | Ground clear controls. | 41 | 42.34 | 676.17
2554 | TIN-INTERP | Interpolated Ground | 16182.3 | 4.99 | 646.03 | 0 | 25 | 0 | OK | Ground clear controls. | 41 | 42.34 | 671.03
2555 | TIN-INTERP | Interpolated Ground | 16182.3 | 4.5 | 645.98 | 0 | 35.62 | 0 | OK | Ground clear controls. | 41 | 42.34 | 681.6
2556 | TIN-INTERP | Interpolated Ground | 16182.39 | -6.71 | 644.77 | 0 | 31.44 | 0 | OK | Ground clear controls. | 41 | 42.34 | 676.21
2557 | TIN-INTERP | Interpolated Ground | 16182.4 | -4.71 | 644.95 | 0 | 36.42 | 0 | OK | Ground clear controls. | 41 | 42.34 | 681.37
2558 | TIN-INTERP | Interpolated Ground | 16182.41 | -5.21 | 644.89 | 0 | 25.85 | 0 | OK | Ground clear controls. | 41 | 42.34 | 670.74
2559 | TIN-INTERP | Interpolated Ground | 16222.29 | 6.5 | 646.31 | 0 | 35.66 | 0 | OK | Ground clear controls. | 41 | 42.34 | 681.97
2560 | TIN-INTERP | Interpolated Ground | 16222.3 | 5 | 646.15 | 0 | 30.65 | 0 | OK | Ground clear controls. | 41 | 42.34 | 676.8
2561 | TIN-INTERP | Interpolated Ground | 16222.3 | 4.5 | 646.1 | 0 | 41.36 | 0 | OK | Ground clear controls. | 41 | 42.34 | 687.46
2562 | TIN-INTERP | Interpolated Ground | 16222.39 | -6.71 | 644.72 | 0 | 37.26 | 0 | OK | Ground clear controls. | 41 | 42.34 | 681.98
2563 | TIN-INTERP | Interpolated Ground | 16222.4 | -4.71 | 644.85 | 0 | 42.34 | 0 | OK | Ground clear controls. | 41 | 42.34 | 687.19
2564 | TIN-INTERP | Interpolated Ground | 16222.41 | -5.21 | 644.84 | 0 | 31.65 | 0 | OK | Ground clear controls. | 41 | 31.65 | 676.49
2565 | TIN-INTERP | Interpolated Ground | 16228.76 | 5 | 645.95 | 0 | 31.87 | 0 | OK | Ground clear controls. | 42 | 43.21 | 677.82
2566 | TIN-INTERP | Interpolated Ground | 16228.76 | 4.5 | 645.91 | 0 | 42.58 | 0 | OK | Ground clear controls. | 42 | 43.21 | 688.49
2567 | TIN-INTERP | Interpolated Ground | 16228.77 | 6.5 | 646.39 | 0 | 36.6 | 0 | OK | Ground clear controls. | 42 | 43.21 | 682.99
2568 | TIN-INTERP | Interpolated Ground | 16228.79 | -6.71 | 644.77 | 0 | 38.22 | 0 | OK | Ground clear controls. | 42 | 43.21 | 682.99
2569 | TIN-INTERP | Interpolated Ground | 16228.8 | -5.21 | 644.93 | 0 | 32.56 | 0 | OK | Ground clear controls. | 42 | 43.21 | 677.49
2570 | TIN-INTERP | Interpolated Ground | 16228.83 | -4.71 | 645 | 0 | 43.21 | 0 | OK | Ground clear controls. | 42 | 43.21 | 688.21
2571 | TIN-INTERP | Interpolated Ground | 16268.76 | 5.01 | 645.91 | 0 | 26.28 | 0 | OK | Ground clear controls. | 42 | 39.24 | 672.19
2572 | TIN-INTERP | Interpolated Ground | 16268.76 | 4.52 | 645.85 | 0 | 36.94 | 0 | OK | Ground clear controls. | 42 | 39.24 | 682.79
2573 | TIN-INTERP | Interpolated Ground | 16268.77 | 6.51 | 646.14 | 0 | 31.2 | 0 | OK | Ground clear controls. | 42 | 39.24 | 677.34
2574 | TIN-INTERP | Interpolated Ground | 16268.79 | -6.74 | 644.41 | 0 | 32.97 | 0 | OK | Ground clear controls. | 42 | 39.24 | 677.38
2575 | TIN-INTERP | Interpolated Ground | 16268.8 | -5.24 | 644.68 | 0 | 27.26 | 0 | OK | Ground clear controls. | 42 | 39.24 | 671.94
2576 | TIN-INTERP | Interpolated Ground | 16268.83 | -4.75 | 644.79 | 0 | 37.81 | 0 | OK | Ground clear controls. | 42 | 39.24 | 682.6
2577 | TIN-INTERP | Interpolated Ground | 16308.76 | 5.02 | 644.35 | 0 | 23.15 | 0 | OK | Ground clear controls. | 42 | 39.24 | 667.5
2578 | TIN-INTERP | Interpolated Ground | 16308.76 | 4.54 | 644.27 | 0 | 33.76 | 0 | OK | Ground clear controls. | 42 | 39.24 | 678.03
2579 | TIN-INTERP | Interpolated Ground | 16308.77 | 6.52 | 644.6 | 0 | 28.03 | 0 | OK | Ground clear controls. | 42 | 39.24 | 672.63
2580 | TIN-INTERP | Interpolated Ground | 16308.79 | -6.77 | 642.72 | 0 | 29.99 | 0 | OK | Ground clear controls. | 42 | 39.24 | 672.71
2581 | TIN-INTERP | Interpolated Ground | 16308.8 | -5.27 | 643.18 | 0 | 24.13 | 0 | OK | Ground clear controls. | 42 | 39.24 | 667.31
2582 | TIN-INTERP | Interpolated Ground | 16308.83 | -4.78 | 643.25 | 0 | 34.67 | 0 | OK | Ground clear controls. | 42 | 39.24 | 677.92
2583 | TIN-INTERP | Interpolated Ground | 16348.76 | 5.03 | 643.67 | 0 | 20.06 | 0 | OK | Ground clear controls. | 42 | 39.24 | 663.73
2584 | TIN-INTERP | Interpolated Ground | 16348.76 | 4.55 | 643.57 | 0 | 30.64 | 0 | OK | Ground clear controls. | 42 | 39.24 | 674.21
2585 | TIN-INTERP | Interpolated Ground | 16348.77 | 6.53 | 643.96 | 0 | 24.89 | 0 | OK | Ground clear controls. | 42 | 39.24 | 668.85
2586 | TIN-INTERP | Interpolated Ground | 16348.79 | -6.8 | 641.91 | 0 | 27.05 | 0 | OK | Ground clear controls. | 42 | 39.24 | 668.96
2587 | TIN-INTERP | Interpolated Ground | 16348.8 | -5.3 | 642.09 | 0 | 21.5 | 0 | OK | Ground clear controls. | 42 | 39.24 | 663.59
2588 | TIN-INTERP | Interpolated Ground | 16348.83 | -4.82 | 642.17 | 0 | 32.01 | 0 | OK | Ground clear controls. | 42 | 39.24 | 674.18
2589 | TIN-INTERP | Interpolated Ground | 16388.76 | 5.04 | 644.48 | 0 | 16.4 | 0 | OK | Ground clear controls. | 42 | 39.24 | 660.88
2590 | TIN-INTERP | Interpolated Ground | 16388.76 | 4.57 | 644.39 | 0 | 26.94 | 0 | OK | Ground clear controls. | 42 | 39.24 | 671.33
2591 | TIN-INTERP | Interpolated Ground | 16388.77 | 6.54 | 644.74 | 0 | 21.26 | 0 | OK | Ground clear controls. | 42 | 39.24 | 666
2592 | TIN-INTERP | Interpolated Ground | 16388.79 | -6.83 | 642.78 | 0 | 23.35 | 0 | OK | Ground clear controls. | 42 | 39.24 | 666.13
2593 | TIN-INTERP | Interpolated Ground | 16388.8 | -5.33 | 642.97 | 0 | 17.82 | 0 | OK | Ground clear controls. | 42 | 39.24 | 660.79
2594 | TIN-INTERP | Interpolated Ground | 16388.83 | -4.86 | 643.02 | 0 | 28.34 | 0 | OK | Ground clear controls. | 42 | 39.24 | 671.36
2595 | TIN-INTERP | Interpolated Ground | 16428.76 | 5.05 | 643.51 | 0 | 15.45 | 0 | OK | Ground clear controls. | 42 | 39.24 | 658.96
2596 | TIN-INTERP | Interpolated Ground | 16428.76 | 4.59 | 643.46 | 0 | 25.95 | 0 | OK | Ground clear controls. | 42 | 39.24 | 669.41
2597 | TIN-INTERP | Interpolated Ground | 16428.77 | 6.55 | 643.76 | 0 | 20.33 | 0 | OK | Ground clear controls. | 42 | 39.24 | 664.09
2598 | TIN-INTERP | Interpolated Ground | 16428.79 | -6.86 | 641.47 | 0 | 22.76 | 0 | OK | Ground clear controls. | 42 | 39.24 | 664.23
2599 | TIN-INTERP | Interpolated Ground | 16428.8 | -5.36 | 641.72 | 0 | 17.2 | 0 | OK | Ground clear controls. | 42 | 39.24 | 658.92
2600 | TIN-INTERP | Interpolated Ground | 16428.83 | -4.9 | 641.8 | 0 | 27.69 | 0 | OK | Ground clear controls. | 42 | 39.24 | 669.49
2601 | TIN-INTERP | Interpolated Ground | 16468.76 | 5.06 | 643.89 | 0 | 14.08 | 0 | OK | Ground clear controls. | 42 | 39.24 | 657.97
2602 | TIN-INTERP | Interpolated Ground | 16468.76 | 4.61 | 643.8 | 0 | 24.62 | 0 | OK | Ground clear controls. | 42 | 39.24 | 668.42
2603 | TIN-INTERP | Interpolated Ground | 16468.77 | 6.56 | 644.14 | 0 | 18.96 | 0 | OK | Ground clear controls. | 42 | 39.24 | 663.1
2604 | TIN-INTERP | Interpolated Ground | 16468.79 | -6.89 | 641.99 | 0 | 21.27 | 0 | OK | Ground clear controls. | 42 | 39.24 | 663.26
2605 | TIN-INTERP | Interpolated Ground | 16468.8 | -5.39 | 642.18 | 0 | 15.78 | 0 | OK | Ground clear controls. | 42 | 39.24 | 657.96
2606 | TIN-INTERP | Interpolated Ground | 16468.83 | -4.94 | 642.25 | 0 | 26.3 | 0 | OK | Ground clear controls. | 42 | 39.24 | 668.55
2607 | TIN-INTERP | Interpolated Ground | 16508.76 | 5.07 | 645.1 | 0 | 12.78 | 0 | OK | Ground clear controls. | 42 | 39.24 | 657.88
2608 | TIN-INTERP | Interpolated Ground | 16508.76 | 4.62 | 645.03 | 0 | 23.36 | 0 | OK | Ground clear controls. | 42 | 39.24 | 668.39
2609 | TIN-INTERP | Interpolated Ground | 16508.77 | 6.57 | 645.35 | 0 | 17.69 | 0 | OK | Ground clear controls. | 42 | 39.24 | 663.04
2610 | TIN-INTERP | Interpolated Ground | 16508.79 | -6.92 | 642.95 | 0 | 20.26 | 0 | OK | Ground clear controls. | 42 | 39.24 | 663.21
2611 | TIN-INTERP | Interpolated Ground | 16508.8 | -5.42 | 643.19 | 0 | 14.72 | 0 | OK | Ground clear controls. | 42 | 39.24 | 657.91
2612 | TIN-INTERP | Interpolated Ground | 16508.83 | -4.97 | 643.27 | 0 | 25.27 | 0 | OK | Ground clear controls. | 42 | 39.24 | 668.54
2613 | TIN-INTERP | Interpolated Ground | 16548.76 | 5.08 | 645.27 | 0 | 13.45 | 0 | OK | Ground clear controls. | 42 | 39.24 | 658.72
2614 | TIN-INTERP | Interpolated Ground | 16548.76 | 4.64 | 645.2 | 0 | 24.09 | 0 | OK | Ground clear controls. | 42 | 39.24 | 669.29
2615 | TIN-INTERP | Interpolated Ground | 16548.77 | 6.58 | 645.52 | 0 | 18.39 | 0 | OK | Ground clear controls. | 42 | 39.24 | 663.91
2616 | TIN-INTERP | Interpolated Ground | 16548.79 | -6.95 | 643.86 | 0 | 20.22 | 0 | OK | Ground clear controls. | 42 | 39.24 | 664.08
2617 | TIN-INTERP | Interpolated Ground | 16548.8 | -5.45 | 644.01 | 0 | 14.76 | 0 | OK | Ground clear controls. | 42 | 39.24 | 658.77
2618 | TIN-INTERP | Interpolated Ground | 16548.83 | -5.01 | 644.05 | 0 | 25.4 | 0 | OK | Ground clear controls. | 42 | 39.24 | 669.45
2619 | TIN-INTERP | Interpolated Ground | 16588.76 | 5.09 | 645.23 | 0 | 15.27 | 0 | OK | Ground clear controls. | 42 | 39.24 | 660.5
2620 | TIN-INTERP | Interpolated Ground | 16588.76 | 4.66 | 645.16 | 0 | 25.96 | 0 | OK | Ground clear controls. | 42 | 39.24 | 671.12
2621 | TIN-INTERP | Interpolated Ground | 16588.77 | 6.59 | 645.43 | 0 | 20.28 | 0 | OK | Ground clear controls. | 42 | 39.24 | 665.71
2622 | TIN-INTERP | Interpolated Ground | 16588.79 | -6.99 | 644.4 | 0 | 21.46 | 0 | OK | Ground clear controls. | 42 | 39.24 | 665.86
2623 | TIN-INTERP | Interpolated Ground | 16588.8 | -5.49 | 644.51 | 0 | 16.05 | 0 | OK | Ground clear controls. | 42 | 39.24 | 660.56
2624 | TIN-INTERP | Interpolated Ground | 16588.83 | -5.05 | 644.54 | 0 | 26.76 | 0 | OK | Ground clear controls. | 42 | 39.24 | 671.3
2625 | TIN-INTERP | Interpolated Ground | 16628.76 | 5.11 | 647.24 | 0 | 15.95 | 0 | OK | Ground clear controls. | 42 | 39.24 | 663.19
2626 | TIN-INTERP | Interpolated Ground | 16628.76 | 4.68 | 647.18 | 0 | 26.74 | 0 | OK | Ground clear controls. | 42 | 39.24 | 673.92
2627 | TIN-INTERP | Interpolated Ground | 16628.77 | 6.61 | 647.41 | 0 | 21.04 | 0 | OK | Ground clear controls. | 42 | 39.24 | 668.45
2628 | TIN-INTERP | Interpolated Ground | 16628.79 | -7.02 | 646.51 | 0 | 22.08 | 0 | OK | Ground clear controls. | 42 | 39.24 | 668.59
2629 | TIN-INTERP | Interpolated Ground | 16628.8 | -5.52 | 646.59 | 0 | 16.66 | 0 | OK | Ground clear controls. | 42 | 39.24 | 663.25
2630 | TIN-INTERP | Interpolated Ground | 16628.83 | -5.09 | 646.6 | 0 | 27.48 | 0 | OK | Ground clear controls. | 42 | 39.24 | 674.08
2631 | TIN-INTERP | Interpolated Ground | 16668.76 | 5.12 | 649.24 | 0 | 17.56 | 0 | OK | Ground clear controls. | 42 | 39.24 | 666.8
2632 | TIN-INTERP | Interpolated Ground | 16668.76 | 4.69 | 649.14 | 0 | 28.51 | 0 | OK | Ground clear controls. | 42 | 39.24 | 677.65
2633 | TIN-INTERP | Interpolated Ground | 16668.77 | 6.62 | 649.5 | 0 | 22.61 | 0 | OK | Ground clear controls. | 42 | 39.24 | 672.11
2634 | TIN-INTERP | Interpolated Ground | 16668.79 | -7.05 | 647.33 | 0 | 24.9 | 0 | OK | Ground clear controls. | 42 | 39.24 | 672.23
2635 | TIN-INTERP | Interpolated Ground | 16668.8 | -5.55 | 647.53 | 0 | 19.34 | 0 | OK | Ground clear controls. | 42 | 39.24 | 666.87
2636 | TIN-INTERP | Interpolated Ground | 16668.83 | -5.12 | 647.57 | 0 | 30.23 | 0 | OK | Ground clear controls. | 42 | 39.24 | 677.8
2637 | TIN-INTERP | Interpolated Ground | 16708.76 | 5.13 | 648.71 | 0 | 22.63 | 0 | OK | Ground clear controls. | 42 | 39.24 | 671.34
2638 | TIN-INTERP | Interpolated Ground | 16708.76 | 4.71 | 648.66 | 0 | 33.67 | 0 | OK | Ground clear controls. | 42 | 39.24 | 682.33
2639 | TIN-INTERP | Interpolated Ground | 16708.77 | 6.63 | 648.89 | 0 | 27.82 | 0 | OK | Ground clear controls. | 42 | 39.24 | 676.71
2640 | TIN-INTERP | Interpolated Ground | 16708.79 | -7.08 | 647.44 | 0 | 29.36 | 0 | OK | Ground clear controls. | 42 | 39.24 | 676.8
2641 | TIN-INTERP | Interpolated Ground | 16708.8 | -5.58 | 647.69 | 0 | 23.72 | 0 | OK | Ground clear controls. | 42 | 39.24 | 671.41
2642 | TIN-INTERP | Interpolated Ground | 16708.83 | -5.16 | 647.74 | 0 | 34.7 | 0 | OK | Ground clear controls. | 42 | 39.24 | 682.44
2643 | TIN-INTERP | Interpolated Ground | 16748.76 | 5.14 | 649.3 | 0 | 27.51 | 0 | OK | Ground clear controls. | 42 | 39.24 | 676.81
2644 | TIN-INTERP | Interpolated Ground | 16748.76 | 4.73 | 649.26 | 0 | 38.69 | 0 | OK | Ground clear controls. | 42 | 39.24 | 687.95
2645 | TIN-INTERP | Interpolated Ground | 16748.77 | 6.64 | 649.46 | 0 | 32.78 | 0 | OK | Ground clear controls. | 42 | 39.24 | 682.24
2646 | TIN-INTERP | Interpolated Ground | 16748.79 | -7.11 | 648.78 | 0 | 33.53 | 0 | OK | Ground clear controls. | 42 | 39.24 | 682.31
2647 | TIN-INTERP | Interpolated Ground | 16748.8 | -5.61 | 648.78 | 0 | 28.08 | 0 | OK | Ground clear controls. | 42 | 39.24 | 676.86
2648 | TIN-INTERP | Interpolated Ground | 16748.83 | -5.2 | 648.79 | 0 | 39.24 | 0 | OK | Ground clear controls. | 42 | 39.24 | 688.03
2649 | TIN-INTERP | Interpolated Ground | 16784.8 | -5.23 | 649.2 | 0 | 44.66 | 0 | OK | Ground clear controls. | 43 | 44.66 | 693.86
2650 | TIN-INTERP | Interpolated Ground | 16784.82 | -7.14 | 648.97 | 0 | 39.09 | 0 | OK | Ground clear controls. | 43 | 44.2 | 688.06
2651 | TIN-INTERP | Interpolated Ground | 16784.82 | -5.64 | 649.16 | 0 | 33.4 | 0 | OK | Ground clear controls. | 43 | 44.2 | 682.56
2652 | TIN-INTERP | Interpolated Ground | 16784.94 | 6.65 | 649.7 | 0 | 38.36 | 0 | OK | Ground clear controls. | 43 | 44.2 | 688.06
2653 | TIN-INTERP | Interpolated Ground | 16784.95 | 4.74 | 649.66 | 0 | 44.2 | 0 | OK | Ground clear controls. | 43 | 44.2 | 693.86
2654 | TIN-INTERP | Interpolated Ground | 16784.97 | 5.15 | 649.65 | 0 | 32.91 | 0 | OK | Ground clear controls. | 43 | 39.96 | 682.56
2655 | TIN-INTERP | Interpolated Ground | 16824.79 | -5.2 | 649.85 | 0 | 38.75 | 0 | OK | Ground clear controls. | 43 | 39.96 | 688.6
2656 | TIN-INTERP | Interpolated Ground | 16824.82 | -7.1 | 649.63 | 0 | 33.27 | 0 | OK | Ground clear controls. | 43 | 39.96 | 682.9
2657 | TIN-INTERP | Interpolated Ground | 16824.82 | -5.6 | 649.81 | 0 | 27.63 | 0 | OK | Ground clear controls. | 43 | 39.96 | 677.44
2658 | TIN-INTERP | Interpolated Ground | 16824.94 | 6.64 | 649.23 | 0 | 33.62 | 0 | OK | Ground clear controls. | 43 | 39.96 | 682.85
2659 | TIN-INTERP | Interpolated Ground | 16824.95 | 4.73 | 649.4 | 0 | 39.17 | 0 | OK | Ground clear controls. | 43 | 39.96 | 688.57
2660 | TIN-INTERP | Interpolated Ground | 16824.97 | 5.14 | 649.34 | 0 | 28.1 | 0 | OK | Ground clear controls. | 43 | 39.96 | 677.44
2661 | TIN-INTERP | Interpolated Ground | 16864.79 | -5.16 | 647.69 | 0 | 36.58 | 0 | OK | Ground clear controls. | 43 | 39.96 | 684.27
2662 | TIN-INTERP | Interpolated Ground | 16864.82 | -7.07 | 647.36 | 0 | 31.3 | 0 | OK | Ground clear controls. | 43 | 39.96 | 678.66
2663 | TIN-INTERP | Interpolated Ground | 16864.82 | -5.57 | 647.63 | 0 | 25.61 | 0 | OK | Ground clear controls. | 43 | 39.96 | 673.24
2664 | TIN-INTERP | Interpolated Ground | 16864.94 | 6.63 | 649.54 | 0 | 29.04 | 0 | OK | Ground clear controls. | 43 | 39.96 | 678.58
2665 | TIN-INTERP | Interpolated Ground | 16864.95 | 4.71 | 649.21 | 0 | 35.01 | 0 | OK | Ground clear controls. | 43 | 39.96 | 684.22
2666 | TIN-INTERP | Interpolated Ground | 16864.97 | 5.13 | 649.29 | 0 | 23.94 | 0 | OK | Ground clear controls. | 43 | 39.96 | 673.23
2667 | TIN-INTERP | Interpolated Ground | 16904.79 | -5.12 | 650.58 | 0 | 30.29 | 0 | OK | Ground clear controls. | 43 | 39.96 | 680.87
2668 | TIN-INTERP | Interpolated Ground | 16904.82 | -7.04 | 650.56 | 0 | 24.78 | 0 | OK | Ground clear controls. | 43 | 39.96 | 675.34
2669 | TIN-INTERP | Interpolated Ground | 16904.82 | -5.54 | 650.58 | 0 | 19.37 | 0 | OK | Ground clear controls. | 43 | 39.96 | 669.95
2670 | TIN-INTERP | Interpolated Ground | 16904.94 | 6.61 | 649.84 | 0 | 25.39 | 0 | OK | Ground clear controls. | 43 | 39.96 | 675.23
2671 | TIN-INTERP | Interpolated Ground | 16904.95 | 4.69 | 649.94 | 0 | 30.87 | 0 | OK | Ground clear controls. | 43 | 39.96 | 680.81
2672 | TIN-INTERP | Interpolated Ground | 16904.97 | 5.11 | 649.92 | 0 | 20.02 | 0 | OK | Ground clear controls. | 43 | 39.96 | 669.94
2673 | TIN-INTERP | Interpolated Ground | 16944.79 | -5.08 | 651.26 | 0 | 27.16 | 0 | OK | Ground clear controls. | 43 | 39.96 | 678.42
2674 | TIN-INTERP | Interpolated Ground | 16944.82 | -7.01 | 651.08 | 0 | 21.88 | 0 | OK | Ground clear controls. | 43 | 39.96 | 672.96
2675 | TIN-INTERP | Interpolated Ground | 16944.82 | -5.51 | 651.19 | 0 | 16.4 | 0 | OK | Ground clear controls. | 43 | 39.96 | 667.59
2676 | TIN-INTERP | Interpolated Ground | 16944.94 | 6.6 | 652.16 | 0 | 20.66 | 0 | OK | Ground clear controls. | 43 | 39.96 | 672.82
2677 | TIN-INTERP | Interpolated Ground | 16944.95 | 4.67 | 652.1 | 0 | 26.25 | 0 | OK | Ground clear controls. | 43 | 39.96 | 678.35
2678 | TIN-INTERP | Interpolated Ground | 16944.97 | 5.1 | 652.13 | 0 | 15.45 | 0 | OK | Ground clear controls. | 43 | 39.96 | 667.58
2679 | TIN-INTERP | Interpolated Ground | 16984.79 | -5.04 | 651.61 | 0 | 25.3 | 0 | OK | Ground clear controls. | 43 | 39.96 | 676.91
2680 | TIN-INTERP | Interpolated Ground | 16984.82 | -6.98 | 651.41 | 0 | 20.08 | 0 | OK | Ground clear controls. | 43 | 39.96 | 671.49
2681 | TIN-INTERP | Interpolated Ground | 16984.82 | -5.48 | 651.56 | 0 | 14.58 | 0 | OK | Ground clear controls. | 43 | 39.96 | 666.14
2682 | TIN-INTERP | Interpolated Ground | 16984.94 | 6.59 | 652.53 | 0 | 18.8 | 0 | OK | Ground clear controls. | 43 | 39.96 | 671.33
2683 | TIN-INTERP | Interpolated Ground | 16984.95 | 4.66 | 652.4 | 0 | 24.43 | 0 | OK | Ground clear controls. | 43 | 39.96 | 676.83
2684 | TIN-INTERP | Interpolated Ground | 16984.97 | 5.09 | 652.42 | 0 | 13.7 | 0 | OK | Ground clear controls. | 43 | 39.96 | 666.12
2685 | TIN-INTERP | Interpolated Ground | 17024.79 | -5.01 | 650.33 | 0 | 25.99 | 0 | OK | Ground clear controls. | 43 | 39.96 | 676.32
2686 | TIN-INTERP | Interpolated Ground | 17024.82 | -6.95 | 650.26 | 0 | 20.68 | 0 | OK | Ground clear controls. | 43 | 39.96 | 670.94
2687 | TIN-INTERP | Interpolated Ground | 17024.82 | -5.45 | 650.32 | 0 | 15.28 | 0 | OK | Ground clear controls. | 43 | 39.96 | 665.6
2688 | TIN-INTERP | Interpolated Ground | 17024.94 | 6.58 | 651.62 | 0 | 19.16 | 0 | OK | Ground clear controls. | 43 | 39.96 | 670.78
2689 | TIN-INTERP | Interpolated Ground | 17024.95 | 4.64 | 651.3 | 0 | 24.94 | 0 | OK | Ground clear controls. | 43 | 39.96 | 676.24
2690 | TIN-INTERP | Interpolated Ground | 17024.97 | 5.08 | 651.36 | 0 | 14.22 | 0 | OK | Ground clear controls. | 43 | 39.96 | 665.58
2691 | TIN-INTERP | Interpolated Ground | 17064.79 | -4.97 | 651.42 | 0 | 25.24 | 0 | OK | Ground clear controls. | 43 | 39.96 | 676.66
2692 | TIN-INTERP | Interpolated Ground | 17064.82 | -6.92 | 651.58 | 0 | 19.74 | 0 | OK | Ground clear controls. | 43 | 39.96 | 671.32
2693 | TIN-INTERP | Interpolated Ground | 17064.82 | -5.42 | 651.43 | 0 | 14.55 | 0 | OK | Ground clear controls. | 43 | 39.96 | 665.98
2694 | TIN-INTERP | Interpolated Ground | 17064.94 | 6.57 | 651.72 | 0 | 19.43 | 0 | OK | Ground clear controls. | 43 | 39.96 | 671.15
2695 | TIN-INTERP | Interpolated Ground | 17064.95 | 4.62 | 651.61 | 0 | 24.96 | 0 | OK | Ground clear controls. | 43 | 39.96 | 676.57
2696 | TIN-INTERP | Interpolated Ground | 17064.97 | 5.07 | 651.64 | 0 | 14.32 | 0 | OK | Ground clear controls. | 43 | 39.96 | 665.96
2697 | TIN-INTERP | Interpolated Ground | 17104.79 | -4.93 | 652.95 | 0 | 25.01 | 0 | OK | Ground clear controls. | 43 | 39.96 | 677.96
2698 | TIN-INTERP | Interpolated Ground | 17104.82 | -6.89 | 653 | 0 | 19.62 | 0 | OK | Ground clear controls. | 43 | 39.96 | 672.62
2699 | TIN-INTERP | Interpolated Ground | 17104.82 | -5.39 | 652.96 | 0 | 14.32 | 0 | OK | Ground clear controls. | 43 | 39.96 | 667.28
2700 | TIN-INTERP | Interpolated Ground | 17104.94 | 6.56 | 653.09 | 0 | 19.36 | 0 | OK | Ground clear controls. | 43 | 39.96 | 672.45
2701 | TIN-INTERP | Interpolated Ground | 17104.95 | 4.6 | 653.05 | 0 | 24.82 | 0 | OK | Ground clear controls. | 43 | 39.96 | 677.87
2702 | TIN-INTERP | Interpolated Ground | 17104.97 | 5.06 | 653.08 | 0 | 14.18 | 0 | OK | Ground clear controls. | 43 | 39.96 | 667.26
2703 | TIN-INTERP | Interpolated Ground | 17144.79 | -4.89 | 656.53 | 0 | 23.65 | 0 | OK | Ground clear controls. | 43 | 39.96 | 680.18
2704 | TIN-INTERP | Interpolated Ground | 17144.82 | -6.86 | 656.35 | 0 | 18.5 | 0 | OK | Ground clear controls. | 43 | 39.96 | 674.85
2705 | TIN-INTERP | Interpolated Ground | 17144.82 | -5.36 | 656.5 | 0 | 13 | 0 | OK | Ground clear controls. | 43 | 39.96 | 669.5
2706 | TIN-INTERP | Interpolated Ground | 17144.94 | 6.55 | 655.47 | 0 | 19.21 | 0 | OK | Ground clear controls. | 43 | 39.96 | 674.68
2707 | TIN-INTERP | Interpolated Ground | 17144.95 | 4.59 | 655.84 | 0 | 24.25 | 0 | OK | Ground clear controls. | 43 | 39.96 | 680.09
2708 | TIN-INTERP | Interpolated Ground | 17144.97 | 5.05 | 655.82 | 0 | 13.66 | 0 | OK | Ground clear controls. | 43 | 39.96 | 669.48
2709 | TIN-INTERP | Interpolated Ground | 17184.79 | -4.85 | 657.59 | 0 | 25.74 | 0 | OK | Ground clear controls. | 43 | 39.96 | 683.33
2710 | TIN-INTERP | Interpolated Ground | 17184.82 | -6.83 | 657.73 | 0 | 20.26 | 0 | OK | Ground clear controls. | 43 | 39.96 | 677.99
2711 | TIN-INTERP | Interpolated Ground | 17184.82 | -5.33 | 657.68 | 0 | 14.94 | 0 | OK | Ground clear controls. | 43 | 39.96 | 672.62
2712 | TIN-INTERP | Interpolated Ground | 17184.94 | 6.54 | 657.56 | 0 | 20.28 | 0 | OK | Ground clear controls. | 43 | 39.96 | 677.84
2713 | TIN-INTERP | Interpolated Ground | 17184.95 | 4.57 | 657.64 | 0 | 25.62 | 0 | OK | Ground clear controls. | 43 | 39.96 | 683.26
2714 | TIN-INTERP | Interpolated Ground | 17184.97 | 5.04 | 657.65 | 0 | 14.95 | 0 | OK | Ground clear controls. | 43 | 39.96 | 672.6
2715 | TIN-INTERP | Interpolated Ground | 17224.79 | -4.82 | 658.42 | 0 | 29 | 0 | OK | Ground clear controls. | 43 | 39.96 | 687.42
2716 | TIN-INTERP | Interpolated Ground | 17224.82 | -6.79 | 658.15 | 0 | 23.91 | 0 | OK | Ground clear controls. | 43 | 39.96 | 682.06
2717 | TIN-INTERP | Interpolated Ground | 17224.82 | -5.29 | 658.38 | 0 | 18.28 | 0 | OK | Ground clear controls. | 43 | 39.96 | 676.66
2718 | TIN-INTERP | Interpolated Ground | 17224.94 | 6.53 | 659.51 | 0 | 22.43 | 0 | OK | Ground clear controls. | 43 | 39.96 | 681.94
2719 | TIN-INTERP | Interpolated Ground | 17224.95 | 4.55 | 659.31 | 0 | 28.05 | 0 | OK | Ground clear controls. | 43 | 39.96 | 687.36
2720 | TIN-INTERP | Interpolated Ground | 17224.97 | 5.03 | 659.35 | 0 | 17.3 | 0 | OK | Ground clear controls. | 43 | 39.96 | 676.65
2721 | TIN-INTERP | Interpolated Ground | 17264.79 | -4.78 | 658.68 | 0 | 33.79 | 0 | OK | Ground clear controls. | 43 | 39.96 | 692.47
2722 | TIN-INTERP | Interpolated Ground | 17264.82 | -6.76 | 658.58 | 0 | 28.48 | 0 | OK | Ground clear controls. | 43 | 39.96 | 687.06
2723 | TIN-INTERP | Interpolated Ground | 17264.82 | -5.26 | 658.69 | 0 | 22.94 | 0 | OK | Ground clear controls. | 43 | 39.96 | 681.63
2724 | TIN-INTERP | Interpolated Ground | 17264.94 | 6.52 | 660 | 0 | 26.97 | 0 | OK | Ground clear controls. | 43 | 39.96 | 686.97
2725 | TIN-INTERP | Interpolated Ground | 17264.95 | 4.53 | 660.03 | 0 | 32.39 | 0 | OK | Ground clear controls. | 43 | 39.96 | 692.42
2726 | TIN-INTERP | Interpolated Ground | 17264.97 | 5.02 | 660.03 | 0 | 21.59 | 0 | OK | Ground clear controls. | 43 | 39.96 | 681.62
2727 | TIN-INTERP | Interpolated Ground | 17304.79 | -4.74 | 658.71 | 0 | 39.72 | 0 | OK | Ground clear controls. | 43 | 39.96 | 698.43
2728 | TIN-INTERP | Interpolated Ground | 17304.82 | -6.73 | 658.75 | 0 | 34.25 | 0 | OK | Ground clear controls. | 43 | 39.96 | 693
2729 | TIN-INTERP | Interpolated Ground | 17304.82 | -5.23 | 658.71 | 0 | 28.81 | 0 | OK | Ground clear controls. | 43 | 39.96 | 687.52
2730 | TIN-INTERP | Interpolated Ground | 17304.94 | 6.51 | 658.57 | 0 | 34.37 | 0 | OK | Ground clear controls. | 43 | 39.96 | 692.94
2731 | TIN-INTERP | Interpolated Ground | 17304.95 | 4.52 | 658.46 | 0 | 39.96 | 0 | OK | Ground clear controls. | 43 | 39.96 | 698.42
2732 | TIN-INTERP | Interpolated Ground | 17304.97 | 5.01 | 658.48 | 0 | 29.03 | 0 | OK | Ground clear controls. | 43 | 29.03 | 687.51
2733 | TIN-INTERP | Interpolated Ground | 17335.51 | -6.71 | 661.18 | 0 | 36.99 | 0 | OK | Ground clear controls. | 44 | 44.49 | 698.17
2734 | TIN-INTERP | Interpolated Ground | 17335.54 | -4.71 | 660.64 | 0 | 43.03 | 0 | OK | Ground clear controls. | 44 | 44.49 | 703.67
2735 | TIN-INTERP | Interpolated Ground | 17335.6 | -5.21 | 660.84 | 0 | 31.84 | 0 | OK | Ground clear controls. | 44 | 44.49 | 692.68
2736 | TIN-INTERP | Interpolated Ground | 17335.69 | 4.5 | 659.18 | 0 | 44.49 | 0 | OK | Ground clear controls. | 44 | 44.49 | 703.67
2737 | TIN-INTERP | Interpolated Ground | 17335.72 | 5 | 659.24 | 0 | 33.44 | 0 | OK | Ground clear controls. | 44 | 41.45 | 692.68
2738 | TIN-INTERP | Interpolated Ground | 17335.75 | 6.5 | 659.41 | 0 | 38.77 | 0 | OK | Ground clear controls. | 44 | 41.45 | 698.18
2739 | TIN-INTERP | Interpolated Ground | 17375.51 | -6.71 | 664.69 | 0 | 30.09 | 0 | OK | Ground clear controls. | 44 | 41.45 | 694.78
2740 | TIN-INTERP | Interpolated Ground | 17375.54 | -4.71 | 664.47 | 0 | 35.74 | 0 | OK | Ground clear controls. | 44 | 41.45 | 700.21
2741 | TIN-INTERP | Interpolated Ground | 17375.6 | -5.21 | 664.55 | 0 | 24.81 | 0 | OK | Ground clear controls. | 44 | 41.45 | 689.36
2742 | TIN-INTERP | Interpolated Ground | 17375.69 | 4.5 | 663.96 | 0 | 36.23 | 0 | OK | Ground clear controls. | 44 | 41.45 | 700.19
2743 | TIN-INTERP | Interpolated Ground | 17375.72 | 5 | 663.9 | 0 | 25.42 | 0 | OK | Ground clear controls. | 44 | 41.45 | 689.32
2744 | TIN-INTERP | Interpolated Ground | 17375.75 | 6.5 | 663.37 | 0 | 31.37 | 0 | OK | Ground clear controls. | 44 | 41.45 | 694.74
2745 | TIN-INTERP | Interpolated Ground | 17415.51 | -6.71 | 666.41 | 0 | 25.89 | 0 | OK | Ground clear controls. | 44 | 41.45 | 692.3
2746 | TIN-INTERP | Interpolated Ground | 17415.54 | -4.71 | 665.79 | 0 | 31.89 | 0 | OK | Ground clear controls. | 44 | 41.45 | 697.68
2747 | TIN-INTERP | Interpolated Ground | 17415.6 | -5.21 | 665.94 | 0 | 21 | 0 | OK | Ground clear controls. | 44 | 41.45 | 686.94
2748 | TIN-INTERP | Interpolated Ground | 17415.69 | 4.5 | 664.3 | 0 | 33.33 | 0 | OK | Ground clear controls. | 44 | 41.45 | 697.63
2749 | TIN-INTERP | Interpolated Ground | 17415.72 | 5 | 664.28 | 0 | 22.6 | 0 | OK | Ground clear controls. | 44 | 41.45 | 686.88
2750 | TIN-INTERP | Interpolated Ground | 17415.75 | 6.5 | 664.04 | 0 | 28.21 | 0 | OK | Ground clear controls. | 44 | 41.45 | 692.25
2751 | TIN-INTERP | Interpolated Ground | 17455.51 | -6.7 | 666.3 | 0 | 24.44 | 0 | OK | Ground clear controls. | 44 | 41.45 | 690.74
2752 | TIN-INTERP | Interpolated Ground | 17455.54 | -4.71 | 665.86 | 0 | 30.21 | 0 | OK | Ground clear controls. | 44 | 41.45 | 696.07
2753 | TIN-INTERP | Interpolated Ground | 17455.6 | -5.21 | 665.97 | 0 | 19.45 | 0 | OK | Ground clear controls. | 44 | 41.45 | 685.42
2754 | TIN-INTERP | Interpolated Ground | 17455.69 | 4.51 | 663.77 | 0 | 32.24 | 0 | OK | Ground clear controls. | 44 | 41.45 | 696.01
2755 | TIN-INTERP | Interpolated Ground | 17455.72 | 5 | 663.74 | 0 | 21.6 | 0 | OK | Ground clear controls. | 44 | 41.45 | 685.34
2756 | TIN-INTERP | Interpolated Ground | 17455.75 | 6.5 | 663.76 | 0 | 26.9 | 0 | OK | Ground clear controls. | 44 | 41.45 | 690.66
2757 | TIN-INTERP | Interpolated Ground | 17495.51 | -6.7 | 667.6 | 0 | 22.47 | 0 | OK | Ground clear controls. | 44 | 41.45 | 690.07
2758 | TIN-INTERP | Interpolated Ground | 17495.54 | -4.71 | 666.89 | 0 | 28.48 | 0 | OK | Ground clear controls. | 44 | 41.45 | 695.37
2759 | TIN-INTERP | Interpolated Ground | 17495.6 | -5.2 | 667.06 | 0 | 17.74 | 0 | OK | Ground clear controls. | 44 | 41.45 | 684.8
2760 | TIN-INTERP | Interpolated Ground | 17495.69 | 4.51 | 665.42 | 0 | 29.89 | 0 | OK | Ground clear controls. | 44 | 41.45 | 695.31
2761 | TIN-INTERP | Interpolated Ground | 17495.72 | 5.01 | 665.42 | 0 | 19.27 | 0 | OK | Ground clear controls. | 44 | 41.45 | 684.69
2762 | TIN-INTERP | Interpolated Ground | 17495.75 | 6.5 | 665.42 | 0 | 24.56 | 0 | OK | Ground clear controls. | 44 | 41.45 | 689.98
2763 | TIN-INTERP | Interpolated Ground | 17535.51 | -6.7 | 668.38 | 0 | 21.95 | 0 | OK | Ground clear controls. | 44 | 41.45 | 690.33
2764 | TIN-INTERP | Interpolated Ground | 17535.54 | -4.7 | 668.03 | 0 | 27.58 | 0 | OK | Ground clear controls. | 44 | 41.45 | 695.61
2765 | TIN-INTERP | Interpolated Ground | 17535.6 | -5.2 | 668.19 | 0 | 16.89 | 0 | OK | Ground clear controls. | 44 | 41.45 | 685.08
2766 | TIN-INTERP | Interpolated Ground | 17535.69 | 4.51 | 666.83 | 0 | 28.7 | 0 | OK | Ground clear controls. | 44 | 41.45 | 695.53
2767 | TIN-INTERP | Interpolated Ground | 17535.72 | 5.01 | 666.81 | 0 | 18.15 | 0 | OK | Ground clear controls. | 44 | 41.45 | 684.96
2768 | TIN-INTERP | Interpolated Ground | 17535.75 | 6.51 | 666.76 | 0 | 23.46 | 0 | OK | Ground clear controls. | 44 | 41.45 | 690.22
2769 | TIN-INTERP | Interpolated Ground | 17575.51 | -6.7 | 671.03 | 0 | 20.46 | 0 | OK | Ground clear controls. | 44 | 41.45 | 691.49
2770 | TIN-INTERP | Interpolated Ground | 17575.54 | -4.7 | 670.69 | 0 | 26.07 | 0 | OK | Ground clear controls. | 44 | 41.45 | 696.76
2771 | TIN-INTERP | Interpolated Ground | 17575.6 | -5.2 | 670.82 | 0 | 15.43 | 0 | OK | Ground clear controls. | 44 | 41.45 | 686.25
2772 | TIN-INTERP | Interpolated Ground | 17575.69 | 4.51 | 668.41 | 0 | 28.28 | 0 | OK | Ground clear controls. | 44 | 41.45 | 696.69
2773 | TIN-INTERP | Interpolated Ground | 17575.72 | 5.01 | 668.35 | 0 | 17.78 | 0 | OK | Ground clear controls. | 44 | 41.45 | 686.13
2774 | TIN-INTERP | Interpolated Ground | 17575.75 | 6.51 | 668.35 | 0 | 23.03 | 0 | OK | Ground clear controls. | 44 | 41.45 | 691.38
2775 | TIN-INTERP | Interpolated Ground | 17615.51 | -6.7 | 674.51 | 0 | 19.05 | 0 | OK | Ground clear controls. | 44 | 41.45 | 693.56
2776 | TIN-INTERP | Interpolated Ground | 17615.54 | -4.7 | 674.17 | 0 | 24.67 | 0 | OK | Ground clear controls. | 44 | 41.45 | 698.84
2777 | TIN-INTERP | Interpolated Ground | 17615.6 | -5.2 | 674.28 | 0 | 14.05 | 0 | OK | Ground clear controls. | 44 | 41.45 | 688.33
2778 | TIN-INTERP | Interpolated Ground | 17615.69 | 4.51 | 671.81 | 0 | 26.95 | 0 | OK | Ground clear controls. | 44 | 41.45 | 698.76
2779 | TIN-INTERP | Interpolated Ground | 17615.72 | 5.01 | 671.68 | 0 | 16.52 | 0 | OK | Ground clear controls. | 44 | 41.45 | 688.2
2780 | TIN-INTERP | Interpolated Ground | 17615.75 | 6.51 | 671.32 | 0 | 22.13 | 0 | OK | Ground clear controls. | 44 | 41.45 | 693.45
2781 | TIN-INTERP | Interpolated Ground | 17655.51 | -6.7 | 676.53 | 0 | 20.01 | 0 | OK | Ground clear controls. | 44 | 41.45 | 696.54
2782 | TIN-INTERP | Interpolated Ground | 17655.54 | -4.7 | 676.24 | 0 | 25.6 | 0 | OK | Ground clear controls. | 44 | 41.45 | 701.84
2783 | TIN-INTERP | Interpolated Ground | 17655.6 | -5.2 | 676.28 | 0 | 15.01 | 0 | OK | Ground clear controls. | 44 | 41.45 | 691.29
2784 | TIN-INTERP | Interpolated Ground | 17655.69 | 4.51 | 674.95 | 0 | 26.82 | 0 | OK | Ground clear controls. | 44 | 41.45 | 701.77
2785 | TIN-INTERP | Interpolated Ground | 17655.72 | 5.01 | 674.86 | 0 | 16.31 | 0 | OK | Ground clear controls. | 44 | 41.45 | 691.17
2786 | TIN-INTERP | Interpolated Ground | 17655.75 | 6.51 | 674.55 | 0 | 21.89 | 0 | OK | Ground clear controls. | 44 | 41.45 | 696.44
2787 | TIN-INTERP | Interpolated Ground | 17695.51 | -6.7 | 678.1 | 0 | 22.34 | 0 | OK | Ground clear controls. | 44 | 41.45 | 700.44
2788 | TIN-INTERP | Interpolated Ground | 17695.54 | -4.7 | 677.74 | 0 | 28.02 | 0 | OK | Ground clear controls. | 44 | 41.45 | 705.76
2789 | TIN-INTERP | Interpolated Ground | 17695.6 | -5.2 | 677.87 | 0 | 17.3 | 0 | OK | Ground clear controls. | 44 | 41.45 | 695.17
2790 | TIN-INTERP | Interpolated Ground | 17695.69 | 4.51 | 676.45 | 0 | 29.26 | 0 | OK | Ground clear controls. | 44 | 41.45 | 705.71
2791 | TIN-INTERP | Interpolated Ground | 17695.72 | 5.01 | 676.27 | 0 | 18.79 | 0 | OK | Ground clear controls. | 44 | 41.45 | 695.06
2792 | TIN-INTERP | Interpolated Ground | 17695.75 | 6.51 | 676.19 | 0 | 24.17 | 0 | OK | Ground clear controls. | 44 | 41.45 | 700.36
2793 | TIN-INTERP | Interpolated Ground | 17735.51 | -6.7 | 679.08 | 0 | 26.18 | 0 | OK | Ground clear controls. | 44 | 41.45 | 705.26
2794 | TIN-INTERP | Interpolated Ground | 17735.54 | -4.7 | 678.63 | 0 | 31.99 | 0 | OK | Ground clear controls. | 44 | 41.45 | 710.62
2795 | TIN-INTERP | Interpolated Ground | 17735.6 | -5.2 | 678.76 | 0 | 21.18 | 0 | OK | Ground clear controls. | 44 | 41.45 | 699.94
2796 | TIN-INTERP | Interpolated Ground | 17735.69 | 4.52 | 677.2 | 0 | 33.38 | 0 | OK | Ground clear controls. | 44 | 41.45 | 710.58
2797 | TIN-INTERP | Interpolated Ground | 17735.72 | 5.01 | 677.38 | 0 | 22.48 | 0 | OK | Ground clear controls. | 44 | 41.45 | 699.86
2798 | TIN-INTERP | Interpolated Ground | 17735.75 | 6.51 | 678.29 | 0 | 26.9 | 0 | OK | Ground clear controls. | 44 | 41.45 | 705.19
2799 | TIN-INTERP | Interpolated Ground | 17775.51 | -6.7 | 681.17 | 0 | 29.82 | 0 | OK | Ground clear controls. | 44 | 41.45 | 710.99
2800 | TIN-INTERP | Interpolated Ground | 17775.54 | -4.7 | 681.21 | 0 | 35.2 | 0 | OK | Ground clear controls. | 44 | 41.45 | 716.41
2801 | TIN-INTERP | Interpolated Ground | 17775.6 | -5.2 | 681.21 | 0 | 24.41 | 0 | OK | Ground clear controls. | 44 | 41.45 | 705.62
2802 | TIN-INTERP | Interpolated Ground | 17775.69 | 4.52 | 681.07 | 0 | 35.31 | 0 | OK | Ground clear controls. | 44 | 41.45 | 716.38
2803 | TIN-INTERP | Interpolated Ground | 17775.72 | 5.01 | 681.09 | 0 | 24.47 | 0 | OK | Ground clear controls. | 44 | 41.45 | 705.56
2804 | TIN-INTERP | Interpolated Ground | 17775.75 | 6.51 | 681.05 | 0 | 29.91 | 0 | OK | Ground clear controls. | 44 | 41.45 | 710.96
2805 | TIN-INTERP | Interpolated Ground | 17815.51 | -6.7 | 682.03 | 0 | 35.62 | 0 | OK | Ground clear controls. | 44 | 41.45 | 717.65
2806 | TIN-INTERP | Interpolated Ground | 17815.54 | -4.7 | 682.08 | 0 | 41.06 | 0 | OK | Ground clear controls. | 44 | 41.45 | 723.14
2807 | TIN-INTERP | Interpolated Ground | 17815.6 | -5.2 | 682.07 | 0 | 30.14 | 0 | OK | Ground clear controls. | 44 | 41.45 | 712.21
2808 | TIN-INTERP | Interpolated Ground | 17815.69 | 4.52 | 681.67 | 0 | 41.45 | 0 | OK | Ground clear controls. | 44 | 41.45 | 723.12
2809 | TIN-INTERP | Interpolated Ground | 17815.72 | 5.02 | 681.62 | 0 | 30.56 | 0 | OK | Ground clear controls. | 44 | 36.18 | 712.18
2810 | TIN-INTERP | Interpolated Ground | 17815.75 | 6.52 | 681.46 | 0 | 36.18 | 0 | OK | Ground clear controls. | 44 | 36.18 | 717.64
2811 | TIN-INTERP | Interpolated Ground | 17818.81 | -5.2 | 682.32 | 0 | 30.45 | 0 | OK | Ground clear controls. | 45 | 42.31 | 712.77
2812 | TIN-INTERP | Interpolated Ground | 17818.98 | -6.69 | 682.17 | 0 | 36.09 | 0 | OK | Ground clear controls. | 45 | 42.31 | 718.26
2813 | TIN-INTERP | Interpolated Ground | 17819.04 | -4.7 | 682.41 | 0 | 41.35 | 0 | OK | Ground clear controls. | 45 | 42.31 | 723.76
2814 | TIN-INTERP | Interpolated Ground | 17819.06 | 5.02 | 681.36 | 0 | 31.4 | 0 | OK | Ground clear controls. | 45 | 42.31 | 712.76
2815 | TIN-INTERP | Interpolated Ground | 17819.22 | 4.52 | 681.45 | 0 | 42.31 | 0 | OK | Ground clear controls. | 45 | 42.31 | 723.76
2816 | TIN-INTERP | Interpolated Ground | 17819.22 | 6.52 | 681.08 | 0 | 37.18 | 0 | OK | Ground clear controls. | 45 | 39.74 | 718.26
2817 | TIN-INTERP | Interpolated Ground | 17858.81 | -5.22 | 683.55 | 0 | 25.42 | 0 | OK | Ground clear controls. | 45 | 39.74 | 708.97
2818 | TIN-INTERP | Interpolated Ground | 17858.98 | -6.72 | 684.13 | 0 | 30.36 | 0 | OK | Ground clear controls. | 45 | 39.74 | 714.49
2819 | TIN-INTERP | Interpolated Ground | 17859.04 | -4.73 | 683.35 | 0 | 36.63 | 0 | OK | Ground clear controls. | 45 | 39.74 | 719.98
2820 | TIN-INTERP | Interpolated Ground | 17859.06 | 5.04 | 680.13 | 0 | 28.85 | 0 | OK | Ground clear controls. | 45 | 39.74 | 708.98
2821 | TIN-INTERP | Interpolated Ground | 17859.22 | 4.56 | 680.23 | 0 | 39.74 | 0 | OK | Ground clear controls. | 45 | 39.74 | 719.97
2822 | TIN-INTERP | Interpolated Ground | 17859.22 | 6.54 | 679.77 | 0 | 34.7 | 0 | OK | Ground clear controls. | 45 | 34.7 | 714.47
2823 | TIN-INTERP | Interpolated Ground | 17898.81 | -5.25 | 684.26 | 0 | 21.83 | 0 | OK | Ground clear controls. | 45 | 34.3 | 706.09
2824 | TIN-INTERP | Interpolated Ground | 17898.98 | -6.75 | 684.75 | 0 | 26.9 | 0 | OK | Ground clear controls. | 45 | 34.3 | 711.65
2825 | TIN-INTERP | Interpolated Ground | 17899.04 | -4.77 | 684.16 | 0 | 32.96 | 0 | OK | Ground clear controls. | 45 | 34.3 | 717.12
2826 | TIN-INTERP | Interpolated Ground | 17899.06 | 5.07 | 682.72 | 0 | 23.38 | 0 | OK | Ground clear controls. | 45 | 34.3 | 706.1
2827 | TIN-INTERP | Interpolated Ground | 17899.22 | 4.59 | 682.8 | 0 | 34.3 | 0 | OK | Ground clear controls. | 45 | 34.3 | 717.1
2828 | TIN-INTERP | Interpolated Ground | 17899.22 | 6.57 | 682.22 | 0 | 29.38 | 0 | OK | Ground clear controls. | 45 | 31.35 | 711.6
2829 | TIN-INTERP | Interpolated Ground | 17938.81 | -5.28 | 687.32 | 0 | 16.82 | 0 | OK | Ground clear controls. | 45 | 31.35 | 704.14
2830 | TIN-INTERP | Interpolated Ground | 17938.98 | -6.77 | 687.54 | 0 | 22.18 | 0 | OK | Ground clear controls. | 45 | 31.35 | 709.72
2831 | TIN-INTERP | Interpolated Ground | 17939.04 | -4.81 | 687.22 | 0 | 27.97 | 0 | OK | Ground clear controls. | 45 | 31.35 | 715.19
2832 | TIN-INTERP | Interpolated Ground | 17939.06 | 5.1 | 684.96 | 0 | 19.19 | 0 | OK | Ground clear controls. | 45 | 31.35 | 704.15
2833 | TIN-INTERP | Interpolated Ground | 17939.22 | 4.63 | 685.09 | 0 | 30.08 | 0 | OK | Ground clear controls. | 45 | 31.35 | 715.17
2834 | TIN-INTERP | Interpolated Ground | 17939.22 | 6.6 | 684.72 | 0 | 24.95 | 0 | OK | Ground clear controls. | 45 | 31.35 | 709.67
2835 | TIN-INTERP | Interpolated Ground | 17978.81 | -5.3 | 689.92 | 0 | 13.18 | 0 | OK | Ground clear controls. | 45 | 31.35 | 703.1
2836 | TIN-INTERP | Interpolated Ground | 17978.98 | -6.8 | 689.79 | 0 | 18.9 | 0 | OK | Ground clear controls. | 45 | 31.35 | 708.69
2837 | TIN-INTERP | Interpolated Ground | 17979.04 | -4.84 | 689.94 | 0 | 24.25 | 0 | OK | Ground clear controls. | 45 | 31.35 | 714.19
2838 | TIN-INTERP | Interpolated Ground | 17979.06 | 5.13 | 689.81 | 0 | 13.32 | 0 | OK | Ground clear controls. | 45 | 31.35 | 703.13
2839 | TIN-INTERP | Interpolated Ground | 17979.22 | 4.67 | 689.82 | 0 | 24.35 | 0 | OK | Ground clear controls. | 45 | 31.35 | 714.17
2840 | TIN-INTERP | Interpolated Ground | 17979.22 | 6.63 | 689.67 | 0 | 18.96 | 0 | OK | Ground clear controls. | 45 | 31.35 | 708.63
2841 | TIN-INTERP | Interpolated Ground | 18018.81 | -5.33 | 691.45 | 0 | 11.55 | 0 | OK | Ground clear controls. | 45 | 31.35 | 703
2842 | TIN-INTERP | Interpolated Ground | 18018.98 | -6.83 | 691.38 | 0 | 17.21 | 0 | OK | Ground clear controls. | 45 | 31.35 | 708.59
2843 | TIN-INTERP | Interpolated Ground | 18019.04 | -4.88 | 691.51 | 0 | 22.6 | 0 | OK | Ground clear controls. | 45 | 31.35 | 714.11
2844 | TIN-INTERP | Interpolated Ground | 18019.06 | 5.16 | 691.8 | 0 | 11.22 | 0 | OK | Ground clear controls. | 45 | 31.35 | 703.02
2845 | TIN-INTERP | Interpolated Ground | 18019.22 | 4.71 | 691.81 | 0 | 22.29 | 0 | OK | Ground clear controls. | 45 | 31.35 | 714.1
2846 | TIN-INTERP | Interpolated Ground | 18019.22 | 6.66 | 691.76 | 0 | 16.78 | 0 | OK | Ground clear controls. | 45 | 31.35 | 708.54
2847 | TIN-INTERP | Interpolated Ground | 18058.81 | -5.36 | 690.76 | 0 | 13.05 | 0 | OK | Ground clear controls. | 45 | 31.35 | 703.81
2848 | TIN-INTERP | Interpolated Ground | 18058.98 | -6.85 | 690.56 | 0 | 18.84 | 0 | OK | Ground clear controls. | 45 | 31.35 | 709.4
2849 | TIN-INTERP | Interpolated Ground | 18059.04 | -4.91 | 690.76 | 0 | 24.2 | 0 | OK | Ground clear controls. | 45 | 31.35 | 714.96
2850 | TIN-INTERP | Interpolated Ground | 18059.06 | 5.19 | 692.04 | 0 | 11.79 | 0 | OK | Ground clear controls. | 45 | 31.35 | 703.83
2851 | TIN-INTERP | Interpolated Ground | 18059.22 | 4.75 | 692 | 0 | 22.94 | 0 | OK | Ground clear controls. | 45 | 31.35 | 714.94
2852 | TIN-INTERP | Interpolated Ground | 18059.22 | 6.69 | 692.16 | 0 | 17.19 | 0 | OK | Ground clear controls. | 45 | 31.35 | 709.35
2853 | TIN-INTERP | Interpolated Ground | 18098.81 | -5.38 | 689.36 | 0 | 16.19 | 0 | OK | Ground clear controls. | 45 | 31.35 | 705.55
2854 | TIN-INTERP | Interpolated Ground | 18098.98 | -6.88 | 689.24 | 0 | 21.89 | 0 | OK | Ground clear controls. | 45 | 31.35 | 711.13
2855 | TIN-INTERP | Interpolated Ground | 18099.04 | -4.95 | 689.37 | 0 | 27.36 | 0 | OK | Ground clear controls. | 45 | 31.35 | 716.73
2856 | TIN-INTERP | Interpolated Ground | 18099.06 | 5.22 | 690.22 | 0 | 15.35 | 0 | OK | Ground clear controls. | 45 | 31.35 | 705.57
2857 | TIN-INTERP | Interpolated Ground | 18099.22 | 4.79 | 690.18 | 0 | 26.54 | 0 | OK | Ground clear controls. | 45 | 31.35 | 716.72
2858 | TIN-INTERP | Interpolated Ground | 18099.22 | 6.72 | 690.3 | 0 | 20.78 | 0 | OK | Ground clear controls. | 45 | 31.35 | 711.08
2859 | TIN-INTERP | Interpolated Ground | 18138.81 | -5.41 | 688.99 | 0 | 19.22 | 0 | OK | Ground clear controls. | 45 | 31.35 | 708.21
2860 | TIN-INTERP | Interpolated Ground | 18138.98 | -6.91 | 688.81 | 0 | 24.96 | 0 | OK | Ground clear controls. | 45 | 31.35 | 713.77
2861 | TIN-INTERP | Interpolated Ground | 18139.04 | -4.98 | 689.09 | 0 | 30.34 | 0 | OK | Ground clear controls. | 45 | 31.35 | 719.43
2862 | TIN-INTERP | Interpolated Ground | 18139.06 | 5.25 | 689.5 | 0 | 18.73 | 0 | OK | Ground clear controls. | 45 | 31.35 | 708.23
2863 | TIN-INTERP | Interpolated Ground | 18139.22 | 4.83 | 689.53 | 0 | 29.89 | 0 | OK | Ground clear controls. | 45 | 31.35 | 719.42
2864 | TIN-INTERP | Interpolated Ground | 18139.22 | 6.75 | 689.39 | 0 | 24.35 | 0 | OK | Ground clear controls. | 45 | 31.35 | 713.74
2865 | TIN-INTERP | Interpolated Ground | 18178.81 | -5.44 | 691.69 | 0 | 20.1 | 0 | OK | Ground clear controls. | 45 | 31.35 | 711.79
2866 | TIN-INTERP | Interpolated Ground | 18178.98 | -6.93 | 691.54 | 0 | 25.79 | 0 | OK | Ground clear controls. | 45 | 31.35 | 717.33
2867 | TIN-INTERP | Interpolated Ground | 18179.04 | -5.02 | 691.71 | 0 | 31.35 | 0 | OK | Ground clear controls. | 45 | 31.35 | 723.06
2868 | TIN-INTERP | Interpolated Ground | 18179.06 | 5.28 | 692.27 | 0 | 19.53 | 0 | OK | Ground clear controls. | 45 | 30.79 | 711.8
2869 | TIN-INTERP | Interpolated Ground | 18179.22 | 4.86 | 692.26 | 0 | 30.79 | 0 | OK | Ground clear controls. | 45 | 30.79 | 723.05
2870 | TIN-INTERP | Interpolated Ground | 18179.22 | 6.78 | 692.41 | 0 | 24.9 | 0 | OK | Ground clear controls. | 45 | 24.9 | 717.31
2871 | TIN-INTERP | Interpolated Ground | 18216.32 | -5.46 | 692.94 | 0 | 23.04 | 0 | OK | Ground clear controls. | 46 | 39.5 | 715.98
2872 | TIN-INTERP | Interpolated Ground | 18216.37 | -6.96 | 692.57 | 0 | 28.91 | 0 | OK | Ground clear controls. | 46 | 39.5 | 721.48
2873 | TIN-INTERP | Interpolated Ground | 18216.4 | -5.05 | 693.05 | 0 | 34.23 | 0 | OK | Ground clear controls. | 46 | 39.5 | 727.28
2874 | TIN-INTERP | Interpolated Ground | 18216.44 | 5.31 | 693.81 | 0 | 22.17 | 0 | OK | Ground clear controls. | 46 | 39.5 | 715.98
2875 | TIN-INTERP | Interpolated Ground | 18216.5 | 6.81 | 693.91 | 0 | 27.57 | 0 | OK | Ground clear controls. | 46 | 39.5 | 721.48
2876 | TIN-INTERP | Interpolated Ground | 18216.51 | 4.9 | 693.76 | 0 | 33.52 | 0 | OK | Ground clear controls. | 46 | 39.5 | 727.28
2877 | TIN-INTERP | Interpolated Ground | 18256.31 | -5.43 | 695.38 | 0 | 18.35 | 0 | OK | Ground clear controls. | 46 | 39.5 | 713.73
2878 | TIN-INTERP | Interpolated Ground | 18256.37 | -6.93 | 695.36 | 0 | 23.94 | 0 | OK | Ground clear controls. | 46 | 39.5 | 719.3
2879 | TIN-INTERP | Interpolated Ground | 18256.4 | -5.02 | 695.39 | 0 | 29.63 | 0 | OK | Ground clear controls. | 46 | 39.5 | 725.02
2880 | TIN-INTERP | Interpolated Ground | 18256.44 | 5.28 | 695.8 | 0 | 17.96 | 0 | OK | Ground clear controls. | 46 | 39.5 | 713.76
2881 | TIN-INTERP | Interpolated Ground | 18256.5 | 6.78 | 695.93 | 0 | 23.35 | 0 | OK | Ground clear controls. | 46 | 39.5 | 719.28
2882 | TIN-INTERP | Interpolated Ground | 18256.51 | 4.87 | 695.78 | 0 | 29.24 | 0 | OK | Ground clear controls. | 46 | 39.5 | 725.02
2883 | TIN-INTERP | Interpolated Ground | 18296.31 | -5.41 | 694.23 | 0 | 18.19 | 0 | OK | Ground clear controls. | 46 | 39.5 | 712.42
2884 | TIN-INTERP | Interpolated Ground | 18296.37 | -6.91 | 694.09 | 0 | 23.95 | 0 | OK | Ground clear controls. | 46 | 39.5 | 718.04
2885 | TIN-INTERP | Interpolated Ground | 18296.4 | -4.99 | 694.26 | 0 | 29.43 | 0 | OK | Ground clear controls. | 46 | 39.5 | 723.69
2886 | TIN-INTERP | Interpolated Ground | 18296.44 | 5.26 | 695.12 | 0 | 17.34 | 0 | OK | Ground clear controls. | 46 | 39.5 | 712.46
2887 | TIN-INTERP | Interpolated Ground | 18296.5 | 6.76 | 695.15 | 0 | 22.85 | 0 | OK | Ground clear controls. | 46 | 39.5 | 718
2888 | TIN-INTERP | Interpolated Ground | 18296.51 | 4.84 | 695.11 | 0 | 28.59 | 0 | OK | Ground clear controls. | 46 | 39.5 | 723.7
2889 | TIN-INTERP | Interpolated Ground | 18336.31 | -5.38 | 693.29 | 0 | 18.75 | 0 | OK | Ground clear controls. | 46 | 39.5 | 712.04
2890 | TIN-INTERP | Interpolated Ground | 18336.37 | -6.88 | 692.96 | 0 | 24.74 | 0 | OK | Ground clear controls. | 46 | 39.5 | 717.7
2891 | TIN-INTERP | Interpolated Ground | 18336.4 | -4.95 | 693.37 | 0 | 29.92 | 0 | OK | Ground clear controls. | 46 | 39.5 | 723.29
2892 | TIN-INTERP | Interpolated Ground | 18336.44 | 5.24 | 694.29 | 0 | 17.8 | 0 | OK | Ground clear controls. | 46 | 39.5 | 712.09
2893 | TIN-INTERP | Interpolated Ground | 18336.5 | 6.74 | 694.29 | 0 | 23.35 | 0 | OK | Ground clear controls. | 46 | 39.5 | 717.64
2894 | TIN-INTERP | Interpolated Ground | 18336.51 | 4.81 | 694.27 | 0 | 29.03 | 0 | OK | Ground clear controls. | 46 | 39.5 | 723.3
2895 | TIN-INTERP | Interpolated Ground | 18376.31 | -5.36 | 689.57 | 0 | 23.02 | 0 | OK | Ground clear controls. | 46 | 39.5 | 712.59
2896 | TIN-INTERP | Interpolated Ground | 18376.37 | -6.86 | 690.17 | 0 | 28.11 | 0 | OK | Ground clear controls. | 46 | 39.5 | 718.28
2897 | TIN-INTERP | Interpolated Ground | 18376.4 | -4.92 | 689.54 | 0 | 34.28 | 0 | OK | Ground clear controls. | 46 | 39.5 | 723.82
2898 | TIN-INTERP | Interpolated Ground | 18376.44 | 5.22 | 691.04 | 0 | 21.61 | 0 | OK | Ground clear controls. | 46 | 39.5 | 712.65
2899 | TIN-INTERP | Interpolated Ground | 18376.5 | 6.72 | 691.25 | 0 | 26.95 | 0 | OK | Ground clear controls. | 46 | 39.5 | 718.2
2900 | TIN-INTERP | Interpolated Ground | 18376.51 | 4.78 | 690.95 | 0 | 32.88 | 0 | OK | Ground clear controls. | 46 | 39.5 | 723.83
2901 | TIN-INTERP | Interpolated Ground | 18416.31 | -5.33 | 696 | 0 | 18.06 | 0 | OK | Ground clear controls. | 46 | 39.5 | 714.06
2902 | TIN-INTERP | Interpolated Ground | 18416.37 | -6.83 | 695.92 | 0 | 23.86 | 0 | OK | Ground clear controls. | 46 | 39.5 | 719.78
2903 | TIN-INTERP | Interpolated Ground | 18416.4 | -4.89 | 696.06 | 0 | 29.22 | 0 | OK | Ground clear controls. | 46 | 39.5 | 725.28
2904 | TIN-INTERP | Interpolated Ground | 18416.44 | 5.19 | 692.94 | 0 | 21.21 | 0 | OK | Ground clear controls. | 46 | 39.5 | 714.15
2905 | TIN-INTERP | Interpolated Ground | 18416.5 | 6.69 | 693.23 | 0 | 26.48 | 0 | OK | Ground clear controls. | 46 | 39.5 | 719.71
2906 | TIN-INTERP | Interpolated Ground | 18416.51 | 4.75 | 692.95 | 0 | 32.34 | 0 | OK | Ground clear controls. | 46 | 39.5 | 725.29
2907 | TIN-INTERP | Interpolated Ground | 18456.31 | -5.31 | 697.47 | 0 | 19.01 | 0 | OK | Ground clear controls. | 46 | 39.5 | 716.48
2908 | TIN-INTERP | Interpolated Ground | 18456.37 | -6.81 | 697.37 | 0 | 24.83 | 0 | OK | Ground clear controls. | 46 | 39.5 | 722.2
2909 | TIN-INTERP | Interpolated Ground | 18456.4 | -4.85 | 697.58 | 0 | 30.1 | 0 | OK | Ground clear controls. | 46 | 39.5 | 727.68
2910 | TIN-INTERP | Interpolated Ground | 18456.44 | 5.17 | 698.82 | 0 | 17.74 | 0 | OK | Ground clear controls. | 46 | 39.5 | 716.56
2911 | TIN-INTERP | Interpolated Ground | 18456.5 | 6.67 | 699.02 | 0 | 23.1 | 0 | OK | Ground clear controls. | 46 | 39.5 | 722.12
2912 | TIN-INTERP | Interpolated Ground | 18456.51 | 4.72 | 698.78 | 0 | 28.9 | 0 | OK | Ground clear controls. | 46 | 39.5 | 727.68
2913 | TIN-INTERP | Interpolated Ground | 18496.31 | -5.28 | 704.54 | 0 | 15.29 | 0 | OK | Ground clear controls. | 46 | 39.5 | 719.83
2914 | TIN-INTERP | Interpolated Ground | 18496.37 | -6.78 | 704.42 | 0 | 21.12 | 0 | OK | Ground clear controls. | 46 | 39.5 | 725.54
2915 | TIN-INTERP | Interpolated Ground | 18496.4 | -4.82 | 704.55 | 0 | 26.45 | 0 | OK | Ground clear controls. | 46 | 39.5 | 731
2916 | TIN-INTERP | Interpolated Ground | 18496.44 | 5.15 | 703.97 | 0 | 15.94 | 0 | OK | Ground clear controls. | 46 | 39.5 | 719.91
2917 | TIN-INTERP | Interpolated Ground | 18496.5 | 6.65 | 704.16 | 0 | 21.31 | 0 | OK | Ground clear controls. | 46 | 39.5 | 725.47
2918 | TIN-INTERP | Interpolated Ground | 18496.51 | 4.69 | 703.86 | 0 | 27.15 | 0 | OK | Ground clear controls. | 46 | 39.5 | 731.01
2919 | TIN-INTERP | Interpolated Ground | 18536.31 | -5.26 | 707.92 | 0 | 16.2 | 0 | OK | Ground clear controls. | 46 | 39.5 | 724.12
2920 | TIN-INTERP | Interpolated Ground | 18536.37 | -6.76 | 707.71 | 0 | 22.1 | 0 | OK | Ground clear controls. | 46 | 39.5 | 729.81
2921 | TIN-INTERP | Interpolated Ground | 18536.4 | -4.79 | 707.96 | 0 | 27.3 | 0 | OK | Ground clear controls. | 46 | 39.5 | 735.26
2922 | TIN-INTERP | Interpolated Ground | 18536.44 | 5.12 | 707.64 | 0 | 16.55 | 0 | OK | Ground clear controls. | 46 | 39.5 | 724.19
2923 | TIN-INTERP | Interpolated Ground | 18536.5 | 6.62 | 707.56 | 0 | 22.19 | 0 | OK | Ground clear controls. | 46 | 39.5 | 729.75
2924 | TIN-INTERP | Interpolated Ground | 18536.51 | 4.65 | 707.68 | 0 | 27.59 | 0 | OK | Ground clear controls. | 46 | 39.5 | 735.27
2925 | TIN-INTERP | Interpolated Ground | 18576.31 | -5.23 | 710.52 | 0 | 18.83 | 0 | OK | Ground clear controls. | 46 | 39.5 | 729.35
2926 | TIN-INTERP | Interpolated Ground | 18576.37 | -6.73 | 710.51 | 0 | 24.5 | 0 | OK | Ground clear controls. | 46 | 39.5 | 735.01
2927 | TIN-INTERP | Interpolated Ground | 18576.4 | -4.75 | 710.51 | 0 | 29.94 | 0 | OK | Ground clear controls. | 46 | 39.5 | 740.45
2928 | TIN-INTERP | Interpolated Ground | 18576.44 | 5.1 | 710.3 | 0 | 19.12 | 0 | OK | Ground clear controls. | 46 | 39.5 | 729.42
2929 | TIN-INTERP | Interpolated Ground | 18576.5 | 6.6 | 710.27 | 0 | 24.68 | 0 | OK | Ground clear controls. | 46 | 39.5 | 734.95
2930 | TIN-INTERP | Interpolated Ground | 18576.51 | 4.62 | 710.29 | 0 | 30.18 | 0 | OK | Ground clear controls. | 46 | 39.5 | 740.47
2931 | TIN-INTERP | Interpolated Ground | 18616.31 | -5.21 | 710.94 | 0 | 24.57 | 0 | OK | Ground clear controls. | 46 | 39.5 | 735.51
2932 | TIN-INTERP | Interpolated Ground | 18616.37 | -6.71 | 710.8 | 0 | 30.33 | 0 | OK | Ground clear controls. | 46 | 39.5 | 741.13
2933 | TIN-INTERP | Interpolated Ground | 18616.4 | -4.72 | 711.01 | 0 | 35.58 | 0 | OK | Ground clear controls. | 46 | 39.5 | 746.59
2934 | TIN-INTERP | Interpolated Ground | 18616.44 | 5.08 | 711.62 | 0 | 23.95 | 0 | OK | Ground clear controls. | 46 | 39.5 | 735.57
2935 | TIN-INTERP | Interpolated Ground | 18616.5 | 6.58 | 711.63 | 0 | 29.46 | 0 | OK | Ground clear controls. | 46 | 39.5 | 741.09
2936 | TIN-INTERP | Interpolated Ground | 18616.51 | 4.59 | 711.66 | 0 | 34.95 | 0 | OK | Ground clear controls. | 46 | 39.5 | 746.61
2937 | TIN-INTERP | Interpolated Ground | 18656.31 | -5.18 | 714.1 | 0 | 28.53 | 0 | OK | Ground clear controls. | 46 | 39.5 | 742.63
2938 | TIN-INTERP | Interpolated Ground | 18656.37 | -6.68 | 713.93 | 0 | 34.25 | 0 | OK | Ground clear controls. | 46 | 39.5 | 748.18
2939 | TIN-INTERP | Interpolated Ground | 18656.4 | -4.69 | 714.16 | 0 | 39.5 | 0 | OK | Ground clear controls. | 46 | 39.5 | 753.66
2940 | TIN-INTERP | Interpolated Ground | 18656.44 | 5.06 | 714.62 | 0 | 28.05 | 0 | OK | Ground clear controls. | 46 | 39.07 | 742.67
2941 | TIN-INTERP | Interpolated Ground | 18656.5 | 6.56 | 714.63 | 0 | 33.54 | 0 | OK | Ground clear controls. | 46 | 39.07 | 748.17
2942 | TIN-INTERP | Interpolated Ground | 18656.51 | 4.56 | 714.61 | 0 | 39.07 | 0 | OK | Ground clear controls. | 46 | 39.07 | 753.68
2943 | TIN-INTERP | Interpolated Ground | 18679.35 | -5.17 | 714.48 | 0 | 32.69 | 0 | OK | Ground clear controls. | 47 | 43.5 | 747.17
2944 | TIN-INTERP | Interpolated Ground | 18679.35 | 5.04 | 715.41 | 0 | 31.75 | 0 | OK | Ground clear controls. | 47 | 43.5 | 747.16
2945 | TIN-INTERP | Interpolated Ground | 18679.36 | -6.67 | 713.92 | 0 | 38.74 | 0 | OK | Ground clear controls. | 47 | 43.5 | 752.66
2946 | TIN-INTERP | Interpolated Ground | 18679.38 | 4.55 | 715.34 | 0 | 42.82 | 0 | OK | Ground clear controls. | 47 | 43.5 | 758.16
2947 | TIN-INTERP | Interpolated Ground | 18679.38 | -4.67 | 714.66 | 0 | 43.5 | 0 | OK | Ground clear controls. | 47 | 43.5 | 758.16
2948 | TIN-INTERP | Interpolated Ground | 18679.46 | 6.54 | 715.94 | 0 | 36.72 | 0 | OK | Ground clear controls. | 47 | 43.17 | 752.66
2949 | TIN-INTERP | Interpolated Ground | 18719.35 | -5.17 | 711.1 | 0 | 32.25 | 0 | OK | Ground clear controls. | 47 | 43.17 | 743.35
2950 | TIN-INTERP | Interpolated Ground | 18719.35 | 5.04 | 713.89 | 0 | 29.47 | 0 | OK | Ground clear controls. | 47 | 43.17 | 743.36
2951 | TIN-INTERP | Interpolated Ground | 18719.36 | -6.67 | 711.02 | 0 | 37.91 | 0 | OK | Ground clear controls. | 47 | 43.17 | 748.93
2952 | TIN-INTERP | Interpolated Ground | 18719.38 | 4.55 | 713.8 | 0 | 40.58 | 0 | OK | Ground clear controls. | 47 | 43.17 | 754.38
2953 | TIN-INTERP | Interpolated Ground | 18719.38 | -4.67 | 711.21 | 0 | 43.17 | 0 | OK | Ground clear controls. | 47 | 43.17 | 754.38
2954 | TIN-INTERP | Interpolated Ground | 18719.46 | 6.54 | 714.23 | 0 | 34.73 | 0 | OK | Ground clear controls. | 47 | 42.3 | 748.96
2955 | TIN-INTERP | Interpolated Ground | 18759.35 | -5.16 | 718.03 | 0 | 22.44 | 0 | OK | Ground clear controls. | 47 | 42.3 | 740.47
2956 | TIN-INTERP | Interpolated Ground | 18759.35 | 5.05 | 716.61 | 0 | 23.91 | 0 | OK | Ground clear controls. | 47 | 42.3 | 740.52
2957 | TIN-INTERP | Interpolated Ground | 18759.36 | -6.66 | 718.28 | 0 | 27.84 | 0 | OK | Ground clear controls. | 47 | 42.3 | 746.12
2958 | TIN-INTERP | Interpolated Ground | 18759.38 | 4.55 | 716.64 | 0 | 34.89 | 0 | OK | Ground clear controls. | 47 | 42.3 | 751.53
2959 | TIN-INTERP | Interpolated Ground | 18759.38 | -4.67 | 717.94 | 0 | 33.59 | 0 | OK | Ground clear controls. | 47 | 42.3 | 751.53
2960 | TIN-INTERP | Interpolated Ground | 18759.46 | 6.55 | 716.51 | 0 | 29.67 | 0 | OK | Ground clear controls. | 47 | 42.3 | 746.18
2961 | TIN-INTERP | Interpolated Ground | 18799.35 | -5.16 | 721.85 | 0 | 16.68 | 0 | OK | Ground clear controls. | 47 | 42.3 | 738.53
2962 | TIN-INTERP | Interpolated Ground | 18799.35 | 5.05 | 722.13 | 0 | 16.46 | 0 | OK | Ground clear controls. | 47 | 42.3 | 738.59
2963 | TIN-INTERP | Interpolated Ground | 18799.36 | -6.66 | 721.75 | 0 | 22.49 | 0 | OK | Ground clear controls. | 47 | 42.3 | 744.24
2964 | TIN-INTERP | Interpolated Ground | 18799.38 | 4.55 | 722.12 | 0 | 27.5 | 0 | OK | Ground clear controls. | 47 | 42.3 | 749.62
2965 | TIN-INTERP | Interpolated Ground | 18799.38 | -4.66 | 721.88 | 0 | 27.74 | 0 | OK | Ground clear controls. | 47 | 42.3 | 749.62
2966 | TIN-INTERP | Interpolated Ground | 18799.46 | 6.55 | 722.24 | 0 | 22.08 | 0 | OK | Ground clear controls. | 47 | 42.3 | 744.32
2967 | TIN-INTERP | Interpolated Ground | 18839.35 | -5.16 | 723 | 0 | 14.53 | 0 | OK | Ground clear controls. | 47 | 42.3 | 737.53
2968 | TIN-INTERP | Interpolated Ground | 18839.35 | 5.05 | 722.42 | 0 | 15.18 | 0 | OK | Ground clear controls. | 47 | 42.3 | 737.6
2969 | TIN-INTERP | Interpolated Ground | 18839.36 | -6.66 | 723.22 | 0 | 20.06 | 0 | OK | Ground clear controls. | 47 | 42.3 | 743.28
2970 | TIN-INTERP | Interpolated Ground | 18839.38 | 4.55 | 722.44 | 0 | 26.19 | 0 | OK | Ground clear controls. | 47 | 42.3 | 748.63
2971 | TIN-INTERP | Interpolated Ground | 18839.38 | -4.66 | 722.92 | 0 | 25.72 | 0 | OK | Ground clear controls. | 47 | 42.3 | 748.64
2972 | TIN-INTERP | Interpolated Ground | 18839.46 | 6.55 | 722.36 | 0 | 21.01 | 0 | OK | Ground clear controls. | 47 | 42.3 | 743.37
2973 | TIN-INTERP | Interpolated Ground | 18879.35 | -5.16 | 725.22 | 0 | 12.26 | 0 | OK | Ground clear controls. | 47 | 42.3 | 737.48
2974 | TIN-INTERP | Interpolated Ground | 18879.35 | 5.05 | 725.59 | 0 | 11.97 | 0 | OK | Ground clear controls. | 47 | 42.3 | 737.56
2975 | TIN-INTERP | Interpolated Ground | 18879.36 | -6.66 | 725.31 | 0 | 17.95 | 0 | OK | Ground clear controls. | 47 | 42.3 | 743.26
2976 | TIN-INTERP | Interpolated Ground | 18879.38 | 4.55 | 725.5 | 0 | 23.09 | 0 | OK | Ground clear controls. | 47 | 42.3 | 748.59
2977 | TIN-INTERP | Interpolated Ground | 18879.38 | -4.66 | 725.18 | 0 | 23.42 | 0 | OK | Ground clear controls. | 47 | 42.3 | 748.6
2978 | TIN-INTERP | Interpolated Ground | 18879.46 | 6.55 | 725.82 | 0 | 17.53 | 0 | OK | Ground clear controls. | 47 | 42.3 | 743.35
2979 | TIN-INTERP | Interpolated Ground | 18919.35 | -5.16 | 726.31 | 0 | 12.06 | 0 | OK | Ground clear controls. | 47 | 42.3 | 738.37
2980 | TIN-INTERP | Interpolated Ground | 18919.35 | 5.05 | 726.79 | 0 | 11.66 | 0 | OK | Ground clear controls. | 47 | 42.3 | 738.45
2981 | TIN-INTERP | Interpolated Ground | 18919.36 | -6.66 | 726.26 | 0 | 17.89 | 0 | OK | Ground clear controls. | 47 | 42.3 | 744.15
2982 | TIN-INTERP | Interpolated Ground | 18919.38 | 4.55 | 726.74 | 0 | 22.74 | 0 | OK | Ground clear controls. | 47 | 42.3 | 749.48
2983 | TIN-INTERP | Interpolated Ground | 18919.38 | -4.66 | 726.29 | 0 | 23.2 | 0 | OK | Ground clear controls. | 47 | 42.3 | 749.49
2984 | TIN-INTERP | Interpolated Ground | 18919.46 | 6.55 | 727.02 | 0 | 17.24 | 0 | OK | Ground clear controls. | 47 | 42.3 | 744.26
2985 | TIN-INTERP | Interpolated Ground | 18959.35 | -5.16 | 726.43 | 0 | 13.76 | 0 | OK | Ground clear controls. | 47 | 42.3 | 740.19
2986 | TIN-INTERP | Interpolated Ground | 18959.35 | 5.05 | 726.61 | 0 | 13.66 | 0 | OK | Ground clear controls. | 47 | 42.3 | 740.27
2987 | TIN-INTERP | Interpolated Ground | 18959.36 | -6.66 | 726.3 | 0 | 19.67 | 0 | OK | Ground clear controls. | 47 | 42.3 | 745.97
2988 | TIN-INTERP | Interpolated Ground | 18959.38 | 4.55 | 726.65 | 0 | 24.65 | 0 | OK | Ground clear controls. | 47 | 42.3 | 751.3
2989 | TIN-INTERP | Interpolated Ground | 18959.38 | -4.66 | 726.49 | 0 | 24.82 | 0 | OK | Ground clear controls. | 47 | 42.3 | 751.31
2990 | TIN-INTERP | Interpolated Ground | 18959.46 | 6.55 | 726.55 | 0 | 19.53 | 0 | OK | Ground clear controls. | 47 | 42.3 | 746.08
2991 | TIN-INTERP | Interpolated Ground | 18999.35 | -5.16 | 728.39 | 0 | 14.56 | 0 | OK | Ground clear controls. | 47 | 42.3 | 742.95
2992 | TIN-INTERP | Interpolated Ground | 18999.35 | 5.05 | 729.36 | 0 | 13.67 | 0 | OK | Ground clear controls. | 47 | 42.3 | 743.03
2993 | TIN-INTERP | Interpolated Ground | 18999.36 | -6.66 | 728.37 | 0 | 20.35 | 0 | OK | Ground clear controls. | 47 | 42.3 | 748.72
2994 | TIN-INTERP | Interpolated Ground | 18999.38 | 4.55 | 729.3 | 0 | 24.76 | 0 | OK | Ground clear controls. | 47 | 42.3 | 754.06
2995 | TIN-INTERP | Interpolated Ground | 18999.38 | -4.66 | 728.38 | 0 | 25.69 | 0 | OK | Ground clear controls. | 47 | 42.3 | 754.07
2996 | TIN-INTERP | Interpolated Ground | 18999.46 | 6.55 | 729.37 | 0 | 19.45 | 0 | OK | Ground clear controls. | 47 | 42.3 | 748.82
2997 | TIN-INTERP | Interpolated Ground | 19039.35 | -5.16 | 728.36 | 0 | 18.3 | 0 | OK | Ground clear controls. | 47 | 42.3 | 746.66
2998 | TIN-INTERP | Interpolated Ground | 19039.35 | 5.05 | 729.39 | 0 | 17.34 | 0 | OK | Ground clear controls. | 47 | 42.3 | 746.73
2999 | TIN-INTERP | Interpolated Ground | 19039.36 | -6.66 | 728.24 | 0 | 24.16 | 0 | OK | Ground clear controls. | 47 | 42.3 | 752.4
3000 | TIN-INTERP | Interpolated Ground | 19039.38 | 4.55 | 729.3 | 0 | 28.45 | 0 | OK | Ground clear controls. | 47 | 42.3 | 757.75
3001 | TIN-INTERP | Interpolated Ground | 19039.38 | -4.66 | 728.39 | 0 | 29.37 | 0 | OK | Ground clear controls. | 47 | 42.3 | 757.76
3002 | TIN-INTERP | Interpolated Ground | 19039.46 | 6.55 | 729.72 | 0 | 22.76 | 0 | OK | Ground clear controls. | 47 | 42.3 | 752.48
3003 | TIN-INTERP | Interpolated Ground | 19079.35 | -5.16 | 730.11 | 0 | 21.2 | 0 | OK | Ground clear controls. | 47 | 42.3 | 751.31
3004 | TIN-INTERP | Interpolated Ground | 19079.35 | 5.05 | 731.36 | 0 | 20.01 | 0 | OK | Ground clear controls. | 47 | 42.3 | 751.37
3005 | TIN-INTERP | Interpolated Ground | 19079.36 | -6.66 | 730.05 | 0 | 26.96 | 0 | OK | Ground clear controls. | 47 | 42.3 | 757.01
3006 | TIN-INTERP | Interpolated Ground | 19079.38 | 4.55 | 731.24 | 0 | 31.15 | 0 | OK | Ground clear controls. | 47 | 42.3 | 762.39
3007 | TIN-INTERP | Interpolated Ground | 19079.38 | -4.66 | 730.1 | 0 | 32.29 | 0 | OK | Ground clear controls. | 47 | 42.3 | 762.39
3008 | TIN-INTERP | Interpolated Ground | 19079.46 | 6.55 | 731.65 | 0 | 25.42 | 0 | OK | Ground clear controls. | 47 | 42.3 | 757.07
3009 | TIN-INTERP | Interpolated Ground | 19119.35 | -5.16 | 727.54 | 0 | 29.37 | 0 | OK | Ground clear controls. | 47 | 42.3 | 756.91
3010 | TIN-INTERP | Interpolated Ground | 19119.35 | 5.05 | 728.54 | 0 | 28.41 | 0 | OK | Ground clear controls. | 47 | 42.3 | 756.95
3011 | TIN-INTERP | Interpolated Ground | 19119.36 | -6.66 | 727.36 | 0 | 35.18 | 0 | OK | Ground clear controls. | 47 | 42.3 | 762.54
3012 | TIN-INTERP | Interpolated Ground | 19119.38 | 4.56 | 728.57 | 0 | 39.39 | 0 | OK | Ground clear controls. | 47 | 42.3 | 767.96
3013 | TIN-INTERP | Interpolated Ground | 19119.38 | -4.66 | 727.6 | 0 | 40.36 | 0 | OK | Ground clear controls. | 47 | 42.3 | 767.96
3014 | TIN-INTERP | Interpolated Ground | 19119.46 | 6.55 | 728.43 | 0 | 34.14 | 0 | OK | Ground clear controls. | 47 | 42.3 | 762.57
3015 | TIN-INTERP | Interpolated Ground | 19159.35 | -5.15 | 732.1 | 0 | 31.36 | 0 | OK | Ground clear controls. | 47 | 42.3 | 763.46
3016 | TIN-INTERP | Interpolated Ground | 19159.35 | 5.05 | 732.57 | 0 | 30.91 | 0 | OK | Ground clear controls. | 47 | 42.3 | 763.48
3017 | TIN-INTERP | Interpolated Ground | 19159.36 | -6.65 | 731.75 | 0 | 37.26 | 0 | OK | Ground clear controls. | 47 | 42.3 | 769.01
3018 | TIN-INTERP | Interpolated Ground | 19159.38 | 4.56 | 732.56 | 0 | 41.92 | 0 | OK | Ground clear controls. | 47 | 42.3 | 774.48
3019 | TIN-INTERP | Interpolated Ground | 19159.38 | -4.66 | 732.18 | 0 | 42.3 | 0 | OK | Ground clear controls. | 47 | 42.3 | 774.48
3020 | TIN-INTERP | Interpolated Ground | 19159.46 | 6.55 | 732.68 | 0 | 36.33 | 0 | OK | Ground clear controls. | 47 | 36.33 | 769.01
3021 | TIN-INTERP | Interpolated Ground | 19177.1 | -6.65 | 733.28 | 0 | 38.9 | 0 | OK | Ground clear controls. | 48 | 44.35 | 772.18
3022 | TIN-INTERP | Interpolated Ground | 19177.12 | 5.05 | 734.05 | 0 | 32.63 | 0 | OK | Ground clear controls. | 48 | 44.35 | 766.68
3023 | TIN-INTERP | Interpolated Ground | 19177.13 | 4.56 | 733.9 | 0 | 43.78 | 0 | OK | Ground clear controls. | 48 | 44.35 | 777.68
3024 | TIN-INTERP | Interpolated Ground | 19177.16 | -5.15 | 733.39 | 0 | 33.29 | 0 | OK | Ground clear controls. | 48 | 44.35 | 766.68
3025 | TIN-INTERP | Interpolated Ground | 19177.17 | -4.66 | 733.43 | 0 | 44.25 | 0 | OK | Ground clear controls. | 48 | 44.35 | 777.68
3026 | TIN-INTERP | Interpolated Ground | 19177.25 | 6.56 | 734.29 | 0 | 37.89 | 0 | OK | Ground clear controls. | 48 | 44.35 | 772.18
3027 | TIN-INTERP | Interpolated Ground | 19217.1 | -6.68 | 735.29 | 0 | 31.3 | 0 | OK | Ground clear controls. | 48 | 44.35 | 766.59
3028 | TIN-INTERP | Interpolated Ground | 19217.12 | 5.08 | 735.57 | 0 | 25.46 | 0 | OK | Ground clear controls. | 48 | 44.35 | 761.03
3029 | TIN-INTERP | Interpolated Ground | 19217.14 | 4.59 | 735.49 | 0 | 36.58 | 0 | OK | Ground clear controls. | 48 | 44.35 | 772.07
3030 | TIN-INTERP | Interpolated Ground | 19217.16 | -5.18 | 735.42 | 0 | 25.62 | 0 | OK | Ground clear controls. | 48 | 44.35 | 761.04
3031 | TIN-INTERP | Interpolated Ground | 19217.17 | -4.69 | 735.41 | 0 | 36.7 | 0 | OK | Ground clear controls. | 48 | 44.35 | 772.11
3032 | TIN-INTERP | Interpolated Ground | 19217.25 | 6.58 | 735.79 | 0 | 30.94 | 0 | OK | Ground clear controls. | 48 | 44.35 | 766.73
3033 | TIN-INTERP | Interpolated Ground | 19257.1 | -6.7 | 739.71 | 0 | 22.21 | 0 | OK | Ground clear controls. | 48 | 44.35 | 761.92
3034 | TIN-INTERP | Interpolated Ground | 19257.12 | 5.1 | 738.59 | 0 | 17.73 | 0 | OK | Ground clear controls. | 48 | 44.35 | 756.32
3035 | TIN-INTERP | Interpolated Ground | 19257.14 | 4.62 | 738.59 | 0 | 28.81 | 0 | OK | Ground clear controls. | 48 | 44.35 | 767.4
3036 | TIN-INTERP | Interpolated Ground | 19257.16 | -5.2 | 739.66 | 0 | 16.67 | 0 | OK | Ground clear controls. | 48 | 44.35 | 756.33
3037 | TIN-INTERP | Interpolated Ground | 19257.17 | -4.72 | 739.64 | 0 | 27.82 | 0 | OK | Ground clear controls. | 48 | 44.35 | 767.46
3038 | TIN-INTERP | Interpolated Ground | 19257.25 | 6.6 | 738.59 | 0 | 23.59 | 0 | OK | Ground clear controls. | 48 | 44.35 | 762.18
3039 | TIN-INTERP | Interpolated Ground | 19297.1 | -6.72 | 739.9 | 0 | 18.29 | 0 | OK | Ground clear controls. | 48 | 44.35 | 758.19
3040 | TIN-INTERP | Interpolated Ground | 19297.12 | 5.12 | 740.85 | 0 | 11.72 | 0 | OK | Ground clear controls. | 48 | 44.35 | 752.57
3041 | TIN-INTERP | Interpolated Ground | 19297.14 | 4.65 | 740.78 | 0 | 22.9 | 0 | OK | Ground clear controls. | 48 | 44.35 | 763.68
3042 | TIN-INTERP | Interpolated Ground | 19297.16 | -5.22 | 740.08 | 0 | 12.5 | 0 | OK | Ground clear controls. | 48 | 44.35 | 752.58
3043 | TIN-INTERP | Interpolated Ground | 19297.17 | -4.75 | 740.15 | 0 | 23.61 | 0 | OK | Ground clear controls. | 48 | 44.35 | 763.76
3044 | TIN-INTERP | Interpolated Ground | 19297.25 | 6.62 | 740.96 | 0 | 17.59 | 0 | OK | Ground clear controls. | 48 | 44.35 | 758.55
3045 | TIN-INTERP | Interpolated Ground | 19337.1 | -6.75 | 733.5 | 0 | 21.91 | 0 | OK | Ground clear controls. | 48 | 44.35 | 755.41
3046 | TIN-INTERP | Interpolated Ground | 19337.12 | 5.15 | 734.04 | 0 | 15.71 | 0 | OK | Ground clear controls. | 48 | 44.35 | 749.75
3047 | TIN-INTERP | Interpolated Ground | 19337.14 | 4.68 | 734 | 0 | 26.9 | 0 | OK | Ground clear controls. | 48 | 44.35 | 760.9
3048 | TIN-INTERP | Interpolated Ground | 19337.16 | -5.25 | 733.67 | 0 | 16.11 | 0 | OK | Ground clear controls. | 48 | 44.35 | 749.78
3049 | TIN-INTERP | Interpolated Ground | 19337.17 | -4.78 | 733.74 | 0 | 27.26 | 0 | OK | Ground clear controls. | 48 | 44.35 | 761
3050 | TIN-INTERP | Interpolated Ground | 19337.25 | 6.65 | 734.18 | 0 | 21.65 | 0 | OK | Ground clear controls. | 48 | 44.35 | 755.83
3051 | TIN-INTERP | Interpolated Ground | 19377.1 | -6.77 | 731.4 | 0 | 22.16 | 0 | OK | Ground clear controls. | 48 | 44.35 | 753.56
3052 | TIN-INTERP | Interpolated Ground | 19377.12 | 5.17 | 731.84 | 0 | 16.06 | 0 | OK | Ground clear controls. | 48 | 44.35 | 747.9
3053 | TIN-INTERP | Interpolated Ground | 19377.14 | 4.71 | 731.77 | 0 | 27.31 | 0 | OK | Ground clear controls. | 48 | 44.35 | 759.08
3054 | TIN-INTERP | Interpolated Ground | 19377.16 | -5.27 | 731.53 | 0 | 16.38 | 0 | OK | Ground clear controls. | 48 | 44.35 | 747.91
3055 | TIN-INTERP | Interpolated Ground | 19377.17 | -4.81 | 731.52 | 0 | 27.66 | 0 | OK | Ground clear controls. | 48 | 44.35 | 759.18
3056 | TIN-INTERP | Interpolated Ground | 19377.25 | 6.67 | 732.07 | 0 | 21.96 | 0 | OK | Ground clear controls. | 48 | 44.35 | 754.03
3057 | TIN-INTERP | Interpolated Ground | 19417.1 | -6.8 | 730.07 | 0 | 22.57 | 0 | OK | Ground clear controls. | 48 | 44.35 | 752.64
3058 | TIN-INTERP | Interpolated Ground | 19417.12 | 5.19 | 731.17 | 0 | 15.8 | 0 | OK | Ground clear controls. | 48 | 44.35 | 746.97
3059 | TIN-INTERP | Interpolated Ground | 19417.14 | 4.74 | 731.09 | 0 | 27.09 | 0 | OK | Ground clear controls. | 48 | 44.35 | 758.18
3060 | TIN-INTERP | Interpolated Ground | 19417.16 | -5.29 | 730.14 | 0 | 16.86 | 0 | OK | Ground clear controls. | 48 | 44.35 | 747
3061 | TIN-INTERP | Interpolated Ground | 19417.17 | -4.84 | 730.15 | 0 | 28.14 | 0 | OK | Ground clear controls. | 48 | 44.35 | 758.29
3062 | TIN-INTERP | Interpolated Ground | 19417.25 | 6.69 | 731.38 | 0 | 21.77 | 0 | OK | Ground clear controls. | 48 | 44.35 | 753.15
3063 | TIN-INTERP | Interpolated Ground | 19457.1 | -6.82 | 728.65 | 0 | 24.02 | 0 | OK | Ground clear controls. | 48 | 44.35 | 752.67
3064 | TIN-INTERP | Interpolated Ground | 19457.12 | 5.22 | 728.19 | 0 | 18.81 | 0 | OK | Ground clear controls. | 48 | 44.35 | 747
3065 | TIN-INTERP | Interpolated Ground | 19457.14 | 4.77 | 728.13 | 0 | 30.09 | 0 | OK | Ground clear controls. | 48 | 44.35 | 758.22
3066 | TIN-INTERP | Interpolated Ground | 19457.16 | -5.32 | 728.46 | 0 | 18.56 | 0 | OK | Ground clear controls. | 48 | 44.35 | 747.02
3067 | TIN-INTERP | Interpolated Ground | 19457.17 | -4.87 | 728.36 | 0 | 29.97 | 0 | OK | Ground clear controls. | 48 | 44.35 | 758.33
3068 | TIN-INTERP | Interpolated Ground | 19457.25 | 6.72 | 728.37 | 0 | 24.8 | 0 | OK | Ground clear controls. | 48 | 44.35 | 753.17
3069 | TIN-INTERP | Interpolated Ground | 19497.1 | -6.84 | 727.1 | 0 | 26.53 | 0 | OK | Ground clear controls. | 48 | 44.35 | 753.63
3070 | TIN-INTERP | Interpolated Ground | 19497.12 | 5.24 | 729.5 | 0 | 18.46 | 0 | OK | Ground clear controls. | 48 | 44.35 | 747.96
3071 | TIN-INTERP | Interpolated Ground | 19497.14 | 4.8 | 729.26 | 0 | 29.94 | 0 | OK | Ground clear controls. | 48 | 44.35 | 759.2
3072 | TIN-INTERP | Interpolated Ground | 19497.16 | -5.34 | 727.24 | 0 | 20.74 | 0 | OK | Ground clear controls. | 48 | 44.35 | 747.98
3073 | TIN-INTERP | Interpolated Ground | 19497.17 | -4.9 | 727.22 | 0 | 32.09 | 0 | OK | Ground clear controls. | 48 | 44.35 | 759.31
3074 | TIN-INTERP | Interpolated Ground | 19497.25 | 6.74 | 729.8 | 0 | 24.31 | 0 | OK | Ground clear controls. | 48 | 44.35 | 754.11
3075 | TIN-INTERP | Interpolated Ground | 19537.1 | -6.87 | 728.17 | 0 | 27.35 | 0 | OK | Ground clear controls. | 48 | 44.35 | 755.52
3076 | TIN-INTERP | Interpolated Ground | 19537.12 | 5.26 | 726.81 | 0 | 23.06 | 0 | OK | Ground clear controls. | 48 | 44.35 | 749.87
3077 | TIN-INTERP | Interpolated Ground | 19537.14 | 4.83 | 726.9 | 0 | 34.23 | 0 | OK | Ground clear controls. | 48 | 44.35 | 761.13
3078 | TIN-INTERP | Interpolated Ground | 19537.16 | -5.37 | 728.09 | 0 | 21.8 | 0 | OK | Ground clear controls. | 48 | 44.35 | 749.89
3079 | TIN-INTERP | Interpolated Ground | 19537.17 | -4.93 | 728 | 0 | 33.23 | 0 | OK | Ground clear controls. | 48 | 44.35 | 761.23
3080 | TIN-INTERP | Interpolated Ground | 19537.25 | 6.76 | 726.55 | 0 | 29.41 | 0 | OK | Ground clear controls. | 48 | 44.35 | 755.96
3081 | TIN-INTERP | Interpolated Ground | 19577.1 | -6.89 | 729.8 | 0 | 28.55 | 0 | OK | Ground clear controls. | 48 | 44.35 | 758.35
3082 | TIN-INTERP | Interpolated Ground | 19577.12 | 5.29 | 730.35 | 0 | 22.37 | 0 | OK | Ground clear controls. | 48 | 44.35 | 752.72
3083 | TIN-INTERP | Interpolated Ground | 19577.14 | 4.86 | 730.34 | 0 | 33.66 | 0 | OK | Ground clear controls. | 48 | 44.35 | 764
3084 | TIN-INTERP | Interpolated Ground | 19577.16 | -5.39 | 729.84 | 0 | 22.9 | 0 | OK | Ground clear controls. | 48 | 44.35 | 752.74
3085 | TIN-INTERP | Interpolated Ground | 19577.17 | -4.96 | 729.87 | 0 | 34.22 | 0 | OK | Ground clear controls. | 48 | 44.35 | 764.09
3086 | TIN-INTERP | Interpolated Ground | 19577.25 | 6.79 | 730.4 | 0 | 28.31 | 0 | OK | Ground clear controls. | 48 | 44.35 | 758.71
3087 | TIN-INTERP | Interpolated Ground | 19617.1 | -6.91 | 729.86 | 0 | 32.26 | 0 | OK | Ground clear controls. | 48 | 44.35 | 762.12
3088 | TIN-INTERP | Interpolated Ground | 19617.12 | 5.31 | 730.41 | 0 | 26.11 | 0 | OK | Ground clear controls. | 48 | 44.35 | 756.52
3089 | TIN-INTERP | Interpolated Ground | 19617.14 | 4.89 | 730.31 | 0 | 37.49 | 0 | OK | Ground clear controls. | 48 | 44.35 | 767.8
3090 | TIN-INTERP | Interpolated Ground | 19617.16 | -5.41 | 729.71 | 0 | 26.82 | 0 | OK | Ground clear controls. | 48 | 44.35 | 756.53
3091 | TIN-INTERP | Interpolated Ground | 19617.17 | -4.99 | 729.68 | 0 | 38.2 | 0 | OK | Ground clear controls. | 48 | 44.35 | 767.88
3092 | TIN-INTERP | Interpolated Ground | 19617.25 | 6.81 | 730.78 | 0 | 31.61 | 0 | OK | Ground clear controls. | 48 | 44.35 | 762.39
3093 | TIN-INTERP | Interpolated Ground | 19657.1 | -6.94 | 733.07 | 0 | 33.75 | 0 | OK | Ground clear controls. | 48 | 44.35 | 766.82
3094 | TIN-INTERP | Interpolated Ground | 19657.12 | 5.33 | 733.41 | 0 | 27.86 | 0 | OK | Ground clear controls. | 48 | 44.35 | 761.27
3095 | TIN-INTERP | Interpolated Ground | 19657.14 | 4.92 | 733.39 | 0 | 39.17 | 0 | OK | Ground clear controls. | 48 | 44.35 | 772.56
3096 | TIN-INTERP | Interpolated Ground | 19657.16 | -5.44 | 733.06 | 0 | 28.23 | 0 | OK | Ground clear controls. | 48 | 44.35 | 761.29
3097 | TIN-INTERP | Interpolated Ground | 19657.17 | -5.02 | 733.05 | 0 | 39.56 | 0 | OK | Ground clear controls. | 48 | 44.35 | 772.61
3098 | TIN-INTERP | Interpolated Ground | 19657.25 | 6.83 | 733.48 | 0 | 33.51 | 0 | OK | Ground clear controls. | 48 | 44.35 | 766.99
3099 | TIN-INTERP | Interpolated Ground | 19697.1 | -6.96 | 733.72 | 0 | 38.75 | 0 | OK | Ground clear controls. | 48 | 44.35 | 772.47
3100 | TIN-INTERP | Interpolated Ground | 19697.12 | 5.36 | 734.49 | 0 | 32.47 | 0 | OK | Ground clear controls. | 48 | 44.35 | 766.96
3101 | TIN-INTERP | Interpolated Ground | 19697.14 | 4.95 | 734.37 | 0 | 43.89 | 0 | OK | Ground clear controls. | 48 | 44.35 | 778.26
3102 | TIN-INTERP | Interpolated Ground | 19697.16 | -5.46 | 733.95 | 0 | 33.03 | 0 | OK | Ground clear controls. | 48 | 44.35 | 766.98
3103 | TIN-INTERP | Interpolated Ground | 19697.17 | -5.06 | 733.93 | 0 | 44.35 | 0 | OK | Ground clear controls. | 48 | 44.35 | 778.28
3104 | TIN-INTERP | Interpolated Ground | 19697.25 | 6.85 | 734.55 | 0 | 37.96 | 0 | OK | Ground clear controls. | 48 | 37.96 | 772.51
3105 | TIN-INTERP | Interpolated Ground | 19699.07 | -6.96 | 733.78 | 0 | 38.99 | 0 | OK | Ground clear controls. | 49 | 44.6 | 772.77
3106 | TIN-INTERP | Interpolated Ground | 19699.08 | -5.46 | 734 | 0 | 33.27 | 0 | OK | Ground clear controls. | 49 | 44.6 | 767.27
3107 | TIN-INTERP | Interpolated Ground | 19699.09 | -5.06 | 733.97 | 0 | 44.6 | 0 | OK | Ground clear controls. | 49 | 44.6 | 778.57
3108 | TIN-INTERP | Interpolated Ground | 19699.1 | 6.86 | 734.57 | 0 | 38.21 | 0 | OK | Ground clear controls. | 49 | 44.39 | 772.78
3109 | TIN-INTERP | Interpolated Ground | 19699.13 | 5.36 | 734.32 | 0 | 32.95 | 0 | OK | Ground clear controls. | 49 | 44.39 | 767.27
3110 | TIN-INTERP | Interpolated Ground | 19699.14 | 4.95 | 734.18 | 0 | 44.39 | 0 | OK | Ground clear controls. | 49 | 44.39 | 778.57
3111 | TIN-INTERP | Interpolated Ground | 19739.07 | -7.09 | 730.6 | 0 | 35.48 | 0 | OK | Ground clear controls. | 49 | 41.16 | 766.08
3112 | TIN-INTERP | Interpolated Ground | 19739.09 | -5.58 | 730.72 | 0 | 29.79 | 0 | OK | Ground clear controls. | 49 | 41.16 | 760.51
3113 | TIN-INTERP | Interpolated Ground | 19739.09 | -5.16 | 730.75 | 0 | 41.16 | 0 | OK | Ground clear controls. | 49 | 41.16 | 771.91
3114 | TIN-INTERP | Interpolated Ground | 19739.09 | 6.87 | 731.79 | 0 | 34.37 | 0 | OK | Ground clear controls. | 49 | 40.43 | 766.16
3115 | TIN-INTERP | Interpolated Ground | 19739.13 | 5.38 | 731.5 | 0 | 28.95 | 0 | OK | Ground clear controls. | 49 | 40.43 | 760.45
3116 | TIN-INTERP | Interpolated Ground | 19739.14 | 4.95 | 731.41 | 0 | 40.43 | 0 | OK | Ground clear controls. | 49 | 40.43 | 771.84
3117 | TIN-INTERP | Interpolated Ground | 19779.07 | -7.21 | 731.39 | 0 | 28.94 | 0 | OK | Ground clear controls. | 49 | 39.22 | 760.33
3118 | TIN-INTERP | Interpolated Ground | 19779.09 | -5.7 | 731.46 | 0 | 23.24 | 0 | OK | Ground clear controls. | 49 | 39.22 | 754.7
3119 | TIN-INTERP | Interpolated Ground | 19779.09 | -5.26 | 731.47 | 0 | 34.74 | 0 | OK | Ground clear controls. | 49 | 39.22 | 766.21
3120 | TIN-INTERP | Interpolated Ground | 19779.09 | 6.89 | 733.12 | 0 | 27.36 | 0 | OK | Ground clear controls. | 49 | 39.22 | 760.48
3121 | TIN-INTERP | Interpolated Ground | 19779.13 | 5.4 | 732.96 | 0 | 21.64 | 0 | OK | Ground clear controls. | 49 | 39.22 | 754.6
3122 | TIN-INTERP | Interpolated Ground | 19779.14 | 4.95 | 732.89 | 0 | 33.18 | 0 | OK | Ground clear controls. | 49 | 39.22 | 766.07
3123 | TIN-INTERP | Interpolated Ground | 19819.07 | -7.34 | 730.29 | 0 | 25.25 | 0 | OK | Ground clear controls. | 49 | 39.22 | 755.54
3124 | TIN-INTERP | Interpolated Ground | 19819.09 | -5.82 | 730.42 | 0 | 19.43 | 0 | OK | Ground clear controls. | 49 | 39.22 | 749.85
3125 | TIN-INTERP | Interpolated Ground | 19819.09 | -5.36 | 730.39 | 0 | 31.07 | 0 | OK | Ground clear controls. | 49 | 39.22 | 761.46
3126 | TIN-INTERP | Interpolated Ground | 19819.09 | 6.91 | 732.13 | 0 | 23.62 | 0 | OK | Ground clear controls. | 49 | 39.22 | 755.75
3127 | TIN-INTERP | Interpolated Ground | 19819.13 | 5.42 | 732.02 | 0 | 17.69 | 0 | OK | Ground clear controls. | 49 | 39.22 | 749.71
3128 | TIN-INTERP | Interpolated Ground | 19819.14 | 4.95 | 731.97 | 0 | 29.3 | 0 | OK | Ground clear controls. | 49 | 39.22 | 761.27
3129 | TIN-INTERP | Interpolated Ground | 19859.07 | -7.46 | 726.6 | 0 | 25.1 | 0 | OK | Ground clear controls. | 49 | 39.22 | 751.7
3130 | TIN-INTERP | Interpolated Ground | 19859.09 | -5.94 | 726.55 | 0 | 19.42 | 0 | OK | Ground clear controls. | 49 | 39.22 | 745.97
3131 | TIN-INTERP | Interpolated Ground | 19859.09 | -5.47 | 726.51 | 0 | 31.14 | 0 | OK | Ground clear controls. | 49 | 39.22 | 757.65
3132 | TIN-INTERP | Interpolated Ground | 19859.09 | 6.93 | 727.67 | 0 | 24.28 | 0 | OK | Ground clear controls. | 49 | 39.22 | 751.95
3133 | TIN-INTERP | Interpolated Ground | 19859.13 | 5.44 | 727.42 | 0 | 18.36 | 0 | OK | Ground clear controls. | 49 | 39.22 | 745.78
3134 | TIN-INTERP | Interpolated Ground | 19859.14 | 4.95 | 727.31 | 0 | 30.11 | 0 | OK | Ground clear controls. | 49 | 39.22 | 757.42
3135 | TIN-INTERP | Interpolated Ground | 19899.07 | -7.59 | 727.8 | 0 | 21.01 | 0 | OK | Ground clear controls. | 49 | 39.22 | 748.81
3136 | TIN-INTERP | Interpolated Ground | 19899.09 | -6.06 | 727.86 | 0 | 15.17 | 0 | OK | Ground clear controls. | 49 | 39.22 | 743.03
3137 | TIN-INTERP | Interpolated Ground | 19899.09 | -5.57 | 727.87 | 0 | 26.92 | 0 | OK | Ground clear controls. | 49 | 39.22 | 754.79
3138 | TIN-INTERP | Interpolated Ground | 19899.09 | 6.95 | 728.14 | 0 | 20.95 | 0 | OK | Ground clear controls. | 49 | 39.22 | 749.09
3139 | TIN-INTERP | Interpolated Ground | 19899.13 | 5.46 | 728.31 | 0 | 14.51 | 0 | OK | Ground clear controls. | 49 | 39.22 | 742.82
3140 | TIN-INTERP | Interpolated Ground | 19899.14 | 4.96 | 728.35 | 0 | 26.17 | 0 | OK | Ground clear controls. | 49 | 39.22 | 754.52
3141 | TIN-INTERP | Interpolated Ground | 19939.07 | -7.71 | 726.41 | 0 | 20.45 | 0 | OK | Ground clear controls. | 49 | 39.22 | 746.86
3142 | TIN-INTERP | Interpolated Ground | 19939.09 | -6.17 | 726.71 | 0 | 14.32 | 0 | OK | Ground clear controls. | 49 | 39.22 | 741.03
3143 | TIN-INTERP | Interpolated Ground | 19939.09 | -5.67 | 726.89 | 0 | 25.99 | 0 | OK | Ground clear controls. | 49 | 39.22 | 752.88
3144 | TIN-INTERP | Interpolated Ground | 19939.09 | 6.97 | 728.1 | 0 | 19.05 | 0 | OK | Ground clear controls. | 49 | 39.22 | 747.15
3145 | TIN-INTERP | Interpolated Ground | 19939.13 | 5.47 | 728.14 | 0 | 12.67 | 0 | OK | Ground clear controls. | 49 | 39.22 | 740.81
3146 | TIN-INTERP | Interpolated Ground | 19939.14 | 4.96 | 728.13 | 0 | 24.45 | 0 | OK | Ground clear controls. | 49 | 39.22 | 752.58
3147 | TIN-INTERP | Interpolated Ground | 19979.07 | -7.84 | 724.19 | 0 | 21.65 | 0 | OK | Ground clear controls. | 49 | 39.22 | 745.84
3148 | TIN-INTERP | Interpolated Ground | 19979.09 | -6.29 | 724.27 | 0 | 15.73 | 0 | OK | Ground clear controls. | 49 | 39.22 | 740
3149 | TIN-INTERP | Interpolated Ground | 19979.09 | -5.78 | 724.27 | 0 | 27.62 | 0 | OK | Ground clear controls. | 49 | 39.22 | 751.89
3150 | TIN-INTERP | Interpolated Ground | 19979.09 | 6.99 | 725.5 | 0 | 20.65 | 0 | OK | Ground clear controls. | 49 | 39.22 | 746.15
3151 | TIN-INTERP | Interpolated Ground | 19979.13 | 5.49 | 725.19 | 0 | 14.57 | 0 | OK | Ground clear controls. | 49 | 39.22 | 739.76
3152 | TIN-INTERP | Interpolated Ground | 19979.14 | 4.96 | 725.11 | 0 | 26.48 | 0 | OK | Ground clear controls. | 49 | 39.22 | 751.59
3153 | TIN-INTERP | Interpolated Ground | 20019.07 | -7.96 | 724.47 | 0 | 21.3 | 0 | OK | Ground clear controls. | 49 | 39.22 | 745.77
3154 | TIN-INTERP | Interpolated Ground | 20019.09 | -6.41 | 724.42 | 0 | 15.49 | 0 | OK | Ground clear controls. | 49 | 39.22 | 739.91
3155 | TIN-INTERP | Interpolated Ground | 20019.09 | -5.88 | 724.41 | 0 | 27.45 | 0 | OK | Ground clear controls. | 49 | 39.22 | 751.86
3156 | TIN-INTERP | Interpolated Ground | 20019.09 | 7.01 | 725.29 | 0 | 20.78 | 0 | OK | Ground clear controls. | 49 | 39.22 | 746.07
3157 | TIN-INTERP | Interpolated Ground | 20019.13 | 5.51 | 725.11 | 0 | 14.55 | 0 | OK | Ground clear controls. | 49 | 39.22 | 739.66
3158 | TIN-INTERP | Interpolated Ground | 20019.14 | 4.96 | 725.01 | 0 | 26.54 | 0 | OK | Ground clear controls. | 49 | 39.22 | 751.55
3159 | TIN-INTERP | Interpolated Ground | 20059.07 | -8.09 | 728.59 | 0 | 18.06 | 0 | OK | Ground clear controls. | 49 | 39.22 | 746.65
3160 | TIN-INTERP | Interpolated Ground | 20059.09 | -6.53 | 728.33 | 0 | 12.44 | 0 | OK | Ground clear controls. | 49 | 39.22 | 740.77
3161 | TIN-INTERP | Interpolated Ground | 20059.09 | -5.98 | 728.27 | 0 | 24.5 | 0 | OK | Ground clear controls. | 49 | 39.22 | 752.77
3162 | TIN-INTERP | Interpolated Ground | 20059.09 | 7.02 | 726.89 | 0 | 20.04 | 0 | OK | Ground clear controls. | 49 | 39.22 | 746.93
3163 | TIN-INTERP | Interpolated Ground | 20059.13 | 5.53 | 727.09 | 0 | 13.44 | 0 | OK | Ground clear controls. | 49 | 39.22 | 740.53
3164 | TIN-INTERP | Interpolated Ground | 20059.14 | 4.96 | 727.18 | 0 | 25.28 | 0 | OK | Ground clear controls. | 49 | 39.22 | 752.46
3165 | TIN-INTERP | Interpolated Ground | 20099.07 | -8.21 | 730.49 | 0 | 17.98 | 0 | OK | Ground clear controls. | 49 | 39.22 | 748.47
3166 | TIN-INTERP | Interpolated Ground | 20099.09 | -6.65 | 730.58 | 0 | 12 | 0 | OK | Ground clear controls. | 49 | 39.22 | 742.58
3167 | TIN-INTERP | Interpolated Ground | 20099.09 | -6.08 | 730.6 | 0 | 24.01 | 0 | OK | Ground clear controls. | 49 | 39.22 | 754.61
3168 | TIN-INTERP | Interpolated Ground | 20099.09 | 7.04 | 731.08 | 0 | 17.64 | 0 | OK | Ground clear controls. | 49 | 39.22 | 748.72
3169 | TIN-INTERP | Interpolated Ground | 20099.13 | 5.55 | 731.1 | 0 | 11.25 | 0 | OK | Ground clear controls. | 49 | 39.22 | 742.35
3170 | TIN-INTERP | Interpolated Ground | 20099.14 | 4.96 | 731.06 | 0 | 23.26 | 0 | OK | Ground clear controls. | 49 | 39.22 | 754.32
3171 | TIN-INTERP | Interpolated Ground | 20139.07 | -8.34 | 730.2 | 0 | 21.02 | 0 | OK | Ground clear controls. | 49 | 39.22 | 751.22
3172 | TIN-INTERP | Interpolated Ground | 20139.08 | -6.77 | 730.3 | 0 | 15.04 | 0 | OK | Ground clear controls. | 49 | 39.22 | 745.34
3173 | TIN-INTERP | Interpolated Ground | 20139.09 | -6.19 | 730.3 | 0 | 27.1 | 0 | OK | Ground clear controls. | 49 | 39.22 | 757.4
3174 | TIN-INTERP | Interpolated Ground | 20139.09 | 7.06 | 730.96 | 0 | 20.47 | 0 | OK | Ground clear controls. | 49 | 39.22 | 751.43
3175 | TIN-INTERP | Interpolated Ground | 20139.13 | 5.57 | 730.91 | 0 | 14.22 | 0 | OK | Ground clear controls. | 49 | 39.22 | 745.13
3176 | TIN-INTERP | Interpolated Ground | 20139.14 | 4.96 | 730.87 | 0 | 26.27 | 0 | OK | Ground clear controls. | 49 | 39.22 | 757.14
3177 | TIN-INTERP | Interpolated Ground | 20179.07 | -8.46 | 729.63 | 0 | 25.3 | 0 | OK | Ground clear controls. | 49 | 39.22 | 754.93
3178 | TIN-INTERP | Interpolated Ground | 20179.08 | -6.89 | 729.67 | 0 | 19.38 | 0 | OK | Ground clear controls. | 49 | 39.22 | 749.05
3179 | TIN-INTERP | Interpolated Ground | 20179.09 | -6.29 | 729.66 | 0 | 31.47 | 0 | OK | Ground clear controls. | 49 | 39.22 | 761.13
3180 | TIN-INTERP | Interpolated Ground | 20179.09 | 7.08 | 729.96 | 0 | 25.13 | 0 | OK | Ground clear controls. | 49 | 39.22 | 755.09
3181 | TIN-INTERP | Interpolated Ground | 20179.13 | 5.59 | 729.84 | 0 | 19.03 | 0 | OK | Ground clear controls. | 49 | 39.22 | 748.87
3182 | TIN-INTERP | Interpolated Ground | 20179.14 | 4.96 | 729.79 | 0 | 31.11 | 0 | OK | Ground clear controls. | 49 | 39.22 | 760.9
3183 | TIN-INTERP | Interpolated Ground | 20219.07 | -8.59 | 730.66 | 0 | 28.92 | 0 | OK | Ground clear controls. | 49 | 39.22 | 759.58
3184 | TIN-INTERP | Interpolated Ground | 20219.08 | -7.01 | 730.69 | 0 | 23.04 | 0 | OK | Ground clear controls. | 49 | 39.22 | 753.73
3185 | TIN-INTERP | Interpolated Ground | 20219.09 | -6.39 | 730.7 | 0 | 35.12 | 0 | OK | Ground clear controls. | 49 | 39.22 | 765.82
3186 | TIN-INTERP | Interpolated Ground | 20219.09 | 7.1 | 730.87 | 0 | 28.8 | 0 | OK | Ground clear controls. | 49 | 39.22 | 759.67
3187 | TIN-INTERP | Interpolated Ground | 20219.13 | 5.61 | 730.97 | 0 | 22.59 | 0 | OK | Ground clear controls. | 49 | 39.22 | 753.56
3188 | TIN-INTERP | Interpolated Ground | 20219.14 | 4.96 | 731.03 | 0 | 34.6 | 0 | OK | Ground clear controls. | 49 | 39.22 | 765.63
3189 | TIN-INTERP | Interpolated Ground | 20259.07 | -8.71 | 731.99 | 0 | 33.2 | 0 | OK | Ground clear controls. | 49 | 39.22 | 765.19
3190 | TIN-INTERP | Interpolated Ground | 20259.08 | -7.13 | 732.18 | 0 | 27.16 | 0 | OK | Ground clear controls. | 49 | 39.22 | 759.34
3191 | TIN-INTERP | Interpolated Ground | 20259.09 | -6.5 | 732.27 | 0 | 39.18 | 0 | OK | Ground clear controls. | 49 | 39.22 | 771.45
3192 | TIN-INTERP | Interpolated Ground | 20259.09 | 7.12 | 731.75 | 0 | 33.44 | 0 | OK | Ground clear controls. | 49 | 39.22 | 765.19
3193 | TIN-INTERP | Interpolated Ground | 20259.13 | 5.63 | 731.99 | 0 | 27.24 | 0 | OK | Ground clear controls. | 49 | 39.22 | 759.23
3194 | TIN-INTERP | Interpolated Ground | 20259.14 | 4.96 | 732.1 | 0 | 39.22 | 0 | OK | Ground clear controls. | 49 | 39.22 | 771.32
3195 | TIN-INTERP | Interpolated Ground | 20298.23 | 4.97 | 732.71 | 0 | 45.15 | 0 | OK | Ground clear controls. | 50 | 45.15 | 777.86
3196 | TIN-INTERP | Interpolated Ground | 20298.23 | 5.66 | 732.63 | 0 | 33.13 | 0 | OK | Ground clear controls. | 50 | 43.68 | 765.76
3197 | TIN-INTERP | Interpolated Ground | 20298.23 | 7.14 | 732.45 | 0 | 39.11 | 0 | OK | Ground clear controls. | 50 | 43.68 | 771.56
3198 | TIN-INTERP | Interpolated Ground | 20298.57 | -6.59 | 734.15 | 0 | 43.68 | 0 | OK | Ground clear controls. | 50 | 43.68 | 777.83
3199 | TIN-INTERP | Interpolated Ground | 20298.62 | -7.24 | 734.14 | 0 | 31.59 | 0 | OK | Ground clear controls. | 50 | 40.26 | 765.73
3200 | TIN-INTERP | Interpolated Ground | 20298.64 | -8.84 | 734.2 | 0 | 37.33 | 0 | OK | Ground clear controls. | 50 | 40.26 | 771.53
3201 | TIN-INTERP | Interpolated Ground | 20337.9 | 7.05 | 733.7 | 0 | 33.8 | 0 | OK | Ground clear controls. | 50 | 40.26 | 767.5
3202 | TIN-INTERP | Interpolated Ground | 20338.03 | 5.58 | 733.46 | 0 | 28.16 | 0 | OK | Ground clear controls. | 50 | 40.26 | 761.62
3203 | TIN-INTERP | Interpolated Ground | 20338.06 | 4.9 | 733.39 | 0 | 40.26 | 0 | OK | Ground clear controls. | 50 | 40.26 | 773.65
3204 | TIN-INTERP | Interpolated Ground | 20338.57 | -6.36 | 734.7 | 0 | 39.01 | 0 | OK | Ground clear controls. | 50 | 39.01 | 773.71
3205 | TIN-INTERP | Interpolated Ground | 20338.62 | -6.99 | 734.78 | 0 | 26.9 | 0 | OK | Ground clear controls. | 50 | 34.26 | 761.68
3206 | TIN-INTERP | Interpolated Ground | 20338.64 | -8.58 | 735.05 | 0 | 32.42 | 0 | OK | Ground clear controls. | 50 | 34.26 | 767.47
3207 | TIN-INTERP | Interpolated Ground | 20377.9 | 6.97 | 736.18 | 0 | 28.2 | 0 | OK | Ground clear controls. | 50 | 34.26 | 764.38
3208 | TIN-INTERP | Interpolated Ground | 20378.03 | 5.51 | 736.14 | 0 | 22.3 | 0 | OK | Ground clear controls. | 50 | 34.26 | 758.44
3209 | TIN-INTERP | Interpolated Ground | 20378.06 | 4.83 | 736.14 | 0 | 34.26 | 0 | OK | Ground clear controls. | 50 | 34.26 | 770.4
3210 | TIN-INTERP | Interpolated Ground | 20378.57 | -6.14 | 736.38 | 0 | 34.16 | 0 | OK | Ground clear controls. | 50 | 34.16 | 770.54
3211 | TIN-INTERP | Interpolated Ground | 20378.62 | -6.75 | 736.38 | 0 | 22.19 | 0 | OK | Ground clear controls. | 50 | 33.08 | 758.57
3212 | TIN-INTERP | Interpolated Ground | 20378.64 | -8.33 | 736.38 | 0 | 27.97 | 0 | OK | Ground clear controls. | 50 | 33.08 | 764.35
3213 | TIN-INTERP | Interpolated Ground | 20417.9 | 6.89 | 737.63 | 0 | 24.56 | 0 | OK | Ground clear controls. | 50 | 33.08 | 762.19
3214 | TIN-INTERP | Interpolated Ground | 20418.03 | 5.43 | 737.88 | 0 | 18.34 | 0 | OK | Ground clear controls. | 50 | 33.08 | 756.22
3215 | TIN-INTERP | Interpolated Ground | 20418.06 | 4.76 | 737.97 | 0 | 30.12 | 0 | OK | Ground clear controls. | 50 | 33.08 | 768.09
3216 | TIN-INTERP | Interpolated Ground | 20418.57 | -5.91 | 738.54 | 0 | 29.76 | 0 | OK | Ground clear controls. | 50 | 33.08 | 768.3
3217 | TIN-INTERP | Interpolated Ground | 20418.62 | -6.5 | 738.54 | 0 | 17.88 | 0 | OK | Ground clear controls. | 50 | 33.08 | 756.42
3218 | TIN-INTERP | Interpolated Ground | 20418.64 | -8.07 | 738.56 | 0 | 23.61 | 0 | OK | Ground clear controls. | 50 | 33.08 | 762.17
3219 | TIN-INTERP | Interpolated Ground | 20457.9 | 6.81 | 739.73 | 0 | 21.2 | 0 | OK | Ground clear controls. | 50 | 33.08 | 760.93
3220 | TIN-INTERP | Interpolated Ground | 20458.03 | 5.35 | 739.62 | 0 | 15.32 | 0 | OK | Ground clear controls. | 50 | 33.08 | 754.94
3221 | TIN-INTERP | Interpolated Ground | 20458.06 | 4.69 | 739.52 | 0 | 27.22 | 0 | OK | Ground clear controls. | 50 | 33.08 | 766.74
3222 | TIN-INTERP | Interpolated Ground | 20458.57 | -5.68 | 739.2 | 0 | 27.81 | 0 | OK | Ground clear controls. | 50 | 33.08 | 767.01
3223 | TIN-INTERP | Interpolated Ground | 20458.62 | -6.26 | 739.22 | 0 | 15.99 | 0 | OK | Ground clear controls. | 50 | 33.08 | 755.21
3224 | TIN-INTERP | Interpolated Ground | 20458.64 | -7.82 | 739.24 | 0 | 21.71 | 0 | OK | Ground clear controls. | 50 | 33.08 | 760.95
3225 | TIN-INTERP | Interpolated Ground | 20497.9 | 6.73 | 740.43 | 0 | 20.17 | 0 | OK | Ground clear controls. | 50 | 33.08 | 760.6
3226 | TIN-INTERP | Interpolated Ground | 20498.03 | 5.28 | 740.45 | 0 | 14.17 | 0 | OK | Ground clear controls. | 50 | 33.08 | 754.62
3227 | TIN-INTERP | Interpolated Ground | 20498.06 | 4.62 | 740.45 | 0 | 25.88 | 0 | OK | Ground clear controls. | 50 | 33.08 | 766.33
3228 | TIN-INTERP | Interpolated Ground | 20498.57 | -5.45 | 740.61 | 0 | 26.03 | 0 | OK | Ground clear controls. | 50 | 33.08 | 766.64
3229 | TIN-INTERP | Interpolated Ground | 20498.62 | -6.02 | 740.61 | 0 | 14.32 | 0 | OK | Ground clear controls. | 50 | 33.08 | 754.93
3230 | TIN-INTERP | Interpolated Ground | 20498.64 | -7.57 | 740.6 | 0 | 20.07 | 0 | OK | Ground clear controls. | 50 | 33.08 | 760.67
3231 | TIN-INTERP | Interpolated Ground | 20537.9 | 6.65 | 743.28 | 0 | 17.92 | 0 | OK | Ground clear controls. | 50 | 33.08 | 761.2
3232 | TIN-INTERP | Interpolated Ground | 20538.03 | 5.2 | 743.35 | 0 | 11.89 | 0 | OK | Ground clear controls. | 50 | 33.08 | 755.24
3233 | TIN-INTERP | Interpolated Ground | 20538.06 | 4.55 | 743.38 | 0 | 23.49 | 0 | OK | Ground clear controls. | 50 | 33.08 | 766.87
3234 | TIN-INTERP | Interpolated Ground | 20538.57 | -5.23 | 743.85 | 0 | 23.37 | 0 | OK | Ground clear controls. | 50 | 33.08 | 767.22
3235 | TIN-INTERP | Interpolated Ground | 20538.62 | -5.77 | 743.85 | 0 | 11.75 | 0 | OK | Ground clear controls. | 50 | 33.08 | 755.6
3236 | TIN-INTERP | Interpolated Ground | 20538.64 | -7.31 | 743.88 | 0 | 17.44 | 0 | OK | Ground clear controls. | 50 | 33.08 | 761.32
3237 | TIN-INTERP | Interpolated Ground | 20577.9 | 6.57 | 744.23 | 0 | 18.5 | 0 | OK | Ground clear controls. | 50 | 33.08 | 762.73
3238 | TIN-INTERP | Interpolated Ground | 20578.03 | 5.13 | 744.49 | 0 | 12.32 | 0 | OK | Ground clear controls. | 50 | 33.08 | 756.81
3239 | TIN-INTERP | Interpolated Ground | 20578.06 | 4.48 | 744.61 | 0 | 23.74 | 0 | OK | Ground clear controls. | 50 | 33.08 | 768.35
3240 | TIN-INTERP | Interpolated Ground | 20578.57 | -5 | 746.08 | 0 | 22.66 | 0 | OK | Ground clear controls. | 50 | 33.08 | 768.74
3241 | TIN-INTERP | Interpolated Ground | 20578.62 | -5.53 | 746.11 | 0 | 11.12 | 0 | OK | Ground clear controls. | 50 | 33.08 | 757.23
3242 | TIN-INTERP | Interpolated Ground | 20578.64 | -7.06 | 746.15 | 0 | 16.76 | 0 | OK | Ground clear controls. | 50 | 33.08 | 762.91
3243 | TIN-INTERP | Interpolated Ground | 20617.9 | 6.49 | 746.51 | 0 | 18.68 | 0 | OK | Ground clear controls. | 50 | 33.08 | 765.19
3244 | TIN-INTERP | Interpolated Ground | 20618.03 | 5.05 | 746.57 | 0 | 12.77 | 0 | OK | Ground clear controls. | 50 | 33.08 | 759.34
3245 | TIN-INTERP | Interpolated Ground | 20618.06 | 4.41 | 746.57 | 0 | 24.21 | 0 | OK | Ground clear controls. | 50 | 33.08 | 770.78
3246 | TIN-INTERP | Interpolated Ground | 20618.57 | -4.77 | 746.45 | 0 | 24.75 | 0 | OK | Ground clear controls. | 50 | 33.08 | 771.2
3247 | TIN-INTERP | Interpolated Ground | 20618.62 | -5.28 | 746.48 | 0 | 13.31 | 0 | OK | Ground clear controls. | 50 | 33.08 | 759.79
3248 | TIN-INTERP | Interpolated Ground | 20618.64 | -6.81 | 746.56 | 0 | 18.9 | 0 | OK | Ground clear controls. | 50 | 33.08 | 765.46
3249 | TIN-INTERP | Interpolated Ground | 20657.9 | 6.41 | 747.2 | 0 | 21.4 | 0 | OK | Ground clear controls. | 50 | 33.08 | 768.6
3250 | TIN-INTERP | Interpolated Ground | 20658.03 | 4.97 | 747.19 | 0 | 15.64 | 0 | OK | Ground clear controls. | 50 | 33.08 | 762.83
3251 | TIN-INTERP | Interpolated Ground | 20658.06 | 4.34 | 747.21 | 0 | 26.95 | 0 | OK | Ground clear controls. | 50 | 33.08 | 774.16
3252 | TIN-INTERP | Interpolated Ground | 20658.57 | -4.54 | 747.83 | 0 | 26.76 | 0 | OK | Ground clear controls. | 50 | 33.08 | 774.59
3253 | TIN-INTERP | Interpolated Ground | 20658.62 | -5.04 | 747.86 | 0 | 15.45 | 0 | OK | Ground clear controls. | 50 | 33.08 | 763.31
3254 | TIN-INTERP | Interpolated Ground | 20658.64 | -6.55 | 747.99 | 0 | 20.95 | 0 | OK | Ground clear controls. | 50 | 33.08 | 768.94
3255 | TIN-INTERP | Interpolated Ground | 20697.9 | 6.33 | 749.69 | 0 | 23.24 | 0 | OK | Ground clear controls. | 50 | 33.08 | 772.93
3256 | TIN-INTERP | Interpolated Ground | 20698.03 | 4.9 | 749.85 | 0 | 17.41 | 0 | OK | Ground clear controls. | 50 | 33.08 | 767.26
3257 | TIN-INTERP | Interpolated Ground | 20698.06 | 4.27 | 749.9 | 0 | 28.58 | 0 | OK | Ground clear controls. | 50 | 33.08 | 778.48
3258 | TIN-INTERP | Interpolated Ground | 20698.57 | -4.32 | 750.37 | 0 | 28.56 | 0 | OK | Ground clear controls. | 50 | 33.08 | 778.93
3259 | TIN-INTERP | Interpolated Ground | 20698.61 | -4.8 | 750.37 | 0 | 17.39 | 0 | OK | Ground clear controls. | 50 | 33.08 | 767.76
3260 | TIN-INTERP | Interpolated Ground | 20698.64 | -6.3 | 750.4 | 0 | 22.97 | 0 | OK | Ground clear controls. | 50 | 33.08 | 773.37
3261 | TIN-INTERP | Interpolated Ground | 20737.9 | 6.25 | 751.1 | 0 | 27.09 | 0 | OK | Ground clear controls. | 50 | 33.08 | 778.19
3262 | TIN-INTERP | Interpolated Ground | 20738.03 | 4.82 | 751.01 | 0 | 21.66 | 0 | OK | Ground clear controls. | 50 | 33.08 | 772.67
3263 | TIN-INTERP | Interpolated Ground | 20738.06 | 4.2 | 750.98 | 0 | 32.78 | 0 | OK | Ground clear controls. | 50 | 33.08 | 783.76
3264 | TIN-INTERP | Interpolated Ground | 20738.57 | -4.09 | 751.14 | 0 | 33.08 | 0 | OK | Ground clear controls. | 50 | 33.08 | 784.22
3265 | TIN-INTERP | Interpolated Ground | 20738.61 | -4.55 | 751.19 | 0 | 21.98 | 0 | OK | Ground clear controls. | 50 | 27.33 | 773.17
3266 | TIN-INTERP | Interpolated Ground | 20738.64 | -6.04 | 751.42 | 0 | 27.33 | 0 | OK | Ground clear controls. | 50 | 27.33 | 778.75
3267 | TIN-INTERP | Interpolated Ground | 20780.59 | 6.16 | 752.68 | 0 | 31.46 | 0 | OK | Ground clear controls. | 51 | 36.86 | 784.14
3268 | TIN-INTERP | Interpolated Ground | 20780.89 | 4.13 | 752.78 | 0 | 36.86 | 0 | OK | Ground clear controls. | 51 | 36.86 | 789.64
3269 | TIN-INTERP | Interpolated Ground | 20780.96 | 4.71 | 752.56 | 0 | 26.08 | 0 | OK | Ground clear controls. | 51 | 36.82 | 778.64
3270 | TIN-INTERP | Interpolated Ground | 20782.74 | -3.97 | 752.83 | 0 | 36.82 | 0 | OK | Ground clear controls. | 51 | 36.82 | 789.65
3271 | TIN-INTERP | Interpolated Ground | 20783.15 | -4.44 | 752.89 | 0 | 25.75 | 0 | OK | Ground clear controls. | 51 | 31.01 | 778.64
3272 | TIN-INTERP | Interpolated Ground | 20783.37 | -5.93 | 753.13 | 0 | 31.01 | 0 | OK | Ground clear controls. | 51 | 31.01 | 784.14
3273 | TIN-INTERP | Interpolated Ground | 20820.59 | 6.2 | 754.61 | 0 | 23.88 | 0 | OK | Ground clear controls. | 51 | 30.61 | 778.49
3274 | TIN-INTERP | Interpolated Ground | 20820.89 | 4.17 | 754.4 | 0 | 29.62 | 0 | OK | Ground clear controls. | 51 | 30.61 | 784.02
3275 | TIN-INTERP | Interpolated Ground | 20820.96 | 4.75 | 754.45 | 0 | 18.55 | 0 | OK | Ground clear controls. | 51 | 30.61 | 773
3276 | TIN-INTERP | Interpolated Ground | 20822.74 | -4.03 | 754.23 | 0 | 29.95 | 0 | OK | Ground clear controls. | 51 | 30.61 | 784.18
3277 | TIN-INTERP | Interpolated Ground | 20823.15 | -4.5 | 754.26 | 0 | 18.86 | 0 | OK | Ground clear controls. | 51 | 30.61 | 773.12
3278 | TIN-INTERP | Interpolated Ground | 20823.37 | -5.99 | 754.49 | 0 | 24.06 | 0 | OK | Ground clear controls. | 51 | 30.61 | 778.55
3279 | TIN-INTERP | Interpolated Ground | 20860.59 | 6.25 | 753.17 | 0 | 20.62 | 0 | OK | Ground clear controls. | 51 | 30.61 | 773.79
3280 | TIN-INTERP | Interpolated Ground | 20860.89 | 4.22 | 753.63 | 0 | 25.72 | 0 | OK | Ground clear controls. | 51 | 30.61 | 779.35
3281 | TIN-INTERP | Interpolated Ground | 20860.96 | 4.79 | 753.53 | 0 | 14.79 | 0 | OK | Ground clear controls. | 51 | 30.61 | 768.32
3282 | TIN-INTERP | Interpolated Ground | 20862.74 | -4.08 | 753.44 | 0 | 26.19 | 0 | OK | Ground clear controls. | 51 | 30.61 | 779.63
3283 | TIN-INTERP | Interpolated Ground | 20863.15 | -4.56 | 753.42 | 0 | 15.11 | 0 | OK | Ground clear controls. | 51 | 30.61 | 768.53
3284 | TIN-INTERP | Interpolated Ground | 20863.37 | -6.05 | 753.36 | 0 | 20.55 | 0 | OK | Ground clear controls. | 51 | 30.61 | 773.91
3285 | TIN-INTERP | Interpolated Ground | 20900.59 | 6.29 | 751.27 | 0 | 18.79 | 0 | OK | Ground clear controls. | 51 | 30.61 | 770.06
3286 | TIN-INTERP | Interpolated Ground | 20900.89 | 4.27 | 750.95 | 0 | 24.67 | 0 | OK | Ground clear controls. | 51 | 30.61 | 775.62
3287 | TIN-INTERP | Interpolated Ground | 20900.96 | 4.83 | 751.02 | 0 | 13.58 | 0 | OK | Ground clear controls. | 51 | 30.61 | 764.6
3288 | TIN-INTERP | Interpolated Ground | 20902.74 | -4.14 | 750.87 | 0 | 25.13 | 0 | OK | Ground clear controls. | 51 | 30.61 | 776
3289 | TIN-INTERP | Interpolated Ground | 20903.15 | -4.62 | 750.77 | 0 | 14.11 | 0 | OK | Ground clear controls. | 51 | 30.61 | 764.88
3290 | TIN-INTERP | Interpolated Ground | 20903.37 | -6.11 | 750.69 | 0 | 19.53 | 0 | OK | Ground clear controls. | 51 | 30.61 | 770.22
3291 | TIN-INTERP | Interpolated Ground | 20940.59 | 6.34 | 749.59 | 0 | 17.68 | 0 | OK | Ground clear controls. | 51 | 30.61 | 767.27
3292 | TIN-INTERP | Interpolated Ground | 20940.89 | 4.32 | 749.44 | 0 | 23.42 | 0 | OK | Ground clear controls. | 51 | 30.61 | 772.86
3293 | TIN-INTERP | Interpolated Ground | 20940.96 | 4.87 | 749.5 | 0 | 12.34 | 0 | OK | Ground clear controls. | 51 | 30.61 | 761.84
3294 | TIN-INTERP | Interpolated Ground | 20942.74 | -4.19 | 749.18 | 0 | 24.12 | 0 | OK | Ground clear controls. | 51 | 30.61 | 773.3
3295 | TIN-INTERP | Interpolated Ground | 20943.15 | -4.68 | 749.14 | 0 | 13.03 | 0 | OK | Ground clear controls. | 51 | 30.61 | 762.17
3296 | TIN-INTERP | Interpolated Ground | 20943.37 | -6.17 | 749.14 | 0 | 18.34 | 0 | OK | Ground clear controls. | 51 | 30.61 | 767.48
3297 | TIN-INTERP | Interpolated Ground | 20980.59 | 6.38 | 747.8 | 0 | 17.64 | 0 | OK | Ground clear controls. | 51 | 30.61 | 765.44
3298 | TIN-INTERP | Interpolated Ground | 20980.89 | 4.37 | 747.68 | 0 | 23.35 | 0 | OK | Ground clear controls. | 51 | 30.61 | 771.03
3299 | TIN-INTERP | Interpolated Ground | 20980.96 | 4.91 | 747.71 | 0 | 12.3 | 0 | OK | Ground clear controls. | 51 | 30.61 | 760.01
3300 | TIN-INTERP | Interpolated Ground | 20982.74 | -4.25 | 747.18 | 0 | 24.34 | 0 | OK | Ground clear controls. | 51 | 30.61 | 771.52
3301 | TIN-INTERP | Interpolated Ground | 20983.15 | -4.73 | 747.16 | 0 | 13.22 | 0 | OK | Ground clear controls. | 51 | 30.61 | 760.38
3302 | TIN-INTERP | Interpolated Ground | 20983.37 | -6.23 | 747.04 | 0 | 18.64 | 0 | OK | Ground clear controls. | 51 | 30.61 | 765.68
3303 | TIN-INTERP | Interpolated Ground | 21020.59 | 6.43 | 746.2 | 0 | 18.36 | 0 | OK | Ground clear controls. | 51 | 30.61 | 764.56
3304 | TIN-INTERP | Interpolated Ground | 21020.89 | 4.41 | 746.27 | 0 | 23.9 | 0 | OK | Ground clear controls. | 51 | 30.61 | 770.17
3305 | TIN-INTERP | Interpolated Ground | 21020.96 | 4.95 | 746.23 | 0 | 12.91 | 0 | OK | Ground clear controls. | 51 | 30.61 | 759.14
3306 | TIN-INTERP | Interpolated Ground | 21022.74 | -4.3 | 746.35 | 0 | 24.31 | 0 | OK | Ground clear controls. | 51 | 30.61 | 770.66
3307 | TIN-INTERP | Interpolated Ground | 21023.15 | -4.79 | 746.31 | 0 | 13.22 | 0 | OK | Ground clear controls. | 51 | 30.61 | 759.53
3308 | TIN-INTERP | Interpolated Ground | 21023.37 | -6.28 | 746.24 | 0 | 18.6 | 0 | OK | Ground clear controls. | 51 | 30.61 | 764.84
3309 | TIN-INTERP | Interpolated Ground | 21060.59 | 6.48 | 744.78 | 0 | 19.86 | 0 | OK | Ground clear controls. | 51 | 30.61 | 764.64
3310 | TIN-INTERP | Interpolated Ground | 21060.89 | 4.46 | 744.74 | 0 | 25.49 | 0 | OK | Ground clear controls. | 51 | 30.61 | 770.23
3311 | TIN-INTERP | Interpolated Ground | 21060.96 | 4.99 | 744.74 | 0 | 14.47 | 0 | OK | Ground clear controls. | 51 | 30.61 | 759.21
3312 | TIN-INTERP | Interpolated Ground | 21062.74 | -4.36 | 744.7 | 0 | 26.03 | 0 | OK | Ground clear controls. | 51 | 30.61 | 770.73
3313 | TIN-INTERP | Interpolated Ground | 21063.15 | -4.85 | 744.65 | 0 | 14.95 | 0 | OK | Ground clear controls. | 51 | 30.61 | 759.6
3314 | TIN-INTERP | Interpolated Ground | 21063.37 | -6.34 | 744.58 | 0 | 20.36 | 0 | OK | Ground clear controls. | 51 | 30.61 | 764.94
3315 | TIN-INTERP | Interpolated Ground | 21100.59 | 6.52 | 744.33 | 0 | 21.34 | 0 | OK | Ground clear controls. | 51 | 30.61 | 765.67
3316 | TIN-INTERP | Interpolated Ground | 21100.89 | 4.51 | 744.26 | 0 | 26.99 | 0 | OK | Ground clear controls. | 51 | 30.61 | 771.25
3317 | TIN-INTERP | Interpolated Ground | 21100.96 | 5.03 | 744.29 | 0 | 15.95 | 0 | OK | Ground clear controls. | 51 | 30.61 | 760.24
3318 | TIN-INTERP | Interpolated Ground | 21102.74 | -4.41 | 744.29 | 0 | 27.42 | 0 | OK | Ground clear controls. | 51 | 30.61 | 771.71
3319 | TIN-INTERP | Interpolated Ground | 21103.15 | -4.91 | 744.3 | 0 | 16.31 | 0 | OK | Ground clear controls. | 51 | 30.61 | 760.61
3320 | TIN-INTERP | Interpolated Ground | 21103.37 | -6.4 | 744.25 | 0 | 21.73 | 0 | OK | Ground clear controls. | 51 | 30.61 | 765.98
3321 | TIN-INTERP | Interpolated Ground | 21140.59 | 6.57 | 744.16 | 0 | 23.49 | 0 | OK | Ground clear controls. | 51 | 30.61 | 767.65
3322 | TIN-INTERP | Interpolated Ground | 21140.89 | 4.56 | 744.09 | 0 | 29.13 | 0 | OK | Ground clear controls. | 51 | 30.61 | 773.22
3323 | TIN-INTERP | Interpolated Ground | 21140.96 | 5.08 | 744.11 | 0 | 18.1 | 0 | OK | Ground clear controls. | 51 | 30.61 | 762.21
3324 | TIN-INTERP | Interpolated Ground | 21142.74 | -4.47 | 745.12 | 0 | 28.49 | 0 | OK | Ground clear controls. | 51 | 30.61 | 773.61
3325 | TIN-INTERP | Interpolated Ground | 21143.15 | -4.97 | 745.16 | 0 | 17.39 | 0 | OK | Ground clear controls. | 51 | 30.61 | 762.55
3326 | TIN-INTERP | Interpolated Ground | 21143.37 | -6.46 | 745.22 | 0 | 22.74 | 0 | OK | Ground clear controls. | 51 | 30.61 | 767.96
3327 | TIN-INTERP | Interpolated Ground | 21180.59 | 6.61 | 745.44 | 0 | 25.14 | 0 | OK | Ground clear controls. | 51 | 30.61 | 770.58
3328 | TIN-INTERP | Interpolated Ground | 21180.89 | 4.6 | 745.53 | 0 | 30.61 | 0 | OK | Ground clear controls. | 51 | 30.61 | 776.14
3329 | TIN-INTERP | Interpolated Ground | 21180.96 | 5.12 | 745.56 | 0 | 19.58 | 0 | OK | Ground clear controls. | 51 | 30.46 | 765.14
3330 | TIN-INTERP | Interpolated Ground | 21182.74 | -4.52 | 745.99 | 0 | 30.46 | 0 | OK | Ground clear controls. | 51 | 30.46 | 776.45
3331 | TIN-INTERP | Interpolated Ground | 21183.15 | -5.02 | 745.91 | 0 | 19.51 | 0 | OK | Ground clear controls. | 51 | 24.93 | 765.42
3332 | TIN-INTERP | Interpolated Ground | 21183.37 | -6.52 | 745.96 | 0 | 24.93 | 0 | OK | Ground clear controls. | 51 | 24.93 | 770.89
3333 | TIN-INTERP | Interpolated Ground | 21219.29 | -4.57 | 746.75 | 0 | 33.08 | 0 | OK | Ground clear controls. | 52 | 40.11 | 779.83
3334 | TIN-INTERP | Interpolated Ground | 21219.32 | -6.57 | 746.86 | 0 | 27.48 | 0 | OK | Ground clear controls. | 52 | 40.11 | 774.34
3335 | TIN-INTERP | Interpolated Ground | 21219.34 | 5.16 | 746.56 | 0 | 22.27 | 0 | OK | Ground clear controls. | 52 | 40.11 | 768.83
3336 | TIN-INTERP | Interpolated Ground | 21219.34 | 6.65 | 746.59 | 0 | 27.74 | 0 | OK | Ground clear controls. | 52 | 40.11 | 774.33
3337 | TIN-INTERP | Interpolated Ground | 21219.36 | 4.65 | 746.56 | 0 | 33.28 | 0 | OK | Ground clear controls. | 52 | 40.11 | 779.84
3338 | TIN-INTERP | Interpolated Ground | 21219.36 | -5.08 | 746.78 | 0 | 22.05 | 0 | OK | Ground clear controls. | 52 | 40.11 | 768.83
3339 | TIN-INTERP | Interpolated Ground | 21259.29 | -4.51 | 745.11 | 0 | 28.16 | 0 | OK | Ground clear controls. | 52 | 40.11 | 773.27
3340 | TIN-INTERP | Interpolated Ground | 21259.32 | -6.52 | 745.08 | 0 | 22.49 | 0 | OK | Ground clear controls. | 52 | 40.11 | 767.57
3341 | TIN-INTERP | Interpolated Ground | 21259.34 | 5.44 | 745.63 | 0 | 16.41 | 0 | OK | Ground clear controls. | 52 | 40.11 | 762.04
3342 | TIN-INTERP | Interpolated Ground | 21259.34 | 6.94 | 745.64 | 0 | 21.91 | 0 | OK | Ground clear controls. | 52 | 40.11 | 767.55
3343 | TIN-INTERP | Interpolated Ground | 21259.36 | 4.92 | 745.6 | 0 | 27.56 | 0 | OK | Ground clear controls. | 52 | 40.11 | 773.16
3344 | TIN-INTERP | Interpolated Ground | 21259.36 | -5.04 | 745.12 | 0 | 17.02 | 0 | OK | Ground clear controls. | 52 | 40.11 | 762.14
3345 | TIN-INTERP | Interpolated Ground | 21299.29 | -4.45 | 740.01 | 0 | 27.63 | 0 | OK | Ground clear controls. | 52 | 40.11 | 767.64
3346 | TIN-INTERP | Interpolated Ground | 21299.32 | -6.47 | 739.93 | 0 | 21.86 | 0 | OK | Ground clear controls. | 52 | 40.11 | 761.79
3347 | TIN-INTERP | Interpolated Ground | 21299.34 | 5.73 | 740.54 | 0 | 15.69 | 0 | OK | Ground clear controls. | 52 | 40.11 | 756.23
3348 | TIN-INTERP | Interpolated Ground | 21299.34 | 7.22 | 740.64 | 0 | 21.11 | 0 | OK | Ground clear controls. | 52 | 40.11 | 761.75
3349 | TIN-INTERP | Interpolated Ground | 21299.35 | 5.19 | 740.49 | 0 | 26.95 | 0 | OK | Ground clear controls. | 52 | 40.11 | 767.44
3350 | TIN-INTERP | Interpolated Ground | 21299.36 | -5 | 739.95 | 0 | 16.44 | 0 | OK | Ground clear controls. | 52 | 40.11 | 756.39
3351 | TIN-INTERP | Interpolated Ground | 21339.29 | -4.38 | 733.91 | 0 | 29.05 | 0 | OK | Ground clear controls. | 52 | 40.11 | 762.96
3352 | TIN-INTERP | Interpolated Ground | 21339.32 | -6.42 | 733.74 | 0 | 23.21 | 0 | OK | Ground clear controls. | 52 | 40.11 | 756.95
3353 | TIN-INTERP | Interpolated Ground | 21339.34 | 6.01 | 734.1 | 0 | 17.27 | 0 | OK | Ground clear controls. | 52 | 40.11 | 751.37
3354 | TIN-INTERP | Interpolated Ground | 21339.34 | 7.51 | 734.16 | 0 | 22.76 | 0 | OK | Ground clear controls. | 52 | 40.11 | 756.92
3355 | TIN-INTERP | Interpolated Ground | 21339.35 | 5.46 | 734.05 | 0 | 28.66 | 0 | OK | Ground clear controls. | 52 | 40.11 | 762.71
3356 | TIN-INTERP | Interpolated Ground | 21339.36 | -4.96 | 733.89 | 0 | 17.71 | 0 | OK | Ground clear controls. | 52 | 40.11 | 751.6
3357 | TIN-INTERP | Interpolated Ground | 21379.29 | -4.32 | 728.26 | 0 | 30.97 | 0 | OK | Ground clear controls. | 52 | 40.11 | 759.23
3358 | TIN-INTERP | Interpolated Ground | 21379.32 | -6.37 | 728.49 | 0 | 24.6 | 0 | OK | Ground clear controls. | 52 | 40.11 | 753.09
3359 | TIN-INTERP | Interpolated Ground | 21379.34 | 6.3 | 728.12 | 0 | 19.37 | 0 | OK | Ground clear controls. | 52 | 40.11 | 747.49
3360 | TIN-INTERP | Interpolated Ground | 21379.34 | 7.79 | 728.11 | 0 | 24.93 | 0 | OK | Ground clear controls. | 52 | 40.11 | 753.04
3361 | TIN-INTERP | Interpolated Ground | 21379.35 | 5.73 | 728.15 | 0 | 30.77 | 0 | OK | Ground clear controls. | 52 | 40.11 | 758.92
3362 | TIN-INTERP | Interpolated Ground | 21379.36 | -4.92 | 728.33 | 0 | 19.41 | 0 | OK | Ground clear controls. | 52 | 40.11 | 747.74
3363 | TIN-INTERP | Interpolated Ground | 21419.29 | -4.26 | 725.95 | 0 | 30.47 | 0 | OK | Ground clear controls. | 52 | 40.11 | 756.42
3364 | TIN-INTERP | Interpolated Ground | 21419.32 | -6.32 | 725.91 | 0 | 24.28 | 0 | OK | Ground clear controls. | 52 | 40.11 | 750.19
3365 | TIN-INTERP | Interpolated Ground | 21419.34 | 6.59 | 725.37 | 0 | 19.19 | 0 | OK | Ground clear controls. | 52 | 40.11 | 744.56
3366 | TIN-INTERP | Interpolated Ground | 21419.34 | 8.08 | 725.39 | 0 | 24.76 | 0 | OK | Ground clear controls. | 52 | 40.11 | 750.15
3367 | TIN-INTERP | Interpolated Ground | 21419.35 | 6 | 725.34 | 0 | 30.75 | 0 | OK | Ground clear controls. | 52 | 40.11 | 756.09
3368 | TIN-INTERP | Interpolated Ground | 21419.36 | -4.88 | 725.96 | 0 | 18.87 | 0 | OK | Ground clear controls. | 52 | 40.11 | 744.83
3369 | TIN-INTERP | Interpolated Ground | 21459.29 | -4.2 | 723.53 | 0 | 31.04 | 0 | OK | Ground clear controls. | 52 | 40.11 | 754.57
3370 | TIN-INTERP | Interpolated Ground | 21459.32 | -6.27 | 723.75 | 0 | 24.5 | 0 | OK | Ground clear controls. | 52 | 40.11 | 748.25
3371 | TIN-INTERP | Interpolated Ground | 21459.34 | 6.87 | 722.34 | 0 | 20.25 | 0 | OK | Ground clear controls. | 52 | 40.11 | 742.59
3372 | TIN-INTERP | Interpolated Ground | 21459.34 | 8.37 | 722.21 | 0 | 25.99 | 0 | OK | Ground clear controls. | 52 | 40.11 | 748.2
3373 | TIN-INTERP | Interpolated Ground | 21459.35 | 6.26 | 722.35 | 0 | 31.86 | 0 | OK | Ground clear controls. | 52 | 40.11 | 754.21
3374 | TIN-INTERP | Interpolated Ground | 21459.36 | -4.84 | 723.59 | 0 | 19.27 | 0 | OK | Ground clear controls. | 52 | 40.11 | 742.86
3375 | TIN-INTERP | Interpolated Ground | 21499.29 | -4.14 | 721.56 | 0 | 32.07 | 0 | OK | Ground clear controls. | 52 | 40.11 | 753.63
3376 | TIN-INTERP | Interpolated Ground | 21499.32 | -6.22 | 721.52 | 0 | 25.73 | 0 | OK | Ground clear controls. | 52 | 40.11 | 747.25
3377 | TIN-INTERP | Interpolated Ground | 21499.34 | 7.16 | 721.44 | 0 | 20.15 | 0 | OK | Ground clear controls. | 52 | 40.11 | 741.59
3378 | TIN-INTERP | Interpolated Ground | 21499.34 | 8.65 | 721.33 | 0 | 25.9 | 0 | OK | Ground clear controls. | 52 | 40.11 | 747.23
3379 | TIN-INTERP | Interpolated Ground | 21499.35 | 6.53 | 721.49 | 0 | 31.81 | 0 | OK | Ground clear controls. | 52 | 40.11 | 753.3
3380 | TIN-INTERP | Interpolated Ground | 21499.36 | -4.8 | 721.55 | 0 | 20.28 | 0 | OK | Ground clear controls. | 52 | 40.11 | 741.83
3381 | TIN-INTERP | Interpolated Ground | 21539.29 | -4.07 | 721.16 | 0 | 32.48 | 0 | OK | Ground clear controls. | 52 | 40.11 | 753.64
3382 | TIN-INTERP | Interpolated Ground | 21539.32 | -6.17 | 720.92 | 0 | 26.3 | 0 | OK | Ground clear controls. | 52 | 40.11 | 747.22
3383 | TIN-INTERP | Interpolated Ground | 21539.34 | 7.45 | 721.41 | 0 | 20.13 | 0 | OK | Ground clear controls. | 52 | 40.11 | 741.54
3384 | TIN-INTERP | Interpolated Ground | 21539.34 | 8.94 | 721.34 | 0 | 25.87 | 0 | OK | Ground clear controls. | 52 | 40.11 | 747.21
3385 | TIN-INTERP | Interpolated Ground | 21539.35 | 6.8 | 721.42 | 0 | 31.92 | 0 | OK | Ground clear controls. | 52 | 40.11 | 753.34
3386 | TIN-INTERP | Interpolated Ground | 21539.36 | -4.76 | 721.11 | 0 | 20.63 | 0 | OK | Ground clear controls. | 52 | 40.11 | 741.74
3387 | TIN-INTERP | Interpolated Ground | 21579.29 | -4.01 | 719.78 | 0 | 34.8 | 0 | OK | Ground clear controls. | 52 | 40.11 | 754.58
3388 | TIN-INTERP | Interpolated Ground | 21579.32 | -6.11 | 719.74 | 0 | 28.42 | 0 | OK | Ground clear controls. | 52 | 40.11 | 748.16
3389 | TIN-INTERP | Interpolated Ground | 21579.34 | 7.73 | 720.14 | 0 | 22.31 | 0 | OK | Ground clear controls. | 52 | 40.11 | 742.45
3390 | TIN-INTERP | Interpolated Ground | 21579.34 | 9.22 | 720.16 | 0 | 28 | 0 | OK | Ground clear controls. | 52 | 40.11 | 748.16
3391 | TIN-INTERP | Interpolated Ground | 21579.35 | 7.07 | 720.13 | 0 | 34.2 | 0 | OK | Ground clear controls. | 52 | 40.11 | 754.33
3392 | TIN-INTERP | Interpolated Ground | 21579.36 | -4.72 | 719.75 | 0 | 22.83 | 0 | OK | Ground clear controls. | 52 | 40.11 | 742.58
3393 | TIN-INTERP | Interpolated Ground | 21619.29 | -3.95 | 718.96 | 0 | 37.5 | 0 | OK | Ground clear controls. | 52 | 40.11 | 756.46
3394 | TIN-INTERP | Interpolated Ground | 21619.32 | -6.06 | 719.01 | 0 | 31.04 | 0 | OK | Ground clear controls. | 52 | 40.11 | 750.05
3395 | TIN-INTERP | Interpolated Ground | 21619.33 | 8.02 | 719.48 | 0 | 24.84 | 0 | OK | Ground clear controls. | 52 | 40.11 | 744.32
3396 | TIN-INTERP | Interpolated Ground | 21619.33 | 9.51 | 719.56 | 0 | 30.5 | 0 | OK | Ground clear controls. | 52 | 40.11 | 750.06
3397 | TIN-INTERP | Interpolated Ground | 21619.35 | 7.34 | 719.46 | 0 | 36.81 | 0 | OK | Ground clear controls. | 52 | 40.11 | 756.27
3398 | TIN-INTERP | Interpolated Ground | 21619.36 | -4.69 | 718.98 | 0 | 25.39 | 0 | OK | Ground clear controls. | 52 | 40.11 | 744.37
3399 | TIN-INTERP | Interpolated Ground | 21659.29 | -3.89 | 719.16 | 0 | 40.11 | 0 | OK | Ground clear controls. | 52 | 40.11 | 759.27
3400 | TIN-INTERP | Interpolated Ground | 21659.32 | -6.01 | 719.09 | 0 | 33.8 | 0 | OK | Ground clear controls. | 52 | 40.09 | 752.89
3401 | TIN-INTERP | Interpolated Ground | 21659.33 | 8.3 | 719.07 | 0 | 28.08 | 0 | OK | Ground clear controls. | 52 | 40.09 | 747.15
3402 | TIN-INTERP | Interpolated Ground | 21659.33 | 9.79 | 719.06 | 0 | 33.87 | 0 | OK | Ground clear controls. | 52 | 40.09 | 752.93
3403 | TIN-INTERP | Interpolated Ground | 21659.35 | 7.61 | 719.09 | 0 | 40.09 | 0 | OK | Ground clear controls. | 52 | 40.09 | 759.18
3404 | TIN-INTERP | Interpolated Ground | 21659.36 | -4.65 | 719.11 | 0 | 27.98 | 0 | OK | Ground clear controls. | 52 | 27.98 | 747.09
3405 | TIN-INTERP | Interpolated Ground | 21688.07 | -6.05 | 722.3 | 0 | 33.32 | 0 | OK | Ground clear controls. | 53 | 39.76 | 755.62
3406 | TIN-INTERP | Interpolated Ground | 21688.07 | -4.67 | 722.27 | 0 | 27.42 | 0 | OK | Ground clear controls. | 53 | 39.76 | 749.69
3407 | TIN-INTERP | Interpolated Ground | 21688.07 | -3.89 | 722.16 | 0 | 39.76 | 0 | OK | Ground clear controls. | 53 | 39.76 | 761.92
3408 | TIN-INTERP | Interpolated Ground | 21689.29 | 7.78 | 722.06 | 0 | 39.67 | 0 | OK | Ground clear controls. | 53 | 39.67 | 761.73
3409 | TIN-INTERP | Interpolated Ground | 21689.42 | 8.48 | 722.06 | 0 | 27.58 | 0 | OK | Ground clear controls. | 53 | 37.87 | 749.64
3410 | TIN-INTERP | Interpolated Ground | 21689.68 | 9.95 | 722.08 | 0 | 33.36 | 0 | OK | Ground clear controls. | 53 | 37.87 | 755.44
3411 | TIN-INTERP | Interpolated Ground | 21727.2 | -6.03 | 720.31 | 0 | 29.67 | 0 | OK | Ground clear controls. | 53 | 37.87 | 749.98
3412 | TIN-INTERP | Interpolated Ground | 21727.39 | -4.66 | 720.21 | 0 | 23.99 | 0 | OK | Ground clear controls. | 53 | 37.87 | 744.2
3413 | TIN-INTERP | Interpolated Ground | 21727.5 | -3.9 | 720.14 | 0 | 36.22 | 0 | OK | Ground clear controls. | 53 | 37.87 | 756.36
3414 | TIN-INTERP | Interpolated Ground | 21729.29 | 7.55 | 719.68 | 0 | 36.44 | 0 | OK | Ground clear controls. | 53 | 37.87 | 756.12
3415 | TIN-INTERP | Interpolated Ground | 21729.42 | 8.23 | 719.74 | 0 | 24.37 | 0 | OK | Ground clear controls. | 53 | 37.87 | 744.11
3416 | TIN-INTERP | Interpolated Ground | 21729.68 | 9.7 | 719.87 | 0 | 30.04 | 0 | OK | Ground clear controls. | 53 | 37.87 | 749.91
3417 | TIN-INTERP | Interpolated Ground | 21767.2 | -6.08 | 718.31 | 0 | 26.99 | 0 | OK | Ground clear controls. | 53 | 37.87 | 745.3
3418 | TIN-INTERP | Interpolated Ground | 21767.39 | -4.7 | 718.28 | 0 | 21.36 | 0 | OK | Ground clear controls. | 53 | 37.87 | 739.64
3419 | TIN-INTERP | Interpolated Ground | 21767.5 | -3.96 | 718.26 | 0 | 33.46 | 0 | OK | Ground clear controls. | 53 | 37.87 | 751.72
3420 | TIN-INTERP | Interpolated Ground | 21769.28 | 7.31 | 718.4 | 0 | 33.03 | 0 | OK | Ground clear controls. | 53 | 37.87 | 751.43
3421 | TIN-INTERP | Interpolated Ground | 21769.42 | 7.98 | 718.42 | 0 | 21.1 | 0 | OK | Ground clear controls. | 53 | 37.87 | 739.52
3422 | TIN-INTERP | Interpolated Ground | 21769.68 | 9.46 | 718.37 | 0 | 26.94 | 0 | OK | Ground clear controls. | 53 | 37.87 | 745.31
3423 | TIN-INTERP | Interpolated Ground | 21807.2 | -6.13 | 718.31 | 0 | 23.26 | 0 | OK | Ground clear controls. | 53 | 37.87 | 741.57
3424 | TIN-INTERP | Interpolated Ground | 21807.39 | -4.74 | 718.39 | 0 | 17.63 | 0 | OK | Ground clear controls. | 53 | 37.87 | 736.02
3425 | TIN-INTERP | Interpolated Ground | 21807.5 | -4.02 | 718.43 | 0 | 29.6 | 0 | OK | Ground clear controls. | 53 | 37.87 | 748.03
3426 | TIN-INTERP | Interpolated Ground | 21809.28 | 7.07 | 718.96 | 0 | 28.76 | 0 | OK | Ground clear controls. | 53 | 37.87 | 747.72
3427 | TIN-INTERP | Interpolated Ground | 21809.42 | 7.73 | 719.01 | 0 | 16.87 | 0 | OK | Ground clear controls. | 53 | 37.87 | 735.88
3428 | TIN-INTERP | Interpolated Ground | 21809.68 | 9.21 | 719.16 | 0 | 22.51 | 0 | OK | Ground clear controls. | 53 | 37.87 | 741.67
3429 | TIN-INTERP | Interpolated Ground | 21847.2 | -6.18 | 715.32 | 0 | 23.49 | 0 | OK | Ground clear controls. | 53 | 37.87 | 738.81
3430 | TIN-INTERP | Interpolated Ground | 21847.39 | -4.77 | 715.48 | 0 | 17.87 | 0 | OK | Ground clear controls. | 53 | 37.87 | 733.35
3431 | TIN-INTERP | Interpolated Ground | 21847.5 | -4.08 | 715.53 | 0 | 29.74 | 0 | OK | Ground clear controls. | 53 | 37.87 | 745.27
3432 | TIN-INTERP | Interpolated Ground | 21849.28 | 6.84 | 716.42 | 0 | 28.53 | 0 | OK | Ground clear controls. | 53 | 37.87 | 744.95
3433 | TIN-INTERP | Interpolated Ground | 21849.41 | 7.48 | 716.47 | 0 | 16.72 | 0 | OK | Ground clear controls. | 53 | 37.87 | 733.19
3434 | TIN-INTERP | Interpolated Ground | 21849.68 | 8.96 | 716.57 | 0 | 22.4 | 0 | OK | Ground clear controls. | 53 | 37.87 | 738.97
3435 | TIN-INTERP | Interpolated Ground | 21887.2 | -6.22 | 714 | 0 | 22.99 | 0 | OK | Ground clear controls. | 53 | 37.87 | 736.99
3436 | TIN-INTERP | Interpolated Ground | 21887.39 | -4.81 | 714.03 | 0 | 17.57 | 0 | OK | Ground clear controls. | 53 | 37.87 | 731.6
3437 | TIN-INTERP | Interpolated Ground | 21887.5 | -4.14 | 714.03 | 0 | 29.41 | 0 | OK | Ground clear controls. | 53 | 37.87 | 743.44
3438 | TIN-INTERP | Interpolated Ground | 21889.28 | 6.6 | 714.43 | 0 | 28.68 | 0 | OK | Ground clear controls. | 53 | 37.87 | 743.11
3439 | TIN-INTERP | Interpolated Ground | 21889.41 | 7.23 | 714.47 | 0 | 16.99 | 0 | OK | Ground clear controls. | 53 | 37.87 | 731.46
3440 | TIN-INTERP | Interpolated Ground | 21889.68 | 8.71 | 714.54 | 0 | 22.68 | 0 | OK | Ground clear controls. | 53 | 37.87 | 737.22
3441 | TIN-INTERP | Interpolated Ground | 21927.2 | -6.27 | 715.07 | 0 | 21.07 | 0 | OK | Ground clear controls. | 53 | 37.87 | 736.14
3442 | TIN-INTERP | Interpolated Ground | 21927.39 | -4.85 | 714.94 | 0 | 15.87 | 0 | OK | Ground clear controls. | 53 | 37.87 | 730.81
3443 | TIN-INTERP | Interpolated Ground | 21927.5 | -4.19 | 714.93 | 0 | 27.63 | 0 | OK | Ground clear controls. | 53 | 37.87 | 742.56
3444 | TIN-INTERP | Interpolated Ground | 21929.28 | 6.36 | 715.15 | 0 | 27.11 | 0 | OK | Ground clear controls. | 53 | 37.87 | 742.26
3445 | TIN-INTERP | Interpolated Ground | 21929.41 | 6.97 | 715.17 | 0 | 15.51 | 0 | OK | Ground clear controls. | 53 | 37.87 | 730.68
3446 | TIN-INTERP | Interpolated Ground | 21929.67 | 8.46 | 715.15 | 0 | 21.27 | 0 | OK | Ground clear controls. | 53 | 37.87 | 736.42
3447 | TIN-INTERP | Interpolated Ground | 21967.2 | -6.32 | 715.5 | 0 | 20.74 | 0 | OK | Ground clear controls. | 53 | 37.87 | 736.24
3448 | TIN-INTERP | Interpolated Ground | 21967.39 | -4.89 | 715.48 | 0 | 15.46 | 0 | OK | Ground clear controls. | 53 | 37.87 | 730.94
3449 | TIN-INTERP | Interpolated Ground | 21967.5 | -4.25 | 715.46 | 0 | 27.15 | 0 | OK | Ground clear controls. | 53 | 37.87 | 742.61
3450 | TIN-INTERP | Interpolated Ground | 21969.28 | 6.13 | 715.77 | 0 | 26.56 | 0 | OK | Ground clear controls. | 53 | 37.87 | 742.33
3451 | TIN-INTERP | Interpolated Ground | 21969.41 | 6.72 | 715.81 | 0 | 15.02 | 0 | OK | Ground clear controls. | 53 | 37.87 | 730.83
3452 | TIN-INTERP | Interpolated Ground | 21969.67 | 8.21 | 715.85 | 0 | 20.71 | 0 | OK | Ground clear controls. | 53 | 37.87 | 736.56
3453 | TIN-INTERP | Interpolated Ground | 22007.2 | -6.37 | 717.69 | 0 | 19.59 | 0 | OK | Ground clear controls. | 53 | 37.87 | 737.28
3454 | TIN-INTERP | Interpolated Ground | 22007.39 | -4.93 | 717.59 | 0 | 14.41 | 0 | OK | Ground clear controls. | 53 | 37.87 | 732
3455 | TIN-INTERP | Interpolated Ground | 22007.5 | -4.31 | 717.67 | 0 | 25.9 | 0 | OK | Ground clear controls. | 53 | 37.87 | 743.57
3456 | TIN-INTERP | Interpolated Ground | 22009.28 | 5.89 | 718.69 | 0 | 24.66 | 0 | OK | Ground clear controls. | 53 | 37.87 | 743.35
3457 | TIN-INTERP | Interpolated Ground | 22009.41 | 6.47 | 718.8 | 0 | 13.13 | 0 | OK | Ground clear controls. | 53 | 37.87 | 731.93
3458 | TIN-INTERP | Interpolated Ground | 22009.67 | 7.96 | 719 | 0 | 18.64 | 0 | OK | Ground clear controls. | 53 | 37.87 | 737.64
3459 | TIN-INTERP | Interpolated Ground | 22047.2 | -6.42 | 718.42 | 0 | 20.86 | 0 | OK | Ground clear controls. | 53 | 37.87 | 739.28
3460 | TIN-INTERP | Interpolated Ground | 22047.39 | -4.96 | 718.45 | 0 | 15.57 | 0 | OK | Ground clear controls. | 53 | 37.87 | 734.02
3461 | TIN-INTERP | Interpolated Ground | 22047.5 | -4.37 | 718.47 | 0 | 27.02 | 0 | OK | Ground clear controls. | 53 | 37.87 | 745.49
3462 | TIN-INTERP | Interpolated Ground | 22049.28 | 5.65 | 718.57 | 0 | 26.76 | 0 | OK | Ground clear controls. | 53 | 37.87 | 745.33
3463 | TIN-INTERP | Interpolated Ground | 22049.41 | 6.22 | 718.57 | 0 | 15.42 | 0 | OK | Ground clear controls. | 53 | 37.87 | 733.99
3464 | TIN-INTERP | Interpolated Ground | 22049.67 | 7.71 | 718.62 | 0 | 21.06 | 0 | OK | Ground clear controls. | 53 | 37.87 | 739.68
3465 | TIN-INTERP | Interpolated Ground | 22087.2 | -6.46 | 718.94 | 0 | 23.3 | 0 | OK | Ground clear controls. | 53 | 37.87 | 742.24
3466 | TIN-INTERP | Interpolated Ground | 22087.39 | -5 | 718.95 | 0 | 18.01 | 0 | OK | Ground clear controls. | 53 | 37.87 | 736.96
3467 | TIN-INTERP | Interpolated Ground | 22087.5 | -4.43 | 718.97 | 0 | 29.37 | 0 | OK | Ground clear controls. | 53 | 37.87 | 748.34
3468 | TIN-INTERP | Interpolated Ground | 22089.28 | 5.42 | 719.06 | 0 | 29.19 | 0 | OK | Ground clear controls. | 53 | 37.87 | 748.25
3469 | TIN-INTERP | Interpolated Ground | 22089.41 | 5.97 | 719.05 | 0 | 17.95 | 0 | OK | Ground clear controls. | 53 | 37.87 | 737
3470 | TIN-INTERP | Interpolated Ground | 22089.67 | 7.46 | 718.99 | 0 | 23.66 | 0 | OK | Ground clear controls. | 53 | 37.87 | 742.65
3471 | TIN-INTERP | Interpolated Ground | 22127.2 | -6.51 | 719.93 | 0 | 26.22 | 0 | OK | Ground clear controls. | 53 | 37.87 | 746.15
3472 | TIN-INTERP | Interpolated Ground | 22127.39 | -5.04 | 720 | 0 | 20.84 | 0 | OK | Ground clear controls. | 53 | 37.87 | 740.84
3473 | TIN-INTERP | Interpolated Ground | 22127.5 | -4.49 | 720 | 0 | 32.12 | 0 | OK | Ground clear controls. | 53 | 37.87 | 752.12
3474 | TIN-INTERP | Interpolated Ground | 22129.28 | 5.18 | 719.86 | 0 | 32.27 | 0 | OK | Ground clear controls. | 53 | 37.87 | 752.13
3475 | TIN-INTERP | Interpolated Ground | 22129.41 | 5.72 | 719.88 | 0 | 21.08 | 0 | OK | Ground clear controls. | 53 | 37.87 | 740.96
3476 | TIN-INTERP | Interpolated Ground | 22129.67 | 7.21 | 719.94 | 0 | 26.65 | 0 | OK | Ground clear controls. | 53 | 37.87 | 746.59
3477 | TIN-INTERP | Interpolated Ground | 22167.2 | -6.56 | 721.25 | 0 | 29.79 | 0 | OK | Ground clear controls. | 53 | 37.87 | 751.04
3478 | TIN-INTERP | Interpolated Ground | 22167.39 | -5.08 | 721.39 | 0 | 24.29 | 0 | OK | Ground clear controls. | 53 | 37.87 | 745.68
3479 | TIN-INTERP | Interpolated Ground | 22167.5 | -4.54 | 721.44 | 0 | 35.41 | 0 | OK | Ground clear controls. | 53 | 37.87 | 756.85
3480 | TIN-INTERP | Interpolated Ground | 22169.28 | 4.95 | 721.57 | 0 | 35.39 | 0 | OK | Ground clear controls. | 53 | 37.87 | 756.96
3481 | TIN-INTERP | Interpolated Ground | 22169.41 | 5.47 | 721.59 | 0 | 24.27 | 0 | OK | Ground clear controls. | 53 | 37.87 | 745.86
3482 | TIN-INTERP | Interpolated Ground | 22169.67 | 6.96 | 721.72 | 0 | 29.74 | 0 | OK | Ground clear controls. | 53 | 37.87 | 751.46
3483 | TIN-INTERP | Interpolated Ground | 22207.2 | -6.61 | 724.34 | 0 | 32.52 | 0 | OK | Ground clear controls. | 53 | 37.87 | 756.86
3484 | TIN-INTERP | Interpolated Ground | 22207.39 | -5.12 | 724.55 | 0 | 26.89 | 0 | OK | Ground clear controls. | 53 | 37.87 | 751.44
3485 | TIN-INTERP | Interpolated Ground | 22207.5 | -4.6 | 724.63 | 0 | 37.87 | 0 | OK | Ground clear controls. | 53 | 37.87 | 762.5
3486 | TIN-INTERP | Interpolated Ground | 22209.28 | 4.71 | 725.52 | 0 | 37.22 | 0 | OK | Ground clear controls. | 53 | 37.22 | 762.74
3487 | TIN-INTERP | Interpolated Ground | 22209.41 | 5.22 | 725.54 | 0 | 26.19 | 0 | OK | Ground clear controls. | 53 | 31.76 | 751.73
3488 | TIN-INTERP | Interpolated Ground | 22209.67 | 6.71 | 725.53 | 0 | 31.76 | 0 | OK | Ground clear controls. | 53 | 31.76 | 757.29
3489 | TIN-INTERP | Interpolated Ground | 22226.42 | -5.13 | 726.09 | 0 | 28.43 | 0 | OK | Ground clear controls. | 54 | 40.86 | 754.52
3490 | TIN-INTERP | Interpolated Ground | 22226.48 | 5.11 | 726.54 | 0 | 27.98 | 0 | OK | Ground clear controls. | 54 | 40.86 | 754.52
3491 | TIN-INTERP | Interpolated Ground | 22226.49 | -4.63 | 726.17 | 0 | 39.35 | 0 | OK | Ground clear controls. | 54 | 40.86 | 765.52
3492 | TIN-INTERP | Interpolated Ground | 22226.5 | -6.63 | 725.8 | 0 | 34.22 | 0 | OK | Ground clear controls. | 54 | 40.86 | 760.02
3493 | TIN-INTERP | Interpolated Ground | 22226.51 | 4.61 | 726.45 | 0 | 39.08 | 0 | OK | Ground clear controls. | 54 | 40.86 | 765.53
3494 | TIN-INTERP | Interpolated Ground | 22226.51 | 6.61 | 726.72 | 0 | 33.3 | 0 | OK | Ground clear controls. | 54 | 40.86 | 760.02
3495 | TIN-INTERP | Interpolated Ground | 22266.42 | -5.14 | 725.91 | 0 | 23.69 | 0 | OK | Ground clear controls. | 54 | 40.86 | 749.6
3496 | TIN-INTERP | Interpolated Ground | 22266.48 | 5.1 | 726.52 | 0 | 23.06 | 0 | OK | Ground clear controls. | 54 | 40.86 | 749.58
3497 | TIN-INTERP | Interpolated Ground | 22266.49 | -4.63 | 725.91 | 0 | 34.75 | 0 | OK | Ground clear controls. | 54 | 40.86 | 760.66
3498 | TIN-INTERP | Interpolated Ground | 22266.5 | -6.63 | 725.9 | 0 | 29.16 | 0 | OK | Ground clear controls. | 54 | 40.86 | 755.06
3499 | TIN-INTERP | Interpolated Ground | 22266.51 | 4.6 | 726.5 | 0 | 34.09 | 0 | OK | Ground clear controls. | 54 | 40.86 | 760.59
3500 | TIN-INTERP | Interpolated Ground | 22266.51 | 6.6 | 726.51 | 0 | 28.6 | 0 | OK | Ground clear controls. | 54 | 40.86 | 755.11
3501 | TIN-INTERP | Interpolated Ground | 22306.42 | -5.14 | 722.9 | 0 | 22.72 | 0 | OK | Ground clear controls. | 54 | 40.86 | 745.62
3502 | TIN-INTERP | Interpolated Ground | 22306.48 | 5.1 | 723.28 | 0 | 22.3 | 0 | OK | Ground clear controls. | 54 | 40.86 | 745.58
3503 | TIN-INTERP | Interpolated Ground | 22306.49 | -4.63 | 722.99 | 0 | 33.75 | 0 | OK | Ground clear controls. | 54 | 40.86 | 756.74
3504 | TIN-INTERP | Interpolated Ground | 22306.5 | -6.64 | 722.63 | 0 | 28.42 | 0 | OK | Ground clear controls. | 54 | 40.86 | 751.05
3505 | TIN-INTERP | Interpolated Ground | 22306.51 | 4.6 | 723.27 | 0 | 33.34 | 0 | OK | Ground clear controls. | 54 | 40.86 | 756.61
3506 | TIN-INTERP | Interpolated Ground | 22306.51 | 6.6 | 723.32 | 0 | 27.82 | 0 | OK | Ground clear controls. | 54 | 40.86 | 751.14
3507 | TIN-INTERP | Interpolated Ground | 22346.42 | -5.14 | 724.32 | 0 | 18.26 | 0 | OK | Ground clear controls. | 54 | 40.86 | 742.58
3508 | TIN-INTERP | Interpolated Ground | 22346.48 | 5.09 | 724.47 | 0 | 18.06 | 0 | OK | Ground clear controls. | 54 | 40.86 | 742.53
3509 | TIN-INTERP | Interpolated Ground | 22346.49 | -4.64 | 724.32 | 0 | 29.41 | 0 | OK | Ground clear controls. | 54 | 40.86 | 753.73
3510 | TIN-INTERP | Interpolated Ground | 22346.5 | -6.64 | 724.34 | 0 | 23.64 | 0 | OK | Ground clear controls. | 54 | 40.86 | 747.98
3511 | TIN-INTERP | Interpolated Ground | 22346.51 | 4.59 | 724.48 | 0 | 29.08 | 0 | OK | Ground clear controls. | 54 | 40.86 | 753.56
3512 | TIN-INTERP | Interpolated Ground | 22346.51 | 6.59 | 724.36 | 0 | 23.75 | 0 | OK | Ground clear controls. | 54 | 40.86 | 748.11
3513 | TIN-INTERP | Interpolated Ground | 22386.42 | -5.14 | 724.92 | 0 | 15.56 | 0 | OK | Ground clear controls. | 54 | 40.86 | 740.48
3514 | TIN-INTERP | Interpolated Ground | 22386.48 | 5.09 | 725.16 | 0 | 15.25 | 0 | OK | Ground clear controls. | 54 | 40.86 | 740.41
3515 | TIN-INTERP | Interpolated Ground | 22386.49 | -4.64 | 724.94 | 0 | 26.72 | 0 | OK | Ground clear controls. | 54 | 40.86 | 751.66
3516 | TIN-INTERP | Interpolated Ground | 22386.5 | -6.64 | 724.86 | 0 | 21 | 0 | OK | Ground clear controls. | 54 | 40.86 | 745.86
3517 | TIN-INTERP | Interpolated Ground | 22386.51 | 4.59 | 725.13 | 0 | 26.33 | 0 | OK | Ground clear controls. | 54 | 40.86 | 751.46
3518 | TIN-INTERP | Interpolated Ground | 22386.51 | 6.59 | 725.23 | 0 | 20.78 | 0 | OK | Ground clear controls. | 54 | 40.86 | 746.01
3519 | TIN-INTERP | Interpolated Ground | 22426.42 | -5.14 | 726 | 0 | 13.32 | 0 | OK | Ground clear controls. | 54 | 40.86 | 739.32
3520 | TIN-INTERP | Interpolated Ground | 22426.48 | 5.08 | 726.23 | 0 | 13.01 | 0 | OK | Ground clear controls. | 54 | 40.86 | 739.24
3521 | TIN-INTERP | Interpolated Ground | 22426.49 | -4.64 | 725.92 | 0 | 24.6 | 0 | OK | Ground clear controls. | 54 | 40.86 | 750.52
3522 | TIN-INTERP | Interpolated Ground | 22426.5 | -6.64 | 726.19 | 0 | 18.49 | 0 | OK | Ground clear controls. | 54 | 40.86 | 744.68
3523 | TIN-INTERP | Interpolated Ground | 22426.51 | 4.58 | 726.23 | 0 | 24.06 | 0 | OK | Ground clear controls. | 54 | 40.86 | 750.29
3524 | TIN-INTERP | Interpolated Ground | 22426.51 | 6.58 | 726.3 | 0 | 18.56 | 0 | OK | Ground clear controls. | 54 | 40.86 | 744.86
3525 | TIN-INTERP | Interpolated Ground | 22466.42 | -5.15 | 726.69 | 0 | 12.41 | 0 | OK | Ground clear controls. | 54 | 40.86 | 739.1
3526 | TIN-INTERP | Interpolated Ground | 22466.48 | 5.08 | 726.99 | 0 | 12.03 | 0 | OK | Ground clear controls. | 54 | 40.86 | 739.02
3527 | TIN-INTERP | Interpolated Ground | 22466.49 | -4.64 | 726.66 | 0 | 23.65 | 0 | OK | Ground clear controls. | 54 | 40.86 | 750.31
3528 | TIN-INTERP | Interpolated Ground | 22466.5 | -6.64 | 726.69 | 0 | 17.77 | 0 | OK | Ground clear controls. | 54 | 40.86 | 744.46
3529 | TIN-INTERP | Interpolated Ground | 22466.51 | 4.58 | 726.98 | 0 | 23.09 | 0 | OK | Ground clear controls. | 54 | 40.86 | 750.07
3530 | TIN-INTERP | Interpolated Ground | 22466.51 | 6.58 | 727.09 | 0 | 17.55 | 0 | OK | Ground clear controls. | 54 | 40.86 | 744.64
3531 | TIN-INTERP | Interpolated Ground | 22506.42 | -5.15 | 727.49 | 0 | 12.31 | 0 | OK | Ground clear controls. | 54 | 40.86 | 739.8
3532 | TIN-INTERP | Interpolated Ground | 22506.48 | 5.07 | 727.89 | 0 | 11.84 | 0 | OK | Ground clear controls. | 54 | 40.86 | 739.73
3533 | TIN-INTERP | Interpolated Ground | 22506.49 | -4.65 | 727.52 | 0 | 23.5 | 0 | OK | Ground clear controls. | 54 | 40.86 | 751.02
3534 | TIN-INTERP | Interpolated Ground | 22506.5 | -6.65 | 727.5 | 0 | 17.67 | 0 | OK | Ground clear controls. | 54 | 40.86 | 745.17
3535 | TIN-INTERP | Interpolated Ground | 22506.51 | 4.57 | 727.87 | 0 | 22.91 | 0 | OK | Ground clear controls. | 54 | 40.86 | 750.78
3536 | TIN-INTERP | Interpolated Ground | 22506.51 | 6.57 | 728.01 | 0 | 17.34 | 0 | OK | Ground clear controls. | 54 | 40.86 | 745.35
3537 | TIN-INTERP | Interpolated Ground | 22546.42 | -5.15 | 727.78 | 0 | 13.68 | 0 | OK | Ground clear controls. | 54 | 40.86 | 741.46
3538 | TIN-INTERP | Interpolated Ground | 22546.48 | 5.07 | 728.09 | 0 | 13.29 | 0 | OK | Ground clear controls. | 54 | 40.86 | 741.38
3539 | TIN-INTERP | Interpolated Ground | 22546.49 | -4.65 | 727.78 | 0 | 24.87 | 0 | OK | Ground clear controls. | 54 | 40.86 | 752.65
3540 | TIN-INTERP | Interpolated Ground | 22546.5 | -6.65 | 727.76 | 0 | 19.07 | 0 | OK | Ground clear controls. | 54 | 40.86 | 746.83
3541 | TIN-INTERP | Interpolated Ground | 22546.51 | 4.57 | 728.07 | 0 | 24.36 | 0 | OK | Ground clear controls. | 54 | 40.86 | 752.43
3542 | TIN-INTERP | Interpolated Ground | 22546.51 | 6.57 | 728.15 | 0 | 18.84 | 0 | OK | Ground clear controls. | 54 | 40.86 | 746.99
3543 | TIN-INTERP | Interpolated Ground | 22586.42 | -5.15 | 727.96 | 0 | 16.08 | 0 | OK | Ground clear controls. | 54 | 40.86 | 744.04
3544 | TIN-INTERP | Interpolated Ground | 22586.48 | 5.06 | 728.3 | 0 | 15.68 | 0 | OK | Ground clear controls. | 54 | 40.86 | 743.98
3545 | TIN-INTERP | Interpolated Ground | 22586.49 | -4.65 | 727.98 | 0 | 27.23 | 0 | OK | Ground clear controls. | 54 | 40.86 | 755.21
3546 | TIN-INTERP | Interpolated Ground | 22586.5 | -6.65 | 727.99 | 0 | 21.45 | 0 | OK | Ground clear controls. | 54 | 40.86 | 749.44
3547 | TIN-INTERP | Interpolated Ground | 22586.51 | 4.56 | 728.29 | 0 | 26.74 | 0 | OK | Ground clear controls. | 54 | 40.86 | 755.03
3548 | TIN-INTERP | Interpolated Ground | 22586.51 | 6.56 | 728.49 | 0 | 21.09 | 0 | OK | Ground clear controls. | 54 | 40.86 | 749.58
3549 | TIN-INTERP | Interpolated Ground | 22626.42 | -5.15 | 728.24 | 0 | 19.33 | 0 | OK | Ground clear controls. | 54 | 40.86 | 747.57
3550 | TIN-INTERP | Interpolated Ground | 22626.48 | 5.06 | 728.71 | 0 | 18.82 | 0 | OK | Ground clear controls. | 54 | 40.86 | 747.53
3551 | TIN-INTERP | Interpolated Ground | 22626.49 | -4.65 | 728.31 | 0 | 30.4 | 0 | OK | Ground clear controls. | 54 | 40.86 | 758.71
3552 | TIN-INTERP | Interpolated Ground | 22626.5 | -6.65 | 728.21 | 0 | 24.79 | 0 | OK | Ground clear controls. | 54 | 40.86 | 753
3553 | TIN-INTERP | Interpolated Ground | 22626.51 | 4.56 | 728.71 | 0 | 29.85 | 0 | OK | Ground clear controls. | 54 | 40.86 | 758.56
3554 | TIN-INTERP | Interpolated Ground | 22626.51 | 6.56 | 728.76 | 0 | 24.34 | 0 | OK | Ground clear controls. | 54 | 40.86 | 753.1
3555 | TIN-INTERP | Interpolated Ground | 22666.42 | -5.16 | 728.08 | 0 | 23.97 | 0 | OK | Ground clear controls. | 54 | 40.86 | 752.05
3556 | TIN-INTERP | Interpolated Ground | 22666.48 | 5.05 | 728.59 | 0 | 23.42 | 0 | OK | Ground clear controls. | 54 | 40.86 | 752.01
3557 | TIN-INTERP | Interpolated Ground | 22666.49 | -4.65 | 728.13 | 0 | 35 | 0 | OK | Ground clear controls. | 54 | 40.86 | 763.13
3558 | TIN-INTERP | Interpolated Ground | 22666.5 | -6.65 | 728.06 | 0 | 29.44 | 0 | OK | Ground clear controls. | 54 | 40.86 | 757.5
3559 | TIN-INTERP | Interpolated Ground | 22666.51 | 4.55 | 728.53 | 0 | 34.5 | 0 | OK | Ground clear controls. | 54 | 40.86 | 763.03
3560 | TIN-INTERP | Interpolated Ground | 22666.51 | 6.55 | 728.84 | 0 | 28.73 | 0 | OK | Ground clear controls. | 54 | 40.86 | 757.57
3561 | TIN-INTERP | Interpolated Ground | 22706.42 | -5.16 | 727.62 | 0 | 29.84 | 0 | OK | Ground clear controls. | 54 | 40.86 | 757.46
3562 | TIN-INTERP | Interpolated Ground | 22706.48 | 5.05 | 728.3 | 0 | 29.14 | 0 | OK | Ground clear controls. | 54 | 40.86 | 757.44
3563 | TIN-INTERP | Interpolated Ground | 22706.49 | -4.66 | 727.63 | 0 | 40.86 | 0 | OK | Ground clear controls. | 54 | 40.86 | 768.49
3564 | TIN-INTERP | Interpolated Ground | 22706.5 | -6.66 | 727.45 | 0 | 35.51 | 0 | OK | Ground clear controls. | 54 | 40.23 | 762.96
3565 | TIN-INTERP | Interpolated Ground | 22706.51 | 4.54 | 728.23 | 0 | 40.23 | 0 | OK | Ground clear controls. | 54 | 40.23 | 768.46
3566 | TIN-INTERP | Interpolated Ground | 22706.51 | 6.54 | 728.42 | 0 | 34.55 | 0 | OK | Ground clear controls. | 54 | 34.55 | 762.97
3567 | TIN-INTERP | Interpolated Ground | 22721.81 | -6.66 | 727 | 0 | 38.29 | 0 | OK | Ground clear controls. | 55 | 43.9 | 765.29
3568 | TIN-INTERP | Interpolated Ground | 22721.81 | -4.66 | 726.89 | 0 | 43.9 | 0 | OK | Ground clear controls. | 55 | 43.9 | 770.79
3569 | TIN-INTERP | Interpolated Ground | 22721.83 | -5.16 | 726.96 | 0 | 32.83 | 0 | OK | Ground clear controls. | 55 | 43.73 | 759.79
3570 | TIN-INTERP | Interpolated Ground | 22721.85 | 6.54 | 727.33 | 0 | 37.96 | 0 | OK | Ground clear controls. | 55 | 43.73 | 765.29
3571 | TIN-INTERP | Interpolated Ground | 22721.85 | 4.54 | 727.06 | 0 | 43.73 | 0 | OK | Ground clear controls. | 55 | 43.73 | 770.79
3572 | TIN-INTERP | Interpolated Ground | 22721.89 | 5.04 | 727.09 | 0 | 32.7 | 0 | OK | Ground clear controls. | 55 | 38.51 | 759.79
3573 | TIN-INTERP | Interpolated Ground | 22761.82 | -6.65 | 725.86 | 0 | 32.96 | 0 | OK | Ground clear controls. | 55 | 38.51 | 758.82
3574 | TIN-INTERP | Interpolated Ground | 22761.83 | -4.65 | 725.93 | 0 | 38.51 | 0 | OK | Ground clear controls. | 55 | 38.51 | 764.44
3575 | TIN-INTERP | Interpolated Ground | 22761.84 | -5.15 | 725.87 | 0 | 27.52 | 0 | OK | Ground clear controls. | 55 | 37.83 | 753.39
3576 | TIN-INTERP | Interpolated Ground | 22761.85 | 6.55 | 726.63 | 0 | 32.28 | 0 | OK | Ground clear controls. | 55 | 37.83 | 758.91
3577 | TIN-INTERP | Interpolated Ground | 22761.85 | 4.55 | 726.56 | 0 | 37.83 | 0 | OK | Ground clear controls. | 55 | 37.83 | 764.39
3578 | TIN-INTERP | Interpolated Ground | 22761.89 | 5.05 | 726.56 | 0 | 26.85 | 0 | OK | Ground clear controls. | 55 | 34.09 | 753.41
3579 | TIN-INTERP | Interpolated Ground | 22801.82 | -6.64 | 726.04 | 0 | 27.26 | 0 | OK | Ground clear controls. | 55 | 34.09 | 753.3
3580 | TIN-INTERP | Interpolated Ground | 22801.83 | -4.64 | 726.08 | 0 | 32.93 | 0 | OK | Ground clear controls. | 55 | 34.09 | 759.01
3581 | TIN-INTERP | Interpolated Ground | 22801.84 | -5.14 | 726.06 | 0 | 21.87 | 0 | OK | Ground clear controls. | 55 | 34.09 | 747.93
3582 | TIN-INTERP | Interpolated Ground | 22801.85 | 6.56 | 726.43 | 0 | 27.04 | 0 | OK | Ground clear controls. | 55 | 34.09 | 753.47
3583 | TIN-INTERP | Interpolated Ground | 22801.85 | 4.56 | 726.39 | 0 | 32.54 | 0 | OK | Ground clear controls. | 55 | 34.09 | 758.93
3584 | TIN-INTERP | Interpolated Ground | 22801.89 | 5.06 | 726.39 | 0 | 21.57 | 0 | OK | Ground clear controls. | 55 | 34.09 | 747.96
3585 | TIN-INTERP | Interpolated Ground | 22841.82 | -6.63 | 724.91 | 0 | 23.84 | 0 | OK | Ground clear controls. | 55 | 34.09 | 748.75
3586 | TIN-INTERP | Interpolated Ground | 22841.83 | -4.63 | 724.78 | 0 | 29.75 | 0 | OK | Ground clear controls. | 55 | 34.09 | 754.53
3587 | TIN-INTERP | Interpolated Ground | 22841.84 | -5.13 | 724.83 | 0 | 18.57 | 0 | OK | Ground clear controls. | 55 | 34.09 | 743.4
3588 | TIN-INTERP | Interpolated Ground | 22841.85 | 6.57 | 724.84 | 0 | 24.13 | 0 | OK | Ground clear controls. | 55 | 34.09 | 748.97
3589 | TIN-INTERP | Interpolated Ground | 22841.85 | 4.57 | 724.75 | 0 | 29.67 | 0 | OK | Ground clear controls. | 55 | 34.09 | 754.42
3590 | TIN-INTERP | Interpolated Ground | 22841.89 | 5.07 | 724.74 | 0 | 18.72 | 0 | OK | Ground clear controls. | 55 | 34.09 | 743.46
3591 | TIN-INTERP | Interpolated Ground | 22881.82 | -6.63 | 723.44 | 0 | 21.7 | 0 | OK | Ground clear controls. | 55 | 34.09 | 745.14
3592 | TIN-INTERP | Interpolated Ground | 22881.83 | -4.63 | 723.44 | 0 | 27.55 | 0 | OK | Ground clear controls. | 55 | 34.09 | 750.99
3593 | TIN-INTERP | Interpolated Ground | 22881.84 | -5.13 | 723.38 | 0 | 16.45 | 0 | OK | Ground clear controls. | 55 | 34.09 | 739.83
3594 | TIN-INTERP | Interpolated Ground | 22881.85 | 6.57 | 724.22 | 0 | 21.18 | 0 | OK | Ground clear controls. | 55 | 34.09 | 745.4
3595 | TIN-INTERP | Interpolated Ground | 22881.85 | 4.57 | 724.01 | 0 | 26.85 | 0 | OK | Ground clear controls. | 55 | 34.09 | 750.86
3596 | TIN-INTERP | Interpolated Ground | 22881.89 | 5.07 | 724.05 | 0 | 15.85 | 0 | OK | Ground clear controls. | 55 | 34.09 | 739.9
3597 | TIN-INTERP | Interpolated Ground | 22921.82 | -6.62 | 722.24 | 0 | 20.24 | 0 | OK | Ground clear controls. | 55 | 34.09 | 742.48
3598 | TIN-INTERP | Interpolated Ground | 22921.83 | -4.62 | 722.34 | 0 | 26.02 | 0 | OK | Ground clear controls. | 55 | 34.09 | 748.36
3599 | TIN-INTERP | Interpolated Ground | 22921.84 | -5.12 | 722.28 | 0 | 14.91 | 0 | OK | Ground clear controls. | 55 | 34.09 | 737.19
3600 | TIN-INTERP | Interpolated Ground | 22921.85 | 6.58 | 722.96 | 0 | 19.81 | 0 | OK | Ground clear controls. | 55 | 34.09 | 742.77
3601 | TIN-INTERP | Interpolated Ground | 22921.85 | 4.58 | 722.89 | 0 | 25.33 | 0 | OK | Ground clear controls. | 55 | 34.09 | 748.22
3602 | TIN-INTERP | Interpolated Ground | 22921.89 | 5.08 | 722.89 | 0 | 14.37 | 0 | OK | Ground clear controls. | 55 | 34.09 | 737.26
3603 | TIN-INTERP | Interpolated Ground | 22961.82 | -6.61 | 721.33 | 0 | 19.45 | 0 | OK | Ground clear controls. | 55 | 34.09 | 740.78
3604 | TIN-INTERP | Interpolated Ground | 22961.83 | -4.61 | 721.37 | 0 | 25.31 | 0 | OK | Ground clear controls. | 55 | 34.09 | 746.68
3605 | TIN-INTERP | Interpolated Ground | 22961.84 | -5.11 | 721.33 | 0 | 14.17 | 0 | OK | Ground clear controls. | 55 | 34.09 | 735.5
3606 | TIN-INTERP | Interpolated Ground | 22961.85 | 6.59 | 722.02 | 0 | 19.06 | 0 | OK | Ground clear controls. | 55 | 34.09 | 741.08
3607 | TIN-INTERP | Interpolated Ground | 22961.85 | 4.59 | 722 | 0 | 24.53 | 0 | OK | Ground clear controls. | 55 | 34.09 | 746.53
3608 | TIN-INTERP | Interpolated Ground | 22961.89 | 5.09 | 721.98 | 0 | 13.6 | 0 | OK | Ground clear controls. | 55 | 34.09 | 735.58
3609 | TIN-INTERP | Interpolated Ground | 23001.82 | -6.6 | 720.88 | 0 | 19.14 | 0 | OK | Ground clear controls. | 55 | 34.09 | 740.02
3610 | TIN-INTERP | Interpolated Ground | 23001.83 | -4.6 | 720.93 | 0 | 24.99 | 0 | OK | Ground clear controls. | 55 | 34.09 | 745.92
3611 | TIN-INTERP | Interpolated Ground | 23001.84 | -5.1 | 720.92 | 0 | 13.82 | 0 | OK | Ground clear controls. | 55 | 34.09 | 734.74
3612 | TIN-INTERP | Interpolated Ground | 23001.85 | 6.6 | 720.98 | 0 | 19.35 | 0 | OK | Ground clear controls. | 55 | 34.09 | 740.33
3613 | TIN-INTERP | Interpolated Ground | 23001.85 | 4.6 | 720.9 | 0 | 24.87 | 0 | OK | Ground clear controls. | 55 | 34.09 | 745.77
3614 | TIN-INTERP | Interpolated Ground | 23001.89 | 5.1 | 720.93 | 0 | 13.89 | 0 | OK | Ground clear controls. | 55 | 34.09 | 734.82
3615 | TIN-INTERP | Interpolated Ground | 23041.82 | -6.59 | 720.97 | 0 | 19.23 | 0 | OK | Ground clear controls. | 55 | 34.09 | 740.2
3616 | TIN-INTERP | Interpolated Ground | 23041.83 | -4.59 | 721.02 | 0 | 25.07 | 0 | OK | Ground clear controls. | 55 | 34.09 | 746.09
3617 | TIN-INTERP | Interpolated Ground | 23041.84 | -5.09 | 721.01 | 0 | 13.91 | 0 | OK | Ground clear controls. | 55 | 34.09 | 734.92
3618 | TIN-INTERP | Interpolated Ground | 23041.85 | 6.61 | 721.53 | 0 | 18.97 | 0 | OK | Ground clear controls. | 55 | 34.09 | 740.5
3619 | TIN-INTERP | Interpolated Ground | 23041.85 | 4.61 | 721.53 | 0 | 24.42 | 0 | OK | Ground clear controls. | 55 | 34.09 | 745.95
3620 | TIN-INTERP | Interpolated Ground | 23041.89 | 5.11 | 721.55 | 0 | 13.45 | 0 | OK | Ground clear controls. | 55 | 34.09 | 735
3621 | TIN-INTERP | Interpolated Ground | 23081.82 | -6.59 | 722.6 | 0 | 18.74 | 0 | OK | Ground clear controls. | 55 | 34.09 | 741.34
3622 | TIN-INTERP | Interpolated Ground | 23081.83 | -4.59 | 722.43 | 0 | 24.76 | 0 | OK | Ground clear controls. | 55 | 34.09 | 747.19
3623 | TIN-INTERP | Interpolated Ground | 23081.84 | -5.09 | 722.5 | 0 | 13.54 | 0 | OK | Ground clear controls. | 55 | 34.09 | 736.04
3624 | TIN-INTERP | Interpolated Ground | 23081.85 | 6.61 | 723.14 | 0 | 18.47 | 0 | OK | Ground clear controls. | 55 | 34.09 | 741.61
3625 | TIN-INTERP | Interpolated Ground | 23081.85 | 4.61 | 723.17 | 0 | 23.9 | 0 | OK | Ground clear controls. | 55 | 34.09 | 747.07
3626 | TIN-INTERP | Interpolated Ground | 23081.89 | 5.11 | 723.16 | 0 | 12.94 | 0 | OK | Ground clear controls. | 55 | 34.09 | 736.1
3627 | TIN-INTERP | Interpolated Ground | 23121.82 | -6.58 | 723.28 | 0 | 20.15 | 0 | OK | Ground clear controls. | 55 | 34.09 | 743.43
3628 | TIN-INTERP | Interpolated Ground | 23121.83 | -4.58 | 723.37 | 0 | 25.85 | 0 | OK | Ground clear controls. | 55 | 34.09 | 749.22
3629 | TIN-INTERP | Interpolated Ground | 23121.84 | -5.08 | 723.34 | 0 | 14.75 | 0 | OK | Ground clear controls. | 55 | 34.09 | 738.09
3630 | TIN-INTERP | Interpolated Ground | 23121.85 | 6.62 | 722.86 | 0 | 20.79 | 0 | OK | Ground clear controls. | 55 | 34.09 | 743.65
3631 | TIN-INTERP | Interpolated Ground | 23121.85 | 4.62 | 722.85 | 0 | 26.26 | 0 | OK | Ground clear controls. | 55 | 34.09 | 749.11
3632 | TIN-INTERP | Interpolated Ground | 23121.89 | 5.12 | 722.83 | 0 | 15.32 | 0 | OK | Ground clear controls. | 55 | 34.09 | 738.15
3633 | TIN-INTERP | Interpolated Ground | 23161.82 | -6.57 | 722.17 | 0 | 24.3 | 0 | OK | Ground clear controls. | 55 | 34.09 | 746.47
3634 | TIN-INTERP | Interpolated Ground | 23161.83 | -4.57 | 722.21 | 0 | 29.96 | 0 | OK | Ground clear controls. | 55 | 34.09 | 752.17
3635 | TIN-INTERP | Interpolated Ground | 23161.84 | -5.07 | 722.21 | 0 | 18.88 | 0 | OK | Ground clear controls. | 55 | 34.09 | 741.09
3636 | TIN-INTERP | Interpolated Ground | 23161.85 | 6.63 | 723.35 | 0 | 23.28 | 0 | OK | Ground clear controls. | 55 | 34.09 | 746.63
3637 | TIN-INTERP | Interpolated Ground | 23161.85 | 4.63 | 722.93 | 0 | 29.17 | 0 | OK | Ground clear controls. | 55 | 34.09 | 752.1
3638 | TIN-INTERP | Interpolated Ground | 23161.89 | 5.13 | 723.04 | 0 | 18.09 | 0 | OK | Ground clear controls. | 55 | 34.09 | 741.13
3639 | TIN-INTERP | Interpolated Ground | 23201.82 | -6.56 | 722.03 | 0 | 28.42 | 0 | OK | Ground clear controls. | 55 | 34.09 | 750.45
3640 | TIN-INTERP | Interpolated Ground | 23201.83 | -4.56 | 721.97 | 0 | 34.09 | 0 | OK | Ground clear controls. | 55 | 34.09 | 756.06
3641 | TIN-INTERP | Interpolated Ground | 23201.84 | -5.06 | 721.96 | 0 | 23.05 | 0 | OK | Ground clear controls. | 55 | 33.53 | 745.01
3642 | TIN-INTERP | Interpolated Ground | 23201.85 | 6.64 | 722.61 | 0 | 27.93 | 0 | OK | Ground clear controls. | 55 | 33.53 | 750.54
3643 | TIN-INTERP | Interpolated Ground | 23201.85 | 4.64 | 722.5 | 0 | 33.53 | 0 | OK | Ground clear controls. | 55 | 33.53 | 756.03
3644 | TIN-INTERP | Interpolated Ground | 23201.89 | 5.14 | 722.5 | 0 | 22.54 | 0 | OK | Ground clear controls. | 55 | 22.54 | 745.04
3645 | TIN-INTERP | Interpolated Ground | 23235.56 | -4.56 | 720.89 | 0 | 39.18 | 0 | OK | Ground clear controls. | 56 | 39.18 | 760.07
3646 | TIN-INTERP | Interpolated Ground | 23235.59 | -5.06 | 720.92 | 0 | 28.15 | 0 | OK | Ground clear controls. | 56 | 39 | 749.07
3647 | TIN-INTERP | Interpolated Ground | 23235.59 | 4.64 | 721.07 | 0 | 39 | 0 | OK | Ground clear controls. | 56 | 39 | 760.07
3648 | TIN-INTERP | Interpolated Ground | 23235.62 | 6.64 | 721.09 | 0 | 33.48 | 0 | OK | Ground clear controls. | 56 | 36.74 | 754.57
3649 | TIN-INTERP | Interpolated Ground | 23235.63 | 5.14 | 721.08 | 0 | 27.99 | 0 | OK | Ground clear controls. | 56 | 36.74 | 749.07
3650 | TIN-INTERP | Interpolated Ground | 23235.78 | -6.56 | 721 | 0 | 33.58 | 0 | OK | Ground clear controls. | 56 | 36.74 | 754.58
3651 | TIN-INTERP | Interpolated Ground | 23275.56 | -4.56 | 720.21 | 0 | 35.61 | 0 | OK | Ground clear controls. | 56 | 36.74 | 755.82
3652 | TIN-INTERP | Interpolated Ground | 23275.59 | -5.06 | 720.18 | 0 | 24.6 | 0 | OK | Ground clear controls. | 56 | 36.74 | 744.78
3653 | TIN-INTERP | Interpolated Ground | 23275.59 | 4.64 | 720.58 | 0 | 35.2 | 0 | OK | Ground clear controls. | 56 | 36.74 | 755.78
3654 | TIN-INTERP | Interpolated Ground | 23275.62 | 6.64 | 721.02 | 0 | 29.29 | 0 | OK | Ground clear controls. | 56 | 36.74 | 750.31
3655 | TIN-INTERP | Interpolated Ground | 23275.63 | 5.14 | 720.66 | 0 | 24.15 | 0 | OK | Ground clear controls. | 56 | 36.74 | 744.81
3656 | TIN-INTERP | Interpolated Ground | 23275.78 | -6.57 | 720.15 | 0 | 30.19 | 0 | OK | Ground clear controls. | 56 | 36.74 | 750.34
3657 | TIN-INTERP | Interpolated Ground | 23315.56 | -4.57 | 720.24 | 0 | 32.25 | 0 | OK | Ground clear controls. | 56 | 36.74 | 752.49
3658 | TIN-INTERP | Interpolated Ground | 23315.59 | -5.07 | 720.26 | 0 | 21.16 | 0 | OK | Ground clear controls. | 56 | 36.74 | 741.42
3659 | TIN-INTERP | Interpolated Ground | 23315.59 | 4.63 | 720.6 | 0 | 31.82 | 0 | OK | Ground clear controls. | 56 | 36.74 | 752.42
3660 | TIN-INTERP | Interpolated Ground | 23315.62 | 6.63 | 720.8 | 0 | 26.17 | 0 | OK | Ground clear controls. | 56 | 36.74 | 746.97
3661 | TIN-INTERP | Interpolated Ground | 23315.63 | 5.13 | 720.68 | 0 | 20.8 | 0 | OK | Ground clear controls. | 56 | 36.74 | 741.48
3662 | TIN-INTERP | Interpolated Ground | 23315.78 | -6.57 | 720.27 | 0 | 26.76 | 0 | OK | Ground clear controls. | 56 | 36.74 | 747.03
3663 | TIN-INTERP | Interpolated Ground | 23355.56 | -4.58 | 720.69 | 0 | 29.41 | 0 | OK | Ground clear controls. | 56 | 36.74 | 750.1
3664 | TIN-INTERP | Interpolated Ground | 23355.59 | -5.08 | 720.7 | 0 | 18.31 | 0 | OK | Ground clear controls. | 56 | 36.74 | 739.01
3665 | TIN-INTERP | Interpolated Ground | 23355.59 | 4.62 | 720.71 | 0 | 29.29 | 0 | OK | Ground clear controls. | 56 | 36.74 | 750
3666 | TIN-INTERP | Interpolated Ground | 23355.62 | 6.62 | 720.78 | 0 | 23.79 | 0 | OK | Ground clear controls. | 56 | 36.74 | 744.57
3667 | TIN-INTERP | Interpolated Ground | 23355.63 | 5.12 | 720.72 | 0 | 18.36 | 0 | OK | Ground clear controls. | 56 | 36.74 | 739.08
3668 | TIN-INTERP | Interpolated Ground | 23355.78 | -6.58 | 720.74 | 0 | 23.89 | 0 | OK | Ground clear controls. | 56 | 36.74 | 744.63
3669 | TIN-INTERP | Interpolated Ground | 23395.56 | -4.59 | 721.17 | 0 | 27.45 | 0 | OK | Ground clear controls. | 56 | 36.74 | 748.62
3670 | TIN-INTERP | Interpolated Ground | 23395.59 | -5.09 | 721.13 | 0 | 16.39 | 0 | OK | Ground clear controls. | 56 | 36.74 | 737.52
3671 | TIN-INTERP | Interpolated Ground | 23395.59 | 4.61 | 721.12 | 0 | 27.39 | 0 | OK | Ground clear controls. | 56 | 36.74 | 748.51
3672 | TIN-INTERP | Interpolated Ground | 23395.62 | 6.61 | 721.26 | 0 | 21.84 | 0 | OK | Ground clear controls. | 56 | 36.74 | 743.1
3673 | TIN-INTERP | Interpolated Ground | 23395.63 | 5.11 | 721.06 | 0 | 16.54 | 0 | OK | Ground clear controls. | 56 | 36.74 | 737.6
3674 | TIN-INTERP | Interpolated Ground | 23395.78 | -6.59 | 721 | 0 | 22.16 | 0 | OK | Ground clear controls. | 56 | 36.74 | 743.16
3675 | TIN-INTERP | Interpolated Ground | 23435.56 | -4.6 | 721.15 | 0 | 26.91 | 0 | OK | Ground clear controls. | 56 | 36.74 | 748.06
3676 | TIN-INTERP | Interpolated Ground | 23435.59 | -5.1 | 721.15 | 0 | 15.8 | 0 | OK | Ground clear controls. | 56 | 36.74 | 736.95
3677 | TIN-INTERP | Interpolated Ground | 23435.59 | 4.6 | 721.14 | 0 | 26.8 | 0 | OK | Ground clear controls. | 56 | 36.74 | 747.94
3678 | TIN-INTERP | Interpolated Ground | 23435.62 | 6.6 | 721.22 | 0 | 21.32 | 0 | OK | Ground clear controls. | 56 | 36.74 | 742.54
3679 | TIN-INTERP | Interpolated Ground | 23435.63 | 5.1 | 721.14 | 0 | 15.91 | 0 | OK | Ground clear controls. | 56 | 36.74 | 737.05
3680 | TIN-INTERP | Interpolated Ground | 23435.78 | -6.6 | 721.18 | 0 | 21.44 | 0 | OK | Ground clear controls. | 56 | 36.74 | 742.62
3681 | TIN-INTERP | Interpolated Ground | 23475.56 | -4.61 | 722.29 | 0 | 26.15 | 0 | OK | Ground clear controls. | 56 | 36.74 | 748.44
3682 | TIN-INTERP | Interpolated Ground | 23475.59 | -5.11 | 722.21 | 0 | 15.11 | 0 | OK | Ground clear controls. | 56 | 36.74 | 737.32
3683 | TIN-INTERP | Interpolated Ground | 23475.59 | 4.59 | 723.03 | 0 | 25.28 | 0 | OK | Ground clear controls. | 56 | 36.74 | 748.31
3684 | TIN-INTERP | Interpolated Ground | 23475.62 | 6.59 | 723.09 | 0 | 19.81 | 0 | OK | Ground clear controls. | 56 | 36.74 | 742.9
3685 | TIN-INTERP | Interpolated Ground | 23475.63 | 5.09 | 723.05 | 0 | 14.37 | 0 | OK | Ground clear controls. | 56 | 36.74 | 737.42
3686 | TIN-INTERP | Interpolated Ground | 23475.78 | -6.61 | 722.04 | 0 | 20.95 | 0 | OK | Ground clear controls. | 56 | 36.74 | 742.99
3687 | TIN-INTERP | Interpolated Ground | 23515.56 | -4.62 | 726.38 | 0 | 23.36 | 0 | OK | Ground clear controls. | 56 | 36.74 | 749.74
3688 | TIN-INTERP | Interpolated Ground | 23515.59 | -5.12 | 726.41 | 0 | 12.21 | 0 | OK | Ground clear controls. | 56 | 36.74 | 738.62
3689 | TIN-INTERP | Interpolated Ground | 23515.59 | 4.58 | 726.06 | 0 | 23.55 | 0 | OK | Ground clear controls. | 56 | 36.74 | 749.61
3690 | TIN-INTERP | Interpolated Ground | 23515.62 | 6.58 | 726.26 | 0 | 17.95 | 0 | OK | Ground clear controls. | 56 | 36.74 | 744.21
3691 | TIN-INTERP | Interpolated Ground | 23515.63 | 5.08 | 726.1 | 0 | 12.62 | 0 | OK | Ground clear controls. | 56 | 36.74 | 738.72
3692 | TIN-INTERP | Interpolated Ground | 23515.78 | -6.62 | 726.52 | 0 | 17.78 | 0 | OK | Ground clear controls. | 56 | 36.74 | 744.3
3693 | TIN-INTERP | Interpolated Ground | 23555.56 | -4.63 | 728.11 | 0 | 23.85 | 0 | OK | Ground clear controls. | 56 | 36.74 | 751.96
3694 | TIN-INTERP | Interpolated Ground | 23555.59 | -5.13 | 728.07 | 0 | 12.79 | 0 | OK | Ground clear controls. | 56 | 36.74 | 740.86
3695 | TIN-INTERP | Interpolated Ground | 23555.59 | 4.57 | 728.82 | 0 | 23.02 | 0 | OK | Ground clear controls. | 56 | 36.74 | 751.84
3696 | TIN-INTERP | Interpolated Ground | 23555.62 | 6.57 | 729.1 | 0 | 17.34 | 0 | OK | Ground clear controls. | 56 | 36.74 | 746.44
3697 | TIN-INTERP | Interpolated Ground | 23555.63 | 5.07 | 728.87 | 0 | 12.08 | 0 | OK | Ground clear controls. | 56 | 36.74 | 740.95
3698 | TIN-INTERP | Interpolated Ground | 23555.78 | -6.63 | 727.94 | 0 | 18.58 | 0 | OK | Ground clear controls. | 56 | 36.74 | 746.52
3699 | TIN-INTERP | Interpolated Ground | 23595.56 | -4.64 | 730.77 | 0 | 24.34 | 0 | OK | Ground clear controls. | 56 | 36.74 | 755.11
3700 | TIN-INTERP | Interpolated Ground | 23595.59 | -5.14 | 730.78 | 0 | 13.24 | 0 | OK | Ground clear controls. | 56 | 36.74 | 744.02
3701 | TIN-INTERP | Interpolated Ground | 23595.59 | 4.56 | 730.64 | 0 | 24.37 | 0 | OK | Ground clear controls. | 56 | 36.74 | 755.01
3702 | TIN-INTERP | Interpolated Ground | 23595.62 | 6.56 | 730.63 | 0 | 18.96 | 0 | OK | Ground clear controls. | 56 | 36.74 | 749.59
3703 | TIN-INTERP | Interpolated Ground | 23595.63 | 5.06 | 730.63 | 0 | 13.46 | 0 | OK | Ground clear controls. | 56 | 36.74 | 744.09
3704 | TIN-INTERP | Interpolated Ground | 23595.78 | -6.64 | 730.63 | 0 | 19.04 | 0 | OK | Ground clear controls. | 56 | 36.74 | 749.67
3705 | TIN-INTERP | Interpolated Ground | 23635.56 | -4.65 | 731.15 | 0 | 28.04 | 0 | OK | Ground clear controls. | 56 | 36.74 | 759.19
3706 | TIN-INTERP | Interpolated Ground | 23635.59 | -5.15 | 731.17 | 0 | 16.95 | 0 | OK | Ground clear controls. | 56 | 36.74 | 748.12
3707 | TIN-INTERP | Interpolated Ground | 23635.59 | 4.55 | 731.42 | 0 | 27.68 | 0 | OK | Ground clear controls. | 56 | 36.74 | 759.1
3708 | TIN-INTERP | Interpolated Ground | 23635.62 | 6.55 | 731.63 | 0 | 22.04 | 0 | OK | Ground clear controls. | 56 | 36.74 | 753.67
3709 | TIN-INTERP | Interpolated Ground | 23635.63 | 5.05 | 731.51 | 0 | 16.67 | 0 | OK | Ground clear controls. | 56 | 36.74 | 748.18
3710 | TIN-INTERP | Interpolated Ground | 23635.78 | -6.65 | 731.3 | 0 | 22.45 | 0 | OK | Ground clear controls. | 56 | 36.74 | 753.75
3711 | TIN-INTERP | Interpolated Ground | 23675.56 | -4.66 | 733.38 | 0 | 30.82 | 0 | OK | Ground clear controls. | 56 | 36.74 | 764.2
3712 | TIN-INTERP | Interpolated Ground | 23675.59 | -5.16 | 733.35 | 0 | 19.8 | 0 | OK | Ground clear controls. | 56 | 36.74 | 753.15
3713 | TIN-INTERP | Interpolated Ground | 23675.59 | 4.54 | 733 | 0 | 31.14 | 0 | OK | Ground clear controls. | 56 | 36.74 | 764.14
3714 | TIN-INTERP | Interpolated Ground | 23675.62 | 6.54 | 732.95 | 0 | 25.74 | 0 | OK | Ground clear controls. | 56 | 36.74 | 758.69
3715 | TIN-INTERP | Interpolated Ground | 23675.63 | 5.04 | 733 | 0 | 20.19 | 0 | OK | Ground clear controls. | 56 | 36.74 | 753.19
3716 | TIN-INTERP | Interpolated Ground | 23675.78 | -6.66 | 733.26 | 0 | 25.49 | 0 | OK | Ground clear controls. | 56 | 36.74 | 758.75
3717 | TIN-INTERP | Interpolated Ground | 23715.56 | -4.67 | 733.68 | 0 | 36.45 | 0 | OK | Ground clear controls. | 56 | 36.74 | 770.13
3718 | TIN-INTERP | Interpolated Ground | 23715.59 | -5.17 | 733.7 | 0 | 25.43 | 0 | OK | Ground clear controls. | 56 | 36.74 | 759.13
3719 | TIN-INTERP | Interpolated Ground | 23715.59 | 4.53 | 733.38 | 0 | 36.74 | 0 | OK | Ground clear controls. | 56 | 36.74 | 770.12
3720 | TIN-INTERP | Interpolated Ground | 23715.62 | 6.53 | 733.51 | 0 | 31.12 | 0 | OK | Ground clear controls. | 56 | 31.12 | 764.63
3721 | TIN-INTERP | Interpolated Ground | 23715.63 | 5.03 | 733.39 | 0 | 25.74 | 0 | OK | Ground clear controls. | 56 | 30.9 | 759.13
3722 | TIN-INTERP | Interpolated Ground | 23715.78 | -6.67 | 733.78 | 0 | 30.9 | 0 | OK | Ground clear controls. | 56 | 30.9 | 764.68
3723 | TIN-INTERP | Interpolated Ground | 23723.46 | -6.67 | 733.96 | 0 | 31.96 | 0 | OK | Ground clear controls. | 57 | 37.65 | 765.92
3724 | TIN-INTERP | Interpolated Ground | 23723.53 | -4.67 | 733.97 | 0 | 37.46 | 0 | OK | Ground clear controls. | 57 | 37.65 | 771.43
3725 | TIN-INTERP | Interpolated Ground | 23723.58 | -5.17 | 734 | 0 | 26.43 | 0 | OK | Ground clear controls. | 57 | 37.65 | 760.43
3726 | TIN-INTERP | Interpolated Ground | 23723.59 | 6.53 | 733.87 | 0 | 32.06 | 0 | OK | Ground clear controls. | 57 | 37.65 | 765.93
3727 | TIN-INTERP | Interpolated Ground | 23723.62 | 5.03 | 733.81 | 0 | 26.62 | 0 | OK | Ground clear controls. | 57 | 37.65 | 760.43
3728 | TIN-INTERP | Interpolated Ground | 23723.65 | 4.53 | 733.78 | 0 | 37.65 | 0 | OK | Ground clear controls. | 57 | 37.65 | 771.43
3729 | TIN-INTERP | Interpolated Ground | 23763.47 | -6.66 | 731.38 | 0 | 29.7 | 0 | OK | Ground clear controls. | 57 | 37.03 | 761.08
3730 | TIN-INTERP | Interpolated Ground | 23763.53 | -4.66 | 731.41 | 0 | 35.18 | 0 | OK | Ground clear controls. | 57 | 37.03 | 766.59
3731 | TIN-INTERP | Interpolated Ground | 23763.58 | -5.16 | 731.39 | 0 | 24.2 | 0 | OK | Ground clear controls. | 57 | 37.03 | 755.59
3732 | TIN-INTERP | Interpolated Ground | 23763.59 | 6.54 | 732.61 | 0 | 28.46 | 0 | OK | Ground clear controls. | 57 | 37.03 | 761.07
3733 | TIN-INTERP | Interpolated Ground | 23763.62 | 5.04 | 732.36 | 0 | 23.24 | 0 | OK | Ground clear controls. | 57 | 37.03 | 755.6
3734 | TIN-INTERP | Interpolated Ground | 23763.65 | 4.54 | 732.29 | 0 | 34.3 | 0 | OK | Ground clear controls. | 57 | 37.03 | 766.59
3735 | TIN-INTERP | Interpolated Ground | 23803.47 | -6.66 | 733.49 | 0 | 23.66 | 0 | OK | Ground clear controls. | 57 | 37.03 | 757.15
3736 | TIN-INTERP | Interpolated Ground | 23803.53 | -4.66 | 733.33 | 0 | 29.34 | 0 | OK | Ground clear controls. | 57 | 37.03 | 762.67
3737 | TIN-INTERP | Interpolated Ground | 23803.58 | -5.16 | 733.4 | 0 | 18.28 | 0 | OK | Ground clear controls. | 57 | 37.03 | 751.68
3738 | TIN-INTERP | Interpolated Ground | 23803.59 | 6.54 | 732.49 | 0 | 24.65 | 0 | OK | Ground clear controls. | 57 | 37.03 | 757.14
3739 | TIN-INTERP | Interpolated Ground | 23803.62 | 5.04 | 732.4 | 0 | 19.28 | 0 | OK | Ground clear controls. | 57 | 37.03 | 751.68
3740 | TIN-INTERP | Interpolated Ground | 23803.65 | 4.54 | 732.43 | 0 | 30.24 | 0 | OK | Ground clear controls. | 57 | 37.03 | 762.67
3741 | TIN-INTERP | Interpolated Ground | 23843.47 | -6.65 | 734.22 | 0 | 19.93 | 0 | OK | Ground clear controls. | 57 | 37.03 | 754.15
3742 | TIN-INTERP | Interpolated Ground | 23843.53 | -4.65 | 734.38 | 0 | 25.3 | 0 | OK | Ground clear controls. | 57 | 37.03 | 759.68
3743 | TIN-INTERP | Interpolated Ground | 23843.58 | -5.15 | 734.33 | 0 | 14.36 | 0 | OK | Ground clear controls. | 57 | 37.03 | 748.69
3744 | TIN-INTERP | Interpolated Ground | 23843.59 | 6.55 | 734.14 | 0 | 19.99 | 0 | OK | Ground clear controls. | 57 | 37.03 | 754.13
3745 | TIN-INTERP | Interpolated Ground | 23843.62 | 5.05 | 734.15 | 0 | 14.55 | 0 | OK | Ground clear controls. | 57 | 37.03 | 748.7
3746 | TIN-INTERP | Interpolated Ground | 23843.65 | 4.55 | 734.16 | 0 | 25.51 | 0 | OK | Ground clear controls. | 57 | 37.03 | 759.67
3747 | TIN-INTERP | Interpolated Ground | 23883.47 | -6.65 | 727.37 | 0 | 24.69 | 0 | OK | Ground clear controls. | 57 | 37.03 | 752.06
3748 | TIN-INTERP | Interpolated Ground | 23883.53 | -4.65 | 727.35 | 0 | 30.25 | 0 | OK | Ground clear controls. | 57 | 37.03 | 757.6
3749 | TIN-INTERP | Interpolated Ground | 23883.58 | -5.15 | 727.36 | 0 | 19.25 | 0 | OK | Ground clear controls. | 57 | 37.03 | 746.61
3750 | TIN-INTERP | Interpolated Ground | 23883.59 | 6.55 | 727.86 | 0 | 24.18 | 0 | OK | Ground clear controls. | 57 | 37.03 | 752.04
3751 | TIN-INTERP | Interpolated Ground | 23883.62 | 5.05 | 727.6 | 0 | 19.02 | 0 | OK | Ground clear controls. | 57 | 37.03 | 746.62
3752 | TIN-INTERP | Interpolated Ground | 23883.65 | 4.55 | 727.57 | 0 | 30.02 | 0 | OK | Ground clear controls. | 57 | 37.03 | 757.59
3753 | TIN-INTERP | Interpolated Ground | 23923.47 | -6.64 | 731.24 | 0 | 19.68 | 0 | OK | Ground clear controls. | 57 | 37.03 | 750.92
3754 | TIN-INTERP | Interpolated Ground | 23923.53 | -4.64 | 730.98 | 0 | 25.47 | 0 | OK | Ground clear controls. | 57 | 37.03 | 756.45
3755 | TIN-INTERP | Interpolated Ground | 23923.58 | -5.14 | 731.08 | 0 | 14.37 | 0 | OK | Ground clear controls. | 57 | 37.03 | 745.45
3756 | TIN-INTERP | Interpolated Ground | 23923.59 | 6.56 | 727.77 | 0 | 23.12 | 0 | OK | Ground clear controls. | 57 | 37.03 | 750.89
3757 | TIN-INTERP | Interpolated Ground | 23923.62 | 5.06 | 727.73 | 0 | 17.74 | 0 | OK | Ground clear controls. | 57 | 37.03 | 745.47
3758 | TIN-INTERP | Interpolated Ground | 23923.65 | 4.56 | 727.71 | 0 | 28.73 | 0 | OK | Ground clear controls. | 57 | 37.03 | 756.44
3759 | TIN-INTERP | Interpolated Ground | 23963.47 | -6.64 | 730 | 0 | 20.68 | 0 | OK | Ground clear controls. | 57 | 37.03 | 750.68
3760 | TIN-INTERP | Interpolated Ground | 23963.53 | -4.64 | 729.44 | 0 | 26.78 | 0 | OK | Ground clear controls. | 57 | 37.03 | 756.22
3761 | TIN-INTERP | Interpolated Ground | 23963.58 | -5.14 | 729.62 | 0 | 15.61 | 0 | OK | Ground clear controls. | 57 | 37.03 | 745.23
3762 | TIN-INTERP | Interpolated Ground | 23963.59 | 6.56 | 727.62 | 0 | 23.04 | 0 | OK | Ground clear controls. | 57 | 37.03 | 750.66
3763 | TIN-INTERP | Interpolated Ground | 23963.62 | 5.06 | 727.81 | 0 | 17.42 | 0 | OK | Ground clear controls. | 57 | 37.03 | 745.23
3764 | TIN-INTERP | Interpolated Ground | 23963.65 | 4.56 | 727.9 | 0 | 28.31 | 0 | OK | Ground clear controls. | 57 | 37.03 | 756.21
3765 | TIN-INTERP | Interpolated Ground | 24003.47 | -6.63 | 728.55 | 0 | 22.81 | 0 | OK | Ground clear controls. | 57 | 37.03 | 751.36
3766 | TIN-INTERP | Interpolated Ground | 24003.53 | -4.63 | 728.3 | 0 | 28.6 | 0 | OK | Ground clear controls. | 57 | 37.03 | 756.9
3767 | TIN-INTERP | Interpolated Ground | 24003.58 | -5.13 | 728.37 | 0 | 17.54 | 0 | OK | Ground clear controls. | 57 | 37.03 | 745.91
3768 | TIN-INTERP | Interpolated Ground | 24003.59 | 6.57 | 728.65 | 0 | 22.7 | 0 | OK | Ground clear controls. | 57 | 37.03 | 751.35
3769 | TIN-INTERP | Interpolated Ground | 24003.62 | 5.07 | 728.61 | 0 | 17.31 | 0 | OK | Ground clear controls. | 57 | 37.03 | 745.92
3770 | TIN-INTERP | Interpolated Ground | 24003.65 | 4.57 | 728.61 | 0 | 28.27 | 0 | OK | Ground clear controls. | 57 | 37.03 | 756.88
3771 | TIN-INTERP | Interpolated Ground | 24043.47 | -6.63 | 732.64 | 0 | 20.33 | 0 | OK | Ground clear controls. | 57 | 37.03 | 752.97
3772 | TIN-INTERP | Interpolated Ground | 24043.53 | -4.63 | 732.93 | 0 | 25.57 | 0 | OK | Ground clear controls. | 57 | 37.03 | 758.5
3773 | TIN-INTERP | Interpolated Ground | 24043.58 | -5.13 | 732.83 | 0 | 14.67 | 0 | OK | Ground clear controls. | 57 | 37.03 | 747.5
3774 | TIN-INTERP | Interpolated Ground | 24043.59 | 6.57 | 734.29 | 0 | 18.67 | 0 | OK | Ground clear controls. | 57 | 37.03 | 752.96
3775 | TIN-INTERP | Interpolated Ground | 24043.62 | 5.07 | 734.09 | 0 | 13.43 | 0 | OK | Ground clear controls. | 57 | 37.03 | 747.52
3776 | TIN-INTERP | Interpolated Ground | 24043.65 | 4.57 | 734.04 | 0 | 24.46 | 0 | OK | Ground clear controls. | 57 | 37.03 | 758.5
3777 | TIN-INTERP | Interpolated Ground | 24083.47 | -6.62 | 729.5 | 0 | 26.01 | 0 | OK | Ground clear controls. | 57 | 37.03 | 755.51
3778 | TIN-INTERP | Interpolated Ground | 24083.53 | -4.62 | 729.54 | 0 | 31.48 | 0 | OK | Ground clear controls. | 57 | 37.03 | 761.02
3779 | TIN-INTERP | Interpolated Ground | 24083.58 | -5.12 | 729.52 | 0 | 20.52 | 0 | OK | Ground clear controls. | 57 | 37.03 | 750.04
3780 | TIN-INTERP | Interpolated Ground | 24083.59 | 6.58 | 730.92 | 0 | 24.57 | 0 | OK | Ground clear controls. | 57 | 37.03 | 755.49
3781 | TIN-INTERP | Interpolated Ground | 24083.62 | 5.08 | 730.65 | 0 | 19.4 | 0 | OK | Ground clear controls. | 57 | 37.03 | 750.05
3782 | TIN-INTERP | Interpolated Ground | 24083.65 | 4.58 | 730.54 | 0 | 30.48 | 0 | OK | Ground clear controls. | 57 | 37.03 | 761.02
3783 | TIN-INTERP | Interpolated Ground | 24123.47 | -6.61 | 730.1 | 0 | 28.86 | 0 | OK | Ground clear controls. | 57 | 37.03 | 758.96
3784 | TIN-INTERP | Interpolated Ground | 24123.53 | -4.61 | 730.16 | 0 | 34.31 | 0 | OK | Ground clear controls. | 57 | 37.03 | 764.47
3785 | TIN-INTERP | Interpolated Ground | 24123.58 | -5.11 | 730.14 | 0 | 23.34 | 0 | OK | Ground clear controls. | 57 | 37.03 | 753.48
3786 | TIN-INTERP | Interpolated Ground | 24123.59 | 6.59 | 730.18 | 0 | 28.77 | 0 | OK | Ground clear controls. | 57 | 37.03 | 758.95
3787 | TIN-INTERP | Interpolated Ground | 24123.62 | 5.09 | 730.13 | 0 | 23.35 | 0 | OK | Ground clear controls. | 57 | 37.03 | 753.48
3788 | TIN-INTERP | Interpolated Ground | 24123.65 | 4.59 | 730.16 | 0 | 34.31 | 0 | OK | Ground clear controls. | 57 | 37.03 | 764.47
3789 | TIN-INTERP | Interpolated Ground | 24163.47 | -6.61 | 732.09 | 0 | 31.24 | 0 | OK | Ground clear controls. | 57 | 37.03 | 763.33
3790 | TIN-INTERP | Interpolated Ground | 24163.53 | -4.61 | 732.26 | 0 | 36.57 | 0 | OK | Ground clear controls. | 57 | 37.03 | 768.83
3791 | TIN-INTERP | Interpolated Ground | 24163.58 | -5.11 | 732.26 | 0 | 25.59 | 0 | OK | Ground clear controls. | 57 | 37.03 | 757.85
3792 | TIN-INTERP | Interpolated Ground | 24163.59 | 6.59 | 731.63 | 0 | 31.71 | 0 | OK | Ground clear controls. | 57 | 37.03 | 763.34
3793 | TIN-INTERP | Interpolated Ground | 24163.62 | 5.09 | 731.81 | 0 | 26.03 | 0 | OK | Ground clear controls. | 57 | 37.03 | 757.84
3794 | TIN-INTERP | Interpolated Ground | 24163.65 | 4.59 | 731.82 | 0 | 37.03 | 0 | OK | Ground clear controls. | 57 | 37.03 | 768.85
3795 | TIN-INTERP | Interpolated Ground | 24171.3 | -6.61 | 732.16 | 0 | 32.14 | 0 | OK | Ground clear controls. | 58 | 39.41 | 764.3
3796 | TIN-INTERP | Interpolated Ground | 24171.37 | -5.11 | 732.29 | 0 | 26.51 | 0 | OK | Ground clear controls. | 58 | 39.41 | 758.8
3797 | TIN-INTERP | Interpolated Ground | 24171.38 | 6.59 | 731.73 | 0 | 32.57 | 0 | OK | Ground clear controls. | 58 | 39.41 | 764.3
3798 | TIN-INTERP | Interpolated Ground | 24171.39 | 4.59 | 732.02 | 0 | 37.78 | 0 | OK | Ground clear controls. | 58 | 39.41 | 769.8
3799 | TIN-INTERP | Interpolated Ground | 24171.39 | 5.09 | 732 | 0 | 26.8 | 0 | OK | Ground clear controls. | 58 | 39.41 | 758.8
3800 | TIN-INTERP | Interpolated Ground | 24171.4 | -4.61 | 732.3 | 0 | 37.51 | 0 | OK | Ground clear controls. | 58 | 39.41 | 769.81
3801 | TIN-INTERP | Interpolated Ground | 24211.3 | -6.61 | 731.01 | 0 | 30.46 | 0 | OK | Ground clear controls. | 58 | 39.41 | 761.47
3802 | TIN-INTERP | Interpolated Ground | 24211.37 | -5.11 | 731.05 | 0 | 24.96 | 0 | OK | Ground clear controls. | 58 | 39.41 | 756.01
3803 | TIN-INTERP | Interpolated Ground | 24211.38 | 6.59 | 732.17 | 0 | 29.32 | 0 | OK | Ground clear controls. | 58 | 39.41 | 761.49
3804 | TIN-INTERP | Interpolated Ground | 24211.39 | 4.59 | 731.71 | 0 | 35.29 | 0 | OK | Ground clear controls. | 58 | 39.41 | 767
3805 | TIN-INTERP | Interpolated Ground | 24211.39 | 5.09 | 731.76 | 0 | 24.26 | 0 | OK | Ground clear controls. | 58 | 39.41 | 756.02
3806 | TIN-INTERP | Interpolated Ground | 24211.4 | -4.61 | 731.07 | 0 | 35.95 | 0 | OK | Ground clear controls. | 58 | 39.41 | 767.02
3807 | TIN-INTERP | Interpolated Ground | 24251.3 | -6.61 | 730.7 | 0 | 28.85 | 0 | OK | Ground clear controls. | 58 | 39.41 | 759.55
3808 | TIN-INTERP | Interpolated Ground | 24251.37 | -5.11 | 730.68 | 0 | 23.44 | 0 | OK | Ground clear controls. | 58 | 39.41 | 754.12
3809 | TIN-INTERP | Interpolated Ground | 24251.38 | 6.59 | 730.78 | 0 | 28.81 | 0 | OK | Ground clear controls. | 58 | 39.41 | 759.59
3810 | TIN-INTERP | Interpolated Ground | 24251.39 | 4.59 | 730.75 | 0 | 34.37 | 0 | OK | Ground clear controls. | 58 | 39.41 | 765.12
3811 | TIN-INTERP | Interpolated Ground | 24251.39 | 5.09 | 730.75 | 0 | 23.39 | 0 | OK | Ground clear controls. | 58 | 39.41 | 754.14
3812 | TIN-INTERP | Interpolated Ground | 24251.4 | -4.61 | 730.69 | 0 | 34.44 | 0 | OK | Ground clear controls. | 58 | 39.41 | 765.13
3813 | TIN-INTERP | Interpolated Ground | 24291.3 | -6.61 | 734.59 | 0 | 23.96 | 0 | OK | Ground clear controls. | 58 | 39.41 | 758.55
3814 | TIN-INTERP | Interpolated Ground | 24291.37 | -5.11 | 734.6 | 0 | 18.53 | 0 | OK | Ground clear controls. | 58 | 39.41 | 753.13
3815 | TIN-INTERP | Interpolated Ground | 24291.38 | 6.59 | 734.55 | 0 | 24.05 | 0 | OK | Ground clear controls. | 58 | 39.41 | 758.6
3816 | TIN-INTERP | Interpolated Ground | 24291.39 | 4.59 | 734.58 | 0 | 29.56 | 0 | OK | Ground clear controls. | 58 | 39.41 | 764.14
3817 | TIN-INTERP | Interpolated Ground | 24291.39 | 5.09 | 734.54 | 0 | 18.63 | 0 | OK | Ground clear controls. | 58 | 39.41 | 753.17
3818 | TIN-INTERP | Interpolated Ground | 24291.4 | -4.61 | 734.62 | 0 | 29.55 | 0 | OK | Ground clear controls. | 58 | 39.41 | 764.17
3819 | TIN-INTERP | Interpolated Ground | 24331.3 | -6.61 | 737.87 | 0 | 20.61 | 0 | OK | Ground clear controls. | 58 | 39.41 | 758.48
3820 | TIN-INTERP | Interpolated Ground | 24331.37 | -5.11 | 737.81 | 0 | 15.26 | 0 | OK | Ground clear controls. | 58 | 39.41 | 753.07
3821 | TIN-INTERP | Interpolated Ground | 24331.38 | 6.59 | 737.72 | 0 | 20.81 | 0 | OK | Ground clear controls. | 58 | 39.41 | 758.53
3822 | TIN-INTERP | Interpolated Ground | 24331.39 | 4.59 | 737.74 | 0 | 26.35 | 0 | OK | Ground clear controls. | 58 | 39.41 | 764.09
3823 | TIN-INTERP | Interpolated Ground | 24331.39 | 5.09 | 737.74 | 0 | 15.37 | 0 | OK | Ground clear controls. | 58 | 39.41 | 753.11
3824 | TIN-INTERP | Interpolated Ground | 24331.4 | -4.61 | 737.8 | 0 | 26.31 | 0 | OK | Ground clear controls. | 58 | 39.41 | 764.11
3825 | TIN-INTERP | Interpolated Ground | 24371.3 | -6.61 | 740.11 | 0 | 19.21 | 0 | OK | Ground clear controls. | 58 | 39.41 | 759.32
3826 | TIN-INTERP | Interpolated Ground | 24371.37 | -5.11 | 739.8 | 0 | 14.13 | 0 | OK | Ground clear controls. | 58 | 39.41 | 753.93
3827 | TIN-INTERP | Interpolated Ground | 24371.38 | 6.59 | 739.51 | 0 | 19.87 | 0 | OK | Ground clear controls. | 58 | 39.41 | 759.38
3828 | TIN-INTERP | Interpolated Ground | 24371.39 | 4.59 | 739.36 | 0 | 25.58 | 0 | OK | Ground clear controls. | 58 | 39.41 | 764.94
3829 | TIN-INTERP | Interpolated Ground | 24371.39 | 5.09 | 739.35 | 0 | 14.61 | 0 | OK | Ground clear controls. | 58 | 39.41 | 753.96
3830 | TIN-INTERP | Interpolated Ground | 24371.4 | -4.61 | 739.72 | 0 | 25.25 | 0 | OK | Ground clear controls. | 58 | 39.41 | 764.97
3831 | TIN-INTERP | Interpolated Ground | 24411.3 | -6.6 | 740.49 | 0 | 20.59 | 0 | OK | Ground clear controls. | 58 | 39.41 | 761.08
3832 | TIN-INTERP | Interpolated Ground | 24411.37 | -5.1 | 740.56 | 0 | 15.13 | 0 | OK | Ground clear controls. | 58 | 39.41 | 755.69
3833 | TIN-INTERP | Interpolated Ground | 24411.38 | 6.59 | 739.96 | 0 | 21.18 | 0 | OK | Ground clear controls. | 58 | 39.41 | 761.14
3834 | TIN-INTERP | Interpolated Ground | 24411.39 | 4.59 | 740.02 | 0 | 26.68 | 0 | OK | Ground clear controls. | 58 | 39.41 | 766.7
3835 | TIN-INTERP | Interpolated Ground | 24411.39 | 5.09 | 739.95 | 0 | 15.77 | 0 | OK | Ground clear controls. | 58 | 39.41 | 755.72
3836 | TIN-INTERP | Interpolated Ground | 24411.4 | -4.6 | 740.57 | 0 | 26.16 | 0 | OK | Ground clear controls. | 58 | 39.41 | 766.73
3837 | TIN-INTERP | Interpolated Ground | 24451.3 | -6.6 | 740.68 | 0 | 23.08 | 0 | OK | Ground clear controls. | 58 | 39.41 | 763.76
3838 | TIN-INTERP | Interpolated Ground | 24451.37 | -5.1 | 740.71 | 0 | 17.66 | 0 | OK | Ground clear controls. | 58 | 39.41 | 758.37
3839 | TIN-INTERP | Interpolated Ground | 24451.38 | 6.6 | 740.45 | 0 | 23.37 | 0 | OK | Ground clear controls. | 58 | 39.41 | 763.82
3840 | TIN-INTERP | Interpolated Ground | 24451.39 | 4.6 | 740.36 | 0 | 29.01 | 0 | OK | Ground clear controls. | 58 | 39.41 | 769.37
3841 | TIN-INTERP | Interpolated Ground | 24451.39 | 5.1 | 740.39 | 0 | 18 | 0 | OK | Ground clear controls. | 58 | 39.41 | 758.39
3842 | TIN-INTERP | Interpolated Ground | 24451.4 | -4.6 | 740.71 | 0 | 28.69 | 0 | OK | Ground clear controls. | 58 | 39.41 | 769.4
3843 | TIN-INTERP | Interpolated Ground | 24491.3 | -6.6 | 740.61 | 0 | 26.76 | 0 | OK | Ground clear controls. | 58 | 39.41 | 767.37
3844 | TIN-INTERP | Interpolated Ground | 24491.37 | -5.1 | 740.68 | 0 | 21.27 | 0 | OK | Ground clear controls. | 58 | 39.41 | 761.95
3845 | TIN-INTERP | Interpolated Ground | 24491.38 | 6.6 | 740.54 | 0 | 26.88 | 0 | OK | Ground clear controls. | 58 | 39.41 | 767.42
3846 | TIN-INTERP | Interpolated Ground | 24491.39 | 4.6 | 740.62 | 0 | 32.34 | 0 | OK | Ground clear controls. | 58 | 39.41 | 772.96
3847 | TIN-INTERP | Interpolated Ground | 24491.39 | 5.1 | 740.57 | 0 | 21.41 | 0 | OK | Ground clear controls. | 58 | 39.41 | 761.98
3848 | TIN-INTERP | Interpolated Ground | 24491.4 | -4.6 | 740.71 | 0 | 32.28 | 0 | OK | Ground clear controls. | 58 | 39.41 | 772.99
3849 | TIN-INTERP | Interpolated Ground | 24531.3 | -6.6 | 740.93 | 0 | 30.99 | 0 | OK | Ground clear controls. | 58 | 39.41 | 771.92
3850 | TIN-INTERP | Interpolated Ground | 24531.37 | -5.1 | 741.06 | 0 | 25.4 | 0 | OK | Ground clear controls. | 58 | 39.41 | 766.46
3851 | TIN-INTERP | Interpolated Ground | 24531.38 | 6.6 | 741.39 | 0 | 30.55 | 0 | OK | Ground clear controls. | 58 | 39.41 | 771.94
3852 | TIN-INTERP | Interpolated Ground | 24531.39 | 4.6 | 741.46 | 0 | 36 | 0 | OK | Ground clear controls. | 58 | 39.41 | 777.46
3853 | TIN-INTERP | Interpolated Ground | 24531.39 | 5.1 | 741.42 | 0 | 25.06 | 0 | OK | Ground clear controls. | 58 | 39.41 | 766.48
3854 | TIN-INTERP | Interpolated Ground | 24531.4 | -4.6 | 741.09 | 0 | 36.4 | 0 | OK | Ground clear controls. | 58 | 39.41 | 777.49
3855 | TIN-INTERP | Interpolated Ground | 24571.3 | -6.6 | 743.5 | 0 | 33.87 | 0 | OK | Ground clear controls. | 58 | 39.41 | 777.37
3856 | TIN-INTERP | Interpolated Ground | 24571.37 | -5.1 | 743.55 | 0 | 28.34 | 0 | OK | Ground clear controls. | 58 | 39.41 | 771.89
3857 | TIN-INTERP | Interpolated Ground | 24571.38 | 6.6 | 742.79 | 0 | 34.58 | 0 | OK | Ground clear controls. | 58 | 39.41 | 777.37
3858 | TIN-INTERP | Interpolated Ground | 24571.39 | 4.6 | 743.48 | 0 | 39.41 | 0 | OK | Ground clear controls. | 58 | 39.41 | 782.89
3859 | TIN-INTERP | Interpolated Ground | 24571.39 | 5.1 | 743.17 | 0 | 28.72 | 0 | OK | Ground clear controls. | 58 | 39.32 | 771.89
3860 | TIN-INTERP | Interpolated Ground | 24571.4 | -4.6 | 743.58 | 0 | 39.32 | 0 | OK | Ground clear controls. | 58 | 39.32 | 782.9
3861 | TIN-INTERP | Interpolated Ground | 24584.82 | -4.6 | 743.67 | 0 | 41.26 | 0 | OK | Ground clear controls. | 59 | 41.26 | 784.93
3862 | TIN-INTERP | Interpolated Ground | 24584.83 | -6.6 | 743.69 | 0 | 35.74 | 0 | OK | Ground clear controls. | 59 | 41.1 | 779.43
3863 | TIN-INTERP | Interpolated Ground | 24584.9 | 4.6 | 743.83 | 0 | 41.1 | 0 | OK | Ground clear controls. | 59 | 41.1 | 784.93
3864 | TIN-INTERP | Interpolated Ground | 24584.9 | -5.1 | 743.76 | 0 | 30.17 | 0 | OK | Ground clear controls. | 59 | 39.83 | 773.93
3865 | TIN-INTERP | Interpolated Ground | 24584.91 | 5.1 | 743.6 | 0 | 30.32 | 0 | OK | Ground clear controls. | 59 | 39.83 | 773.92
3866 | TIN-INTERP | Interpolated Ground | 24584.95 | 6.6 | 743.25 | 0 | 36.17 | 0 | OK | Ground clear controls. | 59 | 39.83 | 779.42
3867 | TIN-INTERP | Interpolated Ground | 24624.83 | -4.6 | 742.62 | 0 | 36.72 | 0 | OK | Ground clear controls. | 59 | 39.83 | 779.34
3868 | TIN-INTERP | Interpolated Ground | 24624.84 | -6.6 | 742.56 | 0 | 31.24 | 0 | OK | Ground clear controls. | 59 | 39.83 | 773.8
3869 | TIN-INTERP | Interpolated Ground | 24624.9 | 4.6 | 743.12 | 0 | 36.2 | 0 | OK | Ground clear controls. | 59 | 39.83 | 779.32
3870 | TIN-INTERP | Interpolated Ground | 24624.9 | -5.1 | 742.59 | 0 | 25.8 | 0 | OK | Ground clear controls. | 59 | 39.83 | 768.39
3871 | TIN-INTERP | Interpolated Ground | 24624.91 | 5.1 | 743.06 | 0 | 25.29 | 0 | OK | Ground clear controls. | 59 | 39.83 | 768.35
3872 | TIN-INTERP | Interpolated Ground | 24624.95 | 6.6 | 743.06 | 0 | 30.77 | 0 | OK | Ground clear controls. | 59 | 39.83 | 773.83
3873 | TIN-INTERP | Interpolated Ground | 24664.83 | -4.6 | 742.01 | 0 | 32.66 | 0 | OK | Ground clear controls. | 59 | 39.83 | 774.67
3874 | TIN-INTERP | Interpolated Ground | 24664.84 | -6.6 | 741.83 | 0 | 27.25 | 0 | OK | Ground clear controls. | 59 | 39.83 | 769.08
3875 | TIN-INTERP | Interpolated Ground | 24664.9 | 4.6 | 742.55 | 0 | 32.09 | 0 | OK | Ground clear controls. | 59 | 39.83 | 774.64
3876 | TIN-INTERP | Interpolated Ground | 24664.9 | -5.1 | 741.91 | 0 | 21.84 | 0 | OK | Ground clear controls. | 59 | 39.83 | 763.75
3877 | TIN-INTERP | Interpolated Ground | 24664.91 | 5.1 | 742.44 | 0 | 21.24 | 0 | OK | Ground clear controls. | 59 | 39.83 | 763.68
3878 | TIN-INTERP | Interpolated Ground | 24664.95 | 6.6 | 742.21 | 0 | 26.93 | 0 | OK | Ground clear controls. | 59 | 39.83 | 769.14
3879 | TIN-INTERP | Interpolated Ground | 24704.83 | -4.6 | 742.03 | 0 | 28.87 | 0 | OK | Ground clear controls. | 59 | 39.83 | 770.9
3880 | TIN-INTERP | Interpolated Ground | 24704.84 | -6.6 | 742.39 | 0 | 22.9 | 0 | OK | Ground clear controls. | 59 | 39.83 | 765.29
3881 | TIN-INTERP | Interpolated Ground | 24704.9 | 4.6 | 741.56 | 0 | 29.31 | 0 | OK | Ground clear controls. | 59 | 39.83 | 770.87
3882 | TIN-INTERP | Interpolated Ground | 24704.9 | -5.1 | 742.14 | 0 | 17.87 | 0 | OK | Ground clear controls. | 59 | 39.83 | 760.01
3883 | TIN-INTERP | Interpolated Ground | 24704.91 | 5.1 | 741.54 | 0 | 18.38 | 0 | OK | Ground clear controls. | 59 | 39.83 | 759.92
3884 | TIN-INTERP | Interpolated Ground | 24704.95 | 6.6 | 741.54 | 0 | 23.83 | 0 | OK | Ground clear controls. | 59 | 39.83 | 765.37
3885 | TIN-INTERP | Interpolated Ground | 24744.83 | -4.6 | 741.71 | 0 | 26.36 | 0 | OK | Ground clear controls. | 59 | 39.83 | 768.07
3886 | TIN-INTERP | Interpolated Ground | 24744.84 | -6.6 | 741.71 | 0 | 20.71 | 0 | OK | Ground clear controls. | 59 | 39.83 | 762.42
3887 | TIN-INTERP | Interpolated Ground | 24744.9 | 4.6 | 741.58 | 0 | 26.44 | 0 | OK | Ground clear controls. | 59 | 39.83 | 768.02
3888 | TIN-INTERP | Interpolated Ground | 24744.9 | -5.1 | 741.71 | 0 | 15.49 | 0 | OK | Ground clear controls. | 59 | 39.83 | 757.2
3889 | TIN-INTERP | Interpolated Ground | 24744.91 | 5.1 | 741.52 | 0 | 15.56 | 0 | OK | Ground clear controls. | 59 | 39.83 | 757.08
3890 | TIN-INTERP | Interpolated Ground | 24744.95 | 6.6 | 741.45 | 0 | 21.07 | 0 | OK | Ground clear controls. | 59 | 39.83 | 762.52
3891 | TIN-INTERP | Interpolated Ground | 24784.83 | -4.6 | 741.85 | 0 | 24.29 | 0 | OK | Ground clear controls. | 59 | 39.83 | 766.14
3892 | TIN-INTERP | Interpolated Ground | 24784.84 | -6.6 | 741.96 | 0 | 18.52 | 0 | OK | Ground clear controls. | 59 | 39.83 | 760.48
3893 | TIN-INTERP | Interpolated Ground | 24784.9 | 4.6 | 741.58 | 0 | 24.51 | 0 | OK | Ground clear controls. | 59 | 39.83 | 766.09
3894 | TIN-INTERP | Interpolated Ground | 24784.9 | -5.1 | 741.86 | 0 | 13.42 | 0 | OK | Ground clear controls. | 59 | 39.83 | 755.28
3895 | TIN-INTERP | Interpolated Ground | 24784.91 | 5.1 | 741.49 | 0 | 13.66 | 0 | OK | Ground clear controls. | 59 | 39.83 | 755.15
3896 | TIN-INTERP | Interpolated Ground | 24784.95 | 6.6 | 741.39 | 0 | 19.2 | 0 | OK | Ground clear controls. | 59 | 39.83 | 760.59
3897 | TIN-INTERP | Interpolated Ground | 24824.83 | -4.6 | 741.97 | 0 | 23.14 | 0 | OK | Ground clear controls. | 59 | 39.83 | 765.11
3898 | TIN-INTERP | Interpolated Ground | 24824.84 | -6.6 | 742.05 | 0 | 17.4 | 0 | OK | Ground clear controls. | 59 | 39.83 | 759.45
3899 | TIN-INTERP | Interpolated Ground | 24824.9 | 4.6 | 741.6 | 0 | 23.47 | 0 | OK | Ground clear controls. | 59 | 39.83 | 765.07
3900 | TIN-INTERP | Interpolated Ground | 24824.9 | -5.1 | 741.96 | 0 | 12.31 | 0 | OK | Ground clear controls. | 59 | 39.83 | 754.27
3901 | TIN-INTERP | Interpolated Ground | 24824.91 | 5.1 | 741.55 | 0 | 12.59 | 0 | OK | Ground clear controls. | 59 | 39.83 | 754.14
3902 | TIN-INTERP | Interpolated Ground | 24824.95 | 6.6 | 741.54 | 0 | 18.03 | 0 | OK | Ground clear controls. | 59 | 39.83 | 759.57
3903 | TIN-INTERP | Interpolated Ground | 24864.83 | -4.6 | 741.98 | 0 | 23.03 | 0 | OK | Ground clear controls. | 59 | 39.83 | 765.01
3904 | TIN-INTERP | Interpolated Ground | 24864.84 | -6.6 | 742.03 | 0 | 17.31 | 0 | OK | Ground clear controls. | 59 | 39.83 | 759.34
3905 | TIN-INTERP | Interpolated Ground | 24864.9 | 4.6 | 741.75 | 0 | 23.21 | 0 | OK | Ground clear controls. | 59 | 39.83 | 764.96
3906 | TIN-INTERP | Interpolated Ground | 24864.9 | -5.1 | 741.98 | 0 | 12.19 | 0 | OK | Ground clear controls. | 59 | 39.83 | 754.17
3907 | TIN-INTERP | Interpolated Ground | 24864.91 | 5.1 | 741.7 | 0 | 12.34 | 0 | OK | Ground clear controls. | 59 | 39.83 | 754.04
3908 | TIN-INTERP | Interpolated Ground | 24864.95 | 6.6 | 741.66 | 0 | 17.8 | 0 | OK | Ground clear controls. | 59 | 39.83 | 759.46
3909 | TIN-INTERP | Interpolated Ground | 24904.83 | -4.6 | 742.15 | 0 | 23.66 | 0 | OK | Ground clear controls. | 59 | 39.83 | 765.81
3910 | TIN-INTERP | Interpolated Ground | 24904.84 | -6.6 | 742.16 | 0 | 17.98 | 0 | OK | Ground clear controls. | 59 | 39.83 | 760.14
3911 | TIN-INTERP | Interpolated Ground | 24904.9 | 4.6 | 741.86 | 0 | 23.92 | 0 | OK | Ground clear controls. | 59 | 39.83 | 765.78
3912 | TIN-INTERP | Interpolated Ground | 24904.9 | -5.1 | 742.19 | 0 | 12.79 | 0 | OK | Ground clear controls. | 59 | 39.83 | 754.98
3913 | TIN-INTERP | Interpolated Ground | 24904.91 | 5.1 | 741.81 | 0 | 13.03 | 0 | OK | Ground clear controls. | 59 | 39.83 | 754.84
3914 | TIN-INTERP | Interpolated Ground | 24904.95 | 6.6 | 741.84 | 0 | 18.44 | 0 | OK | Ground clear controls. | 59 | 39.83 | 760.28
3915 | TIN-INTERP | Interpolated Ground | 24944.83 | -4.6 | 742.28 | 0 | 25.26 | 0 | OK | Ground clear controls. | 59 | 39.83 | 767.54
3916 | TIN-INTERP | Interpolated Ground | 24944.84 | -6.6 | 742.27 | 0 | 19.61 | 0 | OK | Ground clear controls. | 59 | 39.83 | 761.88
3917 | TIN-INTERP | Interpolated Ground | 24944.9 | 4.6 | 742.18 | 0 | 25.32 | 0 | OK | Ground clear controls. | 59 | 39.83 | 767.5
3918 | TIN-INTERP | Interpolated Ground | 24944.9 | -5.1 | 742.27 | 0 | 14.41 | 0 | OK | Ground clear controls. | 59 | 39.83 | 756.68
3919 | TIN-INTERP | Interpolated Ground | 24944.91 | 5.1 | 742.03 | 0 | 14.54 | 0 | OK | Ground clear controls. | 59 | 39.83 | 756.57
3920 | TIN-INTERP | Interpolated Ground | 24944.95 | 6.6 | 742.05 | 0 | 19.95 | 0 | OK | Ground clear controls. | 59 | 39.83 | 762
3921 | TIN-INTERP | Interpolated Ground | 24984.83 | -4.6 | 742.71 | 0 | 27.46 | 0 | OK | Ground clear controls. | 59 | 39.83 | 770.17
3922 | TIN-INTERP | Interpolated Ground | 24984.84 | -6.6 | 742.7 | 0 | 21.82 | 0 | OK | Ground clear controls. | 59 | 39.83 | 764.52
3923 | TIN-INTERP | Interpolated Ground | 24984.9 | 4.6 | 742.93 | 0 | 27.21 | 0 | OK | Ground clear controls. | 59 | 39.83 | 770.14
3924 | TIN-INTERP | Interpolated Ground | 24984.9 | -5.1 | 742.7 | 0 | 16.6 | 0 | OK | Ground clear controls. | 59 | 39.83 | 759.3
3925 | TIN-INTERP | Interpolated Ground | 24984.91 | 5.1 | 742.69 | 0 | 16.5 | 0 | OK | Ground clear controls. | 59 | 39.83 | 759.19
3926 | TIN-INTERP | Interpolated Ground | 24984.95 | 6.6 | 742.45 | 0 | 22.19 | 0 | OK | Ground clear controls. | 59 | 39.83 | 764.64
3927 | TIN-INTERP | Interpolated Ground | 25024.83 | -4.6 | 741.84 | 0 | 31.87 | 0 | OK | Ground clear controls. | 59 | 39.83 | 773.71
3928 | TIN-INTERP | Interpolated Ground | 25024.84 | -6.6 | 741.85 | 0 | 26.24 | 0 | OK | Ground clear controls. | 59 | 39.83 | 768.09
3929 | TIN-INTERP | Interpolated Ground | 25024.9 | 4.6 | 741.86 | 0 | 31.82 | 0 | OK | Ground clear controls. | 59 | 39.83 | 773.68
3930 | TIN-INTERP | Interpolated Ground | 25024.9 | -5.1 | 741.85 | 0 | 20.97 | 0 | OK | Ground clear controls. | 59 | 39.83 | 762.82
3931 | TIN-INTERP | Interpolated Ground | 25024.91 | 5.1 | 741.87 | 0 | 20.86 | 0 | OK | Ground clear controls. | 59 | 39.83 | 762.73
3932 | TIN-INTERP | Interpolated Ground | 25024.95 | 6.6 | 741.91 | 0 | 26.28 | 0 | OK | Ground clear controls. | 59 | 39.83 | 768.19
3933 | TIN-INTERP | Interpolated Ground | 25064.83 | -4.6 | 742.5 | 0 | 35.68 | 0 | OK | Ground clear controls. | 59 | 39.83 | 778.18
3934 | TIN-INTERP | Interpolated Ground | 25064.84 | -6.6 | 742.19 | 0 | 30.41 | 0 | OK | Ground clear controls. | 59 | 39.83 | 772.6
3935 | TIN-INTERP | Interpolated Ground | 25064.9 | 4.6 | 742.15 | 0 | 36.02 | 0 | OK | Ground clear controls. | 59 | 39.83 | 778.17
3936 | TIN-INTERP | Interpolated Ground | 25064.9 | -5.1 | 742.4 | 0 | 24.85 | 0 | OK | Ground clear controls. | 59 | 39.83 | 767.25
3937 | TIN-INTERP | Interpolated Ground | 25064.91 | 5.1 | 742.1 | 0 | 25.1 | 0 | OK | Ground clear controls. | 59 | 39.83 | 767.2
3938 | TIN-INTERP | Interpolated Ground | 25064.95 | 6.6 | 742.08 | 0 | 30.59 | 0 | OK | Ground clear controls. | 59 | 39.83 | 772.67
3939 | TIN-INTERP | Interpolated Ground | 25104.83 | -4.6 | 744.14 | 0 | 39.42 | 0 | OK | Ground clear controls. | 59 | 39.83 | 783.56
3940 | TIN-INTERP | Interpolated Ground | 25104.84 | -6.6 | 744.07 | 0 | 33.95 | 0 | OK | Ground clear controls. | 59 | 39.83 | 778.02
3941 | TIN-INTERP | Interpolated Ground | 25104.9 | 4.6 | 743.74 | 0 | 39.83 | 0 | OK | Ground clear controls. | 59 | 39.83 | 783.57
3942 | TIN-INTERP | Interpolated Ground | 25104.9 | -5.1 | 744.15 | 0 | 28.45 | 0 | OK | Ground clear controls. | 59 | 35.03 | 772.6
3943 | TIN-INTERP | Interpolated Ground | 25104.91 | 5.1 | 743.44 | 0 | 29.14 | 0 | OK | Ground clear controls. | 59 | 35.03 | 772.58
3944 | TIN-INTERP | Interpolated Ground | 25104.95 | 6.6 | 743.04 | 0 | 35.03 | 0 | OK | Ground clear controls. | 59 | 35.03 | 778.07
3945 | TIN-INTERP | Interpolated Ground | 25136.68 | 4.6 | 744.38 | 0 | 44.13 | 0 | OK | Ground clear controls. | 60 | 44.13 | 788.51
3946 | TIN-INTERP | Interpolated Ground | 25136.74 | 5.1 | 744.31 | 0 | 33.2 | 0 | OK | Ground clear controls. | 60 | 43.76 | 777.51
3947 | TIN-INTERP | Interpolated Ground | 25136.75 | -4.6 | 744.75 | 0 | 43.76 | 0 | OK | Ground clear controls. | 60 | 43.76 | 788.51
3948 | TIN-INTERP | Interpolated Ground | 25136.75 | 6.6 | 744.1 | 0 | 38.91 | 0 | OK | Ground clear controls. | 60 | 41.93 | 783.01
3949 | TIN-INTERP | Interpolated Ground | 25136.77 | -6.6 | 744.85 | 0 | 38.16 | 0 | OK | Ground clear controls. | 60 | 41.93 | 783.01
3950 | TIN-INTERP | Interpolated Ground | 25136.79 | -5.1 | 744.78 | 0 | 32.73 | 0 | OK | Ground clear controls. | 60 | 41.93 | 777.51
3951 | TIN-INTERP | Interpolated Ground | 25176.68 | 4.6 | 745.29 | 0 | 37.56 | 0 | OK | Ground clear controls. | 60 | 41.93 | 782.85
3952 | TIN-INTERP | Interpolated Ground | 25176.74 | 5.1 | 745.08 | 0 | 26.83 | 0 | OK | Ground clear controls. | 60 | 41.93 | 771.91
3953 | TIN-INTERP | Interpolated Ground | 25176.75 | -4.6 | 745.36 | 0 | 37.55 | 0 | OK | Ground clear controls. | 60 | 41.93 | 782.91
3954 | TIN-INTERP | Interpolated Ground | 25176.75 | 6.6 | 744.92 | 0 | 32.48 | 0 | OK | Ground clear controls. | 60 | 41.93 | 777.4
3955 | TIN-INTERP | Interpolated Ground | 25176.77 | -6.6 | 745.14 | 0 | 32.24 | 0 | OK | Ground clear controls. | 60 | 41.93 | 777.38
3956 | TIN-INTERP | Interpolated Ground | 25176.79 | -5.1 | 745.33 | 0 | 26.65 | 0 | OK | Ground clear controls. | 60 | 41.93 | 771.98
3957 | TIN-INTERP | Interpolated Ground | 25216.68 | 4.59 | 745.54 | 0 | 32.57 | 0 | OK | Ground clear controls. | 60 | 41.93 | 778.11
3958 | TIN-INTERP | Interpolated Ground | 25216.74 | 5.09 | 745.41 | 0 | 21.81 | 0 | OK | Ground clear controls. | 60 | 41.93 | 767.22
3959 | TIN-INTERP | Interpolated Ground | 25216.75 | -4.61 | 745.46 | 0 | 32.76 | 0 | OK | Ground clear controls. | 60 | 41.93 | 778.22
3960 | TIN-INTERP | Interpolated Ground | 25216.75 | 6.59 | 745.22 | 0 | 27.48 | 0 | OK | Ground clear controls. | 60 | 41.93 | 772.7
3961 | TIN-INTERP | Interpolated Ground | 25216.77 | -6.61 | 745.48 | 0 | 27.19 | 0 | OK | Ground clear controls. | 60 | 41.93 | 772.67
3962 | TIN-INTERP | Interpolated Ground | 25216.79 | -5.11 | 745.45 | 0 | 21.89 | 0 | OK | Ground clear controls. | 60 | 41.93 | 767.34
3963 | TIN-INTERP | Interpolated Ground | 25256.68 | 4.59 | 744.79 | 0 | 29.5 | 0 | OK | Ground clear controls. | 60 | 41.93 | 774.29
3964 | TIN-INTERP | Interpolated Ground | 25256.74 | 5.09 | 744.77 | 0 | 18.67 | 0 | OK | Ground clear controls. | 60 | 41.93 | 763.44
3965 | TIN-INTERP | Interpolated Ground | 25256.75 | -4.61 | 744.94 | 0 | 29.5 | 0 | OK | Ground clear controls. | 60 | 41.93 | 774.44
3966 | TIN-INTERP | Interpolated Ground | 25256.75 | 6.59 | 744.66 | 0 | 24.25 | 0 | OK | Ground clear controls. | 60 | 41.93 | 768.91
3967 | TIN-INTERP | Interpolated Ground | 25256.77 | -6.61 | 745.09 | 0 | 23.78 | 0 | OK | Ground clear controls. | 60 | 41.93 | 768.87
3968 | TIN-INTERP | Interpolated Ground | 25256.79 | -5.11 | 745 | 0 | 18.62 | 0 | OK | Ground clear controls. | 60 | 41.93 | 763.62
3969 | TIN-INTERP | Interpolated Ground | 25296.68 | 4.59 | 744.49 | 0 | 26.9 | 0 | OK | Ground clear controls. | 60 | 41.93 | 771.39
3970 | TIN-INTERP | Interpolated Ground | 25296.74 | 5.09 | 744.45 | 0 | 16.13 | 0 | OK | Ground clear controls. | 60 | 41.93 | 760.58
3971 | TIN-INTERP | Interpolated Ground | 25296.75 | -4.61 | 744.5 | 0 | 27.08 | 0 | OK | Ground clear controls. | 60 | 41.93 | 771.58
3972 | TIN-INTERP | Interpolated Ground | 25296.75 | 6.59 | 744.34 | 0 | 21.71 | 0 | OK | Ground clear controls. | 60 | 41.93 | 766.05
3973 | TIN-INTERP | Interpolated Ground | 25296.77 | -6.61 | 744.51 | 0 | 21.49 | 0 | OK | Ground clear controls. | 60 | 41.93 | 766
3974 | TIN-INTERP | Interpolated Ground | 25296.79 | -5.11 | 744.5 | 0 | 16.29 | 0 | OK | Ground clear controls. | 60 | 41.93 | 760.79
3975 | TIN-INTERP | Interpolated Ground | 25336.68 | 4.58 | 744.38 | 0 | 25.04 | 0 | OK | Ground clear controls. | 60 | 41.93 | 769.42
3976 | TIN-INTERP | Interpolated Ground | 25336.74 | 5.08 | 744.32 | 0 | 14.3 | 0 | OK | Ground clear controls. | 60 | 41.93 | 758.62
3977 | TIN-INTERP | Interpolated Ground | 25336.75 | -4.62 | 744.5 | 0 | 25.13 | 0 | OK | Ground clear controls. | 60 | 41.93 | 769.63
3978 | TIN-INTERP | Interpolated Ground | 25336.75 | 6.58 | 744.26 | 0 | 19.82 | 0 | OK | Ground clear controls. | 60 | 41.93 | 764.08
3979 | TIN-INTERP | Interpolated Ground | 25336.77 | -6.62 | 744.82 | 0 | 19.21 | 0 | OK | Ground clear controls. | 60 | 41.93 | 764.03
3980 | TIN-INTERP | Interpolated Ground | 25336.79 | -5.12 | 744.58 | 0 | 14.28 | 0 | OK | Ground clear controls. | 60 | 41.93 | 758.86
3981 | TIN-INTERP | Interpolated Ground | 25376.68 | 4.58 | 744.39 | 0 | 23.97 | 0 | OK | Ground clear controls. | 60 | 41.93 | 768.36
3982 | TIN-INTERP | Interpolated Ground | 25376.74 | 5.08 | 744.37 | 0 | 13.22 | 0 | OK | Ground clear controls. | 60 | 41.93 | 757.59
3983 | TIN-INTERP | Interpolated Ground | 25376.75 | -4.62 | 744.45 | 0 | 24.13 | 0 | OK | Ground clear controls. | 60 | 41.93 | 768.58
3984 | TIN-INTERP | Interpolated Ground | 25376.75 | 6.58 | 744.43 | 0 | 18.62 | 0 | OK | Ground clear controls. | 60 | 41.93 | 763.05
3985 | TIN-INTERP | Interpolated Ground | 25376.77 | -6.62 | 744.37 | 0 | 18.62 | 0 | OK | Ground clear controls. | 60 | 41.93 | 762.99
3986 | TIN-INTERP | Interpolated Ground | 25376.79 | -5.12 | 744.42 | 0 | 13.41 | 0 | OK | Ground clear controls. | 60 | 41.93 | 757.83
3987 | TIN-INTERP | Interpolated Ground | 25416.68 | 4.57 | 744.88 | 0 | 23.34 | 0 | OK | Ground clear controls. | 60 | 41.93 | 768.22
3988 | TIN-INTERP | Interpolated Ground | 25416.74 | 5.07 | 744.83 | 0 | 12.62 | 0 | OK | Ground clear controls. | 60 | 41.93 | 757.45
3989 | TIN-INTERP | Interpolated Ground | 25416.75 | -4.63 | 745.21 | 0 | 23.24 | 0 | OK | Ground clear controls. | 60 | 41.93 | 768.45
3990 | TIN-INTERP | Interpolated Ground | 25416.75 | 6.57 | 744.82 | 0 | 18.09 | 0 | OK | Ground clear controls. | 60 | 41.93 | 762.91
3991 | TIN-INTERP | Interpolated Ground | 25416.77 | -6.63 | 745.14 | 0 | 17.71 | 0 | OK | Ground clear controls. | 60 | 41.93 | 762.85
3992 | TIN-INTERP | Interpolated Ground | 25416.79 | -5.13 | 745.18 | 0 | 12.52 | 0 | OK | Ground clear controls. | 60 | 41.93 | 757.7
3993 | TIN-INTERP | Interpolated Ground | 25456.68 | 4.57 | 745.15 | 0 | 23.86 | 0 | OK | Ground clear controls. | 60 | 41.93 | 769.01
3994 | TIN-INTERP | Interpolated Ground | 25456.74 | 5.07 | 745.05 | 0 | 13.17 | 0 | OK | Ground clear controls. | 60 | 41.93 | 758.22
3995 | TIN-INTERP | Interpolated Ground | 25456.75 | -4.63 | 745.15 | 0 | 24.07 | 0 | OK | Ground clear controls. | 60 | 41.93 | 769.22
3996 | TIN-INTERP | Interpolated Ground | 25456.75 | 6.57 | 744.84 | 0 | 18.84 | 0 | OK | Ground clear controls. | 60 | 41.93 | 763.68
3997 | TIN-INTERP | Interpolated Ground | 25456.77 | -6.63 | 745.04 | 0 | 18.59 | 0 | OK | Ground clear controls. | 60 | 41.93 | 763.63
3998 | TIN-INTERP | Interpolated Ground | 25456.79 | -5.13 | 745.12 | 0 | 13.34 | 0 | OK | Ground clear controls. | 60 | 41.93 | 758.46
3999 | TIN-INTERP | Interpolated Ground | 25496.68 | 4.57 | 745.29 | 0 | 25.42 | 0 | OK | Ground clear controls. | 60 | 41.93 | 770.71
4000 | TIN-INTERP | Interpolated Ground | 25496.74 | 5.07 | 745.16 | 0 | 14.75 | 0 | OK | Ground clear controls. | 60 | 41.93 | 759.91
4001 | TIN-INTERP | Interpolated Ground | 25496.75 | -4.63 | 745.51 | 0 | 25.41 | 0 | OK | Ground clear controls. | 60 | 41.93 | 770.92
4002 | TIN-INTERP | Interpolated Ground | 25496.75 | 6.57 | 744.7 | 0 | 20.67 | 0 | OK | Ground clear controls. | 60 | 41.93 | 765.37
4003 | TIN-INTERP | Interpolated Ground | 25496.77 | -6.63 | 745.53 | 0 | 19.79 | 0 | OK | Ground clear controls. | 60 | 41.93 | 765.32
4004 | TIN-INTERP | Interpolated Ground | 25496.79 | -5.13 | 745.54 | 0 | 14.59 | 0 | OK | Ground clear controls. | 60 | 41.93 | 760.13
4005 | TIN-INTERP | Interpolated Ground | 25536.68 | 4.56 | 745.22 | 0 | 28.11 | 0 | OK | Ground clear controls. | 60 | 41.93 | 773.33
4006 | TIN-INTERP | Interpolated Ground | 25536.74 | 5.06 | 745.05 | 0 | 17.44 | 0 | OK | Ground clear controls. | 60 | 41.93 | 762.49
4007 | TIN-INTERP | Interpolated Ground | 25536.75 | -4.64 | 745.24 | 0 | 28.26 | 0 | OK | Ground clear controls. | 60 | 41.93 | 773.5
4008 | TIN-INTERP | Interpolated Ground | 25536.75 | 6.56 | 744.86 | 0 | 23.1 | 0 | OK | Ground clear controls. | 60 | 41.93 | 767.96
4009 | TIN-INTERP | Interpolated Ground | 25536.77 | -6.64 | 745.33 | 0 | 22.6 | 0 | OK | Ground clear controls. | 60 | 41.93 | 767.93
4010 | TIN-INTERP | Interpolated Ground | 25536.79 | -5.14 | 745.27 | 0 | 17.42 | 0 | OK | Ground clear controls. | 60 | 41.93 | 762.69
4011 | TIN-INTERP | Interpolated Ground | 25576.68 | 4.56 | 745.43 | 0 | 31.45 | 0 | OK | Ground clear controls. | 60 | 41.93 | 776.88
4012 | TIN-INTERP | Interpolated Ground | 25576.74 | 5.06 | 745.26 | 0 | 20.75 | 0 | OK | Ground clear controls. | 60 | 41.93 | 766.01
4013 | TIN-INTERP | Interpolated Ground | 25576.75 | -4.64 | 744.91 | 0 | 32.11 | 0 | OK | Ground clear controls. | 60 | 41.93 | 777.02
4014 | TIN-INTERP | Interpolated Ground | 25576.75 | 6.56 | 744.84 | 0 | 26.64 | 0 | OK | Ground clear controls. | 60 | 41.93 | 771.48
4015 | TIN-INTERP | Interpolated Ground | 25576.77 | -6.64 | 744.87 | 0 | 26.59 | 0 | OK | Ground clear controls. | 60 | 41.93 | 771.46
4016 | TIN-INTERP | Interpolated Ground | 25576.79 | -5.14 | 744.9 | 0 | 21.26 | 0 | OK | Ground clear controls. | 60 | 41.93 | 766.16
4017 | TIN-INTERP | Interpolated Ground | 25616.68 | 4.55 | 746.04 | 0 | 35.31 | 0 | OK | Ground clear controls. | 60 | 41.93 | 781.35
4018 | TIN-INTERP | Interpolated Ground | 25616.74 | 5.05 | 745.67 | 0 | 24.75 | 0 | OK | Ground clear controls. | 60 | 41.93 | 770.42
4019 | TIN-INTERP | Interpolated Ground | 25616.75 | -4.65 | 744.97 | 0 | 36.47 | 0 | OK | Ground clear controls. | 60 | 41.93 | 781.44
4020 | TIN-INTERP | Interpolated Ground | 25616.75 | 6.55 | 745.03 | 0 | 30.88 | 0 | OK | Ground clear controls. | 60 | 41.93 | 775.91
4021 | TIN-INTERP | Interpolated Ground | 25616.77 | -6.65 | 744.9 | 0 | 31.01 | 0 | OK | Ground clear controls. | 60 | 41.93 | 775.91
4022 | TIN-INTERP | Interpolated Ground | 25616.79 | -5.15 | 744.95 | 0 | 25.57 | 0 | OK | Ground clear controls. | 60 | 41.93 | 770.52
4023 | TIN-INTERP | Interpolated Ground | 25656.68 | 4.55 | 744.99 | 0 | 41.75 | 0 | OK | Ground clear controls. | 60 | 41.93 | 786.74
4024 | TIN-INTERP | Interpolated Ground | 25656.74 | 5.05 | 745.05 | 0 | 30.71 | 0 | OK | Ground clear controls. | 60 | 41.93 | 775.76
4025 | TIN-INTERP | Interpolated Ground | 25656.75 | -4.65 | 744.84 | 0 | 41.93 | 0 | OK | Ground clear controls. | 60 | 41.93 | 786.77
4026 | TIN-INTERP | Interpolated Ground | 25656.75 | 6.55 | 745.11 | 0 | 36.15 | 0 | OK | Ground clear controls. | 60 | 36.22 | 781.26
4027 | TIN-INTERP | Interpolated Ground | 25656.77 | -6.65 | 745.05 | 0 | 36.22 | 0 | OK | Ground clear controls. | 60 | 36.22 | 781.27
4028 | TIN-INTERP | Interpolated Ground | 25656.79 | -5.15 | 744.89 | 0 | 30.9 | 0 | OK | Ground clear controls. | 60 | 30.9 | 775.79
4029 | TIN-INTERP | Interpolated Ground | 25673.45 | -6.65 | 745.46 | 0 | 38.31 | 0 | OK | Ground clear controls. | 61 | 43.88 | 783.77
4030 | TIN-INTERP | Interpolated Ground | 25673.48 | 4.55 | 745.41 | 0 | 43.86 | 0 | OK | Ground clear controls. | 61 | 43.88 | 789.27
4031 | TIN-INTERP | Interpolated Ground | 25673.48 | -4.65 | 745.39 | 0 | 43.88 | 0 | OK | Ground clear controls. | 61 | 43.88 | 789.27
4032 | TIN-INTERP | Interpolated Ground | 25673.54 | 6.55 | 745.23 | 0 | 38.54 | 0 | OK | Ground clear controls. | 61 | 38.65 | 783.77
4033 | TIN-INTERP | Interpolated Ground | 25673.57 | 5.05 | 745.47 | 0 | 32.8 | 0 | OK | Ground clear controls. | 61 | 38.65 | 778.27
4034 | TIN-INTERP | Interpolated Ground | 25673.6 | -5.15 | 745.39 | 0 | 32.88 | 0 | OK | Ground clear controls. | 61 | 38.65 | 778.27
4035 | TIN-INTERP | Interpolated Ground | 25713.46 | -6.65 | 745.77 | 0 | 32.97 | 0 | OK | Ground clear controls. | 61 | 38.65 | 778.74
4036 | TIN-INTERP | Interpolated Ground | 25713.48 | 4.55 | 745.58 | 0 | 38.65 | 0 | OK | Ground clear controls. | 61 | 38.65 | 784.23
4037 | TIN-INTERP | Interpolated Ground | 25713.48 | -4.65 | 745.72 | 0 | 38.56 | 0 | OK | Ground clear controls. | 61 | 38.56 | 784.28
4038 | TIN-INTERP | Interpolated Ground | 25713.54 | 6.55 | 745.42 | 0 | 33.38 | 0 | OK | Ground clear controls. | 61 | 34.24 | 778.8
4039 | TIN-INTERP | Interpolated Ground | 25713.56 | 5.05 | 745.54 | 0 | 27.78 | 0 | OK | Ground clear controls. | 61 | 34.24 | 773.32
4040 | TIN-INTERP | Interpolated Ground | 25713.6 | -5.15 | 745.76 | 0 | 27.64 | 0 | OK | Ground clear controls. | 61 | 34.24 | 773.4
4041 | TIN-INTERP | Interpolated Ground | 25753.46 | -6.64 | 746.34 | 0 | 28.29 | 0 | OK | Ground clear controls. | 61 | 34.24 | 774.63
4042 | TIN-INTERP | Interpolated Ground | 25753.48 | 4.56 | 745.95 | 0 | 34.16 | 0 | OK | Ground clear controls. | 61 | 34.24 | 780.11
4043 | TIN-INTERP | Interpolated Ground | 25753.48 | -4.64 | 746.31 | 0 | 33.9 | 0 | OK | Ground clear controls. | 61 | 34.24 | 780.21
4044 | TIN-INTERP | Interpolated Ground | 25753.54 | 6.56 | 745.79 | 0 | 28.96 | 0 | OK | Ground clear controls. | 61 | 34.24 | 774.75
4045 | TIN-INTERP | Interpolated Ground | 25753.56 | 5.06 | 745.92 | 0 | 23.37 | 0 | OK | Ground clear controls. | 61 | 34.24 | 769.29
4046 | TIN-INTERP | Interpolated Ground | 25753.6 | -5.14 | 746.32 | 0 | 23.11 | 0 | OK | Ground clear controls. | 61 | 34.24 | 769.43
4047 | TIN-INTERP | Interpolated Ground | 25793.46 | -6.64 | 746.8 | 0 | 24.67 | 0 | OK | Ground clear controls. | 61 | 34.24 | 771.47
4048 | TIN-INTERP | Interpolated Ground | 25793.48 | 4.56 | 746.57 | 0 | 30.37 | 0 | OK | Ground clear controls. | 61 | 34.24 | 776.94
4049 | TIN-INTERP | Interpolated Ground | 25793.48 | -4.64 | 746.7 | 0 | 30.36 | 0 | OK | Ground clear controls. | 61 | 34.24 | 777.06
4050 | TIN-INTERP | Interpolated Ground | 25793.54 | 6.56 | 746.51 | 0 | 25.11 | 0 | OK | Ground clear controls. | 61 | 34.24 | 771.62
4051 | TIN-INTERP | Interpolated Ground | 25793.56 | 5.06 | 746.51 | 0 | 19.67 | 0 | OK | Ground clear controls. | 61 | 34.24 | 766.18
4052 | TIN-INTERP | Interpolated Ground | 25793.6 | -5.14 | 746.72 | 0 | 19.64 | 0 | OK | Ground clear controls. | 61 | 34.24 | 766.36
4053 | TIN-INTERP | Interpolated Ground | 25833.46 | -6.63 | 748.46 | 0 | 20.77 | 0 | OK | Ground clear controls. | 61 | 34.24 | 769.23
4054 | TIN-INTERP | Interpolated Ground | 25833.48 | 4.57 | 747.83 | 0 | 26.87 | 0 | OK | Ground clear controls. | 61 | 34.24 | 774.7
4055 | TIN-INTERP | Interpolated Ground | 25833.48 | -4.63 | 748.35 | 0 | 26.5 | 0 | OK | Ground clear controls. | 61 | 34.24 | 774.85
4056 | TIN-INTERP | Interpolated Ground | 25833.54 | 6.57 | 747.31 | 0 | 22.11 | 0 | OK | Ground clear controls. | 61 | 34.24 | 769.42
4057 | TIN-INTERP | Interpolated Ground | 25833.56 | 5.07 | 747.73 | 0 | 16.25 | 0 | OK | Ground clear controls. | 61 | 34.24 | 763.98
4058 | TIN-INTERP | Interpolated Ground | 25833.6 | -5.13 | 748.4 | 0 | 15.79 | 0 | OK | Ground clear controls. | 61 | 34.24 | 764.19
4059 | TIN-INTERP | Interpolated Ground | 25873.46 | -6.63 | 748.87 | 0 | 19.05 | 0 | OK | Ground clear controls. | 61 | 34.24 | 767.92
4060 | TIN-INTERP | Interpolated Ground | 25873.48 | 4.57 | 748.28 | 0 | 25.1 | 0 | OK | Ground clear controls. | 61 | 34.24 | 773.38
4061 | TIN-INTERP | Interpolated Ground | 25873.48 | -4.63 | 748.95 | 0 | 24.59 | 0 | OK | Ground clear controls. | 61 | 34.24 | 773.54
4062 | TIN-INTERP | Interpolated Ground | 25873.54 | 6.57 | 748.23 | 0 | 19.89 | 0 | OK | Ground clear controls. | 61 | 34.24 | 768.12
4063 | TIN-INTERP | Interpolated Ground | 25873.56 | 5.07 | 748.24 | 0 | 14.45 | 0 | OK | Ground clear controls. | 61 | 34.24 | 762.69
4064 | TIN-INTERP | Interpolated Ground | 25873.6 | -5.13 | 748.97 | 0 | 13.95 | 0 | OK | Ground clear controls. | 61 | 34.24 | 762.92
4065 | TIN-INTERP | Interpolated Ground | 25913.46 | -6.62 | 749.76 | 0 | 17.78 | 0 | OK | Ground clear controls. | 61 | 34.24 | 767.54
4066 | TIN-INTERP | Interpolated Ground | 25913.48 | 4.58 | 749.53 | 0 | 23.48 | 0 | OK | Ground clear controls. | 61 | 34.24 | 773.01
4067 | TIN-INTERP | Interpolated Ground | 25913.48 | -4.62 | 749.84 | 0 | 23.34 | 0 | OK | Ground clear controls. | 61 | 34.24 | 773.18
4068 | TIN-INTERP | Interpolated Ground | 25913.54 | 6.58 | 749.55 | 0 | 18.21 | 0 | OK | Ground clear controls. | 61 | 34.24 | 767.76
4069 | TIN-INTERP | Interpolated Ground | 25913.56 | 5.08 | 749.53 | 0 | 12.79 | 0 | OK | Ground clear controls. | 61 | 34.24 | 762.32
4070 | TIN-INTERP | Interpolated Ground | 25913.6 | -5.12 | 749.87 | 0 | 12.69 | 0 | OK | Ground clear controls. | 61 | 34.24 | 762.56
4071 | TIN-INTERP | Interpolated Ground | 25953.46 | -6.62 | 751.41 | 0 | 16.69 | 0 | OK | Ground clear controls. | 61 | 34.24 | 768.1
4072 | TIN-INTERP | Interpolated Ground | 25953.48 | 4.58 | 751.24 | 0 | 22.32 | 0 | OK | Ground clear controls. | 61 | 34.24 | 773.56
4073 | TIN-INTERP | Interpolated Ground | 25953.48 | -4.62 | 751.75 | 0 | 21.97 | 0 | OK | Ground clear controls. | 61 | 34.24 | 773.72
4074 | TIN-INTERP | Interpolated Ground | 25953.54 | 6.58 | 751.15 | 0 | 17.15 | 0 | OK | Ground clear controls. | 61 | 34.24 | 768.3
4075 | TIN-INTERP | Interpolated Ground | 25953.56 | 5.08 | 751.21 | 0 | 11.66 | 0 | OK | Ground clear controls. | 61 | 34.24 | 762.87
4076 | TIN-INTERP | Interpolated Ground | 25953.6 | -5.12 | 751.64 | 0 | 11.44 | 0 | OK | Ground clear controls. | 61 | 34.24 | 763.08
4077 | TIN-INTERP | Interpolated Ground | 25993.46 | -6.62 | 753.56 | 0 | 16.03 | 0 | OK | Ground clear controls. | 61 | 34.24 | 769.59
4078 | TIN-INTERP | Interpolated Ground | 25993.48 | 4.58 | 752.16 | 0 | 22.9 | 0 | OK | Ground clear controls. | 61 | 34.24 | 775.06
4079 | TIN-INTERP | Interpolated Ground | 25993.48 | -4.62 | 753.47 | 0 | 21.72 | 0 | OK | Ground clear controls. | 61 | 34.24 | 775.19
4080 | TIN-INTERP | Interpolated Ground | 25993.54 | 6.58 | 752.18 | 0 | 17.58 | 0 | OK | Ground clear controls. | 61 | 34.24 | 769.76
4081 | TIN-INTERP | Interpolated Ground | 25993.56 | 5.08 | 752.17 | 0 | 12.15 | 0 | OK | Ground clear controls. | 61 | 34.24 | 764.32
4082 | TIN-INTERP | Interpolated Ground | 25993.6 | -5.12 | 753.51 | 0 | 11 | 0 | OK | Ground clear controls. | 61 | 34.24 | 764.51
4083 | TIN-INTERP | Interpolated Ground | 26033.46 | -6.61 | 753.25 | 0 | 18.75 | 0 | OK | Ground clear controls. | 61 | 34.24 | 772
4084 | TIN-INTERP | Interpolated Ground | 26033.48 | 4.59 | 752.29 | 0 | 25.19 | 0 | OK | Ground clear controls. | 61 | 34.24 | 777.48
4085 | TIN-INTERP | Interpolated Ground | 26033.48 | -4.61 | 753.14 | 0 | 24.44 | 0 | OK | Ground clear controls. | 61 | 34.24 | 777.58
4086 | TIN-INTERP | Interpolated Ground | 26033.54 | 6.59 | 751.8 | 0 | 20.34 | 0 | OK | Ground clear controls. | 61 | 34.24 | 772.14
4087 | TIN-INTERP | Interpolated Ground | 26033.56 | 5.09 | 752.12 | 0 | 14.57 | 0 | OK | Ground clear controls. | 61 | 34.24 | 766.69
4088 | TIN-INTERP | Interpolated Ground | 26033.6 | -5.11 | 753.19 | 0 | 13.65 | 0 | OK | Ground clear controls. | 61 | 34.24 | 766.84
4089 | TIN-INTERP | Interpolated Ground | 26073.46 | -6.61 | 751.95 | 0 | 23.39 | 0 | OK | Ground clear controls. | 61 | 34.24 | 775.34
4090 | TIN-INTERP | Interpolated Ground | 26073.48 | 4.59 | 751.16 | 0 | 29.67 | 0 | OK | Ground clear controls. | 61 | 34.24 | 780.83
4091 | TIN-INTERP | Interpolated Ground | 26073.48 | -4.61 | 751.83 | 0 | 29.06 | 0 | OK | Ground clear controls. | 61 | 34.24 | 780.89
4092 | TIN-INTERP | Interpolated Ground | 26073.54 | 6.59 | 751.03 | 0 | 24.41 | 0 | OK | Ground clear controls. | 61 | 34.24 | 775.44
4093 | TIN-INTERP | Interpolated Ground | 26073.56 | 5.09 | 751.14 | 0 | 18.83 | 0 | OK | Ground clear controls. | 61 | 34.24 | 769.97
4094 | TIN-INTERP | Interpolated Ground | 26073.6 | -5.11 | 751.86 | 0 | 18.21 | 0 | OK | Ground clear controls. | 61 | 34.24 | 770.07
4095 | TIN-INTERP | Interpolated Ground | 26113.46 | -6.6 | 751.14 | 0 | 28.48 | 0 | OK | Ground clear controls. | 61 | 34.24 | 779.62
4096 | TIN-INTERP | Interpolated Ground | 26113.48 | 4.6 | 750.88 | 0 | 34.24 | 0 | OK | Ground clear controls. | 61 | 34.24 | 785.12
4097 | TIN-INTERP | Interpolated Ground | 26113.48 | -4.6 | 751.15 | 0 | 33.98 | 0 | OK | Ground clear controls. | 61 | 33.98 | 785.13
4098 | TIN-INTERP | Interpolated Ground | 26113.54 | 6.6 | 750.42 | 0 | 29.24 | 0 | OK | Ground clear controls. | 61 | 29.24 | 779.66
4099 | TIN-INTERP | Interpolated Ground | 26113.56 | 5.1 | 750.78 | 0 | 23.4 | 0 | OK | Ground clear controls. | 61 | 23.4 | 774.18
4100 | TIN-INTERP | Interpolated Ground | 26113.6 | -5.1 | 751.16 | 0 | 23.04 | 0 | OK | Ground clear controls. | 61 | 23.04 | 774.2
4101 | TIN-INTERP | Interpolated Ground | 26127.23 | 6.6 | 749.87 | 0 | 31.45 | 0 | OK | Ground clear controls. | 62 | 39.49 | 781.32
4102 | TIN-INTERP | Interpolated Ground | 26127.24 | 5.1 | 750.13 | 0 | 25.69 | 0 | OK | Ground clear controls. | 62 | 39.49 | 775.82
4103 | TIN-INTERP | Interpolated Ground | 26127.26 | 4.6 | 750.24 | 0 | 36.58 | 0 | OK | Ground clear controls. | 62 | 39.49 | 786.82
4104 | TIN-INTERP | Interpolated Ground | 26127.28 | -5.1 | 750.61 | 0 | 25.21 | 0 | OK | Ground clear controls. | 62 | 39.49 | 775.82
4105 | TIN-INTERP | Interpolated Ground | 26127.31 | -6.6 | 750.59 | 0 | 30.73 | 0 | OK | Ground clear controls. | 62 | 39.49 | 781.32
4106 | TIN-INTERP | Interpolated Ground | 26127.34 | -4.6 | 750.61 | 0 | 36.21 | 0 | OK | Ground clear controls. | 62 | 39.49 | 786.82
4107 | TIN-INTERP | Interpolated Ground | 26167.23 | 6.6 | 747.48 | 0 | 27.69 | 0 | OK | Ground clear controls. | 62 | 39.49 | 775.17
4108 | TIN-INTERP | Interpolated Ground | 26167.24 | 5.1 | 748.18 | 0 | 21.53 | 0 | OK | Ground clear controls. | 62 | 39.49 | 769.71
4109 | TIN-INTERP | Interpolated Ground | 26167.26 | 4.6 | 748.4 | 0 | 32.2 | 0 | OK | Ground clear controls. | 62 | 39.49 | 780.6
4110 | TIN-INTERP | Interpolated Ground | 26167.28 | -5.1 | 748.65 | 0 | 21.18 | 0 | OK | Ground clear controls. | 62 | 39.49 | 769.83
4111 | TIN-INTERP | Interpolated Ground | 26167.31 | -6.6 | 748.6 | 0 | 26.55 | 0 | OK | Ground clear controls. | 62 | 39.49 | 775.15
4112 | TIN-INTERP | Interpolated Ground | 26167.34 | -4.6 | 748.65 | 0 | 32.07 | 0 | OK | Ground clear controls. | 62 | 39.49 | 780.72
4113 | TIN-INTERP | Interpolated Ground | 26207.23 | 6.6 | 745.61 | 0 | 24.35 | 0 | OK | Ground clear controls. | 62 | 39.49 | 769.96
4114 | TIN-INTERP | Interpolated Ground | 26207.24 | 5.1 | 745.97 | 0 | 18.55 | 0 | OK | Ground clear controls. | 62 | 39.49 | 764.52
4115 | TIN-INTERP | Interpolated Ground | 26207.26 | 4.6 | 746.09 | 0 | 29.22 | 0 | OK | Ground clear controls. | 62 | 39.49 | 775.31
4116 | TIN-INTERP | Interpolated Ground | 26207.28 | -5.1 | 746.19 | 0 | 18.54 | 0 | OK | Ground clear controls. | 62 | 39.49 | 764.73
4117 | TIN-INTERP | Interpolated Ground | 26207.31 | -6.6 | 746.24 | 0 | 23.67 | 0 | OK | Ground clear controls. | 62 | 39.49 | 769.91
4118 | TIN-INTERP | Interpolated Ground | 26207.34 | -4.6 | 746.18 | 0 | 29.35 | 0 | OK | Ground clear controls. | 62 | 39.49 | 775.53
4119 | TIN-INTERP | Interpolated Ground | 26247.23 | 6.6 | 743.46 | 0 | 22.2 | 0 | OK | Ground clear controls. | 62 | 39.49 | 765.66
4120 | TIN-INTERP | Interpolated Ground | 26247.24 | 5.1 | 743.65 | 0 | 16.59 | 0 | OK | Ground clear controls. | 62 | 39.49 | 760.24
4121 | TIN-INTERP | Interpolated Ground | 26247.26 | 4.6 | 743.69 | 0 | 27.27 | 0 | OK | Ground clear controls. | 62 | 39.49 | 770.96
4122 | TIN-INTERP | Interpolated Ground | 26247.28 | -5.1 | 744.25 | 0 | 16.3 | 0 | OK | Ground clear controls. | 62 | 39.49 | 760.55
4123 | TIN-INTERP | Interpolated Ground | 26247.31 | -6.6 | 744.36 | 0 | 21.23 | 0 | OK | Ground clear controls. | 62 | 39.49 | 765.59
4124 | TIN-INTERP | Interpolated Ground | 26247.34 | -4.6 | 744.22 | 0 | 27.05 | 0 | OK | Ground clear controls. | 62 | 39.49 | 771.27
4125 | TIN-INTERP | Interpolated Ground | 26287.23 | 6.6 | 742.4 | 0 | 19.89 | 0 | OK | Ground clear controls. | 62 | 39.49 | 762.29
4126 | TIN-INTERP | Interpolated Ground | 26287.24 | 5.1 | 742.71 | 0 | 14.18 | 0 | OK | Ground clear controls. | 62 | 39.49 | 756.89
4127 | TIN-INTERP | Interpolated Ground | 26287.26 | 4.6 | 742.7 | 0 | 24.85 | 0 | OK | Ground clear controls. | 62 | 39.49 | 767.55
4128 | TIN-INTERP | Interpolated Ground | 26287.28 | -5.1 | 743.18 | 0 | 14.08 | 0 | OK | Ground clear controls. | 62 | 39.49 | 757.26
4129 | TIN-INTERP | Interpolated Ground | 26287.31 | -6.6 | 743.27 | 0 | 18.94 | 0 | OK | Ground clear controls. | 62 | 39.49 | 762.21
4130 | TIN-INTERP | Interpolated Ground | 26287.34 | -4.6 | 743.14 | 0 | 24.79 | 0 | OK | Ground clear controls. | 62 | 39.49 | 767.93
4131 | TIN-INTERP | Interpolated Ground | 26327.23 | 6.6 | 741.49 | 0 | 18.35 | 0 | OK | Ground clear controls. | 62 | 39.49 | 759.84
4132 | TIN-INTERP | Interpolated Ground | 26327.24 | 5.1 | 741.58 | 0 | 12.88 | 0 | OK | Ground clear controls. | 62 | 39.49 | 754.46
4133 | TIN-INTERP | Interpolated Ground | 26327.26 | 4.6 | 741.57 | 0 | 23.51 | 0 | OK | Ground clear controls. | 62 | 39.49 | 765.08
4134 | TIN-INTERP | Interpolated Ground | 26327.28 | -5.1 | 741.78 | 0 | 13.1 | 0 | OK | Ground clear controls. | 62 | 39.49 | 754.88
4135 | TIN-INTERP | Interpolated Ground | 26327.31 | -6.6 | 741.99 | 0 | 17.77 | 0 | OK | Ground clear controls. | 62 | 39.49 | 759.76
4136 | TIN-INTERP | Interpolated Ground | 26327.34 | -4.6 | 741.69 | 0 | 23.82 | 0 | OK | Ground clear controls. | 62 | 39.49 | 765.51
4137 | TIN-INTERP | Interpolated Ground | 26367.23 | 6.6 | 740.31 | 0 | 18.01 | 0 | OK | Ground clear controls. | 62 | 39.49 | 758.32
4138 | TIN-INTERP | Interpolated Ground | 26367.24 | 5.1 | 740.34 | 0 | 12.61 | 0 | OK | Ground clear controls. | 62 | 39.49 | 752.95
4139 | TIN-INTERP | Interpolated Ground | 26367.26 | 4.6 | 740.35 | 0 | 23.2 | 0 | OK | Ground clear controls. | 62 | 39.49 | 763.55
4140 | TIN-INTERP | Interpolated Ground | 26367.28 | -5.1 | 740.61 | 0 | 12.78 | 0 | OK | Ground clear controls. | 62 | 39.49 | 753.39
4141 | TIN-INTERP | Interpolated Ground | 26367.31 | -6.6 | 740.61 | 0 | 17.63 | 0 | OK | Ground clear controls. | 62 | 39.49 | 758.24
4142 | TIN-INTERP | Interpolated Ground | 26367.34 | -4.6 | 740.61 | 0 | 23.39 | 0 | OK | Ground clear controls. | 62 | 39.49 | 764
4143 | TIN-INTERP | Interpolated Ground | 26407.23 | 6.6 | 739.53 | 0 | 18.19 | 0 | OK | Ground clear controls. | 62 | 39.49 | 757.72
4144 | TIN-INTERP | Interpolated Ground | 26407.24 | 5.1 | 739.55 | 0 | 12.79 | 0 | OK | Ground clear controls. | 62 | 39.49 | 752.34
4145 | TIN-INTERP | Interpolated Ground | 26407.26 | 4.6 | 739.56 | 0 | 23.38 | 0 | OK | Ground clear controls. | 62 | 39.49 | 762.94
4146 | TIN-INTERP | Interpolated Ground | 26407.28 | -5.1 | 739.62 | 0 | 13.18 | 0 | OK | Ground clear controls. | 62 | 39.49 | 752.8
4147 | TIN-INTERP | Interpolated Ground | 26407.31 | -6.6 | 739.65 | 0 | 17.99 | 0 | OK | Ground clear controls. | 62 | 39.49 | 757.64
4148 | TIN-INTERP | Interpolated Ground | 26407.34 | -4.6 | 739.63 | 0 | 23.77 | 0 | OK | Ground clear controls. | 62 | 39.49 | 763.4
4149 | TIN-INTERP | Interpolated Ground | 26447.23 | 6.6 | 739.7 | 0 | 18.34 | 0 | OK | Ground clear controls. | 62 | 39.49 | 758.04
4150 | TIN-INTERP | Interpolated Ground | 26447.24 | 5.1 | 739.75 | 0 | 12.91 | 0 | OK | Ground clear controls. | 62 | 39.49 | 752.66
4151 | TIN-INTERP | Interpolated Ground | 26447.26 | 4.6 | 739.76 | 0 | 23.51 | 0 | OK | Ground clear controls. | 62 | 39.49 | 763.27
4152 | TIN-INTERP | Interpolated Ground | 26447.28 | -5.1 | 739.51 | 0 | 13.6 | 0 | OK | Ground clear controls. | 62 | 39.49 | 753.11
4153 | TIN-INTERP | Interpolated Ground | 26447.31 | -6.6 | 740.16 | 0 | 17.79 | 0 | OK | Ground clear controls. | 62 | 39.49 | 757.95
4154 | TIN-INTERP | Interpolated Ground | 26447.34 | -4.6 | 739.21 | 0 | 24.51 | 0 | OK | Ground clear controls. | 62 | 39.49 | 763.72
4155 | TIN-INTERP | Interpolated Ground | 26487.23 | 6.6 | 739.35 | 0 | 19.94 | 0 | OK | Ground clear controls. | 62 | 39.49 | 759.29
4156 | TIN-INTERP | Interpolated Ground | 26487.24 | 5.1 | 739.54 | 0 | 14.36 | 0 | OK | Ground clear controls. | 62 | 39.49 | 753.9
4157 | TIN-INTERP | Interpolated Ground | 26487.26 | 4.6 | 739.5 | 0 | 25.03 | 0 | OK | Ground clear controls. | 62 | 39.49 | 764.53
4158 | TIN-INTERP | Interpolated Ground | 26487.28 | -5.1 | 738.9 | 0 | 15.42 | 0 | OK | Ground clear controls. | 62 | 39.49 | 754.32
4159 | TIN-INTERP | Interpolated Ground | 26487.31 | -6.6 | 739.37 | 0 | 19.84 | 0 | OK | Ground clear controls. | 62 | 39.49 | 759.21
4160 | TIN-INTERP | Interpolated Ground | 26487.34 | -4.6 | 738.71 | 0 | 26.24 | 0 | OK | Ground clear controls. | 62 | 39.49 | 764.95
4161 | TIN-INTERP | Interpolated Ground | 26527.23 | 6.6 | 739.31 | 0 | 22.13 | 0 | OK | Ground clear controls. | 62 | 39.49 | 761.44
4162 | TIN-INTERP | Interpolated Ground | 26527.24 | 5.1 | 739.38 | 0 | 16.67 | 0 | OK | Ground clear controls. | 62 | 39.49 | 756.05
4163 | TIN-INTERP | Interpolated Ground | 26527.26 | 4.6 | 739.35 | 0 | 27.37 | 0 | OK | Ground clear controls. | 62 | 39.49 | 766.72
4164 | TIN-INTERP | Interpolated Ground | 26527.28 | -5.1 | 738.75 | 0 | 17.67 | 0 | OK | Ground clear controls. | 62 | 39.49 | 756.42
4165 | TIN-INTERP | Interpolated Ground | 26527.31 | -6.6 | 739.4 | 0 | 21.99 | 0 | OK | Ground clear controls. | 62 | 39.49 | 761.39
4166 | TIN-INTERP | Interpolated Ground | 26527.34 | -4.6 | 738.5 | 0 | 28.6 | 0 | OK | Ground clear controls. | 62 | 39.49 | 767.1
4167 | TIN-INTERP | Interpolated Ground | 26567.23 | 6.6 | 739.17 | 0 | 25.36 | 0 | OK | Ground clear controls. | 62 | 39.49 | 764.53
4168 | TIN-INTERP | Interpolated Ground | 26567.24 | 5.1 | 739.25 | 0 | 19.87 | 0 | OK | Ground clear controls. | 62 | 39.49 | 759.12
4169 | TIN-INTERP | Interpolated Ground | 26567.26 | 4.6 | 739.23 | 0 | 30.62 | 0 | OK | Ground clear controls. | 62 | 39.49 | 769.85
4170 | TIN-INTERP | Interpolated Ground | 26567.28 | -5.1 | 739.01 | 0 | 20.41 | 0 | OK | Ground clear controls. | 62 | 39.49 | 759.42
4171 | TIN-INTERP | Interpolated Ground | 26567.31 | -6.6 | 739.34 | 0 | 25.16 | 0 | OK | Ground clear controls. | 62 | 39.49 | 764.5
4172 | TIN-INTERP | Interpolated Ground | 26567.34 | -4.6 | 738.87 | 0 | 31.29 | 0 | OK | Ground clear controls. | 62 | 39.49 | 770.16
4173 | TIN-INTERP | Interpolated Ground | 26607.23 | 6.6 | 738.85 | 0 | 29.69 | 0 | OK | Ground clear controls. | 62 | 39.49 | 768.54
4174 | TIN-INTERP | Interpolated Ground | 26607.24 | 5.1 | 738.96 | 0 | 24.15 | 0 | OK | Ground clear controls. | 62 | 39.49 | 763.11
4175 | TIN-INTERP | Interpolated Ground | 26607.26 | 4.6 | 739 | 0 | 34.92 | 0 | OK | Ground clear controls. | 62 | 39.49 | 773.92
4176 | TIN-INTERP | Interpolated Ground | 26607.28 | -5.1 | 739.46 | 0 | 23.86 | 0 | OK | Ground clear controls. | 62 | 39.49 | 763.32
4177 | TIN-INTERP | Interpolated Ground | 26607.31 | -6.6 | 739.52 | 0 | 29.01 | 0 | OK | Ground clear controls. | 62 | 39.49 | 768.53
4178 | TIN-INTERP | Interpolated Ground | 26607.34 | -4.6 | 739.46 | 0 | 34.69 | 0 | OK | Ground clear controls. | 62 | 39.49 | 774.15
4179 | TIN-INTERP | Interpolated Ground | 26647.23 | 6.6 | 739.2 | 0 | 34.28 | 0 | OK | Ground clear controls. | 62 | 39.49 | 773.48
4180 | TIN-INTERP | Interpolated Ground | 26647.24 | 5.1 | 739.39 | 0 | 28.63 | 0 | OK | Ground clear controls. | 62 | 39.49 | 768.02
4181 | TIN-INTERP | Interpolated Ground | 26647.26 | 4.6 | 739.45 | 0 | 39.49 | 0 | OK | Ground clear controls. | 62 | 39.49 | 778.94
4182 | TIN-INTERP | Interpolated Ground | 26647.28 | -5.1 | 739.75 | 0 | 28.39 | 0 | OK | Ground clear controls. | 62 | 39.29 | 768.14
4183 | TIN-INTERP | Interpolated Ground | 26647.31 | -6.6 | 739.71 | 0 | 33.79 | 0 | OK | Ground clear controls. | 62 | 39.29 | 773.5
4184 | TIN-INTERP | Interpolated Ground | 26647.34 | -4.6 | 739.77 | 0 | 39.29 | 0 | OK | Ground clear controls. | 62 | 39.29 | 779.06
4185 | TIN-INTERP | Interpolated Ground | 26680.5 | -6.6 | 740.24 | 0 | 38.08 | 0 | OK | Ground clear controls. | 63 | 44.33 | 778.32
4186 | TIN-INTERP | Interpolated Ground | 26680.55 | -5.1 | 739.95 | 0 | 32.87 | 0 | OK | Ground clear controls. | 63 | 44.33 | 772.82
4187 | TIN-INTERP | Interpolated Ground | 26680.56 | -4.6 | 739.77 | 0 | 44.05 | 0 | OK | Ground clear controls. | 63 | 44.33 | 783.82
4188 | TIN-INTERP | Interpolated Ground | 26680.58 | 4.6 | 739.49 | 0 | 44.33 | 0 | OK | Ground clear controls. | 63 | 44.33 | 783.82
4189 | TIN-INTERP | Interpolated Ground | 26680.6 | 5.1 | 739.44 | 0 | 33.38 | 0 | OK | Ground clear controls. | 63 | 39.04 | 772.82
4190 | TIN-INTERP | Interpolated Ground | 26680.73 | 6.6 | 739.29 | 0 | 39.04 | 0 | OK | Ground clear controls. | 63 | 39.04 | 778.33
4191 | TIN-INTERP | Interpolated Ground | 26720.5 | -6.6 | 740.56 | 0 | 32.44 | 0 | OK | Ground clear controls. | 63 | 38.87 | 773
4192 | TIN-INTERP | Interpolated Ground | 26720.55 | -5.1 | 740.55 | 0 | 27.14 | 0 | OK | Ground clear controls. | 63 | 38.87 | 767.69
4193 | TIN-INTERP | Interpolated Ground | 26720.56 | -4.6 | 740.54 | 0 | 38.05 | 0 | OK | Ground clear controls. | 63 | 38.87 | 778.59
4194 | TIN-INTERP | Interpolated Ground | 26720.58 | 4.6 | 740.09 | 0 | 38.36 | 0 | OK | Ground clear controls. | 63 | 38.87 | 778.45
4195 | TIN-INTERP | Interpolated Ground | 26720.6 | 5.1 | 740.08 | 0 | 27.48 | 0 | OK | Ground clear controls. | 63 | 38.87 | 767.56
4196 | TIN-INTERP | Interpolated Ground | 26720.73 | 6.6 | 739.98 | 0 | 33.13 | 0 | OK | Ground clear controls. | 63 | 38.87 | 773.11
4197 | TIN-INTERP | Interpolated Ground | 26760.5 | -6.6 | 741 | 0 | 27.6 | 0 | OK | Ground clear controls. | 63 | 38.87 | 768.6
4198 | TIN-INTERP | Interpolated Ground | 26760.55 | -5.1 | 741 | 0 | 22.45 | 0 | OK | Ground clear controls. | 63 | 38.87 | 763.45
4199 | TIN-INTERP | Interpolated Ground | 26760.56 | -4.6 | 740.97 | 0 | 33.31 | 0 | OK | Ground clear controls. | 63 | 38.87 | 774.28
4200 | TIN-INTERP | Interpolated Ground | 26760.58 | 4.6 | 740.59 | 0 | 33.41 | 0 | OK | Ground clear controls. | 63 | 38.87 | 774
4201 | TIN-INTERP | Interpolated Ground | 26760.6 | 5.1 | 740.53 | 0 | 22.67 | 0 | OK | Ground clear controls. | 63 | 38.87 | 763.2
4202 | TIN-INTERP | Interpolated Ground | 26760.73 | 6.6 | 739.99 | 0 | 28.8 | 0 | OK | Ground clear controls. | 63 | 38.87 | 768.79
4203 | TIN-INTERP | Interpolated Ground | 26800.5 | -6.6 | 741.56 | 0 | 23.58 | 0 | OK | Ground clear controls. | 63 | 38.87 | 765.14
4204 | TIN-INTERP | Interpolated Ground | 26800.55 | -5.1 | 741.53 | 0 | 18.57 | 0 | OK | Ground clear controls. | 63 | 38.87 | 760.1
4205 | TIN-INTERP | Interpolated Ground | 26800.56 | -4.6 | 741.58 | 0 | 29.29 | 0 | OK | Ground clear controls. | 63 | 38.87 | 770.87
4206 | TIN-INTERP | Interpolated Ground | 26800.58 | 4.6 | 741.04 | 0 | 29.45 | 0 | OK | Ground clear controls. | 63 | 38.87 | 770.49
4207 | TIN-INTERP | Interpolated Ground | 26800.6 | 5.1 | 740.85 | 0 | 18.92 | 0 | OK | Ground clear controls. | 63 | 38.87 | 759.77
4208 | TIN-INTERP | Interpolated Ground | 26800.73 | 6.6 | 740.47 | 0 | 24.92 | 0 | OK | Ground clear controls. | 63 | 38.87 | 765.39
4209 | TIN-INTERP | Interpolated Ground | 26840.5 | -6.6 | 741.43 | 0 | 21.16 | 0 | OK | Ground clear controls. | 63 | 38.87 | 762.59
4210 | TIN-INTERP | Interpolated Ground | 26840.55 | -5.1 | 741.42 | 0 | 16.22 | 0 | OK | Ground clear controls. | 63 | 38.87 | 757.64
4211 | TIN-INTERP | Interpolated Ground | 26840.56 | -4.6 | 741.41 | 0 | 26.95 | 0 | OK | Ground clear controls. | 63 | 38.87 | 768.36
4212 | TIN-INTERP | Interpolated Ground | 26840.58 | 4.6 | 741.47 | 0 | 26.44 | 0 | OK | Ground clear controls. | 63 | 38.87 | 767.91
4213 | TIN-INTERP | Interpolated Ground | 26840.6 | 5.1 | 741.48 | 0 | 15.76 | 0 | OK | Ground clear controls. | 63 | 38.87 | 757.24
4214 | TIN-INTERP | Interpolated Ground | 26840.73 | 6.6 | 741.5 | 0 | 21.39 | 0 | OK | Ground clear controls. | 63 | 38.87 | 762.89
4215 | TIN-INTERP | Interpolated Ground | 26880.5 | -6.6 | 742.51 | 0 | 18.44 | 0 | OK | Ground clear controls. | 63 | 38.87 | 760.95
4216 | TIN-INTERP | Interpolated Ground | 26880.55 | -5.1 | 742.51 | 0 | 13.56 | 0 | OK | Ground clear controls. | 63 | 38.87 | 756.07
4217 | TIN-INTERP | Interpolated Ground | 26880.56 | -4.6 | 742.51 | 0 | 24.25 | 0 | OK | Ground clear controls. | 63 | 38.87 | 766.76
4218 | TIN-INTERP | Interpolated Ground | 26880.58 | 4.6 | 742.54 | 0 | 23.71 | 0 | OK | Ground clear controls. | 63 | 38.87 | 766.25
4219 | TIN-INTERP | Interpolated Ground | 26880.6 | 5.1 | 742.41 | 0 | 13.21 | 0 | OK | Ground clear controls. | 63 | 38.87 | 755.62
4220 | TIN-INTERP | Interpolated Ground | 26880.73 | 6.6 | 742.21 | 0 | 19.09 | 0 | OK | Ground clear controls. | 63 | 38.87 | 761.3
4221 | TIN-INTERP | Interpolated Ground | 26920.5 | -6.6 | 742.67 | 0 | 17.58 | 0 | OK | Ground clear controls. | 63 | 38.87 | 760.25
4222 | TIN-INTERP | Interpolated Ground | 26920.55 | -5.1 | 742.73 | 0 | 12.67 | 0 | OK | Ground clear controls. | 63 | 38.87 | 755.4
4223 | TIN-INTERP | Interpolated Ground | 26920.56 | -4.6 | 742.77 | 0 | 23.3 | 0 | OK | Ground clear controls. | 63 | 38.87 | 766.07
4224 | TIN-INTERP | Interpolated Ground | 26920.58 | 4.6 | 742.27 | 0 | 23.27 | 0 | OK | Ground clear controls. | 63 | 38.87 | 765.54
4225 | TIN-INTERP | Interpolated Ground | 26920.6 | 5.1 | 742.36 | 0 | 12.57 | 0 | OK | Ground clear controls. | 63 | 38.87 | 754.93
4226 | TIN-INTERP | Interpolated Ground | 26920.73 | 6.6 | 742.49 | 0 | 18.11 | 0 | OK | Ground clear controls. | 63 | 38.87 | 760.6
4227 | TIN-INTERP | Interpolated Ground | 26960.5 | -6.6 | 742.53 | 0 | 17.92 | 0 | OK | Ground clear controls. | 63 | 38.87 | 760.45
4228 | TIN-INTERP | Interpolated Ground | 26960.55 | -5.1 | 742.57 | 0 | 13.03 | 0 | OK | Ground clear controls. | 63 | 38.87 | 755.6
4229 | TIN-INTERP | Interpolated Ground | 26960.56 | -4.6 | 742.57 | 0 | 23.7 | 0 | OK | Ground clear controls. | 63 | 38.87 | 766.27
4230 | TIN-INTERP | Interpolated Ground | 26960.58 | 4.6 | 742.19 | 0 | 23.55 | 0 | OK | Ground clear controls. | 63 | 38.87 | 765.74
4231 | TIN-INTERP | Interpolated Ground | 26960.6 | 5.1 | 742.08 | 0 | 13.05 | 0 | OK | Ground clear controls. | 63 | 38.87 | 755.13
4232 | TIN-INTERP | Interpolated Ground | 26960.73 | 6.6 | 742.07 | 0 | 18.75 | 0 | OK | Ground clear controls. | 63 | 38.87 | 760.82
4233 | TIN-INTERP | Interpolated Ground | 27000.5 | -6.6 | 742.49 | 0 | 19.1 | 0 | OK | Ground clear controls. | 63 | 38.87 | 761.59
4234 | TIN-INTERP | Interpolated Ground | 27000.55 | -5.1 | 742.52 | 0 | 14.19 | 0 | OK | Ground clear controls. | 63 | 38.87 | 756.71
4235 | TIN-INTERP | Interpolated Ground | 27000.56 | -4.6 | 742.5 | 0 | 24.89 | 0 | OK | Ground clear controls. | 63 | 38.87 | 767.39
4236 | TIN-INTERP | Interpolated Ground | 27000.58 | 4.6 | 742.2 | 0 | 24.69 | 0 | OK | Ground clear controls. | 63 | 38.87 | 766.89
4237 | TIN-INTERP | Interpolated Ground | 27000.6 | 5.1 | 742.1 | 0 | 14.17 | 0 | OK | Ground clear controls. | 63 | 38.87 | 756.27
4238 | TIN-INTERP | Interpolated Ground | 27000.73 | 6.6 | 742.08 | 0 | 19.85 | 0 | OK | Ground clear controls. | 63 | 38.87 | 761.93
4239 | TIN-INTERP | Interpolated Ground | 27040.5 | -6.6 | 742.12 | 0 | 21.51 | 0 | OK | Ground clear controls. | 63 | 38.87 | 763.63
4240 | TIN-INTERP | Interpolated Ground | 27040.55 | -5.1 | 742.19 | 0 | 16.5 | 0 | OK | Ground clear controls. | 63 | 38.87 | 758.69
4241 | TIN-INTERP | Interpolated Ground | 27040.56 | -4.6 | 742.19 | 0 | 27.23 | 0 | OK | Ground clear controls. | 63 | 38.87 | 769.42
4242 | TIN-INTERP | Interpolated Ground | 27040.58 | 4.6 | 741.93 | 0 | 27.04 | 0 | OK | Ground clear controls. | 63 | 38.87 | 768.97
4243 | TIN-INTERP | Interpolated Ground | 27040.6 | 5.1 | 741.88 | 0 | 16.42 | 0 | OK | Ground clear controls. | 63 | 38.87 | 758.3
4244 | TIN-INTERP | Interpolated Ground | 27040.73 | 6.6 | 741.9 | 0 | 22.05 | 0 | OK | Ground clear controls. | 63 | 38.87 | 763.95
4245 | TIN-INTERP | Interpolated Ground | 27080.5 | -6.6 | 742.12 | 0 | 24.49 | 0 | OK | Ground clear controls. | 63 | 38.87 | 766.61
4246 | TIN-INTERP | Interpolated Ground | 27080.55 | -5.1 | 741.86 | 0 | 19.7 | 0 | OK | Ground clear controls. | 63 | 38.87 | 761.56
4247 | TIN-INTERP | Interpolated Ground | 27080.56 | -4.6 | 741.74 | 0 | 30.6 | 0 | OK | Ground clear controls. | 63 | 38.87 | 772.34
4248 | TIN-INTERP | Interpolated Ground | 27080.58 | 4.6 | 741.61 | 0 | 30.36 | 0 | OK | Ground clear controls. | 63 | 38.87 | 771.97
4249 | TIN-INTERP | Interpolated Ground | 27080.6 | 5.1 | 741.6 | 0 | 19.65 | 0 | OK | Ground clear controls. | 63 | 38.87 | 761.25
4250 | TIN-INTERP | Interpolated Ground | 27080.73 | 6.6 | 741.7 | 0 | 25.17 | 0 | OK | Ground clear controls. | 63 | 38.87 | 766.87
4251 | TIN-INTERP | Interpolated Ground | 27120.5 | -6.6 | 741.84 | 0 | 28.67 | 0 | OK | Ground clear controls. | 63 | 38.87 | 770.51
4252 | TIN-INTERP | Interpolated Ground | 27120.55 | -5.1 | 741.84 | 0 | 23.49 | 0 | OK | Ground clear controls. | 63 | 38.87 | 765.33
4253 | TIN-INTERP | Interpolated Ground | 27120.56 | -4.6 | 741.85 | 0 | 34.32 | 0 | OK | Ground clear controls. | 63 | 38.87 | 776.17
4254 | TIN-INTERP | Interpolated Ground | 27120.58 | 4.6 | 741.98 | 0 | 33.93 | 0 | OK | Ground clear controls. | 63 | 38.87 | 775.91
4255 | TIN-INTERP | Interpolated Ground | 27120.6 | 5.1 | 741.86 | 0 | 23.25 | 0 | OK | Ground clear controls. | 63 | 38.87 | 765.11
4256 | TIN-INTERP | Interpolated Ground | 27120.73 | 6.6 | 741.85 | 0 | 28.85 | 0 | OK | Ground clear controls. | 63 | 38.87 | 770.7
4257 | TIN-INTERP | Interpolated Ground | 27160.5 | -6.6 | 742.02 | 0 | 33.31 | 0 | OK | Ground clear controls. | 63 | 38.87 | 775.33
4258 | TIN-INTERP | Interpolated Ground | 27160.55 | -5.1 | 742.02 | 0 | 27.97 | 0 | OK | Ground clear controls. | 63 | 38.87 | 769.99
4259 | TIN-INTERP | Interpolated Ground | 27160.56 | -4.6 | 742.04 | 0 | 38.87 | 0 | OK | Ground clear controls. | 63 | 38.87 | 780.91
4260 | TIN-INTERP | Interpolated Ground | 27160.58 | 4.6 | 741.99 | 0 | 38.79 | 0 | OK | Ground clear controls. | 63 | 38.79 | 780.78
4261 | TIN-INTERP | Interpolated Ground | 27160.6 | 5.1 | 741.94 | 0 | 27.94 | 0 | OK | Ground clear controls. | 63 | 33.49 | 769.88
4262 | TIN-INTERP | Interpolated Ground | 27160.73 | 6.6 | 741.95 | 0 | 33.49 | 0 | OK | Ground clear controls. | 63 | 33.49 | 775.44
4263 | TIN-INTERP | Interpolated Ground | 27196.23 | 4.6 | 742.01 | 0 | 43.9 | 0 | OK | Ground clear controls. | 64 | 43.9 | 785.91
4264 | TIN-INTERP | Interpolated Ground | 27196.25 | -6.6 | 742.17 | 0 | 38.24 | 0 | OK | Ground clear controls. | 64 | 43.75 | 780.41
4265 | TIN-INTERP | Interpolated Ground | 27196.25 | -4.6 | 742.16 | 0 | 43.75 | 0 | OK | Ground clear controls. | 64 | 43.75 | 785.91
4266 | TIN-INTERP | Interpolated Ground | 27196.26 | 5.1 | 742.03 | 0 | 32.88 | 0 | OK | Ground clear controls. | 64 | 38.45 | 774.91
4267 | TIN-INTERP | Interpolated Ground | 27196.26 | 6.6 | 741.96 | 0 | 38.45 | 0 | OK | Ground clear controls. | 64 | 38.45 | 780.41
4268 | TIN-INTERP | Interpolated Ground | 27196.27 | -5.1 | 742.16 | 0 | 32.75 | 0 | OK | Ground clear controls. | 64 | 37.73 | 774.91
4269 | TIN-INTERP | Interpolated Ground | 27236.23 | 4.6 | 742.04 | 0 | 37.55 | 0 | OK | Ground clear controls. | 64 | 37.73 | 779.59
4270 | TIN-INTERP | Interpolated Ground | 27236.25 | -6.6 | 742.05 | 0 | 32.12 | 0 | OK | Ground clear controls. | 64 | 37.73 | 774.17
4271 | TIN-INTERP | Interpolated Ground | 27236.25 | -4.6 | 742.03 | 0 | 37.73 | 0 | OK | Ground clear controls. | 64 | 37.73 | 779.76
4272 | TIN-INTERP | Interpolated Ground | 27236.26 | 5.1 | 741.97 | 0 | 26.75 | 0 | OK | Ground clear controls. | 64 | 34.07 | 768.72
4273 | TIN-INTERP | Interpolated Ground | 27236.26 | 6.6 | 741.9 | 0 | 32.37 | 0 | OK | Ground clear controls. | 64 | 34.07 | 774.27
4274 | TIN-INTERP | Interpolated Ground | 27236.27 | -5.1 | 742 | 0 | 26.86 | 0 | OK | Ground clear controls. | 64 | 34.07 | 768.86
4275 | TIN-INTERP | Interpolated Ground | 27276.23 | 4.59 | 741.42 | 0 | 32.78 | 0 | OK | Ground clear controls. | 64 | 34.07 | 774.2
4276 | TIN-INTERP | Interpolated Ground | 27276.25 | -6.61 | 742.23 | 0 | 26.61 | 0 | OK | Ground clear controls. | 64 | 34.07 | 768.84
4277 | TIN-INTERP | Interpolated Ground | 27276.25 | -4.61 | 742.18 | 0 | 32.33 | 0 | OK | Ground clear controls. | 64 | 34.07 | 774.51
4278 | TIN-INTERP | Interpolated Ground | 27276.26 | 5.09 | 741.18 | 0 | 22.26 | 0 | OK | Ground clear controls. | 64 | 34.07 | 763.44
4279 | TIN-INTERP | Interpolated Ground | 27276.26 | 6.59 | 741.22 | 0 | 27.81 | 0 | OK | Ground clear controls. | 64 | 34.07 | 769.03
4280 | TIN-INTERP | Interpolated Ground | 27276.27 | -5.11 | 742.19 | 0 | 21.52 | 0 | OK | Ground clear controls. | 64 | 34.07 | 763.71
4281 | TIN-INTERP | Interpolated Ground | 27316.23 | 4.59 | 739.66 | 0 | 30.08 | 0 | OK | Ground clear controls. | 64 | 34.07 | 769.74
4282 | TIN-INTERP | Interpolated Ground | 27316.25 | -6.61 | 740.45 | 0 | 24 | 0 | OK | Ground clear controls. | 64 | 34.07 | 764.45
4283 | TIN-INTERP | Interpolated Ground | 27316.25 | -4.61 | 740.19 | 0 | 29.98 | 0 | OK | Ground clear controls. | 64 | 34.07 | 770.17
4284 | TIN-INTERP | Interpolated Ground | 27316.26 | 5.09 | 739.59 | 0 | 19.48 | 0 | OK | Ground clear controls. | 64 | 34.07 | 759.07
4285 | TIN-INTERP | Interpolated Ground | 27316.26 | 6.59 | 739.66 | 0 | 25.04 | 0 | OK | Ground clear controls. | 64 | 34.07 | 764.7
4286 | TIN-INTERP | Interpolated Ground | 27316.27 | -5.11 | 740.28 | 0 | 19.16 | 0 | OK | Ground clear controls. | 64 | 34.07 | 759.44
4287 | TIN-INTERP | Interpolated Ground | 27356.23 | 4.58 | 738.74 | 0 | 27.48 | 0 | OK | Ground clear controls. | 64 | 34.07 | 766.22
4288 | TIN-INTERP | Interpolated Ground | 27356.25 | -6.62 | 738.62 | 0 | 22.35 | 0 | OK | Ground clear controls. | 64 | 34.07 | 760.97
4289 | TIN-INTERP | Interpolated Ground | 27356.25 | -4.62 | 738.17 | 0 | 28.56 | 0 | OK | Ground clear controls. | 64 | 34.07 | 766.73
4290 | TIN-INTERP | Interpolated Ground | 27356.26 | 5.08 | 738.71 | 0 | 16.91 | 0 | OK | Ground clear controls. | 64 | 34.07 | 755.62
4291 | TIN-INTERP | Interpolated Ground | 27356.26 | 6.58 | 738.68 | 0 | 22.59 | 0 | OK | Ground clear controls. | 64 | 34.07 | 761.27
4292 | TIN-INTERP | Interpolated Ground | 27356.27 | -5.12 | 738.12 | 0 | 17.92 | 0 | OK | Ground clear controls. | 64 | 34.07 | 756.04
4293 | TIN-INTERP | Interpolated Ground | 27396.23 | 4.58 | 737.98 | 0 | 25.65 | 0 | OK | Ground clear controls. | 64 | 34.07 | 763.63
4294 | TIN-INTERP | Interpolated Ground | 27396.25 | -6.62 | 738.2 | 0 | 20.2 | 0 | OK | Ground clear controls. | 64 | 34.07 | 758.4
4295 | TIN-INTERP | Interpolated Ground | 27396.25 | -4.62 | 738.23 | 0 | 25.97 | 0 | OK | Ground clear controls. | 64 | 34.07 | 764.2
4296 | TIN-INTERP | Interpolated Ground | 27396.26 | 5.08 | 737.94 | 0 | 15.13 | 0 | OK | Ground clear controls. | 64 | 34.07 | 753.07
4297 | TIN-INTERP | Interpolated Ground | 27396.26 | 6.58 | 738.02 | 0 | 20.71 | 0 | OK | Ground clear controls. | 64 | 34.07 | 758.73
4298 | TIN-INTERP | Interpolated Ground | 27396.27 | -5.12 | 738.24 | 0 | 15.3 | 0 | OK | Ground clear controls. | 64 | 34.07 | 753.54
4299 | TIN-INTERP | Interpolated Ground | 27436.23 | 4.57 | 737.38 | 0 | 24.59 | 0 | OK | Ground clear controls. | 64 | 34.07 | 761.97
4300 | TIN-INTERP | Interpolated Ground | 27436.25 | -6.63 | 737.76 | 0 | 18.99 | 0 | OK | Ground clear controls. | 64 | 34.07 | 756.75
4301 | TIN-INTERP | Interpolated Ground | 27436.25 | -4.63 | 737.67 | 0 | 24.89 | 0 | OK | Ground clear controls. | 64 | 34.07 | 762.56
4302 | TIN-INTERP | Interpolated Ground | 27436.26 | 5.07 | 737.43 | 0 | 14 | 0 | OK | Ground clear controls. | 64 | 34.07 | 751.43
4303 | TIN-INTERP | Interpolated Ground | 27436.26 | 6.57 | 737.54 | 0 | 19.56 | 0 | OK | Ground clear controls. | 64 | 34.07 | 757.1
4304 | TIN-INTERP | Interpolated Ground | 27436.27 | -5.13 | 737.6 | 0 | 14.32 | 0 | OK | Ground clear controls. | 64 | 34.07 | 751.92
4305 | TIN-INTERP | Interpolated Ground | 27476.23 | 4.57 | 737.02 | 0 | 24.21 | 0 | OK | Ground clear controls. | 64 | 34.07 | 761.23
4306 | TIN-INTERP | Interpolated Ground | 27476.25 | -6.63 | 737.28 | 0 | 18.73 | 0 | OK | Ground clear controls. | 64 | 34.07 | 756.01
4307 | TIN-INTERP | Interpolated Ground | 27476.25 | -4.63 | 737.25 | 0 | 24.58 | 0 | OK | Ground clear controls. | 64 | 34.07 | 761.83
4308 | TIN-INTERP | Interpolated Ground | 27476.26 | 5.07 | 737.06 | 0 | 13.63 | 0 | OK | Ground clear controls. | 64 | 34.07 | 750.69
4309 | TIN-INTERP | Interpolated Ground | 27476.26 | 6.57 | 737.15 | 0 | 19.21 | 0 | OK | Ground clear controls. | 64 | 34.07 | 756.36
4310 | TIN-INTERP | Interpolated Ground | 27476.27 | -5.13 | 737.22 | 0 | 13.96 | 0 | OK | Ground clear controls. | 64 | 34.07 | 751.18
4311 | TIN-INTERP | Interpolated Ground | 27516.23 | 4.56 | 736.9 | 0 | 24.52 | 0 | OK | Ground clear controls. | 64 | 34.07 | 761.42
4312 | TIN-INTERP | Interpolated Ground | 27516.25 | -6.64 | 737.07 | 0 | 19.12 | 0 | OK | Ground clear controls. | 64 | 34.07 | 756.19
4313 | TIN-INTERP | Interpolated Ground | 27516.25 | -4.64 | 737.02 | 0 | 24.97 | 0 | OK | Ground clear controls. | 64 | 34.07 | 761.99
4314 | TIN-INTERP | Interpolated Ground | 27516.26 | 5.06 | 736.93 | 0 | 13.92 | 0 | OK | Ground clear controls. | 64 | 34.07 | 750.85
4315 | TIN-INTERP | Interpolated Ground | 27516.26 | 6.56 | 736.98 | 0 | 19.54 | 0 | OK | Ground clear controls. | 64 | 34.07 | 756.52
4316 | TIN-INTERP | Interpolated Ground | 27516.27 | -5.14 | 737.03 | 0 | 14.3 | 0 | OK | Ground clear controls. | 64 | 34.07 | 751.33
4317 | TIN-INTERP | Interpolated Ground | 27556.23 | 4.56 | 737.31 | 0 | 25.24 | 0 | OK | Ground clear controls. | 64 | 34.07 | 762.55
4318 | TIN-INTERP | Interpolated Ground | 27556.25 | -6.64 | 737.33 | 0 | 19.96 | 0 | OK | Ground clear controls. | 64 | 34.07 | 757.29
4319 | TIN-INTERP | Interpolated Ground | 27556.25 | -4.64 | 737.35 | 0 | 25.7 | 0 | OK | Ground clear controls. | 64 | 34.07 | 763.05
4320 | TIN-INTERP | Interpolated Ground | 27556.26 | 5.06 | 737.32 | 0 | 14.62 | 0 | OK | Ground clear controls. | 64 | 34.07 | 751.94
4321 | TIN-INTERP | Interpolated Ground | 27556.26 | 6.56 | 737.43 | 0 | 20.15 | 0 | OK | Ground clear controls. | 64 | 34.07 | 757.58
4322 | TIN-INTERP | Interpolated Ground | 27556.27 | -5.14 | 737.32 | 0 | 15.03 | 0 | OK | Ground clear controls. | 64 | 34.07 | 752.35
4323 | TIN-INTERP | Interpolated Ground | 27596.23 | 4.55 | 737.91 | 0 | 26.68 | 0 | OK | Ground clear controls. | 64 | 34.07 | 764.59
4324 | TIN-INTERP | Interpolated Ground | 27596.25 | -6.65 | 738.39 | 0 | 20.9 | 0 | OK | Ground clear controls. | 64 | 34.07 | 759.29
4325 | TIN-INTERP | Interpolated Ground | 27596.25 | -4.65 | 738.45 | 0 | 26.55 | 0 | OK | Ground clear controls. | 64 | 34.07 | 765
4326 | TIN-INTERP | Interpolated Ground | 27596.26 | 5.05 | 737.92 | 0 | 15.99 | 0 | OK | Ground clear controls. | 64 | 34.07 | 753.91
4327 | TIN-INTERP | Interpolated Ground | 27596.26 | 6.55 | 738.01 | 0 | 21.52 | 0 | OK | Ground clear controls. | 64 | 34.07 | 759.53
4328 | TIN-INTERP | Interpolated Ground | 27596.27 | -5.15 | 738.46 | 0 | 15.8 | 0 | OK | Ground clear controls. | 64 | 34.07 | 754.26
4329 | TIN-INTERP | Interpolated Ground | 27636.23 | 4.55 | 737.5 | 0 | 30.07 | 0 | OK | Ground clear controls. | 64 | 34.07 | 767.57
4330 | TIN-INTERP | Interpolated Ground | 27636.25 | -6.65 | 737.86 | 0 | 24.36 | 0 | OK | Ground clear controls. | 64 | 34.07 | 762.22
4331 | TIN-INTERP | Interpolated Ground | 27636.25 | -4.65 | 737.76 | 0 | 30.11 | 0 | OK | Ground clear controls. | 64 | 34.07 | 767.87
4332 | TIN-INTERP | Interpolated Ground | 27636.26 | 5.05 | 737.54 | 0 | 19.26 | 0 | OK | Ground clear controls. | 64 | 34.07 | 756.8
4333 | TIN-INTERP | Interpolated Ground | 27636.26 | 6.55 | 737.68 | 0 | 24.7 | 0 | OK | Ground clear controls. | 64 | 34.07 | 762.38
4334 | TIN-INTERP | Interpolated Ground | 27636.27 | -5.15 | 737.86 | 0 | 19.18 | 0 | OK | Ground clear controls. | 64 | 34.07 | 757.04
4335 | TIN-INTERP | Interpolated Ground | 27676.23 | 4.54 | 737.64 | 0 | 33.84 | 0 | OK | Ground clear controls. | 64 | 34.07 | 771.48
4336 | TIN-INTERP | Interpolated Ground | 27676.25 | -6.66 | 737.41 | 0 | 28.64 | 0 | OK | Ground clear controls. | 64 | 34.07 | 766.05
4337 | TIN-INTERP | Interpolated Ground | 27676.25 | -4.66 | 737.55 | 0 | 34.07 | 0 | OK | Ground clear controls. | 64 | 34.07 | 771.62
4338 | TIN-INTERP | Interpolated Ground | 27676.26 | 5.04 | 737.68 | 0 | 22.91 | 0 | OK | Ground clear controls. | 64 | 28.34 | 760.59
4339 | TIN-INTERP | Interpolated Ground | 27676.26 | 6.54 | 737.79 | 0 | 28.34 | 0 | OK | Ground clear controls. | 64 | 28.34 | 766.13
4340 | TIN-INTERP | Interpolated Ground | 27676.27 | -5.16 | 737.52 | 0 | 23.2 | 0 | OK | Ground clear controls. | 64 | 23.2 | 760.72
4341 | TIN-INTERP | Interpolated Ground | 27709.42 | 4.54 | 737.2 | 0 | 38.23 | 0 | OK | Ground clear controls. | 65 | 38.72 | 775.43
4342 | TIN-INTERP | Interpolated Ground | 27709.42 | -5.16 | 737.28 | 0 | 27.15 | 0 | OK | Ground clear controls. | 65 | 38.72 | 764.43
4343 | TIN-INTERP | Interpolated Ground | 27709.43 | -4.66 | 737.25 | 0 | 38.18 | 0 | OK | Ground clear controls. | 65 | 38.72 | 775.43
4344 | TIN-INTERP | Interpolated Ground | 27709.44 | 6.54 | 737.07 | 0 | 32.86 | 0 | OK | Ground clear controls. | 65 | 38.72 | 769.93
4345 | TIN-INTERP | Interpolated Ground | 27709.45 | -6.66 | 737.19 | 0 | 32.74 | 0 | OK | Ground clear controls. | 65 | 38.72 | 769.93
4346 | TIN-INTERP | Interpolated Ground | 27709.46 | 5.04 | 737.11 | 0 | 27.32 | 0 | OK | Ground clear controls. | 65 | 38.72 | 764.43
4347 | TIN-INTERP | Interpolated Ground | 27749.41 | 4.52 | 734.78 | 0 | 34.97 | 0 | OK | Ground clear controls. | 65 | 38.72 | 769.75
4348 | TIN-INTERP | Interpolated Ground | 27749.42 | -5.19 | 735.77 | 0 | 23.26 | 0 | OK | Ground clear controls. | 65 | 38.72 | 759.03
4349 | TIN-INTERP | Interpolated Ground | 27749.43 | -4.69 | 735.75 | 0 | 34.18 | 0 | OK | Ground clear controls. | 65 | 38.72 | 769.93
4350 | TIN-INTERP | Interpolated Ground | 27749.44 | 6.52 | 734.57 | 0 | 29.88 | 0 | OK | Ground clear controls. | 65 | 38.72 | 764.45
4351 | TIN-INTERP | Interpolated Ground | 27749.45 | -6.69 | 735.83 | 0 | 28.52 | 0 | OK | Ground clear controls. | 65 | 38.72 | 764.35
4352 | TIN-INTERP | Interpolated Ground | 27749.46 | 5.02 | 734.66 | 0 | 24.25 | 0 | OK | Ground clear controls. | 65 | 38.72 | 758.91
4353 | TIN-INTERP | Interpolated Ground | 27789.41 | 4.5 | 732.99 | 0 | 32.01 | 0 | OK | Ground clear controls. | 65 | 38.72 | 765
4354 | TIN-INTERP | Interpolated Ground | 27789.42 | -5.21 | 733.36 | 0 | 21.15 | 0 | OK | Ground clear controls. | 65 | 38.72 | 754.51
4355 | TIN-INTERP | Interpolated Ground | 27789.43 | -4.71 | 733.3 | 0 | 32.03 | 0 | OK | Ground clear controls. | 65 | 38.72 | 765.33
4356 | TIN-INTERP | Interpolated Ground | 27789.44 | 6.5 | 733.07 | 0 | 26.78 | 0 | OK | Ground clear controls. | 65 | 38.72 | 759.85
4357 | TIN-INTERP | Interpolated Ground | 27789.45 | -6.71 | 733.48 | 0 | 26.21 | 0 | OK | Ground clear controls. | 65 | 38.72 | 759.69
4358 | TIN-INTERP | Interpolated Ground | 27789.46 | 5 | 733.02 | 0 | 21.27 | 0 | OK | Ground clear controls. | 65 | 38.72 | 754.29
4359 | TIN-INTERP | Interpolated Ground | 27829.41 | 4.48 | 732.42 | 0 | 28.76 | 0 | OK | Ground clear controls. | 65 | 38.72 | 761.18
4360 | TIN-INTERP | Interpolated Ground | 27829.42 | -5.24 | 732.38 | 0 | 18.5 | 0 | OK | Ground clear controls. | 65 | 38.72 | 750.88
4361 | TIN-INTERP | Interpolated Ground | 27829.43 | -4.74 | 732.38 | 0 | 29.25 | 0 | OK | Ground clear controls. | 65 | 38.72 | 761.63
4362 | TIN-INTERP | Interpolated Ground | 27829.44 | 6.47 | 732.41 | 0 | 23.76 | 0 | OK | Ground clear controls. | 65 | 38.72 | 756.17
4363 | TIN-INTERP | Interpolated Ground | 27829.45 | -6.74 | 732.33 | 0 | 23.61 | 0 | OK | Ground clear controls. | 65 | 38.72 | 755.94
4364 | TIN-INTERP | Interpolated Ground | 27829.46 | 4.97 | 732.39 | 0 | 18.19 | 0 | OK | Ground clear controls. | 65 | 38.72 | 750.58
4365 | TIN-INTERP | Interpolated Ground | 27869.41 | 4.45 | 731.83 | 0 | 26.46 | 0 | OK | Ground clear controls. | 65 | 38.72 | 758.29
4366 | TIN-INTERP | Interpolated Ground | 27869.42 | -5.26 | 731.92 | 0 | 16.22 | 0 | OK | Ground clear controls. | 65 | 38.72 | 748.14
4367 | TIN-INTERP | Interpolated Ground | 27869.43 | -4.76 | 731.93 | 0 | 26.91 | 0 | OK | Ground clear controls. | 65 | 38.72 | 758.84
4368 | TIN-INTERP | Interpolated Ground | 27869.44 | 6.45 | 731.9 | 0 | 21.48 | 0 | OK | Ground clear controls. | 65 | 38.72 | 753.38
4369 | TIN-INTERP | Interpolated Ground | 27869.45 | -6.76 | 731.99 | 0 | 21.12 | 0 | OK | Ground clear controls. | 65 | 38.72 | 753.11
4370 | TIN-INTERP | Interpolated Ground | 27869.46 | 4.95 | 731.82 | 0 | 15.95 | 0 | OK | Ground clear controls. | 65 | 38.72 | 747.77
4371 | TIN-INTERP | Interpolated Ground | 27909.41 | 4.43 | 731.65 | 0 | 24.68 | 0 | OK | Ground clear controls. | 65 | 38.72 | 756.33
4372 | TIN-INTERP | Interpolated Ground | 27909.42 | -5.29 | 731.71 | 0 | 14.56 | 0 | OK | Ground clear controls. | 65 | 38.72 | 746.27
4373 | TIN-INTERP | Interpolated Ground | 27909.43 | -4.79 | 731.71 | 0 | 25.24 | 0 | OK | Ground clear controls. | 65 | 38.72 | 756.95
4374 | TIN-INTERP | Interpolated Ground | 27909.44 | 6.43 | 731.69 | 0 | 19.79 | 0 | OK | Ground clear controls. | 65 | 38.72 | 751.48
4375 | TIN-INTERP | Interpolated Ground | 27909.45 | -6.79 | 731.68 | 0 | 19.5 | 0 | OK | Ground clear controls. | 65 | 38.72 | 751.18
4376 | TIN-INTERP | Interpolated Ground | 27909.46 | 4.93 | 731.57 | 0 | 14.29 | 0 | OK | Ground clear controls. | 65 | 38.72 | 745.86
4377 | TIN-INTERP | Interpolated Ground | 27949.41 | 4.41 | 731.77 | 0 | 23.54 | 0 | OK | Ground clear controls. | 65 | 38.72 | 755.31
4378 | TIN-INTERP | Interpolated Ground | 27949.42 | -5.32 | 731.52 | 0 | 13.77 | 0 | OK | Ground clear controls. | 65 | 38.72 | 745.29
4379 | TIN-INTERP | Interpolated Ground | 27949.43 | -4.81 | 731.47 | 0 | 24.48 | 0 | OK | Ground clear controls. | 65 | 38.72 | 755.95
4380 | TIN-INTERP | Interpolated Ground | 27949.44 | 6.41 | 731.9 | 0 | 18.59 | 0 | OK | Ground clear controls. | 65 | 38.72 | 750.49
4381 | TIN-INTERP | Interpolated Ground | 27949.45 | -6.81 | 731.73 | 0 | 18.45 | 0 | OK | Ground clear controls. | 65 | 38.72 | 750.18
4382 | TIN-INTERP | Interpolated Ground | 27949.46 | 4.91 | 731.84 | 0 | 13.03 | 0 | OK | Ground clear controls. | 65 | 38.72 | 744.87
4383 | TIN-INTERP | Interpolated Ground | 27989.41 | 4.39 | 731.83 | 0 | 23.38 | 0 | OK | Ground clear controls. | 65 | 38.72 | 755.21
4384 | TIN-INTERP | Interpolated Ground | 27989.42 | -5.34 | 731.36 | 0 | 13.83 | 0 | OK | Ground clear controls. | 65 | 38.72 | 745.19
4385 | TIN-INTERP | Interpolated Ground | 27989.43 | -4.84 | 731.36 | 0 | 24.49 | 0 | OK | Ground clear controls. | 65 | 38.72 | 755.85
4386 | TIN-INTERP | Interpolated Ground | 27989.44 | 6.39 | 731.89 | 0 | 18.5 | 0 | OK | Ground clear controls. | 65 | 38.72 | 750.39
4387 | TIN-INTERP | Interpolated Ground | 27989.45 | -6.84 | 731.34 | 0 | 18.74 | 0 | OK | Ground clear controls. | 65 | 38.72 | 750.08
4388 | TIN-INTERP | Interpolated Ground | 27989.46 | 4.89 | 731.84 | 0 | 12.92 | 0 | OK | Ground clear controls. | 65 | 38.72 | 744.76
4389 | TIN-INTERP | Interpolated Ground | 28029.41 | 4.37 | 731.56 | 0 | 24.47 | 0 | OK | Ground clear controls. | 65 | 38.72 | 756.03
4390 | TIN-INTERP | Interpolated Ground | 28029.42 | -5.37 | 731.05 | 0 | 14.91 | 0 | OK | Ground clear controls. | 65 | 38.72 | 745.96
4391 | TIN-INTERP | Interpolated Ground | 28029.43 | -4.87 | 730.99 | 0 | 25.65 | 0 | OK | Ground clear controls. | 65 | 38.72 | 756.64
4392 | TIN-INTERP | Interpolated Ground | 28029.44 | 6.36 | 731.67 | 0 | 19.5 | 0 | OK | Ground clear controls. | 65 | 38.72 | 751.17
4393 | TIN-INTERP | Interpolated Ground | 28029.45 | -6.86 | 731.19 | 0 | 19.7 | 0 | OK | Ground clear controls. | 65 | 38.72 | 750.89
4394 | TIN-INTERP | Interpolated Ground | 28029.46 | 4.86 | 731.61 | 0 | 13.94 | 0 | OK | Ground clear controls. | 65 | 38.72 | 745.55
4395 | TIN-INTERP | Interpolated Ground | 28069.41 | 4.34 | 731.6 | 0 | 26.2 | 0 | OK | Ground clear controls. | 65 | 38.72 | 757.8
4396 | TIN-INTERP | Interpolated Ground | 28069.42 | -5.39 | 731.42 | 0 | 16.21 | 0 | OK | Ground clear controls. | 65 | 38.72 | 747.63
4397 | TIN-INTERP | Interpolated Ground | 28069.43 | -4.89 | 731.44 | 0 | 26.9 | 0 | OK | Ground clear controls. | 65 | 38.72 | 758.34
4398 | TIN-INTERP | Interpolated Ground | 28069.44 | 6.34 | 731.77 | 0 | 21.1 | 0 | OK | Ground clear controls. | 65 | 38.72 | 752.87
4399 | TIN-INTERP | Interpolated Ground | 28069.45 | -6.89 | 731.41 | 0 | 21.21 | 0 | OK | Ground clear controls. | 65 | 38.72 | 752.62
4400 | TIN-INTERP | Interpolated Ground | 28069.46 | 4.84 | 731.68 | 0 | 15.58 | 0 | OK | Ground clear controls. | 65 | 38.72 | 747.26
4401 | TIN-INTERP | Interpolated Ground | 28109.41 | 4.32 | 732.21 | 0 | 28.27 | 0 | OK | Ground clear controls. | 65 | 38.72 | 760.48
4402 | TIN-INTERP | Interpolated Ground | 28109.42 | -5.42 | 731.64 | 0 | 18.52 | 0 | OK | Ground clear controls. | 65 | 38.72 | 750.16
4403 | TIN-INTERP | Interpolated Ground | 28109.43 | -4.92 | 731.67 | 0 | 29.26 | 0 | OK | Ground clear controls. | 65 | 38.72 | 760.93
4404 | TIN-INTERP | Interpolated Ground | 28109.44 | 6.32 | 732.26 | 0 | 23.19 | 0 | OK | Ground clear controls. | 65 | 38.72 | 755.45
4405 | TIN-INTERP | Interpolated Ground | 28109.45 | -6.91 | 731.61 | 0 | 23.65 | 0 | OK | Ground clear controls. | 65 | 38.72 | 755.26
4406 | TIN-INTERP | Interpolated Ground | 28109.46 | 4.82 | 732.24 | 0 | 17.62 | 0 | OK | Ground clear controls. | 65 | 38.72 | 749.86
4407 | TIN-INTERP | Interpolated Ground | 28149.41 | 4.3 | 731.92 | 0 | 32.18 | 0 | OK | Ground clear controls. | 65 | 38.72 | 764.1
4408 | TIN-INTERP | Interpolated Ground | 28149.42 | -5.45 | 731.55 | 0 | 22.04 | 0 | OK | Ground clear controls. | 65 | 38.72 | 753.59
4409 | TIN-INTERP | Interpolated Ground | 28149.43 | -4.94 | 731.61 | 0 | 32.82 | 0 | OK | Ground clear controls. | 65 | 38.72 | 764.43
4410 | TIN-INTERP | Interpolated Ground | 28149.44 | 6.3 | 731.9 | 0 | 27.03 | 0 | OK | Ground clear controls. | 65 | 38.72 | 758.93
4411 | TIN-INTERP | Interpolated Ground | 28149.45 | -6.94 | 731.35 | 0 | 27.46 | 0 | OK | Ground clear controls. | 65 | 38.72 | 758.81
4412 | TIN-INTERP | Interpolated Ground | 28149.46 | 4.8 | 731.91 | 0 | 21.46 | 0 | OK | Ground clear controls. | 65 | 38.72 | 753.37
4413 | TIN-INTERP | Interpolated Ground | 28189.41 | 4.28 | 729.93 | 0 | 38.72 | 0 | OK | Ground clear controls. | 65 | 38.72 | 768.65
4414 | TIN-INTERP | Interpolated Ground | 28189.42 | -5.47 | 730.21 | 0 | 27.7 | 0 | OK | Ground clear controls. | 65 | 38.51 | 757.91
4415 | TIN-INTERP | Interpolated Ground | 28189.43 | -4.97 | 730.32 | 0 | 38.51 | 0 | OK | Ground clear controls. | 65 | 38.51 | 768.83
4416 | TIN-INTERP | Interpolated Ground | 28189.44 | 6.27 | 730.13 | 0 | 33.18 | 0 | OK | Ground clear controls. | 65 | 33.18 | 763.31
4417 | TIN-INTERP | Interpolated Ground | 28189.45 | -6.96 | 730.13 | 0 | 33.14 | 0 | OK | Ground clear controls. | 65 | 33.14 | 763.27
4418 | TIN-INTERP | Interpolated Ground | 28189.46 | 4.78 | 729.99 | 0 | 27.79 | 0 | OK | Ground clear controls. | 65 | 27.79 | 757.78
4419 | TIN-INTERP | Interpolated Ground | 28220.2 | 4.76 | 729.18 | 0 | 32.63 | 0 | OK | Ground clear controls. | 66 | 43.82 | 761.81
4420 | TIN-INTERP | Interpolated Ground | 28220.2 | 6.26 | 729.06 | 0 | 38.25 | 0 | OK | Ground clear controls. | 66 | 43.82 | 767.31
4421 | TIN-INTERP | Interpolated Ground | 28220.22 | 4.26 | 729.19 | 0 | 43.61 | 0 | OK | Ground clear controls. | 66 | 43.82 | 772.8
4422 | TIN-INTERP | Interpolated Ground | 28220.29 | -5.49 | 729.02 | 0 | 32.8 | 0 | OK | Ground clear controls. | 66 | 43.82 | 761.82
4423 | TIN-INTERP | Interpolated Ground | 28220.3 | -4.99 | 728.99 | 0 | 43.82 | 0 | OK | Ground clear controls. | 66 | 43.82 | 772.81
4424 | TIN-INTERP | Interpolated Ground | 28220.34 | -6.98 | 729.06 | 0 | 38.25 | 0 | OK | Ground clear controls. | 66 | 38.25 | 767.31
4425 | TIN-INTERP | Interpolated Ground | 28260.13 | 6.21 | 728.24 | 0 | 32.96 | 0 | OK | Ground clear controls. | 66 | 38.08 | 761.2
4426 | TIN-INTERP | Interpolated Ground | 28260.15 | 4.71 | 728.49 | 0 | 27.16 | 0 | OK | Ground clear controls. | 66 | 38.08 | 755.65
4427 | TIN-INTERP | Interpolated Ground | 28260.22 | 4.2 | 728.56 | 0 | 38.08 | 0 | OK | Ground clear controls. | 66 | 38.08 | 766.64
4428 | TIN-INTERP | Interpolated Ground | 28260.29 | -5.76 | 728.91 | 0 | 26.85 | 0 | OK | Ground clear controls. | 66 | 37.91 | 755.76
4429 | TIN-INTERP | Interpolated Ground | 28260.3 | -5.25 | 728.87 | 0 | 37.91 | 0 | OK | Ground clear controls. | 66 | 37.91 | 766.78
4430 | TIN-INTERP | Interpolated Ground | 28260.34 | -7.26 | 728.99 | 0 | 32.15 | 0 | OK | Ground clear controls. | 66 | 33.86 | 761.14
4431 | TIN-INTERP | Interpolated Ground | 28300.13 | 6.16 | 727.63 | 0 | 28.37 | 0 | OK | Ground clear controls. | 66 | 33.86 | 756
4432 | TIN-INTERP | Interpolated Ground | 28300.15 | 4.67 | 727.73 | 0 | 22.66 | 0 | OK | Ground clear controls. | 66 | 33.86 | 750.39
4433 | TIN-INTERP | Interpolated Ground | 28300.22 | 4.14 | 727.74 | 0 | 33.65 | 0 | OK | Ground clear controls. | 66 | 33.86 | 761.39
4434 | TIN-INTERP | Interpolated Ground | 28300.29 | -6.04 | 727.79 | 0 | 22.81 | 0 | OK | Ground clear controls. | 66 | 33.86 | 750.6
4435 | TIN-INTERP | Interpolated Ground | 28300.3 | -5.52 | 727.79 | 0 | 33.86 | 0 | OK | Ground clear controls. | 66 | 33.86 | 761.65
4436 | TIN-INTERP | Interpolated Ground | 28300.34 | -7.54 | 727.78 | 0 | 28.11 | 0 | OK | Ground clear controls. | 66 | 33.55 | 755.89
4437 | TIN-INTERP | Interpolated Ground | 28340.13 | 6.11 | 726.94 | 0 | 24.75 | 0 | OK | Ground clear controls. | 66 | 33.55 | 751.69
4438 | TIN-INTERP | Interpolated Ground | 28340.15 | 4.62 | 726.95 | 0 | 19.08 | 0 | OK | Ground clear controls. | 66 | 33.55 | 746.03
4439 | TIN-INTERP | Interpolated Ground | 28340.22 | 4.08 | 726.99 | 0 | 30.08 | 0 | OK | Ground clear controls. | 66 | 33.55 | 757.07
4440 | TIN-INTERP | Interpolated Ground | 28340.29 | -6.31 | 726.86 | 0 | 19.45 | 0 | OK | Ground clear controls. | 66 | 33.55 | 746.31
4441 | TIN-INTERP | Interpolated Ground | 28340.3 | -5.79 | 726.91 | 0 | 30.5 | 0 | OK | Ground clear controls. | 66 | 33.55 | 757.41
4442 | TIN-INTERP | Interpolated Ground | 28340.34 | -7.81 | 726.92 | 0 | 24.62 | 0 | OK | Ground clear controls. | 66 | 33.55 | 751.54
4443 | TIN-INTERP | Interpolated Ground | 28380.13 | 6.07 | 726.39 | 0 | 21.9 | 0 | OK | Ground clear controls. | 66 | 33.55 | 748.29
4444 | TIN-INTERP | Interpolated Ground | 28380.15 | 4.58 | 726.29 | 0 | 16.29 | 0 | OK | Ground clear controls. | 66 | 33.55 | 742.58
4445 | TIN-INTERP | Interpolated Ground | 28380.22 | 4.02 | 726.28 | 0 | 27.38 | 0 | OK | Ground clear controls. | 66 | 33.55 | 753.66
4446 | TIN-INTERP | Interpolated Ground | 28380.29 | -6.58 | 727.24 | 0 | 15.68 | 0 | OK | Ground clear controls. | 66 | 33.55 | 742.92
4447 | TIN-INTERP | Interpolated Ground | 28380.3 | -6.06 | 727.19 | 0 | 26.89 | 0 | OK | Ground clear controls. | 66 | 33.55 | 754.08
4448 | TIN-INTERP | Interpolated Ground | 28380.34 | -8.09 | 727.38 | 0 | 20.73 | 0 | OK | Ground clear controls. | 66 | 33.55 | 748.11
4449 | TIN-INTERP | Interpolated Ground | 28420.13 | 6.02 | 726.31 | 0 | 19.46 | 0 | OK | Ground clear controls. | 66 | 33.55 | 745.77
4450 | TIN-INTERP | Interpolated Ground | 28420.15 | 4.53 | 726.44 | 0 | 13.59 | 0 | OK | Ground clear controls. | 66 | 33.55 | 740.03
4451 | TIN-INTERP | Interpolated Ground | 28420.22 | 3.95 | 726.45 | 0 | 24.73 | 0 | OK | Ground clear controls. | 66 | 33.55 | 751.18
4452 | TIN-INTERP | Interpolated Ground | 28420.29 | -6.86 | 726.18 | 0 | 14.23 | 0 | OK | Ground clear controls. | 66 | 33.55 | 740.41
4453 | TIN-INTERP | Interpolated Ground | 28420.3 | -6.32 | 726.19 | 0 | 25.45 | 0 | OK | Ground clear controls. | 66 | 33.55 | 751.64
4454 | TIN-INTERP | Interpolated Ground | 28420.33 | -8.37 | 726.16 | 0 | 19.44 | 0 | OK | Ground clear controls. | 66 | 33.55 | 745.6
4455 | TIN-INTERP | Interpolated Ground | 28460.13 | 5.97 | 725.44 | 0 | 18.71 | 0 | OK | Ground clear controls. | 66 | 33.55 | 744.15
4456 | TIN-INTERP | Interpolated Ground | 28460.15 | 4.48 | 725.39 | 0 | 12.99 | 0 | OK | Ground clear controls. | 66 | 33.55 | 738.38
4457 | TIN-INTERP | Interpolated Ground | 28460.22 | 3.89 | 725.37 | 0 | 24.25 | 0 | OK | Ground clear controls. | 66 | 33.55 | 749.62
4458 | TIN-INTERP | Interpolated Ground | 28460.29 | -7.13 | 725.03 | 0 | 13.74 | 0 | OK | Ground clear controls. | 66 | 33.55 | 738.77
4459 | TIN-INTERP | Interpolated Ground | 28460.3 | -6.59 | 725.03 | 0 | 25.07 | 0 | OK | Ground clear controls. | 66 | 33.55 | 750.1
4460 | TIN-INTERP | Interpolated Ground | 28460.33 | -8.65 | 724.95 | 0 | 19.04 | 0 | OK | Ground clear controls. | 66 | 33.55 | 743.99
4461 | TIN-INTERP | Interpolated Ground | 28500.13 | 5.92 | 724.96 | 0 | 18.45 | 0 | OK | Ground clear controls. | 66 | 33.55 | 743.41
4462 | TIN-INTERP | Interpolated Ground | 28500.15 | 4.44 | 724.92 | 0 | 12.71 | 0 | OK | Ground clear controls. | 66 | 33.55 | 737.63
4463 | TIN-INTERP | Interpolated Ground | 28500.22 | 3.83 | 724.89 | 0 | 24.1 | 0 | OK | Ground clear controls. | 66 | 33.55 | 748.99
4464 | TIN-INTERP | Interpolated Ground | 28500.29 | -7.4 | 724.57 | 0 | 13.46 | 0 | OK | Ground clear controls. | 66 | 33.55 | 738.03
4465 | TIN-INTERP | Interpolated Ground | 28500.3 | -6.86 | 724.56 | 0 | 24.9 | 0 | OK | Ground clear controls. | 66 | 33.55 | 749.46
4466 | TIN-INTERP | Interpolated Ground | 28500.33 | -8.92 | 724.45 | 0 | 18.84 | 0 | OK | Ground clear controls. | 66 | 33.55 | 743.29
4467 | TIN-INTERP | Interpolated Ground | 28540.13 | 5.87 | 722.93 | 0 | 20.64 | 0 | OK | Ground clear controls. | 66 | 33.55 | 743.57
4468 | TIN-INTERP | Interpolated Ground | 28540.15 | 4.39 | 723.04 | 0 | 14.74 | 0 | OK | Ground clear controls. | 66 | 33.55 | 737.78
4469 | TIN-INTERP | Interpolated Ground | 28540.22 | 3.77 | 723.15 | 0 | 26.12 | 0 | OK | Ground clear controls. | 66 | 33.55 | 749.27
4470 | TIN-INTERP | Interpolated Ground | 28540.29 | -7.67 | 723.48 | 0 | 14.68 | 0 | OK | Ground clear controls. | 66 | 33.55 | 738.16
4471 | TIN-INTERP | Interpolated Ground | 28540.29 | -7.13 | 723.5 | 0 | 26.22 | 0 | OK | Ground clear controls. | 66 | 33.55 | 749.72
4472 | TIN-INTERP | Interpolated Ground | 28540.33 | -9.2 | 723.4 | 0 | 20.1 | 0 | OK | Ground clear controls. | 66 | 33.55 | 743.5
4473 | TIN-INTERP | Interpolated Ground | 28580.13 | 5.83 | 722.46 | 0 | 22.16 | 0 | OK | Ground clear controls. | 66 | 33.55 | 744.62
4474 | TIN-INTERP | Interpolated Ground | 28580.15 | 4.34 | 722.69 | 0 | 16.14 | 0 | OK | Ground clear controls. | 66 | 33.55 | 738.83
4475 | TIN-INTERP | Interpolated Ground | 28580.22 | 3.71 | 722.78 | 0 | 27.68 | 0 | OK | Ground clear controls. | 66 | 33.55 | 750.46
4476 | TIN-INTERP | Interpolated Ground | 28580.28 | -7.95 | 722.7 | 0 | 16.47 | 0 | OK | Ground clear controls. | 66 | 33.55 | 739.17
4477 | TIN-INTERP | Interpolated Ground | 28580.29 | -7.39 | 722.7 | 0 | 28.17 | 0 | OK | Ground clear controls. | 66 | 33.55 | 750.87
4478 | TIN-INTERP | Interpolated Ground | 28580.33 | -9.48 | 722.73 | 0 | 21.89 | 0 | OK | Ground clear controls. | 66 | 33.55 | 744.62
4479 | TIN-INTERP | Interpolated Ground | 28620.13 | 5.78 | 722.94 | 0 | 23.63 | 0 | OK | Ground clear controls. | 66 | 33.55 | 746.57
4480 | TIN-INTERP | Interpolated Ground | 28620.15 | 4.3 | 723.21 | 0 | 17.55 | 0 | OK | Ground clear controls. | 66 | 33.55 | 740.76
4481 | TIN-INTERP | Interpolated Ground | 28620.22 | 3.65 | 723.25 | 0 | 29.33 | 0 | OK | Ground clear controls. | 66 | 33.55 | 752.58
4482 | TIN-INTERP | Interpolated Ground | 28620.28 | -8.22 | 723.45 | 0 | 17.62 | 0 | OK | Ground clear controls. | 66 | 33.55 | 741.07
4483 | TIN-INTERP | Interpolated Ground | 28620.29 | -7.66 | 723.47 | 0 | 29.44 | 0 | OK | Ground clear controls. | 66 | 33.55 | 752.91
4484 | TIN-INTERP | Interpolated Ground | 28620.33 | -9.76 | 723.47 | 0 | 23.17 | 0 | OK | Ground clear controls. | 66 | 33.55 | 746.64
4485 | TIN-INTERP | Interpolated Ground | 28660.13 | 5.73 | 722.56 | 0 | 26.83 | 0 | OK | Ground clear controls. | 66 | 33.55 | 749.39
4486 | TIN-INTERP | Interpolated Ground | 28660.15 | 4.25 | 722.7 | 0 | 20.91 | 0 | OK | Ground clear controls. | 66 | 33.55 | 743.61
4487 | TIN-INTERP | Interpolated Ground | 28660.22 | 3.58 | 722.76 | 0 | 32.85 | 0 | OK | Ground clear controls. | 66 | 33.55 | 755.61
4488 | TIN-INTERP | Interpolated Ground | 28660.28 | -8.49 | 722.32 | 0 | 21.53 | 0 | OK | Ground clear controls. | 66 | 33.55 | 743.85
4489 | TIN-INTERP | Interpolated Ground | 28660.29 | -7.93 | 722.3 | 0 | 33.55 | 0 | OK | Ground clear controls. | 66 | 33.55 | 755.85
4490 | TIN-INTERP | Interpolated Ground | 28660.33 | -10.03 | 722.3 | 0 | 27.28 | 0 | OK | Ground clear controls. | 66 | 27.28 | 749.58
4491 | TIN-INTERP | Interpolated Ground | 28673.29 | -10.12 | 721.84 | 0 | 28.88 | 0 | OK | Ground clear controls. | 67 | 38.31 | 750.72
4492 | TIN-INTERP | Interpolated Ground | 28673.52 | -8.58 | 721.98 | 0 | 22.97 | 0 | OK | Ground clear controls. | 67 | 38.31 | 744.95
4493 | TIN-INTERP | Interpolated Ground | 28673.6 | -8.02 | 721.99 | 0 | 35.04 | 0 | OK | Ground clear controls. | 67 | 38.31 | 757.03
4494 | TIN-INTERP | Interpolated Ground | 28674.91 | 3.63 | 721.27 | 0 | 35.76 | 0 | OK | Ground clear controls. | 67 | 38.31 | 757.03
4495 | TIN-INTERP | Interpolated Ground | 28674.91 | 4.3 | 721.27 | 0 | 23.69 | 0 | OK | Ground clear controls. | 67 | 38.31 | 744.96
4496 | TIN-INTERP | Interpolated Ground | 28674.91 | 5.8 | 721.23 | 0 | 29.53 | 0 | OK | Ground clear controls. | 67 | 38.31 | 750.76
4497 | TIN-INTERP | Interpolated Ground | 28714.11 | 5.9 | 719.88 | 0 | 26.32 | 0 | OK | Ground clear controls. | 67 | 38.31 | 746.2
4498 | TIN-INTERP | Interpolated Ground | 28714.33 | 4.41 | 719.75 | 0 | 20.64 | 0 | OK | Ground clear controls. | 67 | 38.31 | 740.39
4499 | TIN-INTERP | Interpolated Ground | 28714.47 | 3.77 | 719.7 | 0 | 32.62 | 0 | OK | Ground clear controls. | 67 | 38.31 | 752.32
4500 | TIN-INTERP | Interpolated Ground | 28716.15 | -7.71 | 719.57 | 0 | 32.83 | 0 | OK | Ground clear controls. | 67 | 38.31 | 752.4
4501 | TIN-INTERP | Interpolated Ground | 28716.26 | -8.26 | 719.61 | 0 | 20.88 | 0 | OK | Ground clear controls. | 67 | 38.31 | 740.49
4502 | TIN-INTERP | Interpolated Ground | 28716.51 | -9.8 | 719.78 | 0 | 26.33 | 0 | OK | Ground clear controls. | 67 | 38.31 | 746.11
4503 | TIN-INTERP | Interpolated Ground | 28754.11 | 6.05 | 718.98 | 0 | 23.54 | 0 | OK | Ground clear controls. | 67 | 38.31 | 742.52
4504 | TIN-INTERP | Interpolated Ground | 28754.33 | 4.56 | 718.97 | 0 | 17.74 | 0 | OK | Ground clear controls. | 67 | 38.31 | 736.71
4505 | TIN-INTERP | Interpolated Ground | 28754.47 | 3.94 | 718.97 | 0 | 29.55 | 0 | OK | Ground clear controls. | 67 | 38.31 | 748.52
4506 | TIN-INTERP | Interpolated Ground | 28756.15 | -7.4 | 718.93 | 0 | 29.72 | 0 | OK | Ground clear controls. | 67 | 38.31 | 748.65
4507 | TIN-INTERP | Interpolated Ground | 28756.26 | -7.93 | 718.9 | 0 | 17.99 | 0 | OK | Ground clear controls. | 67 | 38.31 | 736.89
4508 | TIN-INTERP | Interpolated Ground | 28756.51 | -9.46 | 718.81 | 0 | 23.59 | 0 | OK | Ground clear controls. | 67 | 38.31 | 742.4
4509 | TIN-INTERP | Interpolated Ground | 28794.11 | 6.2 | 718.72 | 0 | 21.01 | 0 | OK | Ground clear controls. | 67 | 38.31 | 739.73
4510 | TIN-INTERP | Interpolated Ground | 28794.33 | 4.71 | 718.76 | 0 | 15.16 | 0 | OK | Ground clear controls. | 67 | 38.31 | 733.92
4511 | TIN-INTERP | Interpolated Ground | 28794.47 | 4.12 | 718.69 | 0 | 26.93 | 0 | OK | Ground clear controls. | 67 | 38.31 | 745.62
4512 | TIN-INTERP | Interpolated Ground | 28796.15 | -7.09 | 718.61 | 0 | 27.2 | 0 | OK | Ground clear controls. | 67 | 38.31 | 745.81
4513 | TIN-INTERP | Interpolated Ground | 28796.26 | -7.6 | 718.62 | 0 | 15.55 | 0 | OK | Ground clear controls. | 67 | 38.31 | 734.17
4514 | TIN-INTERP | Interpolated Ground | 28796.51 | -9.13 | 718.57 | 0 | 21.02 | 0 | OK | Ground clear controls. | 67 | 38.31 | 739.59
4515 | TIN-INTERP | Interpolated Ground | 28834.11 | 6.35 | 719.13 | 0 | 18.69 | 0 | OK | Ground clear controls. | 67 | 38.31 | 737.82
4516 | TIN-INTERP | Interpolated Ground | 28834.33 | 4.86 | 719.12 | 0 | 12.92 | 0 | OK | Ground clear controls. | 67 | 38.31 | 732.04
4517 | TIN-INTERP | Interpolated Ground | 28834.47 | 4.29 | 719.09 | 0 | 24.55 | 0 | OK | Ground clear controls. | 67 | 38.31 | 743.64
4518 | TIN-INTERP | Interpolated Ground | 28836.15 | -6.77 | 718.99 | 0 | 24.87 | 0 | OK | Ground clear controls. | 67 | 38.31 | 743.86
4519 | TIN-INTERP | Interpolated Ground | 28836.26 | -7.28 | 718.95 | 0 | 13.37 | 0 | OK | Ground clear controls. | 67 | 38.31 | 732.32
4520 | TIN-INTERP | Interpolated Ground | 28836.51 | -8.8 | 718.98 | 0 | 18.7 | 0 | OK | Ground clear controls. | 67 | 38.31 | 737.68
4521 | TIN-INTERP | Interpolated Ground | 28874.11 | 6.5 | 718.01 | 0 | 18.8 | 0 | OK | Ground clear controls. | 67 | 38.31 | 736.81
4522 | TIN-INTERP | Interpolated Ground | 28874.33 | 5 | 718.04 | 0 | 12.99 | 0 | OK | Ground clear controls. | 67 | 38.31 | 731.03
4523 | TIN-INTERP | Interpolated Ground | 28874.47 | 4.46 | 718.04 | 0 | 24.52 | 0 | OK | Ground clear controls. | 67 | 38.31 | 742.56
4524 | TIN-INTERP | Interpolated Ground | 28876.15 | -6.46 | 718.14 | 0 | 24.66 | 0 | OK | Ground clear controls. | 67 | 38.31 | 742.8
4525 | TIN-INTERP | Interpolated Ground | 28876.25 | -6.95 | 718.12 | 0 | 13.24 | 0 | OK | Ground clear controls. | 67 | 38.31 | 731.36
4526 | TIN-INTERP | Interpolated Ground | 28876.51 | -8.47 | 718.11 | 0 | 18.56 | 0 | OK | Ground clear controls. | 67 | 38.31 | 736.67
4527 | TIN-INTERP | Interpolated Ground | 28914.11 | 6.65 | 717.82 | 0 | 18.85 | 0 | OK | Ground clear controls. | 67 | 38.31 | 736.67
4528 | TIN-INTERP | Interpolated Ground | 28914.33 | 5.15 | 717.74 | 0 | 13.18 | 0 | OK | Ground clear controls. | 67 | 38.31 | 730.92
4529 | TIN-INTERP | Interpolated Ground | 28914.47 | 4.63 | 717.71 | 0 | 24.67 | 0 | OK | Ground clear controls. | 67 | 38.31 | 742.38
4530 | TIN-INTERP | Interpolated Ground | 28916.15 | -6.14 | 717.57 | 0 | 25.07 | 0 | OK | Ground clear controls. | 67 | 38.31 | 742.64
4531 | TIN-INTERP | Interpolated Ground | 28916.25 | -6.62 | 717.53 | 0 | 13.73 | 0 | OK | Ground clear controls. | 67 | 38.31 | 731.26
4532 | TIN-INTERP | Interpolated Ground | 28916.51 | -8.14 | 717.49 | 0 | 19.06 | 0 | OK | Ground clear controls. | 67 | 38.31 | 736.55
4533 | TIN-INTERP | Interpolated Ground | 28954.11 | 6.8 | 715.8 | 0 | 21.61 | 0 | OK | Ground clear controls. | 67 | 38.31 | 737.41
4534 | TIN-INTERP | Interpolated Ground | 28954.33 | 5.3 | 715.74 | 0 | 15.97 | 0 | OK | Ground clear controls. | 67 | 38.31 | 731.71
4535 | TIN-INTERP | Interpolated Ground | 28954.47 | 4.8 | 715.73 | 0 | 27.38 | 0 | OK | Ground clear controls. | 67 | 38.31 | 743.11
4536 | TIN-INTERP | Interpolated Ground | 28956.15 | -5.83 | 715.71 | 0 | 27.66 | 0 | OK | Ground clear controls. | 67 | 38.31 | 743.37
4537 | TIN-INTERP | Interpolated Ground | 28956.25 | -6.29 | 715.68 | 0 | 16.37 | 0 | OK | Ground clear controls. | 67 | 38.31 | 732.05
4538 | TIN-INTERP | Interpolated Ground | 28956.51 | -7.81 | 715.59 | 0 | 21.75 | 0 | OK | Ground clear controls. | 67 | 38.31 | 737.34
4539 | TIN-INTERP | Interpolated Ground | 28994.11 | 6.95 | 715.91 | 0 | 23.14 | 0 | OK | Ground clear controls. | 67 | 38.31 | 739.05
4540 | TIN-INTERP | Interpolated Ground | 28994.33 | 5.45 | 715.77 | 0 | 17.62 | 0 | OK | Ground clear controls. | 67 | 38.31 | 733.39
4541 | TIN-INTERP | Interpolated Ground | 28994.47 | 4.97 | 715.75 | 0 | 29 | 0 | OK | Ground clear controls. | 67 | 38.31 | 744.75
4542 | TIN-INTERP | Interpolated Ground | 28996.14 | -5.51 | 715.58 | 0 | 29.42 | 0 | OK | Ground clear controls. | 67 | 38.31 | 745
4543 | TIN-INTERP | Interpolated Ground | 28996.25 | -5.96 | 715.57 | 0 | 18.15 | 0 | OK | Ground clear controls. | 67 | 38.31 | 733.72
4544 | TIN-INTERP | Interpolated Ground | 28996.5 | -7.48 | 715.47 | 0 | 23.55 | 0 | OK | Ground clear controls. | 67 | 38.31 | 739.02
4545 | TIN-INTERP | Interpolated Ground | 29034.11 | 7.1 | 716.46 | 0 | 25.11 | 0 | OK | Ground clear controls. | 67 | 38.31 | 741.57
4546 | TIN-INTERP | Interpolated Ground | 29034.33 | 5.6 | 716.5 | 0 | 19.46 | 0 | OK | Ground clear controls. | 67 | 38.31 | 735.96
4547 | TIN-INTERP | Interpolated Ground | 29034.47 | 5.14 | 716.48 | 0 | 30.81 | 0 | OK | Ground clear controls. | 67 | 38.31 | 747.29
4548 | TIN-INTERP | Interpolated Ground | 29036.14 | -5.2 | 716.2 | 0 | 31.32 | 0 | OK | Ground clear controls. | 67 | 38.31 | 747.52
4549 | TIN-INTERP | Interpolated Ground | 29036.25 | -5.63 | 716.18 | 0 | 20.07 | 0 | OK | Ground clear controls. | 67 | 38.31 | 736.25
4550 | TIN-INTERP | Interpolated Ground | 29036.5 | -7.15 | 716.14 | 0 | 25.46 | 0 | OK | Ground clear controls. | 67 | 38.31 | 741.6
4551 | TIN-INTERP | Interpolated Ground | 29074.11 | 7.25 | 716.25 | 0 | 28.73 | 0 | OK | Ground clear controls. | 67 | 38.31 | 744.98
4552 | TIN-INTERP | Interpolated Ground | 29074.33 | 5.75 | 716.25 | 0 | 23.17 | 0 | OK | Ground clear controls. | 67 | 38.31 | 739.42
4553 | TIN-INTERP | Interpolated Ground | 29074.47 | 5.31 | 716.26 | 0 | 34.48 | 0 | OK | Ground clear controls. | 67 | 38.31 | 750.74
4554 | TIN-INTERP | Interpolated Ground | 29076.14 | -4.89 | 716.3 | 0 | 34.64 | 0 | OK | Ground clear controls. | 67 | 38.31 | 750.94
4555 | TIN-INTERP | Interpolated Ground | 29076.25 | -5.3 | 716.32 | 0 | 23.35 | 0 | OK | Ground clear controls. | 67 | 38.31 | 739.67
4556 | TIN-INTERP | Interpolated Ground | 29076.5 | -6.81 | 716.4 | 0 | 28.69 | 0 | OK | Ground clear controls. | 67 | 38.31 | 745.09
4557 | TIN-INTERP | Interpolated Ground | 29114.11 | 7.4 | 716.79 | 0 | 32.48 | 0 | OK | Ground clear controls. | 67 | 38.31 | 749.27
4558 | TIN-INTERP | Interpolated Ground | 29114.33 | 5.89 | 716.89 | 0 | 26.9 | 0 | OK | Ground clear controls. | 67 | 38.31 | 743.79
4559 | TIN-INTERP | Interpolated Ground | 29114.47 | 5.48 | 716.9 | 0 | 38.2 | 0 | OK | Ground clear controls. | 67 | 38.31 | 755.1
4560 | TIN-INTERP | Interpolated Ground | 29116.14 | -4.57 | 716.94 | 0 | 38.31 | 0 | OK | Ground clear controls. | 67 | 38.31 | 755.25
4561 | TIN-INTERP | Interpolated Ground | 29116.25 | -4.98 | 716.94 | 0 | 27.02 | 0 | OK | Ground clear controls. | 67 | 32.59 | 743.96
4562 | TIN-INTERP | Interpolated Ground | 29116.5 | -6.48 | 716.89 | 0 | 32.59 | 0 | OK | Ground clear controls. | 67 | 32.59 | 749.48
4563 | TIN-INTERP | Interpolated Ground | 29116.98 | 7.41 | 716.73 | 0 | 32.89 | 0 | OK | Ground clear controls. | 68 | 38.74 | 749.62
4564 | TIN-INTERP | Interpolated Ground | 29117.07 | 5.9 | 716.69 | 0 | 27.42 | 0 | OK | Ground clear controls. | 68 | 38.74 | 744.11
4565 | TIN-INTERP | Interpolated Ground | 29117.09 | 5.49 | 716.67 | 0 | 38.74 | 0 | OK | Ground clear controls. | 68 | 38.74 | 755.41
4566 | TIN-INTERP | Interpolated Ground | 29117.25 | -6.48 | 716.91 | 0 | 32.68 | 0 | OK | Ground clear controls. | 68 | 38.53 | 749.59
4567 | TIN-INTERP | Interpolated Ground | 29117.25 | -4.97 | 716.9 | 0 | 27.2 | 0 | OK | Ground clear controls. | 68 | 38.53 | 744.1
4568 | TIN-INTERP | Interpolated Ground | 29117.25 | -4.56 | 716.87 | 0 | 38.53 | 0 | OK | Ground clear controls. | 68 | 38.53 | 755.4
4569 | TIN-INTERP | Interpolated Ground | 29157.12 | -6.5 | 715.08 | 0 | 28.92 | 0 | OK | Ground clear controls. | 68 | 35.35 | 744
4570 | TIN-INTERP | Interpolated Ground | 29157.13 | -4.97 | 715.15 | 0 | 23.42 | 0 | OK | Ground clear controls. | 68 | 35.35 | 738.57
4571 | TIN-INTERP | Interpolated Ground | 29157.14 | -4.55 | 715.14 | 0 | 34.71 | 0 | OK | Ground clear controls. | 68 | 35.35 | 749.85
4572 | TIN-INTERP | Interpolated Ground | 29157.38 | 7.6 | 715.44 | 0 | 28.59 | 0 | OK | Ground clear controls. | 68 | 35.35 | 744.03
4573 | TIN-INTERP | Interpolated Ground | 29157.39 | 5.65 | 715.38 | 0 | 34.42 | 0 | OK | Ground clear controls. | 68 | 35.35 | 749.8
4574 | TIN-INTERP | Interpolated Ground | 29157.39 | 6.09 | 715.41 | 0 | 23.08 | 0 | OK | Ground clear controls. | 68 | 35.35 | 738.49
4575 | TIN-INTERP | Interpolated Ground | 29197.12 | -6.51 | 714.27 | 0 | 25.03 | 0 | OK | Ground clear controls. | 68 | 35.35 | 739.3
4576 | TIN-INTERP | Interpolated Ground | 29197.13 | -4.98 | 714.28 | 0 | 19.64 | 0 | OK | Ground clear controls. | 68 | 35.35 | 733.92
4577 | TIN-INTERP | Interpolated Ground | 29197.14 | -4.54 | 714.28 | 0 | 30.93 | 0 | OK | Ground clear controls. | 68 | 35.35 | 745.21
4578 | TIN-INTERP | Interpolated Ground | 29197.38 | 7.78 | 714.75 | 0 | 24.6 | 0 | OK | Ground clear controls. | 68 | 35.35 | 739.35
4579 | TIN-INTERP | Interpolated Ground | 29197.39 | 5.81 | 714.69 | 0 | 30.42 | 0 | OK | Ground clear controls. | 68 | 35.35 | 745.11
4580 | TIN-INTERP | Interpolated Ground | 29197.39 | 6.28 | 714.71 | 0 | 19.06 | 0 | OK | Ground clear controls. | 68 | 35.35 | 733.77
4581 | TIN-INTERP | Interpolated Ground | 29237.12 | -6.53 | 712.48 | 0 | 23.02 | 0 | OK | Ground clear controls. | 68 | 35.35 | 735.5
4582 | TIN-INTERP | Interpolated Ground | 29237.13 | -4.99 | 712.55 | 0 | 17.59 | 0 | OK | Ground clear controls. | 68 | 35.35 | 730.14
4583 | TIN-INTERP | Interpolated Ground | 29237.14 | -4.52 | 712.59 | 0 | 28.87 | 0 | OK | Ground clear controls. | 68 | 35.35 | 741.46
4584 | TIN-INTERP | Interpolated Ground | 29237.38 | 7.97 | 712.86 | 0 | 22.7 | 0 | OK | Ground clear controls. | 68 | 35.35 | 735.56
4585 | TIN-INTERP | Interpolated Ground | 29237.39 | 5.97 | 712.79 | 0 | 28.53 | 0 | OK | Ground clear controls. | 68 | 35.35 | 741.32
4586 | TIN-INTERP | Interpolated Ground | 29237.39 | 6.47 | 712.82 | 0 | 17.12 | 0 | OK | Ground clear controls. | 68 | 35.35 | 729.94
4587 | TIN-INTERP | Interpolated Ground | 29277.12 | -6.55 | 712.11 | 0 | 20.49 | 0 | OK | Ground clear controls. | 68 | 35.35 | 732.6
4588 | TIN-INTERP | Interpolated Ground | 29277.13 | -4.99 | 712.14 | 0 | 15.12 | 0 | OK | Ground clear controls. | 68 | 35.35 | 727.26
4589 | TIN-INTERP | Interpolated Ground | 29277.14 | -4.51 | 712.14 | 0 | 26.48 | 0 | OK | Ground clear controls. | 68 | 35.35 | 738.62
4590 | TIN-INTERP | Interpolated Ground | 29277.38 | 8.16 | 711.75 | 0 | 20.91 | 0 | OK | Ground clear controls. | 68 | 35.35 | 732.66
4591 | TIN-INTERP | Interpolated Ground | 29277.39 | 6.12 | 711.71 | 0 | 26.75 | 0 | OK | Ground clear controls. | 68 | 35.35 | 738.46
4592 | TIN-INTERP | Interpolated Ground | 29277.39 | 6.65 | 711.73 | 0 | 15.29 | 0 | OK | Ground clear controls. | 68 | 35.35 | 727.02
4593 | TIN-INTERP | Interpolated Ground | 29317.12 | -6.57 | 711.71 | 0 | 18.88 | 0 | OK | Ground clear controls. | 68 | 35.35 | 730.59
4594 | TIN-INTERP | Interpolated Ground | 29317.13 | -5 | 711.8 | 0 | 13.44 | 0 | OK | Ground clear controls. | 68 | 35.35 | 725.24
4595 | TIN-INTERP | Interpolated Ground | 29317.14 | -4.5 | 711.8 | 0 | 24.86 | 0 | OK | Ground clear controls. | 68 | 35.35 | 736.66
4596 | TIN-INTERP | Interpolated Ground | 29317.38 | 8.34 | 712.02 | 0 | 18.65 | 0 | OK | Ground clear controls. | 68 | 35.35 | 730.67
4597 | TIN-INTERP | Interpolated Ground | 29317.39 | 6.28 | 712.02 | 0 | 24.47 | 0 | OK | Ground clear controls. | 68 | 35.35 | 736.49
4598 | TIN-INTERP | Interpolated Ground | 29317.39 | 6.84 | 712.01 | 0 | 12.98 | 0 | OK | Ground clear controls. | 68 | 35.35 | 724.99
4599 | TIN-INTERP | Interpolated Ground | 29357.12 | -6.59 | 710.65 | 0 | 18.83 | 0 | OK | Ground clear controls. | 68 | 35.35 | 729.48
4600 | TIN-INTERP | Interpolated Ground | 29357.13 | -5 | 710.65 | 0 | 13.45 | 0 | OK | Ground clear controls. | 68 | 35.35 | 724.1
4601 | TIN-INTERP | Interpolated Ground | 29357.14 | -4.49 | 710.63 | 0 | 24.97 | 0 | OK | Ground clear controls. | 68 | 35.35 | 735.6
4602 | TIN-INTERP | Interpolated Ground | 29357.38 | 8.53 | 711.23 | 0 | 18.32 | 0 | OK | Ground clear controls. | 68 | 35.35 | 729.55
4603 | TIN-INTERP | Interpolated Ground | 29357.39 | 6.44 | 711.19 | 0 | 24.24 | 0 | OK | Ground clear controls. | 68 | 35.35 | 735.43
4604 | TIN-INTERP | Interpolated Ground | 29357.39 | 7.03 | 711.15 | 0 | 12.7 | 0 | OK | Ground clear controls. | 68 | 35.35 | 723.85
4605 | TIN-INTERP | Interpolated Ground | 29397.12 | -6.6 | 709.13 | 0 | 20.14 | 0 | OK | Ground clear controls. | 68 | 35.35 | 729.27
4606 | TIN-INTERP | Interpolated Ground | 29397.13 | -5.01 | 709.2 | 0 | 14.63 | 0 | OK | Ground clear controls. | 68 | 35.35 | 723.83
4607 | TIN-INTERP | Interpolated Ground | 29397.14 | -4.48 | 709.25 | 0 | 26.17 | 0 | OK | Ground clear controls. | 68 | 35.35 | 735.42
4608 | TIN-INTERP | Interpolated Ground | 29397.38 | 8.72 | 709.51 | 0 | 19.83 | 0 | OK | Ground clear controls. | 68 | 35.35 | 729.34
4609 | TIN-INTERP | Interpolated Ground | 29397.39 | 6.6 | 709.58 | 0 | 25.71 | 0 | OK | Ground clear controls. | 68 | 35.35 | 735.29
4610 | TIN-INTERP | Interpolated Ground | 29397.39 | 7.21 | 709.54 | 0 | 14.07 | 0 | OK | Ground clear controls. | 68 | 35.35 | 723.61
4611 | TIN-INTERP | Interpolated Ground | 29437.12 | -6.62 | 701.36 | 0 | 28.57 | 0 | OK | Ground clear controls. | 68 | 35.35 | 729.93
4612 | TIN-INTERP | Interpolated Ground | 29437.13 | -5.02 | 701.43 | 0 | 23 | 0 | OK | Ground clear controls. | 68 | 35.35 | 724.43
4613 | TIN-INTERP | Interpolated Ground | 29437.14 | -4.46 | 701.45 | 0 | 34.69 | 0 | OK | Ground clear controls. | 68 | 35.35 | 736.14
4614 | TIN-INTERP | Interpolated Ground | 29437.38 | 8.9 | 700.73 | 0 | 29.28 | 0 | OK | Ground clear controls. | 68 | 35.35 | 730.01
4615 | TIN-INTERP | Interpolated Ground | 29437.39 | 6.75 | 700.68 | 0 | 35.35 | 0 | OK | Ground clear controls. | 68 | 35.35 | 736.03
4616 | TIN-INTERP | Interpolated Ground | 29437.39 | 7.4 | 700.7 | 0 | 23.56 | 0 | OK | Ground clear controls. | 68 | 33.26 | 724.26
4617 | TIN-INTERP | Interpolated Ground | 29477.12 | -6.64 | 705.74 | 0 | 25.78 | 0 | OK | Ground clear controls. | 68 | 33.26 | 731.52
4618 | TIN-INTERP | Interpolated Ground | 29477.13 | -5.02 | 705.73 | 0 | 20.19 | 0 | OK | Ground clear controls. | 68 | 33.26 | 725.92
4619 | TIN-INTERP | Interpolated Ground | 29477.14 | -4.45 | 705.73 | 0 | 32.03 | 0 | OK | Ground clear controls. | 68 | 33.26 | 737.76
4620 | TIN-INTERP | Interpolated Ground | 29477.38 | 9.09 | 706.08 | 0 | 25.5 | 0 | OK | Ground clear controls. | 68 | 33.26 | 731.58
4621 | TIN-INTERP | Interpolated Ground | 29477.39 | 6.91 | 705.98 | 0 | 31.71 | 0 | OK | Ground clear controls. | 68 | 33.26 | 737.69
4622 | TIN-INTERP | Interpolated Ground | 29477.39 | 7.59 | 706.02 | 0 | 19.78 | 0 | OK | Ground clear controls. | 68 | 33.26 | 725.8
4623 | TIN-INTERP | Interpolated Ground | 29517.12 | -6.66 | 707.03 | 0 | 26.95 | 0 | OK | Ground clear controls. | 68 | 33.26 | 733.98
4624 | TIN-INTERP | Interpolated Ground | 29517.13 | -5.03 | 707.02 | 0 | 21.25 | 0 | OK | Ground clear controls. | 68 | 33.26 | 728.27
4625 | TIN-INTERP | Interpolated Ground | 29517.14 | -4.44 | 707.01 | 0 | 33.25 | 0 | OK | Ground clear controls. | 68 | 33.26 | 740.26
4626 | TIN-INTERP | Interpolated Ground | 29517.38 | 9.28 | 707.06 | 0 | 26.98 | 0 | OK | Ground clear controls. | 68 | 33.26 | 734.04
4627 | TIN-INTERP | Interpolated Ground | 29517.39 | 7.07 | 707 | 0 | 33.26 | 0 | OK | Ground clear controls. | 68 | 33.26 | 740.26
4628 | TIN-INTERP | Interpolated Ground | 29517.39 | 7.78 | 707.02 | 0 | 21.22 | 0 | OK | Ground clear controls. | 68 | 21.22 | 728.24
4629 | TIN-INTERP | Interpolated Ground | 29536.08 | 9.36 | 707.19 | 0 | 28.3 | 0 | OK | Ground clear controls. | 69 | 40.28 | 735.49
4630 | TIN-INTERP | Interpolated Ground | 29536.13 | 7.86 | 707.26 | 0 | 22.43 | 0 | OK | Ground clear controls. | 69 | 40.28 | 729.69
4631 | TIN-INTERP | Interpolated Ground | 29536.22 | 7.14 | 707.29 | 0 | 34.48 | 0 | OK | Ground clear controls. | 69 | 40.28 | 741.77
4632 | TIN-INTERP | Interpolated Ground | 29536.53 | -6.67 | 707.16 | 0 | 28.36 | 0 | OK | Ground clear controls. | 69 | 40.28 | 735.52
4633 | TIN-INTERP | Interpolated Ground | 29536.53 | -5.04 | 707.14 | 0 | 22.6 | 0 | OK | Ground clear controls. | 69 | 40.28 | 729.74
4634 | TIN-INTERP | Interpolated Ground | 29536.53 | -4.44 | 707.07 | 0 | 34.74 | 0 | OK | Ground clear controls. | 69 | 40.28 | 741.81
4635 | TIN-INTERP | Interpolated Ground | 29576.24 | -6.65 | 708.07 | 0 | 25.51 | 0 | OK | Ground clear controls. | 69 | 40.28 | 733.58
4636 | TIN-INTERP | Interpolated Ground | 29576.29 | -5.02 | 708.27 | 0 | 19.63 | 0 | OK | Ground clear controls. | 69 | 40.28 | 727.9
4637 | TIN-INTERP | Interpolated Ground | 29576.33 | -4.4 | 708.34 | 0 | 31.55 | 0 | OK | Ground clear controls. | 69 | 40.28 | 739.89
4638 | TIN-INTERP | Interpolated Ground | 29576.8 | 7.89 | 708.5 | 0 | 19.28 | 0 | OK | Ground clear controls. | 69 | 40.28 | 727.78
4639 | TIN-INTERP | Interpolated Ground | 29576.84 | 7.17 | 708.4 | 0 | 31.42 | 0 | OK | Ground clear controls. | 69 | 40.28 | 739.82
4640 | TIN-INTERP | Interpolated Ground | 29576.89 | 9.39 | 708.8 | 0 | 24.8 | 0 | OK | Ground clear controls. | 69 | 40.28 | 733.6
4641 | TIN-INTERP | Interpolated Ground | 29616.24 | -6.62 | 708.58 | 0 | 23.96 | 0 | OK | Ground clear controls. | 69 | 40.28 | 732.54
4642 | TIN-INTERP | Interpolated Ground | 29616.29 | -5.02 | 708.63 | 0 | 18.3 | 0 | OK | Ground clear controls. | 69 | 40.28 | 726.93
4643 | TIN-INTERP | Interpolated Ground | 29616.33 | -4.38 | 708.64 | 0 | 30.23 | 0 | OK | Ground clear controls. | 69 | 40.28 | 738.87
4644 | TIN-INTERP | Interpolated Ground | 29616.8 | 7.92 | 708.93 | 0 | 17.84 | 0 | OK | Ground clear controls. | 69 | 40.28 | 726.77
4645 | TIN-INTERP | Interpolated Ground | 29616.83 | 7.19 | 708.95 | 0 | 29.83 | 0 | OK | Ground clear controls. | 69 | 40.28 | 738.78
4646 | TIN-INTERP | Interpolated Ground | 29616.89 | 9.42 | 708.92 | 0 | 23.69 | 0 | OK | Ground clear controls. | 69 | 40.28 | 732.61
4647 | TIN-INTERP | Interpolated Ground | 29656.24 | -6.6 | 709.3 | 0 | 23.11 | 0 | OK | Ground clear controls. | 69 | 40.28 | 732.41
4648 | TIN-INTERP | Interpolated Ground | 29656.29 | -5.01 | 709.39 | 0 | 17.45 | 0 | OK | Ground clear controls. | 69 | 40.28 | 726.84
4649 | TIN-INTERP | Interpolated Ground | 29656.33 | -4.35 | 709.39 | 0 | 29.34 | 0 | OK | Ground clear controls. | 69 | 40.28 | 738.73
4650 | TIN-INTERP | Interpolated Ground | 29656.8 | 7.94 | 710.84 | 0 | 15.81 | 0 | OK | Ground clear controls. | 69 | 40.28 | 726.65
4651 | TIN-INTERP | Interpolated Ground | 29656.83 | 7.22 | 710.7 | 0 | 27.94 | 0 | OK | Ground clear controls. | 69 | 40.28 | 738.64
4652 | TIN-INTERP | Interpolated Ground | 29656.89 | 9.44 | 711.08 | 0 | 21.42 | 0 | OK | Ground clear controls. | 69 | 40.28 | 732.5
4653 | TIN-INTERP | Interpolated Ground | 29696.24 | -6.58 | 715.31 | 0 | 17.85 | 0 | OK | Ground clear controls. | 69 | 40.28 | 733.16
4654 | TIN-INTERP | Interpolated Ground | 29696.29 | -5 | 715.25 | 0 | 12.37 | 0 | OK | Ground clear controls. | 69 | 40.28 | 727.62
4655 | TIN-INTERP | Interpolated Ground | 29696.33 | -4.32 | 715.25 | 0 | 24.24 | 0 | OK | Ground clear controls. | 69 | 40.28 | 739.49
4656 | TIN-INTERP | Interpolated Ground | 29696.8 | 7.97 | 715.41 | 0 | 12.03 | 0 | OK | Ground clear controls. | 69 | 40.28 | 727.44
4657 | TIN-INTERP | Interpolated Ground | 29696.83 | 7.25 | 715.35 | 0 | 24.06 | 0 | OK | Ground clear controls. | 69 | 40.28 | 739.41
4658 | TIN-INTERP | Interpolated Ground | 29696.89 | 9.47 | 715.58 | 0 | 17.72 | 0 | OK | Ground clear controls. | 69 | 40.28 | 733.3
4659 | TIN-INTERP | Interpolated Ground | 29736.24 | -6.56 | 717.45 | 0 | 17.34 | 0 | OK | Ground clear controls. | 69 | 40.28 | 734.79
4660 | TIN-INTERP | Interpolated Ground | 29736.29 | -4.99 | 717.38 | 0 | 11.9 | 0 | OK | Ground clear controls. | 69 | 40.28 | 729.28
4661 | TIN-INTERP | Interpolated Ground | 29736.33 | -4.3 | 717.41 | 0 | 23.73 | 0 | OK | Ground clear controls. | 69 | 40.28 | 741.14
4662 | TIN-INTERP | Interpolated Ground | 29736.8 | 7.99 | 717.26 | 0 | 11.86 | 0 | OK | Ground clear controls. | 69 | 40.28 | 729.12
4663 | TIN-INTERP | Interpolated Ground | 29736.83 | 7.27 | 717.2 | 0 | 23.88 | 0 | OK | Ground clear controls. | 69 | 40.28 | 741.08
4664 | TIN-INTERP | Interpolated Ground | 29736.89 | 9.5 | 717.14 | 0 | 17.84 | 0 | OK | Ground clear controls. | 69 | 40.28 | 734.98
4665 | TIN-INTERP | Interpolated Ground | 29776.24 | -6.53 | 719.18 | 0 | 18.15 | 0 | OK | Ground clear controls. | 69 | 40.28 | 737.33
4666 | TIN-INTERP | Interpolated Ground | 29776.29 | -4.99 | 719.2 | 0 | 12.62 | 0 | OK | Ground clear controls. | 69 | 40.28 | 731.82
4667 | TIN-INTERP | Interpolated Ground | 29776.33 | -4.27 | 719.17 | 0 | 24.51 | 0 | OK | Ground clear controls. | 69 | 40.28 | 743.68
4668 | TIN-INTERP | Interpolated Ground | 29776.8 | 8.01 | 719.13 | 0 | 12.56 | 0 | OK | Ground clear controls. | 69 | 40.28 | 731.69
4669 | TIN-INTERP | Interpolated Ground | 29776.83 | 7.3 | 719.19 | 0 | 24.47 | 0 | OK | Ground clear controls. | 69 | 40.28 | 743.66
4670 | TIN-INTERP | Interpolated Ground | 29776.89 | 9.52 | 718.99 | 0 | 18.56 | 0 | OK | Ground clear controls. | 69 | 40.28 | 737.55
4671 | TIN-INTERP | Interpolated Ground | 29816.24 | -6.51 | 720.16 | 0 | 20.61 | 0 | OK | Ground clear controls. | 69 | 40.28 | 740.77
4672 | TIN-INTERP | Interpolated Ground | 29816.29 | -4.98 | 720.09 | 0 | 15.14 | 0 | OK | Ground clear controls. | 69 | 40.28 | 735.23
4673 | TIN-INTERP | Interpolated Ground | 29816.33 | -4.24 | 720.06 | 0 | 27.07 | 0 | OK | Ground clear controls. | 69 | 40.28 | 747.13
4674 | TIN-INTERP | Interpolated Ground | 29816.8 | 8.04 | 719.81 | 0 | 15.36 | 0 | OK | Ground clear controls. | 69 | 40.28 | 735.17
4675 | TIN-INTERP | Interpolated Ground | 29816.83 | 7.32 | 719.82 | 0 | 27.33 | 0 | OK | Ground clear controls. | 69 | 40.28 | 747.15
4676 | TIN-INTERP | Interpolated Ground | 29816.89 | 9.55 | 719.94 | 0 | 21.09 | 0 | OK | Ground clear controls. | 69 | 40.28 | 741.03
4677 | TIN-INTERP | Interpolated Ground | 29856.24 | -6.49 | 721.41 | 0 | 23.7 | 0 | OK | Ground clear controls. | 69 | 40.28 | 745.11
4678 | TIN-INTERP | Interpolated Ground | 29856.29 | -4.97 | 721.43 | 0 | 18.09 | 0 | OK | Ground clear controls. | 69 | 40.28 | 739.52
4679 | TIN-INTERP | Interpolated Ground | 29856.33 | -4.22 | 721.28 | 0 | 30.19 | 0 | OK | Ground clear controls. | 69 | 40.28 | 751.47
4680 | TIN-INTERP | Interpolated Ground | 29856.8 | 8.06 | 721.45 | 0 | 18.1 | 0 | OK | Ground clear controls. | 69 | 40.28 | 739.55
4681 | TIN-INTERP | Interpolated Ground | 29856.83 | 7.35 | 721.42 | 0 | 30.14 | 0 | OK | Ground clear controls. | 69 | 40.28 | 751.56
4682 | TIN-INTERP | Interpolated Ground | 29856.89 | 9.57 | 721.52 | 0 | 23.88 | 0 | OK | Ground clear controls. | 69 | 40.28 | 745.4
4683 | TIN-INTERP | Interpolated Ground | 29896.24 | -6.47 | 722.17 | 0 | 28.18 | 0 | OK | Ground clear controls. | 69 | 40.28 | 750.35
4684 | TIN-INTERP | Interpolated Ground | 29896.29 | -4.96 | 722.05 | 0 | 22.65 | 0 | OK | Ground clear controls. | 69 | 40.28 | 744.7
4685 | TIN-INTERP | Interpolated Ground | 29896.33 | -4.19 | 722.01 | 0 | 34.7 | 0 | OK | Ground clear controls. | 69 | 40.28 | 756.71
4686 | TIN-INTERP | Interpolated Ground | 29896.8 | 8.09 | 722.33 | 0 | 22.5 | 0 | OK | Ground clear controls. | 69 | 40.28 | 744.83
4687 | TIN-INTERP | Interpolated Ground | 29896.83 | 7.38 | 722.34 | 0 | 34.53 | 0 | OK | Ground clear controls. | 69 | 40.28 | 756.87
4688 | TIN-INTERP | Interpolated Ground | 29896.89 | 9.6 | 722.27 | 0 | 28.41 | 0 | OK | Ground clear controls. | 69 | 40.28 | 750.68
4689 | TIN-INTERP | Interpolated Ground | 29936.24 | -6.45 | 723.04 | 0 | 33.45 | 0 | OK | Ground clear controls. | 69 | 40.28 | 756.49
4690 | TIN-INTERP | Interpolated Ground | 29936.29 | -4.96 | 722.9 | 0 | 27.85 | 0 | OK | Ground clear controls. | 69 | 40.28 | 750.75
4691 | TIN-INTERP | Interpolated Ground | 29936.33 | -4.16 | 722.79 | 0 | 40.05 | 0 | OK | Ground clear controls. | 69 | 40.28 | 762.84
4692 | TIN-INTERP | Interpolated Ground | 29936.8 | 8.11 | 722.77 | 0 | 28.24 | 0 | OK | Ground clear controls. | 69 | 40.28 | 751.01
4693 | TIN-INTERP | Interpolated Ground | 29936.83 | 7.4 | 722.81 | 0 | 40.28 | 0 | OK | Ground clear controls. | 69 | 40.28 | 763.09
4694 | TIN-INTERP | Interpolated Ground | 29936.89 | 9.62 | 722.83 | 0 | 34.02 | 0 | OK | Ground clear controls. | 69 | 34.02 | 756.85
4695 | TIN-INTERP | Interpolated Ground | 29941.5 | -6.49 | 722.95 | 0 | 34.54 | 0 | OK | Ground clear controls. | 70 | 40.94 | 757.49
4696 | TIN-INTERP | Interpolated Ground | 29941.5 | -4.99 | 723 | 0 | 28.7 | 0 | OK | Ground clear controls. | 70 | 40.94 | 751.7
4697 | TIN-INTERP | Interpolated Ground | 29941.5 | -4.19 | 722.9 | 0 | 40.89 | 0 | OK | Ground clear controls. | 70 | 40.94 | 763.79
4698 | TIN-INTERP | Interpolated Ground | 29942.5 | 7.36 | 722.83 | 0 | 40.94 | 0 | OK | Ground clear controls. | 70 | 40.94 | 763.77
4699 | TIN-INTERP | Interpolated Ground | 29942.58 | 8.07 | 722.81 | 0 | 28.87 | 0 | OK | Ground clear controls. | 70 | 39.45 | 751.68
4700 | TIN-INTERP | Interpolated Ground | 29942.87 | 9.56 | 722.8 | 0 | 34.69 | 0 | OK | Ground clear controls. | 70 | 39.45 | 757.49
4701 | TIN-INTERP | Interpolated Ground | 29980.82 | -6.46 | 723.12 | 0 | 29.84 | 0 | OK | Ground clear controls. | 70 | 39.45 | 752.96
4702 | TIN-INTERP | Interpolated Ground | 29981.01 | -4.98 | 723.15 | 0 | 24.17 | 0 | OK | Ground clear controls. | 70 | 39.45 | 747.32
4703 | TIN-INTERP | Interpolated Ground | 29981.11 | -4.21 | 723.13 | 0 | 36.09 | 0 | OK | Ground clear controls. | 70 | 39.45 | 759.22
4704 | TIN-INTERP | Interpolated Ground | 29982.5 | 7.15 | 723.3 | 0 | 35.85 | 0 | OK | Ground clear controls. | 70 | 39.45 | 759.15
4705 | TIN-INTERP | Interpolated Ground | 29982.58 | 7.85 | 723.38 | 0 | 23.82 | 0 | OK | Ground clear controls. | 70 | 39.45 | 747.2
4706 | TIN-INTERP | Interpolated Ground | 29982.87 | 9.33 | 723.51 | 0 | 29.58 | 0 | OK | Ground clear controls. | 70 | 39.45 | 753.09
4707 | TIN-INTERP | Interpolated Ground | 30020.82 | -6.47 | 723.06 | 0 | 26.24 | 0 | OK | Ground clear controls. | 70 | 39.45 | 749.3
4708 | TIN-INTERP | Interpolated Ground | 30021.01 | -4.99 | 723.12 | 0 | 20.67 | 0 | OK | Ground clear controls. | 70 | 39.45 | 743.79
4709 | TIN-INTERP | Interpolated Ground | 30021.11 | -4.24 | 723.17 | 0 | 32.35 | 0 | OK | Ground clear controls. | 70 | 39.45 | 755.52
4710 | TIN-INTERP | Interpolated Ground | 30022.5 | 6.94 | 722.92 | 0 | 32.49 | 0 | OK | Ground clear controls. | 70 | 39.45 | 755.41
4711 | TIN-INTERP | Interpolated Ground | 30022.58 | 7.62 | 722.94 | 0 | 20.65 | 0 | OK | Ground clear controls. | 70 | 39.45 | 743.59
4712 | TIN-INTERP | Interpolated Ground | 30022.87 | 9.1 | 722.92 | 0 | 26.63 | 0 | OK | Ground clear controls. | 70 | 39.45 | 749.55
4713 | TIN-INTERP | Interpolated Ground | 30060.82 | -6.48 | 723.79 | 0 | 22.74 | 0 | OK | Ground clear controls. | 70 | 39.45 | 746.53
4714 | TIN-INTERP | Interpolated Ground | 30061.01 | -5 | 723.87 | 0 | 17.26 | 0 | OK | Ground clear controls. | 70 | 39.45 | 741.13
4715 | TIN-INTERP | Interpolated Ground | 30061.11 | -4.27 | 723.93 | 0 | 28.77 | 0 | OK | Ground clear controls. | 70 | 39.45 | 752.7
4716 | TIN-INTERP | Interpolated Ground | 30062.5 | 6.73 | 723.68 | 0 | 28.9 | 0 | OK | Ground clear controls. | 70 | 39.45 | 752.58
4717 | TIN-INTERP | Interpolated Ground | 30062.58 | 7.39 | 723.74 | 0 | 17.13 | 0 | OK | Ground clear controls. | 70 | 39.45 | 740.87
4718 | TIN-INTERP | Interpolated Ground | 30062.87 | 8.88 | 724.03 | 0 | 22.85 | 0 | OK | Ground clear controls. | 70 | 39.45 | 746.88
4719 | TIN-INTERP | Interpolated Ground | 30100.82 | -6.5 | 724.23 | 0 | 20.41 | 0 | OK | Ground clear controls. | 70 | 39.45 | 744.64
4720 | TIN-INTERP | Interpolated Ground | 30101.01 | -5.01 | 724.11 | 0 | 15.22 | 0 | OK | Ground clear controls. | 70 | 39.45 | 739.33
4721 | TIN-INTERP | Interpolated Ground | 30101.1 | -4.3 | 724.13 | 0 | 26.64 | 0 | OK | Ground clear controls. | 70 | 39.45 | 750.77
4722 | TIN-INTERP | Interpolated Ground | 30102.5 | 6.52 | 723.95 | 0 | 26.68 | 0 | OK | Ground clear controls. | 70 | 39.45 | 750.63
4723 | TIN-INTERP | Interpolated Ground | 30102.58 | 7.16 | 724.02 | 0 | 15 | 0 | OK | Ground clear controls. | 70 | 39.45 | 739.02
4724 | TIN-INTERP | Interpolated Ground | 30102.87 | 8.65 | 724.21 | 0 | 20.86 | 0 | OK | Ground clear controls. | 70 | 39.45 | 745.07
4725 | TIN-INTERP | Interpolated Ground | 30140.82 | -6.51 | 724.14 | 0 | 19.49 | 0 | OK | Ground clear controls. | 70 | 39.45 | 743.63
4726 | TIN-INTERP | Interpolated Ground | 30141.01 | -5.02 | 724.18 | 0 | 14.2 | 0 | OK | Ground clear controls. | 70 | 39.45 | 738.38
4727 | TIN-INTERP | Interpolated Ground | 30141.1 | -4.34 | 724.19 | 0 | 25.52 | 0 | OK | Ground clear controls. | 70 | 39.45 | 749.71
4728 | TIN-INTERP | Interpolated Ground | 30142.5 | 6.31 | 724.12 | 0 | 25.44 | 0 | OK | Ground clear controls. | 70 | 39.45 | 749.56
4729 | TIN-INTERP | Interpolated Ground | 30142.58 | 6.94 | 724.12 | 0 | 13.94 | 0 | OK | Ground clear controls. | 70 | 39.45 | 738.06
4730 | TIN-INTERP | Interpolated Ground | 30142.87 | 8.43 | 724.13 | 0 | 19.99 | 0 | OK | Ground clear controls. | 70 | 39.45 | 744.12
4731 | TIN-INTERP | Interpolated Ground | 30180.82 | -6.52 | 724.32 | 0 | 19.19 | 0 | OK | Ground clear controls. | 70 | 39.45 | 743.51
4732 | TIN-INTERP | Interpolated Ground | 30181.01 | -5.03 | 724.36 | 0 | 13.94 | 0 | OK | Ground clear controls. | 70 | 39.45 | 738.3
4733 | TIN-INTERP | Interpolated Ground | 30181.1 | -4.37 | 724.35 | 0 | 25.19 | 0 | OK | Ground clear controls. | 70 | 39.45 | 749.54
4734 | TIN-INTERP | Interpolated Ground | 30182.5 | 6.1 | 724.31 | 0 | 25.08 | 0 | OK | Ground clear controls. | 70 | 39.45 | 749.39
4735 | TIN-INTERP | Interpolated Ground | 30182.58 | 6.71 | 724.35 | 0 | 13.64 | 0 | OK | Ground clear controls. | 70 | 39.45 | 737.99
4736 | TIN-INTERP | Interpolated Ground | 30182.87 | 8.2 | 724.3 | 0 | 19.73 | 0 | OK | Ground clear controls. | 70 | 39.45 | 744.03
4737 | TIN-INTERP | Interpolated Ground | 30220.82 | -6.53 | 724.66 | 0 | 19.59 | 0 | OK | Ground clear controls. | 70 | 39.45 | 744.25
4738 | TIN-INTERP | Interpolated Ground | 30221.01 | -5.04 | 724.68 | 0 | 14.39 | 0 | OK | Ground clear controls. | 70 | 39.45 | 739.07
4739 | TIN-INTERP | Interpolated Ground | 30221.1 | -4.4 | 724.69 | 0 | 25.53 | 0 | OK | Ground clear controls. | 70 | 39.45 | 750.22
4740 | TIN-INTERP | Interpolated Ground | 30222.49 | 5.89 | 724.54 | 0 | 25.56 | 0 | OK | Ground clear controls. | 70 | 39.45 | 750.1
4741 | TIN-INTERP | Interpolated Ground | 30222.58 | 6.48 | 724.54 | 0 | 14.24 | 0 | OK | Ground clear controls. | 70 | 39.45 | 738.78
4742 | TIN-INTERP | Interpolated Ground | 30222.87 | 7.97 | 724.62 | 0 | 20.19 | 0 | OK | Ground clear controls. | 70 | 39.45 | 744.81
4743 | TIN-INTERP | Interpolated Ground | 30260.82 | -6.54 | 725.42 | 0 | 20.47 | 0 | OK | Ground clear controls. | 70 | 39.45 | 745.89
4744 | TIN-INTERP | Interpolated Ground | 30261.01 | -5.05 | 725.4 | 0 | 15.31 | 0 | OK | Ground clear controls. | 70 | 39.45 | 740.71
4745 | TIN-INTERP | Interpolated Ground | 30261.1 | -4.43 | 725.44 | 0 | 26.37 | 0 | OK | Ground clear controls. | 70 | 39.45 | 751.81
4746 | TIN-INTERP | Interpolated Ground | 30262.49 | 5.67 | 724.97 | 0 | 26.74 | 0 | OK | Ground clear controls. | 70 | 39.45 | 751.71
4747 | TIN-INTERP | Interpolated Ground | 30262.58 | 6.26 | 724.9 | 0 | 15.57 | 0 | OK | Ground clear controls. | 70 | 39.45 | 740.47
4748 | TIN-INTERP | Interpolated Ground | 30262.87 | 7.75 | 724.79 | 0 | 21.66 | 0 | OK | Ground clear controls. | 70 | 39.45 | 746.45
4749 | TIN-INTERP | Interpolated Ground | 30300.82 | -6.55 | 725.91 | 0 | 22.5 | 0 | OK | Ground clear controls. | 70 | 39.45 | 748.41
4750 | TIN-INTERP | Interpolated Ground | 30301.01 | -5.06 | 725.98 | 0 | 17.23 | 0 | OK | Ground clear controls. | 70 | 39.45 | 743.21
4751 | TIN-INTERP | Interpolated Ground | 30301.1 | -4.47 | 726 | 0 | 28.25 | 0 | OK | Ground clear controls. | 70 | 39.45 | 754.25
4752 | TIN-INTERP | Interpolated Ground | 30302.49 | 5.46 | 725.79 | 0 | 28.42 | 0 | OK | Ground clear controls. | 70 | 39.45 | 754.21
4753 | TIN-INTERP | Interpolated Ground | 30302.57 | 6.03 | 725.72 | 0 | 17.31 | 0 | OK | Ground clear controls. | 70 | 39.45 | 743.03
4754 | TIN-INTERP | Interpolated Ground | 30302.87 | 7.52 | 725.75 | 0 | 23.21 | 0 | OK | Ground clear controls. | 70 | 39.45 | 748.96
4755 | TIN-INTERP | Interpolated Ground | 30340.82 | -6.56 | 726.13 | 0 | 25.67 | 0 | OK | Ground clear controls. | 70 | 39.45 | 751.8
4756 | TIN-INTERP | Interpolated Ground | 30341.01 | -5.07 | 726.23 | 0 | 20.35 | 0 | OK | Ground clear controls. | 70 | 39.45 | 746.58
4757 | TIN-INTERP | Interpolated Ground | 30341.1 | -4.5 | 726.3 | 0 | 31.28 | 0 | OK | Ground clear controls. | 70 | 39.45 | 757.58
4758 | TIN-INTERP | Interpolated Ground | 30342.49 | 5.25 | 726.63 | 0 | 30.96 | 0 | OK | Ground clear controls. | 70 | 39.45 | 757.59
4759 | TIN-INTERP | Interpolated Ground | 30342.57 | 5.8 | 726.58 | 0 | 19.89 | 0 | OK | Ground clear controls. | 70 | 39.45 | 746.47
4760 | TIN-INTERP | Interpolated Ground | 30342.86 | 7.3 | 726.45 | 0 | 25.87 | 0 | OK | Ground clear controls. | 70 | 39.45 | 752.32
4761 | TIN-INTERP | Interpolated Ground | 30380.82 | -6.58 | 727.54 | 0 | 28.55 | 0 | OK | Ground clear controls. | 70 | 39.45 | 756.09
4762 | TIN-INTERP | Interpolated Ground | 30381.01 | -5.08 | 727.45 | 0 | 23.36 | 0 | OK | Ground clear controls. | 70 | 39.45 | 750.81
4763 | TIN-INTERP | Interpolated Ground | 30381.1 | -4.53 | 727.46 | 0 | 34.33 | 0 | OK | Ground clear controls. | 70 | 39.45 | 761.79
4764 | TIN-INTERP | Interpolated Ground | 30382.49 | 5.04 | 727.56 | 0 | 34.31 | 0 | OK | Ground clear controls. | 70 | 39.45 | 761.87
4765 | TIN-INTERP | Interpolated Ground | 30382.57 | 5.57 | 727.59 | 0 | 23.21 | 0 | OK | Ground clear controls. | 70 | 39.45 | 750.8
4766 | TIN-INTERP | Interpolated Ground | 30382.86 | 7.07 | 727.49 | 0 | 29.07 | 0 | OK | Ground clear controls. | 70 | 39.45 | 756.56
4767 | TIN-INTERP | Interpolated Ground | 30420.82 | -6.59 | 727.52 | 0 | 33.74 | 0 | OK | Ground clear controls. | 70 | 39.45 | 761.26
4768 | TIN-INTERP | Interpolated Ground | 30421.01 | -5.09 | 727.59 | 0 | 28.3 | 0 | OK | Ground clear controls. | 70 | 39.45 | 755.89
4769 | TIN-INTERP | Interpolated Ground | 30421.1 | -4.56 | 727.57 | 0 | 39.31 | 0 | OK | Ground clear controls. | 70 | 39.45 | 766.88
4770 | TIN-INTERP | Interpolated Ground | 30422.49 | 4.83 | 727.58 | 0 | 39.45 | 0 | OK | Ground clear controls. | 70 | 39.45 | 767.03
4771 | TIN-INTERP | Interpolated Ground | 30422.57 | 5.35 | 727.6 | 0 | 28.41 | 0 | OK | Ground clear controls. | 70 | 34.1 | 756.01
4772 | TIN-INTERP | Interpolated Ground | 30422.86 | 6.85 | 727.56 | 0 | 34.1 | 0 | OK | Ground clear controls. | 70 | 34.1 | 761.66
4773 | TIN-INTERP | Interpolated Ground | 30457.23 | -5.1 | 727.89 | 0 | 33.36 | 0 | OK | Ground clear controls. | 71 | 44.38 | 761.25
4774 | TIN-INTERP | Interpolated Ground | 30457.24 | 4.65 | 728.09 | 0 | 44.16 | 0 | OK | Ground clear controls. | 71 | 44.38 | 772.25
4775 | TIN-INTERP | Interpolated Ground | 30457.28 | -4.59 | 727.87 | 0 | 44.38 | 0 | OK | Ground clear controls. | 71 | 44.38 | 772.25
4776 | TIN-INTERP | Interpolated Ground | 30457.29 | -6.6 | 727.94 | 0 | 38.81 | 0 | OK | Ground clear controls. | 71 | 42.55 | 766.75
4777 | TIN-INTERP | Interpolated Ground | 30457.29 | 5.15 | 728.17 | 0 | 33.08 | 0 | OK | Ground clear controls. | 71 | 42.55 | 761.25
4778 | TIN-INTERP | Interpolated Ground | 30457.31 | 6.65 | 728.35 | 0 | 38.41 | 0 | OK | Ground clear controls. | 71 | 42.55 | 766.76
4779 | TIN-INTERP | Interpolated Ground | 30497.23 | -5.1 | 729.58 | 0 | 27.43 | 0 | OK | Ground clear controls. | 71 | 42.55 | 757.01
4780 | TIN-INTERP | Interpolated Ground | 30497.24 | 4.64 | 729.25 | 0 | 38.6 | 0 | OK | Ground clear controls. | 71 | 42.55 | 767.85
4781 | TIN-INTERP | Interpolated Ground | 30497.28 | -4.59 | 729.62 | 0 | 38.32 | 0 | OK | Ground clear controls. | 71 | 42.55 | 767.94
4782 | TIN-INTERP | Interpolated Ground | 30497.29 | -6.6 | 729.44 | 0 | 32.99 | 0 | OK | Ground clear controls. | 71 | 42.55 | 762.43
4783 | TIN-INTERP | Interpolated Ground | 30497.29 | 5.15 | 729.22 | 0 | 27.71 | 0 | OK | Ground clear controls. | 71 | 42.55 | 756.93
4784 | TIN-INTERP | Interpolated Ground | 30497.31 | 6.65 | 729.09 | 0 | 33.45 | 0 | OK | Ground clear controls. | 71 | 42.55 | 762.54
4785 | TIN-INTERP | Interpolated Ground | 30537.23 | -5.1 | 730.5 | 0 | 23.12 | 0 | OK | Ground clear controls. | 71 | 42.55 | 753.62
4786 | TIN-INTERP | Interpolated Ground | 30537.24 | 4.64 | 730.46 | 0 | 33.89 | 0 | OK | Ground clear controls. | 71 | 42.55 | 764.35
4787 | TIN-INTERP | Interpolated Ground | 30537.28 | -4.59 | 730.53 | 0 | 33.97 | 0 | OK | Ground clear controls. | 71 | 42.55 | 764.5
4788 | TIN-INTERP | Interpolated Ground | 30537.29 | -6.6 | 730.44 | 0 | 28.54 | 0 | OK | Ground clear controls. | 71 | 42.55 | 758.98
4789 | TIN-INTERP | Interpolated Ground | 30537.29 | 5.14 | 730.4 | 0 | 23.08 | 0 | OK | Ground clear controls. | 71 | 42.55 | 753.48
4790 | TIN-INTERP | Interpolated Ground | 30537.31 | 6.64 | 730.14 | 0 | 29.05 | 0 | OK | Ground clear controls. | 71 | 42.55 | 759.19
4791 | TIN-INTERP | Interpolated Ground | 30577.23 | -5.1 | 732.21 | 0 | 18.9 | 0 | OK | Ground clear controls. | 71 | 42.55 | 751.11
4792 | TIN-INTERP | Interpolated Ground | 30577.24 | 4.64 | 732.15 | 0 | 29.58 | 0 | OK | Ground clear controls. | 71 | 42.55 | 761.73
4793 | TIN-INTERP | Interpolated Ground | 30577.28 | -4.59 | 732.22 | 0 | 29.73 | 0 | OK | Ground clear controls. | 71 | 42.55 | 761.95
4794 | TIN-INTERP | Interpolated Ground | 30577.29 | -6.6 | 732.2 | 0 | 24.2 | 0 | OK | Ground clear controls. | 71 | 42.55 | 756.4
4795 | TIN-INTERP | Interpolated Ground | 30577.29 | 5.14 | 732.07 | 0 | 18.85 | 0 | OK | Ground clear controls. | 71 | 42.55 | 750.92
4796 | TIN-INTERP | Interpolated Ground | 30577.31 | 6.64 | 732 | 0 | 24.7 | 0 | OK | Ground clear controls. | 71 | 42.55 | 756.7
4797 | TIN-INTERP | Interpolated Ground | 30617.23 | -5.1 | 733.82 | 0 | 15.63 | 0 | OK | Ground clear controls. | 71 | 42.55 | 749.45
4798 | TIN-INTERP | Interpolated Ground | 30617.24 | 4.63 | 733.59 | 0 | 26.41 | 0 | OK | Ground clear controls. | 71 | 42.55 | 760
4799 | TIN-INTERP | Interpolated Ground | 30617.28 | -4.6 | 733.83 | 0 | 26.42 | 0 | OK | Ground clear controls. | 71 | 42.55 | 760.25
4800 | TIN-INTERP | Interpolated Ground | 30617.29 | -6.6 | 733.66 | 0 | 21.05 | 0 | OK | Ground clear controls. | 71 | 42.55 | 754.71
4801 | TIN-INTERP | Interpolated Ground | 30617.29 | 5.13 | 733.57 | 0 | 15.66 | 0 | OK | Ground clear controls. | 71 | 42.55 | 749.23
4802 | TIN-INTERP | Interpolated Ground | 30617.31 | 6.64 | 733.58 | 0 | 21.47 | 0 | OK | Ground clear controls. | 71 | 42.55 | 755.05
4803 | TIN-INTERP | Interpolated Ground | 30657.23 | -5.1 | 734.39 | 0 | 14.27 | 0 | OK | Ground clear controls. | 71 | 42.55 | 748.66
4804 | TIN-INTERP | Interpolated Ground | 30657.24 | 4.63 | 734.4 | 0 | 24.76 | 0 | OK | Ground clear controls. | 71 | 42.55 | 759.16
4805 | TIN-INTERP | Interpolated Ground | 30657.28 | -4.6 | 734.33 | 0 | 25.11 | 0 | OK | Ground clear controls. | 71 | 42.55 | 759.44
4806 | TIN-INTERP | Interpolated Ground | 30657.29 | -6.6 | 734.54 | 0 | 19.35 | 0 | OK | Ground clear controls. | 71 | 42.55 | 753.89
4807 | TIN-INTERP | Interpolated Ground | 30657.29 | 5.13 | 734.36 | 0 | 14.05 | 0 | OK | Ground clear controls. | 71 | 42.55 | 748.41
4808 | TIN-INTERP | Interpolated Ground | 30657.31 | 6.63 | 734.29 | 0 | 19.97 | 0 | OK | Ground clear controls. | 71 | 42.55 | 754.26
4809 | TIN-INTERP | Interpolated Ground | 30697.23 | -5.1 | 735.48 | 0 | 13.24 | 0 | OK | Ground clear controls. | 71 | 42.55 | 748.72
4810 | TIN-INTERP | Interpolated Ground | 30697.24 | 4.62 | 735.06 | 0 | 24.15 | 0 | OK | Ground clear controls. | 71 | 42.55 | 759.21
4811 | TIN-INTERP | Interpolated Ground | 30697.28 | -4.6 | 735.48 | 0 | 24.02 | 0 | OK | Ground clear controls. | 71 | 42.55 | 759.5
4812 | TIN-INTERP | Interpolated Ground | 30697.29 | -6.6 | 735.5 | 0 | 18.44 | 0 | OK | Ground clear controls. | 71 | 42.55 | 753.94
4813 | TIN-INTERP | Interpolated Ground | 30697.29 | 5.13 | 734.98 | 0 | 13.49 | 0 | OK | Ground clear controls. | 71 | 42.55 | 748.47
4814 | TIN-INTERP | Interpolated Ground | 30697.31 | 6.63 | 734.92 | 0 | 19.42 | 0 | OK | Ground clear controls. | 71 | 42.55 | 754.34
4815 | TIN-INTERP | Interpolated Ground | 30737.23 | -5.1 | 735.78 | 0 | 13.87 | 0 | OK | Ground clear controls. | 71 | 42.55 | 749.65
4816 | TIN-INTERP | Interpolated Ground | 30737.24 | 4.62 | 735.21 | 0 | 24.93 | 0 | OK | Ground clear controls. | 71 | 42.55 | 760.14
4817 | TIN-INTERP | Interpolated Ground | 30737.28 | -4.6 | 735.73 | 0 | 24.7 | 0 | OK | Ground clear controls. | 71 | 42.55 | 760.43
4818 | TIN-INTERP | Interpolated Ground | 30737.29 | -6.6 | 735.89 | 0 | 19 | 0 | OK | Ground clear controls. | 71 | 42.55 | 754.89
4819 | TIN-INTERP | Interpolated Ground | 30737.29 | 5.12 | 735.23 | 0 | 14.17 | 0 | OK | Ground clear controls. | 71 | 42.55 | 749.4
4820 | TIN-INTERP | Interpolated Ground | 30737.31 | 6.62 | 735.27 | 0 | 20 | 0 | OK | Ground clear controls. | 71 | 42.55 | 755.27
4821 | TIN-INTERP | Interpolated Ground | 30777.23 | -5.1 | 736.09 | 0 | 15.35 | 0 | OK | Ground clear controls. | 71 | 42.55 | 751.44
4822 | TIN-INTERP | Interpolated Ground | 30777.24 | 4.62 | 735.85 | 0 | 26.12 | 0 | OK | Ground clear controls. | 71 | 42.55 | 761.97
4823 | TIN-INTERP | Interpolated Ground | 30777.28 | -4.6 | 736.07 | 0 | 26.17 | 0 | OK | Ground clear controls. | 71 | 42.55 | 762.24
4824 | TIN-INTERP | Interpolated Ground | 30777.29 | -6.6 | 736.14 | 0 | 20.55 | 0 | OK | Ground clear controls. | 71 | 42.55 | 756.69
4825 | TIN-INTERP | Interpolated Ground | 30777.29 | 5.12 | 735.86 | 0 | 15.35 | 0 | OK | Ground clear controls. | 71 | 42.55 | 751.21
4826 | TIN-INTERP | Interpolated Ground | 30777.31 | 6.62 | 735.75 | 0 | 21.3 | 0 | OK | Ground clear controls. | 71 | 42.55 | 757.05
4827 | TIN-INTERP | Interpolated Ground | 30817.23 | -5.1 | 736.04 | 0 | 18.06 | 0 | OK | Ground clear controls. | 71 | 42.55 | 754.1
4828 | TIN-INTERP | Interpolated Ground | 30817.24 | 4.61 | 735.9 | 0 | 28.79 | 0 | OK | Ground clear controls. | 71 | 42.55 | 764.69
4829 | TIN-INTERP | Interpolated Ground | 30817.28 | -4.6 | 736 | 0 | 28.92 | 0 | OK | Ground clear controls. | 71 | 42.55 | 764.92
4830 | TIN-INTERP | Interpolated Ground | 30817.29 | -6.6 | 736.04 | 0 | 23.34 | 0 | OK | Ground clear controls. | 71 | 42.55 | 759.38
4831 | TIN-INTERP | Interpolated Ground | 30817.29 | 5.11 | 735.91 | 0 | 17.99 | 0 | OK | Ground clear controls. | 71 | 42.55 | 753.9
4832 | TIN-INTERP | Interpolated Ground | 30817.31 | 6.61 | 735.9 | 0 | 23.79 | 0 | OK | Ground clear controls. | 71 | 42.55 | 759.69
4833 | TIN-INTERP | Interpolated Ground | 30857.23 | -5.1 | 736 | 0 | 21.6 | 0 | OK | Ground clear controls. | 71 | 42.55 | 757.6
4834 | TIN-INTERP | Interpolated Ground | 30857.24 | 4.61 | 736 | 0 | 32.3 | 0 | OK | Ground clear controls. | 71 | 42.55 | 768.3
4835 | TIN-INTERP | Interpolated Ground | 30857.28 | -4.6 | 736.03 | 0 | 32.44 | 0 | OK | Ground clear controls. | 71 | 42.55 | 768.47
4836 | TIN-INTERP | Interpolated Ground | 30857.29 | -6.6 | 736.03 | 0 | 26.91 | 0 | OK | Ground clear controls. | 71 | 42.55 | 762.94
4837 | TIN-INTERP | Interpolated Ground | 30857.29 | 5.11 | 735.96 | 0 | 21.49 | 0 | OK | Ground clear controls. | 71 | 42.55 | 757.45
4838 | TIN-INTERP | Interpolated Ground | 30857.31 | 6.61 | 735.91 | 0 | 27.27 | 0 | OK | Ground clear controls. | 71 | 42.55 | 763.18
4839 | TIN-INTERP | Interpolated Ground | 30897.23 | -5.1 | 735.95 | 0 | 26.03 | 0 | OK | Ground clear controls. | 71 | 42.55 | 761.98
4840 | TIN-INTERP | Interpolated Ground | 30897.24 | 4.61 | 735.72 | 0 | 37.07 | 0 | OK | Ground clear controls. | 71 | 42.55 | 772.79
4841 | TIN-INTERP | Interpolated Ground | 30897.28 | -4.6 | 735.96 | 0 | 36.94 | 0 | OK | Ground clear controls. | 71 | 42.55 | 772.9
4842 | TIN-INTERP | Interpolated Ground | 30897.29 | -6.6 | 735.99 | 0 | 31.4 | 0 | OK | Ground clear controls. | 71 | 42.55 | 767.39
4843 | TIN-INTERP | Interpolated Ground | 30897.29 | 5.11 | 735.64 | 0 | 26.25 | 0 | OK | Ground clear controls. | 71 | 42.55 | 761.89
4844 | TIN-INTERP | Interpolated Ground | 30897.31 | 6.61 | 735.5 | 0 | 32.03 | 0 | OK | Ground clear controls. | 71 | 42.55 | 767.53
4845 | TIN-INTERP | Interpolated Ground | 30937.23 | -5.1 | 735.68 | 0 | 31.56 | 0 | OK | Ground clear controls. | 71 | 42.55 | 767.24
4846 | TIN-INTERP | Interpolated Ground | 30937.24 | 4.6 | 735.64 | 0 | 42.55 | 0 | OK | Ground clear controls. | 71 | 42.55 | 778.19
4847 | TIN-INTERP | Interpolated Ground | 30937.28 | -4.6 | 735.7 | 0 | 42.52 | 0 | OK | Ground clear controls. | 71 | 42.52 | 778.22
4848 | TIN-INTERP | Interpolated Ground | 30937.29 | -6.6 | 735.71 | 0 | 37 | 0 | OK | Ground clear controls. | 71 | 37.14 | 772.71
4849 | TIN-INTERP | Interpolated Ground | 30937.29 | 5.1 | 735.67 | 0 | 31.55 | 0 | OK | Ground clear controls. | 71 | 37.14 | 767.22
4850 | TIN-INTERP | Interpolated Ground | 30937.31 | 6.6 | 735.61 | 0 | 37.14 | 0 | OK | Ground clear controls. | 71 | 37.14 | 772.75
4851 | TIN-INTERP | Interpolated Ground | 30946.83 | -5.1 | 735.82 | 0 | 32.8 | 0 | OK | Ground clear controls. | 72 | 43.9 | 768.62
4852 | TIN-INTERP | Interpolated Ground | 30946.86 | 6.6 | 735.59 | 0 | 38.53 | 0 | OK | Ground clear controls. | 72 | 43.9 | 774.12
4853 | TIN-INTERP | Interpolated Ground | 30946.87 | 4.6 | 735.78 | 0 | 43.84 | 0 | OK | Ground clear controls. | 72 | 43.9 | 779.62
4854 | TIN-INTERP | Interpolated Ground | 30946.87 | -4.6 | 735.72 | 0 | 43.9 | 0 | OK | Ground clear controls. | 72 | 43.9 | 779.62
4855 | TIN-INTERP | Interpolated Ground | 30946.88 | -6.6 | 735.88 | 0 | 38.24 | 0 | OK | Ground clear controls. | 72 | 38.75 | 774.12
4856 | TIN-INTERP | Interpolated Ground | 30946.89 | 5.1 | 735.74 | 0 | 32.88 | 0 | OK | Ground clear controls. | 72 | 38.75 | 768.62
4857 | TIN-INTERP | Interpolated Ground | 30986.83 | -5.1 | 735.97 | 0 | 27.64 | 0 | OK | Ground clear controls. | 72 | 38.75 | 763.61
4858 | TIN-INTERP | Interpolated Ground | 30986.86 | 6.6 | 735.75 | 0 | 33.41 | 0 | OK | Ground clear controls. | 72 | 38.75 | 769.16
4859 | TIN-INTERP | Interpolated Ground | 30986.87 | 4.6 | 735.72 | 0 | 38.75 | 0 | OK | Ground clear controls. | 72 | 38.75 | 774.47
4860 | TIN-INTERP | Interpolated Ground | 30986.87 | -4.6 | 735.96 | 0 | 38.6 | 0 | OK | Ground clear controls. | 72 | 38.6 | 774.56
4861 | TIN-INTERP | Interpolated Ground | 30986.88 | -6.6 | 735.96 | 0 | 33.09 | 0 | OK | Ground clear controls. | 72 | 36.51 | 769.05
4862 | TIN-INTERP | Interpolated Ground | 30986.89 | 5.1 | 735.73 | 0 | 27.81 | 0 | OK | Ground clear controls. | 72 | 36.51 | 763.54
4863 | TIN-INTERP | Interpolated Ground | 31026.83 | -5.1 | 735.95 | 0 | 23.51 | 0 | OK | Ground clear controls. | 72 | 36.51 | 759.46
4864 | TIN-INTERP | Interpolated Ground | 31026.86 | 6.6 | 735.75 | 0 | 29.3 | 0 | OK | Ground clear controls. | 72 | 36.51 | 765.05
4865 | TIN-INTERP | Interpolated Ground | 31026.87 | 4.6 | 735.67 | 0 | 34.53 | 0 | OK | Ground clear controls. | 72 | 36.51 | 770.2
4866 | TIN-INTERP | Interpolated Ground | 31026.87 | -4.6 | 735.96 | 0 | 34.41 | 0 | OK | Ground clear controls. | 72 | 36.51 | 770.37
4867 | TIN-INTERP | Interpolated Ground | 31026.88 | -6.6 | 735.89 | 0 | 28.96 | 0 | OK | Ground clear controls. | 72 | 36.51 | 764.85
4868 | TIN-INTERP | Interpolated Ground | 31026.89 | 5.1 | 735.67 | 0 | 23.66 | 0 | OK | Ground clear controls. | 72 | 36.51 | 759.33
4869 | TIN-INTERP | Interpolated Ground | 31066.83 | -5.11 | 736.28 | 0 | 19.89 | 0 | OK | Ground clear controls. | 72 | 36.51 | 756.17
4870 | TIN-INTERP | Interpolated Ground | 31066.86 | 6.59 | 737.52 | 0 | 24.27 | 0 | OK | Ground clear controls. | 72 | 36.51 | 761.79
4871 | TIN-INTERP | Interpolated Ground | 31066.87 | 4.59 | 737.37 | 0 | 29.45 | 0 | OK | Ground clear controls. | 72 | 36.51 | 766.82
4872 | TIN-INTERP | Interpolated Ground | 31066.87 | -4.61 | 736.3 | 0 | 30.75 | 0 | OK | Ground clear controls. | 72 | 36.51 | 767.05
4873 | TIN-INTERP | Interpolated Ground | 31066.88 | -6.61 | 736.27 | 0 | 25.25 | 0 | OK | Ground clear controls. | 72 | 36.51 | 761.52
4874 | TIN-INTERP | Interpolated Ground | 31066.89 | 5.09 | 737.41 | 0 | 18.57 | 0 | OK | Ground clear controls. | 72 | 36.51 | 755.98
4875 | TIN-INTERP | Interpolated Ground | 31106.83 | -5.11 | 736.51 | 0 | 17.24 | 0 | OK | Ground clear controls. | 72 | 36.51 | 753.75
4876 | TIN-INTERP | Interpolated Ground | 31106.86 | 6.59 | 736.7 | 0 | 22.7 | 0 | OK | Ground clear controls. | 72 | 36.51 | 759.4
4877 | TIN-INTERP | Interpolated Ground | 31106.87 | 4.59 | 736.74 | 0 | 27.59 | 0 | OK | Ground clear controls. | 72 | 36.51 | 764.33
4878 | TIN-INTERP | Interpolated Ground | 31106.87 | -4.61 | 736.53 | 0 | 28.07 | 0 | OK | Ground clear controls. | 72 | 36.51 | 764.6
4879 | TIN-INTERP | Interpolated Ground | 31106.88 | -6.61 | 736.44 | 0 | 22.64 | 0 | OK | Ground clear controls. | 72 | 36.51 | 759.08
4880 | TIN-INTERP | Interpolated Ground | 31106.89 | 5.09 | 736.72 | 0 | 16.8 | 0 | OK | Ground clear controls. | 72 | 36.51 | 753.52
4881 | TIN-INTERP | Interpolated Ground | 31146.83 | -5.11 | 736.71 | 0 | 15.47 | 0 | OK | Ground clear controls. | 72 | 36.51 | 752.18
4882 | TIN-INTERP | Interpolated Ground | 31146.86 | 6.59 | 736.77 | 0 | 21.07 | 0 | OK | Ground clear controls. | 72 | 36.51 | 757.84
4883 | TIN-INTERP | Interpolated Ground | 31146.87 | 4.59 | 736.73 | 0 | 25.98 | 0 | OK | Ground clear controls. | 72 | 36.51 | 762.71
4884 | TIN-INTERP | Interpolated Ground | 31146.87 | -4.61 | 736.76 | 0 | 26.26 | 0 | OK | Ground clear controls. | 72 | 36.51 | 763.02
4885 | TIN-INTERP | Interpolated Ground | 31146.88 | -6.61 | 736.63 | 0 | 20.86 | 0 | OK | Ground clear controls. | 72 | 36.51 | 757.49
4886 | TIN-INTERP | Interpolated Ground | 31146.89 | 5.09 | 736.76 | 0 | 15.15 | 0 | OK | Ground clear controls. | 72 | 36.51 | 751.91
4887 | TIN-INTERP | Interpolated Ground | 31186.83 | -5.11 | 736.99 | 0 | 14.48 | 0 | OK | Ground clear controls. | 72 | 36.51 | 751.47
4888 | TIN-INTERP | Interpolated Ground | 31186.86 | 6.59 | 737.03 | 0 | 20.1 | 0 | OK | Ground clear controls. | 72 | 36.51 | 757.13
4889 | TIN-INTERP | Interpolated Ground | 31186.87 | 4.59 | 736.98 | 0 | 25.01 | 0 | OK | Ground clear controls. | 72 | 36.51 | 761.99
4890 | TIN-INTERP | Interpolated Ground | 31186.87 | -4.61 | 737.01 | 0 | 25.29 | 0 | OK | Ground clear controls. | 72 | 36.51 | 762.3
4891 | TIN-INTERP | Interpolated Ground | 31186.88 | -6.61 | 737.01 | 0 | 19.76 | 0 | OK | Ground clear controls. | 72 | 36.51 | 756.77
4892 | TIN-INTERP | Interpolated Ground | 31186.89 | 5.09 | 736.99 | 0 | 14.17 | 0 | OK | Ground clear controls. | 72 | 36.51 | 751.16
4893 | TIN-INTERP | Interpolated Ground | 31226.83 | -5.12 | 736.96 | 0 | 14.67 | 0 | OK | Ground clear controls. | 72 | 36.51 | 751.63
4894 | TIN-INTERP | Interpolated Ground | 31226.86 | 6.58 | 737 | 0 | 20.29 | 0 | OK | Ground clear controls. | 72 | 36.51 | 757.29
4895 | TIN-INTERP | Interpolated Ground | 31226.87 | 4.58 | 736.92 | 0 | 25.23 | 0 | OK | Ground clear controls. | 72 | 36.51 | 762.15
4896 | TIN-INTERP | Interpolated Ground | 31226.87 | -4.62 | 737 | 0 | 25.47 | 0 | OK | Ground clear controls. | 72 | 36.51 | 762.47
4897 | TIN-INTERP | Interpolated Ground | 31226.88 | -6.62 | 736.87 | 0 | 20.06 | 0 | OK | Ground clear controls. | 72 | 36.51 | 756.93
4898 | TIN-INTERP | Interpolated Ground | 31226.89 | 5.08 | 736.95 | 0 | 14.35 | 0 | OK | Ground clear controls. | 72 | 36.51 | 751.3
4899 | TIN-INTERP | Interpolated Ground | 31266.83 | -5.12 | 736.8 | 0 | 15.85 | 0 | OK | Ground clear controls. | 72 | 36.51 | 752.65
4900 | TIN-INTERP | Interpolated Ground | 31266.86 | 6.58 | 737.11 | 0 | 21.18 | 0 | OK | Ground clear controls. | 72 | 36.51 | 758.29
4901 | TIN-INTERP | Interpolated Ground | 31266.87 | 4.58 | 736.99 | 0 | 26.2 | 0 | OK | Ground clear controls. | 72 | 36.51 | 763.19
4902 | TIN-INTERP | Interpolated Ground | 31266.87 | -4.62 | 736.83 | 0 | 26.65 | 0 | OK | Ground clear controls. | 72 | 36.51 | 763.48
4903 | TIN-INTERP | Interpolated Ground | 31266.88 | -6.62 | 736.76 | 0 | 21.19 | 0 | OK | Ground clear controls. | 72 | 36.51 | 757.95
4904 | TIN-INTERP | Interpolated Ground | 31266.89 | 5.08 | 737.11 | 0 | 15.19 | 0 | OK | Ground clear controls. | 72 | 36.51 | 752.3
4905 | TIN-INTERP | Interpolated Ground | 31306.83 | -5.12 | 737.06 | 0 | 17.45 | 0 | OK | Ground clear controls. | 72 | 36.51 | 754.51
4906 | TIN-INTERP | Interpolated Ground | 31306.86 | 6.58 | 737.22 | 0 | 22.93 | 0 | OK | Ground clear controls. | 72 | 36.51 | 760.15
4907 | TIN-INTERP | Interpolated Ground | 31306.87 | 4.58 | 737.18 | 0 | 27.93 | 0 | OK | Ground clear controls. | 72 | 36.51 | 765.11
4908 | TIN-INTERP | Interpolated Ground | 31306.87 | -4.62 | 737.11 | 0 | 28.26 | 0 | OK | Ground clear controls. | 72 | 36.51 | 765.37
4909 | TIN-INTERP | Interpolated Ground | 31306.88 | -6.62 | 736.93 | 0 | 22.92 | 0 | OK | Ground clear controls. | 72 | 36.51 | 759.85
4910 | TIN-INTERP | Interpolated Ground | 31306.89 | 5.08 | 737.3 | 0 | 16.86 | 0 | OK | Ground clear controls. | 72 | 36.51 | 754.16
4911 | TIN-INTERP | Interpolated Ground | 31346.83 | -5.12 | 737.56 | 0 | 19.7 | 0 | OK | Ground clear controls. | 72 | 36.51 | 757.26
4912 | TIN-INTERP | Interpolated Ground | 31346.86 | 6.58 | 737.67 | 0 | 25.18 | 0 | OK | Ground clear controls. | 72 | 36.51 | 762.85
4913 | TIN-INTERP | Interpolated Ground | 31346.87 | 4.58 | 737.54 | 0 | 30.39 | 0 | OK | Ground clear controls. | 72 | 36.51 | 767.93
4914 | TIN-INTERP | Interpolated Ground | 31346.87 | -4.62 | 737.57 | 0 | 30.58 | 0 | OK | Ground clear controls. | 72 | 36.51 | 768.15
4915 | TIN-INTERP | Interpolated Ground | 31346.88 | -6.62 | 737.59 | 0 | 25.02 | 0 | OK | Ground clear controls. | 72 | 36.51 | 762.61
4916 | TIN-INTERP | Interpolated Ground | 31346.89 | 5.08 | 737.59 | 0 | 19.32 | 0 | OK | Ground clear controls. | 72 | 36.51 | 756.91
4917 | TIN-INTERP | Interpolated Ground | 31386.83 | -5.13 | 738.42 | 0 | 22.43 | 0 | OK | Ground clear controls. | 72 | 36.51 | 760.85
4918 | TIN-INTERP | Interpolated Ground | 31386.86 | 6.57 | 738.08 | 0 | 28.34 | 0 | OK | Ground clear controls. | 72 | 36.51 | 766.42
4919 | TIN-INTERP | Interpolated Ground | 31386.87 | 4.57 | 738.16 | 0 | 33.46 | 0 | OK | Ground clear controls. | 72 | 36.51 | 771.62
4920 | TIN-INTERP | Interpolated Ground | 31386.87 | -4.63 | 738.4 | 0 | 33.37 | 0 | OK | Ground clear controls. | 72 | 36.51 | 771.77
4921 | TIN-INTERP | Interpolated Ground | 31386.88 | -6.63 | 738.34 | 0 | 27.91 | 0 | OK | Ground clear controls. | 72 | 36.51 | 766.25
4922 | TIN-INTERP | Interpolated Ground | 31386.89 | 5.07 | 738.14 | 0 | 22.37 | 0 | OK | Ground clear controls. | 72 | 36.51 | 760.51
4923 | TIN-INTERP | Interpolated Ground | 31426.83 | -5.13 | 739.77 | 0 | 25.55 | 0 | OK | Ground clear controls. | 72 | 36.51 | 765.32
4924 | TIN-INTERP | Interpolated Ground | 31426.86 | 6.57 | 739.84 | 0 | 30.99 | 0 | OK | Ground clear controls. | 72 | 36.51 | 770.83
4925 | TIN-INTERP | Interpolated Ground | 31426.87 | 4.57 | 739.69 | 0 | 36.51 | 0 | OK | Ground clear controls. | 72 | 36.51 | 776.2
4926 | TIN-INTERP | Interpolated Ground | 31426.87 | -4.63 | 739.76 | 0 | 36.51 | 0 | OK | Ground clear controls. | 72 | 36.51 | 776.27
4927 | TIN-INTERP | Interpolated Ground | 31426.88 | -6.63 | 739.68 | 0 | 31.08 | 0 | OK | Ground clear controls. | 72 | 31.08 | 770.76
4928 | TIN-INTERP | Interpolated Ground | 31426.89 | 5.07 | 739.72 | 0 | 25.26 | 0 | OK | Ground clear controls. | 72 | 25.26 | 764.98
4929 | TIN-INTERP | Interpolated Ground | 31452.72 | -5.13 | 740.66 | 0 | 28 | 0 | OK | Ground clear controls. | 73 | 39 | 768.66
4930 | TIN-INTERP | Interpolated Ground | 31452.78 | -4.63 | 740.66 | 0 | 39 | 0 | OK | Ground clear controls. | 73 | 39 | 779.66
4931 | TIN-INTERP | Interpolated Ground | 31452.84 | -6.63 | 740.5 | 0 | 33.66 | 0 | OK | Ground clear controls. | 73 | 38.7 | 774.16
4932 | TIN-INTERP | Interpolated Ground | 31452.88 | 5.07 | 741.48 | 0 | 26.88 | 0 | OK | Ground clear controls. | 73 | 38.7 | 768.36
4933 | TIN-INTERP | Interpolated Ground | 31452.89 | 4.57 | 741.48 | 0 | 38.18 | 0 | OK | Ground clear controls. | 73 | 38.7 | 779.66
4934 | TIN-INTERP | Interpolated Ground | 31452.89 | 6.57 | 741.61 | 0 | 32.54 | 0 | OK | Ground clear controls. | 73 | 38.7 | 774.15
4935 | TIN-INTERP | Interpolated Ground | 31492.72 | -5.13 | 738.26 | 0 | 25.27 | 0 | OK | Ground clear controls. | 73 | 38.7 | 763.53
4936 | TIN-INTERP | Interpolated Ground | 31492.78 | -4.63 | 738.15 | 0 | 36.36 | 0 | OK | Ground clear controls. | 73 | 38.7 | 774.51
4937 | TIN-INTERP | Interpolated Ground | 31492.84 | -6.63 | 738.54 | 0 | 30.51 | 0 | OK | Ground clear controls. | 73 | 38.7 | 769.05
4938 | TIN-INTERP | Interpolated Ground | 31492.88 | 5.07 | 739.68 | 0 | 23.56 | 0 | OK | Ground clear controls. | 73 | 38.7 | 763.24
4939 | TIN-INTERP | Interpolated Ground | 31492.89 | 4.57 | 739.75 | 0 | 34.69 | 0 | OK | Ground clear controls. | 73 | 38.7 | 774.44
4940 | TIN-INTERP | Interpolated Ground | 31492.89 | 6.57 | 739.59 | 0 | 29.52 | 0 | OK | Ground clear controls. | 73 | 38.7 | 769.11
4941 | TIN-INTERP | Interpolated Ground | 31532.72 | -5.13 | 738.07 | 0 | 21.2 | 0 | OK | Ground clear controls. | 73 | 38.7 | 759.27
4942 | TIN-INTERP | Interpolated Ground | 31532.78 | -4.63 | 738.02 | 0 | 32.22 | 0 | OK | Ground clear controls. | 73 | 38.7 | 770.24
4943 | TIN-INTERP | Interpolated Ground | 31532.84 | -6.63 | 738.14 | 0 | 26.65 | 0 | OK | Ground clear controls. | 73 | 38.7 | 764.79
4944 | TIN-INTERP | Interpolated Ground | 31532.88 | 5.07 | 737.5 | 0 | 21.51 | 0 | OK | Ground clear controls. | 73 | 38.7 | 759.01
4945 | TIN-INTERP | Interpolated Ground | 31532.89 | 4.57 | 737.46 | 0 | 32.65 | 0 | OK | Ground clear controls. | 73 | 38.7 | 770.11
4946 | TIN-INTERP | Interpolated Ground | 31532.89 | 6.57 | 737.25 | 0 | 27.67 | 0 | OK | Ground clear controls. | 73 | 38.7 | 764.92
4947 | TIN-INTERP | Interpolated Ground | 31572.72 | -5.13 | 737.01 | 0 | 18.87 | 0 | OK | Ground clear controls. | 73 | 38.7 | 755.88
4948 | TIN-INTERP | Interpolated Ground | 31572.78 | -4.63 | 737.01 | 0 | 29.83 | 0 | OK | Ground clear controls. | 73 | 38.7 | 766.84
4949 | TIN-INTERP | Interpolated Ground | 31572.84 | -6.63 | 737.03 | 0 | 24.38 | 0 | OK | Ground clear controls. | 73 | 38.7 | 761.41
4950 | TIN-INTERP | Interpolated Ground | 31572.88 | 5.07 | 736.88 | 0 | 18.76 | 0 | OK | Ground clear controls. | 73 | 38.7 | 755.64
4951 | TIN-INTERP | Interpolated Ground | 31572.89 | 4.57 | 736.85 | 0 | 29.82 | 0 | OK | Ground clear controls. | 73 | 38.7 | 766.67
4952 | TIN-INTERP | Interpolated Ground | 31572.89 | 6.57 | 736.88 | 0 | 24.71 | 0 | OK | Ground clear controls. | 73 | 38.7 | 761.59
4953 | TIN-INTERP | Interpolated Ground | 31612.72 | -5.12 | 737.09 | 0 | 16.26 | 0 | OK | Ground clear controls. | 73 | 38.7 | 753.35
4954 | TIN-INTERP | Interpolated Ground | 31612.78 | -4.62 | 737.09 | 0 | 27.22 | 0 | OK | Ground clear controls. | 73 | 38.7 | 764.31
4955 | TIN-INTERP | Interpolated Ground | 31612.84 | -6.62 | 737.06 | 0 | 21.84 | 0 | OK | Ground clear controls. | 73 | 38.7 | 758.9
4956 | TIN-INTERP | Interpolated Ground | 31612.88 | 5.07 | 737.03 | 0 | 16.11 | 0 | OK | Ground clear controls. | 73 | 38.7 | 753.14
4957 | TIN-INTERP | Interpolated Ground | 31612.89 | 4.57 | 737.05 | 0 | 27.05 | 0 | OK | Ground clear controls. | 73 | 38.7 | 764.1
4958 | TIN-INTERP | Interpolated Ground | 31612.89 | 6.57 | 736.9 | 0 | 22.21 | 0 | OK | Ground clear controls. | 73 | 38.7 | 759.11
4959 | TIN-INTERP | Interpolated Ground | 31652.72 | -5.12 | 737.45 | 0 | 14.25 | 0 | OK | Ground clear controls. | 73 | 38.7 | 751.7
4960 | TIN-INTERP | Interpolated Ground | 31652.78 | -4.62 | 737.49 | 0 | 25.16 | 0 | OK | Ground clear controls. | 73 | 38.7 | 762.65
4961 | TIN-INTERP | Interpolated Ground | 31652.84 | -6.62 | 737.46 | 0 | 19.79 | 0 | OK | Ground clear controls. | 73 | 38.7 | 757.25
4962 | TIN-INTERP | Interpolated Ground | 31652.88 | 5.08 | 737.6 | 0 | 13.91 | 0 | OK | Ground clear controls. | 73 | 38.7 | 751.51
4963 | TIN-INTERP | Interpolated Ground | 31652.89 | 4.58 | 737.57 | 0 | 24.85 | 0 | OK | Ground clear controls. | 73 | 38.7 | 762.42
4964 | TIN-INTERP | Interpolated Ground | 31652.89 | 6.58 | 737.61 | 0 | 19.86 | 0 | OK | Ground clear controls. | 73 | 38.7 | 757.47
4965 | TIN-INTERP | Interpolated Ground | 31692.72 | -5.12 | 737.15 | 0 | 13.75 | 0 | OK | Ground clear controls. | 73 | 38.7 | 750.9
4966 | TIN-INTERP | Interpolated Ground | 31692.78 | -4.62 | 737.18 | 0 | 24.68 | 0 | OK | Ground clear controls. | 73 | 38.7 | 761.86
4967 | TIN-INTERP | Interpolated Ground | 31692.84 | -6.62 | 737.04 | 0 | 19.41 | 0 | OK | Ground clear controls. | 73 | 38.7 | 756.45
4968 | TIN-INTERP | Interpolated Ground | 31692.88 | 5.08 | 737.09 | 0 | 13.65 | 0 | OK | Ground clear controls. | 73 | 38.7 | 750.74
4969 | TIN-INTERP | Interpolated Ground | 31692.89 | 4.58 | 737.17 | 0 | 24.45 | 0 | OK | Ground clear controls. | 73 | 38.7 | 761.62
4970 | TIN-INTERP | Interpolated Ground | 31692.89 | 6.58 | 736.84 | 0 | 19.85 | 0 | OK | Ground clear controls. | 73 | 38.7 | 756.69
4971 | TIN-INTERP | Interpolated Ground | 31732.72 | -5.12 | 735.96 | 0 | 15.02 | 0 | OK | Ground clear controls. | 73 | 38.7 | 750.98
4972 | TIN-INTERP | Interpolated Ground | 31732.78 | -4.62 | 735.96 | 0 | 25.97 | 0 | OK | Ground clear controls. | 73 | 38.7 | 761.93
4973 | TIN-INTERP | Interpolated Ground | 31732.84 | -6.62 | 736 | 0 | 20.52 | 0 | OK | Ground clear controls. | 73 | 38.7 | 756.52
4974 | TIN-INTERP | Interpolated Ground | 31732.88 | 5.08 | 736.01 | 0 | 14.83 | 0 | OK | Ground clear controls. | 73 | 38.7 | 750.84
4975 | TIN-INTERP | Interpolated Ground | 31732.89 | 4.58 | 735.97 | 0 | 25.74 | 0 | OK | Ground clear controls. | 73 | 38.7 | 761.71
4976 | TIN-INTERP | Interpolated Ground | 31732.89 | 6.58 | 735.97 | 0 | 20.78 | 0 | OK | Ground clear controls. | 73 | 38.7 | 756.75
4977 | TIN-INTERP | Interpolated Ground | 31772.72 | -5.12 | 735.45 | 0 | 16.46 | 0 | OK | Ground clear controls. | 73 | 38.7 | 751.91
4978 | TIN-INTERP | Interpolated Ground | 31772.78 | -4.62 | 735.43 | 0 | 27.44 | 0 | OK | Ground clear controls. | 73 | 38.7 | 762.87
4979 | TIN-INTERP | Interpolated Ground | 31772.84 | -6.62 | 735.48 | 0 | 21.98 | 0 | OK | Ground clear controls. | 73 | 38.7 | 757.46
4980 | TIN-INTERP | Interpolated Ground | 31772.88 | 5.08 | 735.43 | 0 | 16.37 | 0 | OK | Ground clear controls. | 73 | 38.7 | 751.8
4981 | TIN-INTERP | Interpolated Ground | 31772.89 | 4.58 | 735.38 | 0 | 27.29 | 0 | OK | Ground clear controls. | 73 | 38.7 | 762.67
4982 | TIN-INTERP | Interpolated Ground | 31772.89 | 6.58 | 735.56 | 0 | 22.11 | 0 | OK | Ground clear controls. | 73 | 38.7 | 757.67
4983 | TIN-INTERP | Interpolated Ground | 31812.72 | -5.12 | 734.9 | 0 | 18.82 | 0 | OK | Ground clear controls. | 73 | 38.7 | 753.72
4984 | TIN-INTERP | Interpolated Ground | 31812.78 | -4.62 | 734.89 | 0 | 29.8 | 0 | OK | Ground clear controls. | 73 | 38.7 | 764.69
4985 | TIN-INTERP | Interpolated Ground | 31812.84 | -6.62 | 734.86 | 0 | 24.4 | 0 | OK | Ground clear controls. | 73 | 38.7 | 759.26
4986 | TIN-INTERP | Interpolated Ground | 31812.88 | 5.08 | 735.07 | 0 | 18.56 | 0 | OK | Ground clear controls. | 73 | 38.7 | 753.63
4987 | TIN-INTERP | Interpolated Ground | 31812.89 | 4.58 | 735.09 | 0 | 29.42 | 0 | OK | Ground clear controls. | 73 | 38.7 | 764.51
4988 | TIN-INTERP | Interpolated Ground | 31812.89 | 6.58 | 735.1 | 0 | 24.34 | 0 | OK | Ground clear controls. | 73 | 38.7 | 759.44
4989 | TIN-INTERP | Interpolated Ground | 31852.72 | -5.12 | 732.51 | 0 | 23.88 | 0 | OK | Ground clear controls. | 73 | 38.7 | 756.39
4990 | TIN-INTERP | Interpolated Ground | 31852.78 | -4.62 | 732.5 | 0 | 34.86 | 0 | OK | Ground clear controls. | 73 | 38.7 | 767.36
4991 | TIN-INTERP | Interpolated Ground | 31852.84 | -6.62 | 732.5 | 0 | 29.41 | 0 | OK | Ground clear controls. | 73 | 38.7 | 761.91
4992 | TIN-INTERP | Interpolated Ground | 31852.88 | 5.08 | 732.5 | 0 | 23.84 | 0 | OK | Ground clear controls. | 73 | 38.7 | 756.34
4993 | TIN-INTERP | Interpolated Ground | 31852.89 | 4.58 | 732.44 | 0 | 34.8 | 0 | OK | Ground clear controls. | 73 | 38.7 | 767.24
4994 | TIN-INTERP | Interpolated Ground | 31852.89 | 6.58 | 732.6 | 0 | 29.45 | 0 | OK | Ground clear controls. | 73 | 38.7 | 762.05
4995 | TIN-INTERP | Interpolated Ground | 31892.72 | -5.12 | 732.18 | 0 | 27.74 | 0 | OK | Ground clear controls. | 73 | 38.7 | 759.92
4996 | TIN-INTERP | Interpolated Ground | 31892.78 | -4.62 | 732.22 | 0 | 38.7 | 0 | OK | Ground clear controls. | 73 | 38.7 | 770.92
4997 | TIN-INTERP | Interpolated Ground | 31892.84 | -6.62 | 732.07 | 0 | 33.37 | 0 | OK | Ground clear controls. | 73 | 38.37 | 765.44
4998 | TIN-INTERP | Interpolated Ground | 31892.88 | 5.08 | 732.43 | 0 | 27.47 | 0 | OK | Ground clear controls. | 73 | 38.37 | 759.9
4999 | TIN-INTERP | Interpolated Ground | 31892.89 | 4.58 | 732.48 | 0 | 38.37 | 0 | OK | Ground clear controls. | 73 | 38.37 | 770.85
5000 | TIN-INTERP | Interpolated Ground | 31892.89 | 6.58 | 732.29 | 0 | 33.23 | 0 | OK | Ground clear controls. | 73 | 33.23 | 765.52
5001 | TIN-INTERP | Interpolated Ground | 31931.41 | -4.62 | 731.09 | 0 | 44.08 | 0 | OK | Ground clear controls. | 74 | 44.08 | 775.17
5002 | TIN-INTERP | Interpolated Ground | 31931.44 | 6.58 | 731.29 | 0 | 38.38 | 0 | OK | Ground clear controls. | 74 | 43.83 | 769.67
5003 | TIN-INTERP | Interpolated Ground | 31931.46 | -5.12 | 731.1 | 0 | 33.08 | 0 | OK | Ground clear controls. | 74 | 43.83 | 764.18
5004 | TIN-INTERP | Interpolated Ground | 31931.46 | 5.08 | 731.36 | 0 | 32.81 | 0 | OK | Ground clear controls. | 74 | 43.83 | 764.17
5005 | TIN-INTERP | Interpolated Ground | 31931.47 | 4.58 | 731.34 | 0 | 43.83 | 0 | OK | Ground clear controls. | 74 | 43.83 | 775.17
5006 | TIN-INTERP | Interpolated Ground | 31931.49 | -6.62 | 731.1 | 0 | 38.57 | 0 | OK | Ground clear controls. | 74 | 41.84 | 769.67
5007 | TIN-INTERP | Interpolated Ground | 31971.41 | -4.62 | 730.86 | 0 | 38.7 | 0 | OK | Ground clear controls. | 74 | 41.84 | 769.56
5008 | TIN-INTERP | Interpolated Ground | 31971.44 | 6.58 | 730.78 | 0 | 33.42 | 0 | OK | Ground clear controls. | 74 | 41.84 | 764.2
5009 | TIN-INTERP | Interpolated Ground | 31971.46 | -5.12 | 730.86 | 0 | 27.75 | 0 | OK | Ground clear controls. | 74 | 41.84 | 758.61
5010 | TIN-INTERP | Interpolated Ground | 31971.47 | 5.08 | 730.51 | 0 | 28.09 | 0 | OK | Ground clear controls. | 74 | 41.84 | 758.6
5011 | TIN-INTERP | Interpolated Ground | 31971.47 | 4.58 | 730.5 | 0 | 39.01 | 0 | OK | Ground clear controls. | 74 | 41.84 | 769.51
5012 | TIN-INTERP | Interpolated Ground | 31971.49 | -6.62 | 730.82 | 0 | 33.32 | 0 | OK | Ground clear controls. | 74 | 41.84 | 764.14
5013 | TIN-INTERP | Interpolated Ground | 32011.41 | -4.61 | 731.32 | 0 | 33.5 | 0 | OK | Ground clear controls. | 74 | 41.84 | 764.82
5014 | TIN-INTERP | Interpolated Ground | 32011.44 | 6.59 | 731.31 | 0 | 28.26 | 0 | OK | Ground clear controls. | 74 | 41.84 | 759.57
5015 | TIN-INTERP | Interpolated Ground | 32011.46 | -5.11 | 731.29 | 0 | 22.62 | 0 | OK | Ground clear controls. | 74 | 41.84 | 753.91
5016 | TIN-INTERP | Interpolated Ground | 32011.47 | 5.09 | 731.17 | 0 | 22.74 | 0 | OK | Ground clear controls. | 74 | 41.84 | 753.91
5017 | TIN-INTERP | Interpolated Ground | 32011.47 | 4.59 | 731.1 | 0 | 33.64 | 0 | OK | Ground clear controls. | 74 | 41.84 | 764.74
5018 | TIN-INTERP | Interpolated Ground | 32011.49 | -6.61 | 731.21 | 0 | 28.26 | 0 | OK | Ground clear controls. | 74 | 41.84 | 759.47
5019 | TIN-INTERP | Interpolated Ground | 32051.41 | -4.61 | 732.32 | 0 | 28.66 | 0 | OK | Ground clear controls. | 74 | 41.84 | 760.98
5020 | TIN-INTERP | Interpolated Ground | 32051.44 | 6.59 | 732.42 | 0 | 23.4 | 0 | OK | Ground clear controls. | 74 | 41.84 | 755.82
5021 | TIN-INTERP | Interpolated Ground | 32051.46 | -5.11 | 732.37 | 0 | 17.73 | 0 | OK | Ground clear controls. | 74 | 41.84 | 750.1
5022 | TIN-INTERP | Interpolated Ground | 32051.47 | 5.09 | 732.08 | 0 | 18.01 | 0 | OK | Ground clear controls. | 74 | 41.84 | 750.09
5023 | TIN-INTERP | Interpolated Ground | 32051.47 | 4.59 | 731.93 | 0 | 28.94 | 0 | OK | Ground clear controls. | 74 | 41.84 | 760.87
5024 | TIN-INTERP | Interpolated Ground | 32051.49 | -6.61 | 732.36 | 0 | 23.33 | 0 | OK | Ground clear controls. | 74 | 41.84 | 755.69
5025 | TIN-INTERP | Interpolated Ground | 32091.41 | -4.61 | 729.85 | 0 | 28.17 | 0 | OK | Ground clear controls. | 74 | 41.84 | 758.02
5026 | TIN-INTERP | Interpolated Ground | 32091.44 | 6.59 | 729.83 | 0 | 23.1 | 0 | OK | Ground clear controls. | 74 | 41.84 | 752.93
5027 | TIN-INTERP | Interpolated Ground | 32091.46 | -5.11 | 729.84 | 0 | 17.32 | 0 | OK | Ground clear controls. | 74 | 41.84 | 747.16
5028 | TIN-INTERP | Interpolated Ground | 32091.47 | 5.09 | 729.72 | 0 | 17.43 | 0 | OK | Ground clear controls. | 74 | 41.84 | 747.15
5029 | TIN-INTERP | Interpolated Ground | 32091.47 | 4.59 | 729.7 | 0 | 28.18 | 0 | OK | Ground clear controls. | 74 | 41.84 | 757.88
5030 | TIN-INTERP | Interpolated Ground | 32091.49 | -6.61 | 729.78 | 0 | 22.98 | 0 | OK | Ground clear controls. | 74 | 41.84 | 752.76
5031 | TIN-INTERP | Interpolated Ground | 32131.41 | -4.61 | 729.68 | 0 | 26.25 | 0 | OK | Ground clear controls. | 74 | 41.84 | 755.93
5032 | TIN-INTERP | Interpolated Ground | 32131.44 | 6.59 | 729.75 | 0 | 21.14 | 0 | OK | Ground clear controls. | 74 | 41.84 | 750.89
5033 | TIN-INTERP | Interpolated Ground | 32131.46 | -5.11 | 729.71 | 0 | 15.39 | 0 | OK | Ground clear controls. | 74 | 41.84 | 745.1
5034 | TIN-INTERP | Interpolated Ground | 32131.47 | 5.09 | 729.59 | 0 | 15.5 | 0 | OK | Ground clear controls. | 74 | 41.84 | 745.09
5035 | TIN-INTERP | Interpolated Ground | 32131.47 | 4.59 | 729.53 | 0 | 26.26 | 0 | OK | Ground clear controls. | 74 | 41.84 | 755.79
5036 | TIN-INTERP | Interpolated Ground | 32131.49 | -6.61 | 729.66 | 0 | 21.05 | 0 | OK | Ground clear controls. | 74 | 41.84 | 750.71
5037 | TIN-INTERP | Interpolated Ground | 32171.41 | -4.61 | 728.57 | 0 | 26.17 | 0 | OK | Ground clear controls. | 74 | 41.84 | 754.74
5038 | TIN-INTERP | Interpolated Ground | 32171.44 | 6.59 | 728.76 | 0 | 20.96 | 0 | OK | Ground clear controls. | 74 | 41.84 | 749.72
5039 | TIN-INTERP | Interpolated Ground | 32171.46 | -5.11 | 728.55 | 0 | 15.36 | 0 | OK | Ground clear controls. | 74 | 41.84 | 743.91
5040 | TIN-INTERP | Interpolated Ground | 32171.47 | 5.09 | 728.72 | 0 | 15.17 | 0 | OK | Ground clear controls. | 74 | 41.84 | 743.89
5041 | TIN-INTERP | Interpolated Ground | 32171.47 | 4.59 | 728.6 | 0 | 25.98 | 0 | OK | Ground clear controls. | 74 | 41.84 | 754.58
5042 | TIN-INTERP | Interpolated Ground | 32171.49 | -6.61 | 728.51 | 0 | 21.02 | 0 | OK | Ground clear controls. | 74 | 41.84 | 749.53
5043 | TIN-INTERP | Interpolated Ground | 32211.41 | -4.61 | 728.29 | 0 | 26.12 | 0 | OK | Ground clear controls. | 74 | 41.84 | 754.41
5044 | TIN-INTERP | Interpolated Ground | 32211.44 | 6.59 | 728.58 | 0 | 20.82 | 0 | OK | Ground clear controls. | 74 | 41.84 | 749.4
5045 | TIN-INTERP | Interpolated Ground | 32211.46 | -5.11 | 728.21 | 0 | 15.38 | 0 | OK | Ground clear controls. | 74 | 41.84 | 743.59
5046 | TIN-INTERP | Interpolated Ground | 32211.47 | 5.09 | 728.53 | 0 | 15.04 | 0 | OK | Ground clear controls. | 74 | 41.84 | 743.57
5047 | TIN-INTERP | Interpolated Ground | 32211.47 | 4.59 | 728.49 | 0 | 25.77 | 0 | OK | Ground clear controls. | 74 | 41.84 | 754.26
5048 | TIN-INTERP | Interpolated Ground | 32211.49 | -6.61 | 728.11 | 0 | 21.1 | 0 | OK | Ground clear controls. | 74 | 41.84 | 749.21
5049 | TIN-INTERP | Interpolated Ground | 32251.41 | -4.61 | 730.26 | 0 | 24.72 | 0 | OK | Ground clear controls. | 74 | 41.84 | 754.98
5050 | TIN-INTERP | Interpolated Ground | 32251.44 | 6.59 | 730.52 | 0 | 19.42 | 0 | OK | Ground clear controls. | 74 | 41.84 | 749.94
5051 | TIN-INTERP | Interpolated Ground | 32251.46 | -5.11 | 730.25 | 0 | 13.89 | 0 | OK | Ground clear controls. | 74 | 41.84 | 744.14
5052 | TIN-INTERP | Interpolated Ground | 32251.47 | 5.09 | 730.24 | 0 | 13.89 | 0 | OK | Ground clear controls. | 74 | 41.84 | 744.13
5053 | TIN-INTERP | Interpolated Ground | 32251.47 | 4.59 | 730.2 | 0 | 24.63 | 0 | OK | Ground clear controls. | 74 | 41.84 | 754.83
5054 | TIN-INTERP | Interpolated Ground | 32251.49 | -6.61 | 730.2 | 0 | 19.57 | 0 | OK | Ground clear controls. | 74 | 41.84 | 749.77
5055 | TIN-INTERP | Interpolated Ground | 32291.41 | -4.61 | 732.11 | 0 | 24.31 | 0 | OK | Ground clear controls. | 74 | 41.84 | 756.42
5056 | TIN-INTERP | Interpolated Ground | 32291.44 | 6.59 | 732.48 | 0 | 18.86 | 0 | OK | Ground clear controls. | 74 | 41.84 | 751.34
5057 | TIN-INTERP | Interpolated Ground | 32291.46 | -5.11 | 732.1 | 0 | 13.47 | 0 | OK | Ground clear controls. | 74 | 41.84 | 745.57
5058 | TIN-INTERP | Interpolated Ground | 32291.47 | 5.09 | 732.32 | 0 | 13.23 | 0 | OK | Ground clear controls. | 74 | 41.84 | 745.55
5059 | TIN-INTERP | Interpolated Ground | 32291.47 | 4.59 | 732.23 | 0 | 24.06 | 0 | OK | Ground clear controls. | 74 | 41.84 | 756.29
5060 | TIN-INTERP | Interpolated Ground | 32291.49 | -6.61 | 731.95 | 0 | 19.23 | 0 | OK | Ground clear controls. | 74 | 41.84 | 751.18
5061 | TIN-INTERP | Interpolated Ground | 32331.41 | -4.61 | 732.09 | 0 | 26.66 | 0 | OK | Ground clear controls. | 74 | 41.84 | 758.75
5062 | TIN-INTERP | Interpolated Ground | 32331.44 | 6.59 | 731.72 | 0 | 21.89 | 0 | OK | Ground clear controls. | 74 | 41.84 | 753.61
5063 | TIN-INTERP | Interpolated Ground | 32331.46 | -5.11 | 732.09 | 0 | 15.79 | 0 | OK | Ground clear controls. | 74 | 41.84 | 747.88
5064 | TIN-INTERP | Interpolated Ground | 32331.47 | 5.09 | 731.76 | 0 | 16.1 | 0 | OK | Ground clear controls. | 74 | 41.84 | 747.86
5065 | TIN-INTERP | Interpolated Ground | 32331.47 | 4.59 | 731.7 | 0 | 26.93 | 0 | OK | Ground clear controls. | 74 | 41.84 | 758.63
5066 | TIN-INTERP | Interpolated Ground | 32331.49 | -6.61 | 732.05 | 0 | 21.42 | 0 | OK | Ground clear controls. | 74 | 41.84 | 753.47
5067 | TIN-INTERP | Interpolated Ground | 32371.41 | -4.6 | 731.04 | 0 | 30.91 | 0 | OK | Ground clear controls. | 74 | 41.84 | 761.95
5068 | TIN-INTERP | Interpolated Ground | 32371.44 | 6.6 | 730.9 | 0 | 25.83 | 0 | OK | Ground clear controls. | 74 | 41.84 | 756.73
5069 | TIN-INTERP | Interpolated Ground | 32371.46 | -5.1 | 731.03 | 0 | 20.02 | 0 | OK | Ground clear controls. | 74 | 41.84 | 751.05
5070 | TIN-INTERP | Interpolated Ground | 32371.47 | 5.1 | 730.64 | 0 | 20.4 | 0 | OK | Ground clear controls. | 74 | 41.84 | 751.04
5071 | TIN-INTERP | Interpolated Ground | 32371.47 | 4.6 | 730.61 | 0 | 31.25 | 0 | OK | Ground clear controls. | 74 | 41.84 | 761.86
5072 | TIN-INTERP | Interpolated Ground | 32371.49 | -6.6 | 731 | 0 | 25.62 | 0 | OK | Ground clear controls. | 74 | 41.84 | 756.62
5073 | TIN-INTERP | Interpolated Ground | 32411.41 | -4.6 | 730.17 | 0 | 35.87 | 0 | OK | Ground clear controls. | 74 | 41.84 | 766.04
5074 | TIN-INTERP | Interpolated Ground | 32411.44 | 6.6 | 729.85 | 0 | 30.85 | 0 | OK | Ground clear controls. | 74 | 41.84 | 760.7
5075 | TIN-INTERP | Interpolated Ground | 32411.46 | -5.1 | 730.13 | 0 | 24.97 | 0 | OK | Ground clear controls. | 74 | 41.84 | 755.1
5076 | TIN-INTERP | Interpolated Ground | 32411.47 | 5.1 | 730.02 | 0 | 25.07 | 0 | OK | Ground clear controls. | 74 | 41.84 | 755.09
5077 | TIN-INTERP | Interpolated Ground | 32411.47 | 4.6 | 730.09 | 0 | 35.89 | 0 | OK | Ground clear controls. | 74 | 41.84 | 765.98
5078 | TIN-INTERP | Interpolated Ground | 32411.49 | -6.6 | 730.17 | 0 | 30.47 | 0 | OK | Ground clear controls. | 74 | 41.84 | 760.64
5079 | TIN-INTERP | Interpolated Ground | 32451.41 | -4.6 | 729.23 | 0 | 41.78 | 0 | OK | Ground clear controls. | 74 | 41.84 | 771.01
5080 | TIN-INTERP | Interpolated Ground | 32451.44 | 6.6 | 729.24 | 0 | 36.31 | 0 | OK | Ground clear controls. | 74 | 41.84 | 765.55
5081 | TIN-INTERP | Interpolated Ground | 32451.46 | -5.1 | 729.25 | 0 | 30.78 | 0 | OK | Ground clear controls. | 74 | 41.84 | 760.03
5082 | TIN-INTERP | Interpolated Ground | 32451.47 | 5.1 | 729.19 | 0 | 30.84 | 0 | OK | Ground clear controls. | 74 | 41.84 | 760.03
5083 | TIN-INTERP | Interpolated Ground | 32451.47 | 4.6 | 729.16 | 0 | 41.84 | 0 | OK | Ground clear controls. | 74 | 41.84 | 771
5084 | TIN-INTERP | Interpolated Ground | 32451.49 | -6.6 | 729.16 | 0 | 36.38 | 0 | OK | Ground clear controls. | 74 | 36.38 | 765.54
5085 | TIN-INTERP | Interpolated Ground | 32464.09 | -4.6 | 728.98 | 0 | 43.79 | 0 | OK | Ground clear controls. | 75 | 43.79 | 772.77
5086 | TIN-INTERP | Interpolated Ground | 32464.12 | 4.6 | 729.01 | 0 | 43.76 | 0 | OK | Ground clear controls. | 75 | 43.76 | 772.77
5087 | TIN-INTERP | Interpolated Ground | 32464.13 | 6.6 | 729.17 | 0 | 38.1 | 0 | OK | Ground clear controls. | 75 | 38.62 | 767.27
5088 | TIN-INTERP | Interpolated Ground | 32464.14 | 5.1 | 729.08 | 0 | 32.69 | 0 | OK | Ground clear controls. | 75 | 38.62 | 761.77
5089 | TIN-INTERP | Interpolated Ground | 32464.14 | -5.1 | 729.01 | 0 | 32.76 | 0 | OK | Ground clear controls. | 75 | 38.62 | 761.77
5090 | TIN-INTERP | Interpolated Ground | 32464.16 | -6.6 | 729.05 | 0 | 38.22 | 0 | OK | Ground clear controls. | 75 | 38.62 | 767.27
5091 | TIN-INTERP | Interpolated Ground | 32504.09 | -4.6 | 728.9 | 0 | 38.29 | 0 | OK | Ground clear controls. | 75 | 38.62 | 767.19
5092 | TIN-INTERP | Interpolated Ground | 32504.12 | 4.6 | 728.55 | 0 | 38.61 | 0 | OK | Ground clear controls. | 75 | 38.62 | 767.16
5093 | TIN-INTERP | Interpolated Ground | 32504.13 | 6.6 | 728.85 | 0 | 33 | 0 | OK | Ground clear controls. | 75 | 38.62 | 761.85
5094 | TIN-INTERP | Interpolated Ground | 32504.14 | 5.1 | 728.55 | 0 | 27.71 | 0 | OK | Ground clear controls. | 75 | 38.62 | 756.26
5095 | TIN-INTERP | Interpolated Ground | 32504.14 | -5.1 | 728.89 | 0 | 27.37 | 0 | OK | Ground clear controls. | 75 | 38.62 | 756.26
5096 | TIN-INTERP | Interpolated Ground | 32504.16 | -6.6 | 728.83 | 0 | 32.98 | 0 | OK | Ground clear controls. | 75 | 38.62 | 761.81
5097 | TIN-INTERP | Interpolated Ground | 32544.09 | -4.6 | 728.34 | 0 | 34.15 | 0 | OK | Ground clear controls. | 75 | 38.62 | 762.49
5098 | TIN-INTERP | Interpolated Ground | 32544.12 | 4.6 | 728.13 | 0 | 34.32 | 0 | OK | Ground clear controls. | 75 | 38.62 | 762.45
5099 | TIN-INTERP | Interpolated Ground | 32544.13 | 6.6 | 728.41 | 0 | 28.88 | 0 | OK | Ground clear controls. | 75 | 38.62 | 757.29
5100 | TIN-INTERP | Interpolated Ground | 32544.14 | 5.1 | 728.22 | 0 | 23.41 | 0 | OK | Ground clear controls. | 75 | 38.62 | 751.63
5101 | TIN-INTERP | Interpolated Ground | 32544.14 | -5.1 | 728.34 | 0 | 23.29 | 0 | OK | Ground clear controls. | 75 | 38.62 | 751.63
5102 | TIN-INTERP | Interpolated Ground | 32544.16 | -6.6 | 728.24 | 0 | 28.98 | 0 | OK | Ground clear controls. | 75 | 38.62 | 757.22
5103 | TIN-INTERP | Interpolated Ground | 32584.09 | -4.6 | 728.1 | 0 | 30.61 | 0 | OK | Ground clear controls. | 75 | 38.62 | 758.71
5104 | TIN-INTERP | Interpolated Ground | 32584.12 | 4.6 | 727.8 | 0 | 30.85 | 0 | OK | Ground clear controls. | 75 | 38.62 | 758.65
5105 | TIN-INTERP | Interpolated Ground | 32584.13 | 6.6 | 727.82 | 0 | 25.79 | 0 | OK | Ground clear controls. | 75 | 38.62 | 753.61
5106 | TIN-INTERP | Interpolated Ground | 32584.14 | 5.1 | 727.81 | 0 | 20.08 | 0 | OK | Ground clear controls. | 75 | 38.62 | 747.89
5107 | TIN-INTERP | Interpolated Ground | 32584.14 | -5.1 | 728.13 | 0 | 19.77 | 0 | OK | Ground clear controls. | 75 | 38.62 | 747.9
5108 | TIN-INTERP | Interpolated Ground | 32584.16 | -6.6 | 728.11 | 0 | 25.41 | 0 | OK | Ground clear controls. | 75 | 38.62 | 753.52
5109 | TIN-INTERP | Interpolated Ground | 32624.09 | -4.61 | 727.8 | 0 | 28.01 | 0 | OK | Ground clear controls. | 75 | 38.62 | 755.81
5110 | TIN-INTERP | Interpolated Ground | 32624.12 | 4.6 | 727.84 | 0 | 27.89 | 0 | OK | Ground clear controls. | 75 | 38.62 | 755.73
5111 | TIN-INTERP | Interpolated Ground | 32624.13 | 6.6 | 727.74 | 0 | 23.05 | 0 | OK | Ground clear controls. | 75 | 38.62 | 750.79
5112 | TIN-INTERP | Interpolated Ground | 32624.14 | 5.1 | 727.82 | 0 | 17.21 | 0 | OK | Ground clear controls. | 75 | 38.62 | 745.03
5113 | TIN-INTERP | Interpolated Ground | 32624.14 | -5.11 | 727.82 | 0 | 17.22 | 0 | OK | Ground clear controls. | 75 | 38.62 | 745.04
5114 | TIN-INTERP | Interpolated Ground | 32624.16 | -6.61 | 727.87 | 0 | 22.81 | 0 | OK | Ground clear controls. | 75 | 38.62 | 750.68
5115 | TIN-INTERP | Interpolated Ground | 32664.09 | -4.61 | 727.63 | 0 | 26.18 | 0 | OK | Ground clear controls. | 75 | 38.62 | 753.81
5116 | TIN-INTERP | Interpolated Ground | 32664.12 | 4.6 | 727.51 | 0 | 26.23 | 0 | OK | Ground clear controls. | 75 | 38.62 | 753.74
5117 | TIN-INTERP | Interpolated Ground | 32664.13 | 6.6 | 727.53 | 0 | 21.32 | 0 | OK | Ground clear controls. | 75 | 38.62 | 748.85
5118 | TIN-INTERP | Interpolated Ground | 32664.14 | 5.1 | 727.54 | 0 | 15.52 | 0 | OK | Ground clear controls. | 75 | 38.62 | 743.06
5119 | TIN-INTERP | Interpolated Ground | 32664.14 | -5.11 | 727.64 | 0 | 15.43 | 0 | OK | Ground clear controls. | 75 | 38.62 | 743.07
5120 | TIN-INTERP | Interpolated Ground | 32664.16 | -6.61 | 727.61 | 0 | 21.11 | 0 | OK | Ground clear controls. | 75 | 38.62 | 748.72
5121 | TIN-INTERP | Interpolated Ground | 32704.09 | -4.61 | 727.39 | 0 | 25.3 | 0 | OK | Ground clear controls. | 75 | 38.62 | 752.69
5122 | TIN-INTERP | Interpolated Ground | 32704.12 | 4.6 | 727.35 | 0 | 25.27 | 0 | OK | Ground clear controls. | 75 | 38.62 | 752.62
5123 | TIN-INTERP | Interpolated Ground | 32704.13 | 6.6 | 727.35 | 0 | 20.42 | 0 | OK | Ground clear controls. | 75 | 38.62 | 747.77
5124 | TIN-INTERP | Interpolated Ground | 32704.14 | 5.1 | 727.34 | 0 | 14.62 | 0 | OK | Ground clear controls. | 75 | 38.62 | 741.96
5125 | TIN-INTERP | Interpolated Ground | 32704.14 | -5.11 | 727.39 | 0 | 14.59 | 0 | OK | Ground clear controls. | 75 | 38.62 | 741.98
5126 | TIN-INTERP | Interpolated Ground | 32704.16 | -6.61 | 727.33 | 0 | 20.31 | 0 | OK | Ground clear controls. | 75 | 38.62 | 747.64
5127 | TIN-INTERP | Interpolated Ground | 32744.09 | -4.61 | 727.63 | 0 | 24.86 | 0 | OK | Ground clear controls. | 75 | 38.62 | 752.49
5128 | TIN-INTERP | Interpolated Ground | 32744.12 | 4.6 | 727.41 | 0 | 25 | 0 | OK | Ground clear controls. | 75 | 38.62 | 752.41
5129 | TIN-INTERP | Interpolated Ground | 32744.13 | 6.6 | 727.57 | 0 | 19.98 | 0 | OK | Ground clear controls. | 75 | 38.62 | 747.55
5130 | TIN-INTERP | Interpolated Ground | 32744.14 | 5.1 | 727.36 | 0 | 14.39 | 0 | OK | Ground clear controls. | 75 | 38.62 | 741.75
5131 | TIN-INTERP | Interpolated Ground | 32744.14 | -5.11 | 727.62 | 0 | 14.15 | 0 | OK | Ground clear controls. | 75 | 38.62 | 741.77
5132 | TIN-INTERP | Interpolated Ground | 32744.16 | -6.61 | 727.61 | 0 | 19.82 | 0 | OK | Ground clear controls. | 75 | 38.62 | 747.43
5133 | TIN-INTERP | Interpolated Ground | 32784.09 | -4.61 | 727.11 | 0 | 26.06 | 0 | OK | Ground clear controls. | 75 | 38.62 | 753.17
5134 | TIN-INTERP | Interpolated Ground | 32784.12 | 4.6 | 726.87 | 0 | 26.23 | 0 | OK | Ground clear controls. | 75 | 38.62 | 753.1
5135 | TIN-INTERP | Interpolated Ground | 32784.13 | 6.6 | 726.82 | 0 | 21.39 | 0 | OK | Ground clear controls. | 75 | 38.62 | 748.21
5136 | TIN-INTERP | Interpolated Ground | 32784.14 | 5.1 | 726.84 | 0 | 15.58 | 0 | OK | Ground clear controls. | 75 | 38.62 | 742.42
5137 | TIN-INTERP | Interpolated Ground | 32784.14 | -5.11 | 727.05 | 0 | 15.38 | 0 | OK | Ground clear controls. | 75 | 38.62 | 742.43
5138 | TIN-INTERP | Interpolated Ground | 32784.16 | -6.61 | 726.88 | 0 | 21.22 | 0 | OK | Ground clear controls. | 75 | 38.62 | 748.1
5139 | TIN-INTERP | Interpolated Ground | 32824.09 | -4.61 | 726.89 | 0 | 27.85 | 0 | OK | Ground clear controls. | 75 | 38.62 | 754.74
5140 | TIN-INTERP | Interpolated Ground | 32824.12 | 4.6 | 726.67 | 0 | 28.01 | 0 | OK | Ground clear controls. | 75 | 38.62 | 754.68
5141 | TIN-INTERP | Interpolated Ground | 32824.13 | 6.6 | 726.62 | 0 | 23.11 | 0 | OK | Ground clear controls. | 75 | 38.62 | 749.73
5142 | TIN-INTERP | Interpolated Ground | 32824.14 | 5.1 | 726.66 | 0 | 17.31 | 0 | OK | Ground clear controls. | 75 | 38.62 | 743.97
5143 | TIN-INTERP | Interpolated Ground | 32824.14 | -5.11 | 726.83 | 0 | 17.16 | 0 | OK | Ground clear controls. | 75 | 38.62 | 743.99
5144 | TIN-INTERP | Interpolated Ground | 32824.16 | -6.61 | 726.65 | 0 | 22.97 | 0 | OK | Ground clear controls. | 75 | 38.62 | 749.62
5145 | TIN-INTERP | Interpolated Ground | 32864.09 | -4.61 | 726.65 | 0 | 30.56 | 0 | OK | Ground clear controls. | 75 | 38.62 | 757.21
5146 | TIN-INTERP | Interpolated Ground | 32864.12 | 4.6 | 726.72 | 0 | 30.44 | 0 | OK | Ground clear controls. | 75 | 38.62 | 757.16
5147 | TIN-INTERP | Interpolated Ground | 32864.13 | 6.6 | 726.72 | 0 | 25.4 | 0 | OK | Ground clear controls. | 75 | 38.62 | 752.12
5148 | TIN-INTERP | Interpolated Ground | 32864.14 | 5.1 | 726.74 | 0 | 19.66 | 0 | OK | Ground clear controls. | 75 | 38.62 | 746.4
5149 | TIN-INTERP | Interpolated Ground | 32864.14 | -5.11 | 726.67 | 0 | 19.75 | 0 | OK | Ground clear controls. | 75 | 38.62 | 746.42
5150 | TIN-INTERP | Interpolated Ground | 32864.16 | -6.61 | 726.68 | 0 | 25.36 | 0 | OK | Ground clear controls. | 75 | 38.62 | 752.04
5151 | TIN-INTERP | Interpolated Ground | 32904.09 | -4.61 | 726.26 | 0 | 34.32 | 0 | OK | Ground clear controls. | 75 | 38.62 | 760.58
5152 | TIN-INTERP | Interpolated Ground | 32904.12 | 4.6 | 726.3 | 0 | 34.25 | 0 | OK | Ground clear controls. | 75 | 38.62 | 760.55
5153 | TIN-INTERP | Interpolated Ground | 32904.13 | 6.6 | 726.43 | 0 | 28.95 | 0 | OK | Ground clear controls. | 75 | 38.62 | 755.38
5154 | TIN-INTERP | Interpolated Ground | 32904.14 | 5.1 | 726.31 | 0 | 23.42 | 0 | OK | Ground clear controls. | 75 | 38.62 | 749.73
5155 | TIN-INTERP | Interpolated Ground | 32904.14 | -5.11 | 726.23 | 0 | 23.5 | 0 | OK | Ground clear controls. | 75 | 38.62 | 749.73
5156 | TIN-INTERP | Interpolated Ground | 32904.16 | -6.61 | 726.13 | 0 | 29.2 | 0 | OK | Ground clear controls. | 75 | 38.62 | 755.33
5157 | TIN-INTERP | Interpolated Ground | 32944.09 | -4.61 | 726.22 | 0 | 38.62 | 0 | OK | Ground clear controls. | 75 | 38.62 | 764.84
5158 | TIN-INTERP | Interpolated Ground | 32944.12 | 4.6 | 726.22 | 0 | 38.61 | 0 | OK | Ground clear controls. | 75 | 38.61 | 764.83
5159 | TIN-INTERP | Interpolated Ground | 32944.13 | 6.6 | 726.26 | 0 | 33.25 | 0 | OK | Ground clear controls. | 75 | 33.33 | 759.51
5160 | TIN-INTERP | Interpolated Ground | 32944.14 | 5.1 | 726.21 | 0 | 27.72 | 0 | OK | Ground clear controls. | 75 | 33.33 | 753.93
5161 | TIN-INTERP | Interpolated Ground | 32944.14 | -5.11 | 726.21 | 0 | 27.73 | 0 | OK | Ground clear controls. | 75 | 33.33 | 753.94
5162 | TIN-INTERP | Interpolated Ground | 32944.16 | -6.61 | 726.17 | 0 | 33.33 | 0 | OK | Ground clear controls. | 75 | 33.33 | 759.5
5163 | TIN-INTERP | Interpolated Ground | 32983.94 | -6.61 | 726.28 | 0 | 38.22 | 0 | OK | Ground clear controls. | 76 | 43.78 | 764.5
5164 | TIN-INTERP | Interpolated Ground | 32984.01 | 4.6 | 726.22 | 0 | 43.78 | 0 | OK | Ground clear controls. | 76 | 43.78 | 770
5165 | TIN-INTERP | Interpolated Ground | 32984.03 | 5.1 | 726.23 | 0 | 32.77 | 0 | OK | Ground clear controls. | 76 | 38.3 | 759
5166 | TIN-INTERP | Interpolated Ground | 32984.03 | -5.11 | 726.15 | 0 | 32.85 | 0 | OK | Ground clear controls. | 76 | 38.3 | 759
5167 | TIN-INTERP | Interpolated Ground | 32984.05 | 6.6 | 726.2 | 0 | 38.3 | 0 | OK | Ground clear controls. | 76 | 38.3 | 764.5
5168 | TIN-INTERP | Interpolated Ground | 32984.09 | -4.61 | 726.13 | 0 | 43.87 | 0 | OK | Ground clear controls. | 75 | 43.87 | 770
5169 | TIN-INTERP | Interpolated Ground | 32984.12 | -4.61 | 726.13 | 0 | 43.87 | 0 | OK | Ground clear controls. | 76 | 43.87 | 770
5170 | TIN-INTERP | Interpolated Ground | 33023.94 | -6.62 | 725.82 | 0 | 33.29 | 0 | OK | Ground clear controls. | 76 | 38.75 | 759.11
5171 | TIN-INTERP | Interpolated Ground | 33024.01 | 4.65 | 726.22 | 0 | 38.32 | 0 | OK | Ground clear controls. | 76 | 38.75 | 764.54
5172 | TIN-INTERP | Interpolated Ground | 33024.03 | -5.12 | 725.89 | 0 | 27.73 | 0 | OK | Ground clear controls. | 76 | 38.75 | 753.62
5173 | TIN-INTERP | Interpolated Ground | 33024.03 | 5.14 | 726.23 | 0 | 27.39 | 0 | OK | Ground clear controls. | 76 | 38.75 | 753.62
5174 | TIN-INTERP | Interpolated Ground | 33024.05 | 6.64 | 726.06 | 0 | 33.17 | 0 | OK | Ground clear controls. | 76 | 38.75 | 759.23
5175 | TIN-INTERP | Interpolated Ground | 33024.12 | -4.63 | 725.88 | 0 | 38.75 | 0 | OK | Ground clear controls. | 76 | 38.75 | 764.63
5176 | TIN-INTERP | Interpolated Ground | 33063.94 | -6.63 | 725.49 | 0 | 29.14 | 0 | OK | Ground clear controls. | 76 | 37.8 | 754.63
5177 | TIN-INTERP | Interpolated Ground | 33064.01 | 4.69 | 725.62 | 0 | 34.36 | 0 | OK | Ground clear controls. | 76 | 37.8 | 759.98
5178 | TIN-INTERP | Interpolated Ground | 33064.03 | -5.13 | 725.8 | 0 | 23.34 | 0 | OK | Ground clear controls. | 76 | 37.8 | 749.14
5179 | TIN-INTERP | Interpolated Ground | 33064.03 | 5.18 | 725.64 | 0 | 23.5 | 0 | OK | Ground clear controls. | 76 | 37.8 | 749.14
5180 | TIN-INTERP | Interpolated Ground | 33064.05 | 6.68 | 725.64 | 0 | 29.18 | 0 | OK | Ground clear controls. | 76 | 37.8 | 754.82
5181 | TIN-INTERP | Interpolated Ground | 33064.12 | -4.64 | 725.7 | 0 | 34.44 | 0 | OK | Ground clear controls. | 76 | 37.8 | 760.14
5182 | TIN-INTERP | Interpolated Ground | 33103.94 | -6.64 | 725.72 | 0 | 25.31 | 0 | OK | Ground clear controls. | 76 | 37.8 | 751.03
5183 | TIN-INTERP | Interpolated Ground | 33104.01 | 4.74 | 725.78 | 0 | 30.55 | 0 | OK | Ground clear controls. | 76 | 37.8 | 756.33
5184 | TIN-INTERP | Interpolated Ground | 33104.03 | -5.14 | 725.78 | 0 | 19.77 | 0 | OK | Ground clear controls. | 76 | 37.8 | 745.55
5185 | TIN-INTERP | Interpolated Ground | 33104.03 | 5.22 | 725.8 | 0 | 19.75 | 0 | OK | Ground clear controls. | 76 | 37.8 | 745.55
5186 | TIN-INTERP | Interpolated Ground | 33104.05 | 6.72 | 725.82 | 0 | 25.49 | 0 | OK | Ground clear controls. | 76 | 37.8 | 751.31
5187 | TIN-INTERP | Interpolated Ground | 33104.12 | -4.66 | 725.76 | 0 | 30.81 | 0 | OK | Ground clear controls. | 76 | 37.8 | 756.57
5188 | TIN-INTERP | Interpolated Ground | 33143.94 | -6.64 | 725.81 | 0 | 22.51 | 0 | OK | Ground clear controls. | 76 | 37.8 | 748.32
5189 | TIN-INTERP | Interpolated Ground | 33144.01 | 4.79 | 726.19 | 0 | 27.41 | 0 | OK | Ground clear controls. | 76 | 37.8 | 753.6
5190 | TIN-INTERP | Interpolated Ground | 33144.03 | -5.14 | 725.85 | 0 | 17.01 | 0 | OK | Ground clear controls. | 76 | 37.8 | 742.86
5191 | TIN-INTERP | Interpolated Ground | 33144.03 | 5.26 | 726.21 | 0 | 16.64 | 0 | OK | Ground clear controls. | 76 | 37.8 | 742.85
5192 | TIN-INTERP | Interpolated Ground | 33144.05 | 6.76 | 726.24 | 0 | 22.43 | 0 | OK | Ground clear controls. | 76 | 37.8 | 748.67
5193 | TIN-INTERP | Interpolated Ground | 33144.12 | -4.67 | 725.85 | 0 | 28.04 | 0 | OK | Ground clear controls. | 76 | 37.8 | 753.89
5194 | TIN-INTERP | Interpolated Ground | 33183.94 | -6.65 | 725.94 | 0 | 20.57 | 0 | OK | Ground clear controls. | 76 | 37.8 | 746.51
5195 | TIN-INTERP | Interpolated Ground | 33184.01 | 4.83 | 726.03 | 0 | 25.75 | 0 | OK | Ground clear controls. | 76 | 37.8 | 751.78
5196 | TIN-INTERP | Interpolated Ground | 33184.03 | -5.15 | 726.03 | 0 | 15.02 | 0 | OK | Ground clear controls. | 76 | 37.8 | 741.05
5197 | TIN-INTERP | Interpolated Ground | 33184.03 | 5.29 | 726.09 | 0 | 14.95 | 0 | OK | Ground clear controls. | 76 | 37.8 | 741.04
5198 | TIN-INTERP | Interpolated Ground | 33184.05 | 6.8 | 726.14 | 0 | 20.75 | 0 | OK | Ground clear controls. | 76 | 37.8 | 746.89
5199 | TIN-INTERP | Interpolated Ground | 33184.12 | -4.69 | 726.05 | 0 | 26.04 | 0 | OK | Ground clear controls. | 76 | 37.8 | 752.09
5200 | TIN-INTERP | Interpolated Ground | 33223.94 | -6.66 | 725.95 | 0 | 19.65 | 0 | OK | Ground clear controls. | 76 | 37.8 | 745.6
5201 | TIN-INTERP | Interpolated Ground | 33224.01 | 4.88 | 726.08 | 0 | 24.78 | 0 | OK | Ground clear controls. | 76 | 37.8 | 750.86
5202 | TIN-INTERP | Interpolated Ground | 33224.03 | -5.16 | 725.94 | 0 | 14.2 | 0 | OK | Ground clear controls. | 76 | 37.8 | 740.14
5203 | TIN-INTERP | Interpolated Ground | 33224.03 | 5.33 | 726.17 | 0 | 13.96 | 0 | OK | Ground clear controls. | 76 | 37.8 | 740.13
5204 | TIN-INTERP | Interpolated Ground | 33224.05 | 6.84 | 726.23 | 0 | 19.77 | 0 | OK | Ground clear controls. | 76 | 37.8 | 746
5205 | TIN-INTERP | Interpolated Ground | 33224.12 | -4.7 | 725.94 | 0 | 25.26 | 0 | OK | Ground clear controls. | 76 | 37.8 | 751.2
5206 | TIN-INTERP | Interpolated Ground | 33263.94 | -6.67 | 726.07 | 0 | 19.5 | 0 | OK | Ground clear controls. | 76 | 37.8 | 745.57
5207 | TIN-INTERP | Interpolated Ground | 33264.01 | 4.92 | 726.22 | 0 | 24.64 | 0 | OK | Ground clear controls. | 76 | 37.8 | 750.86
5208 | TIN-INTERP | Interpolated Ground | 33264.03 | -5.17 | 726.12 | 0 | 13.99 | 0 | OK | Ground clear controls. | 76 | 37.8 | 740.11
5209 | TIN-INTERP | Interpolated Ground | 33264.03 | 5.37 | 726.22 | 0 | 13.89 | 0 | OK | Ground clear controls. | 76 | 37.8 | 740.11
5210 | TIN-INTERP | Interpolated Ground | 33264.05 | 6.87 | 726.29 | 0 | 19.68 | 0 | OK | Ground clear controls. | 76 | 37.8 | 745.97
5211 | TIN-INTERP | Interpolated Ground | 33264.12 | -4.72 | 726.16 | 0 | 25.04 | 0 | OK | Ground clear controls. | 76 | 37.8 | 751.2
5212 | TIN-INTERP | Interpolated Ground | 33303.94 | -6.68 | 726.17 | 0 | 20.27 | 0 | OK | Ground clear controls. | 76 | 37.8 | 746.44
5213 | TIN-INTERP | Interpolated Ground | 33304.01 | 4.97 | 726.29 | 0 | 25.49 | 0 | OK | Ground clear controls. | 76 | 37.8 | 751.78
5214 | TIN-INTERP | Interpolated Ground | 33304.03 | -5.18 | 726.16 | 0 | 14.82 | 0 | OK | Ground clear controls. | 76 | 37.8 | 740.98
5215 | TIN-INTERP | Interpolated Ground | 33304.03 | 5.41 | 726.33 | 0 | 14.64 | 0 | OK | Ground clear controls. | 76 | 37.8 | 740.97
5216 | TIN-INTERP | Interpolated Ground | 33304.05 | 6.91 | 726.43 | 0 | 20.41 | 0 | OK | Ground clear controls. | 76 | 37.8 | 746.84
5217 | TIN-INTERP | Interpolated Ground | 33304.12 | -4.74 | 726.16 | 0 | 25.93 | 0 | OK | Ground clear controls. | 76 | 37.8 | 752.09
5218 | TIN-INTERP | Interpolated Ground | 33343.94 | -6.69 | 726.36 | 0 | 21.84 | 0 | OK | Ground clear controls. | 76 | 37.8 | 748.2
5219 | TIN-INTERP | Interpolated Ground | 33344.01 | 5.02 | 726.5 | 0 | 27.08 | 0 | OK | Ground clear controls. | 76 | 37.8 | 753.58
5220 | TIN-INTERP | Interpolated Ground | 33344.03 | -5.19 | 726.47 | 0 | 16.26 | 0 | OK | Ground clear controls. | 76 | 37.8 | 742.73
5221 | TIN-INTERP | Interpolated Ground | 33344.03 | 5.45 | 726.56 | 0 | 16.18 | 0 | OK | Ground clear controls. | 76 | 37.8 | 742.74
5222 | TIN-INTERP | Interpolated Ground | 33344.05 | 6.95 | 726.7 | 0 | 21.86 | 0 | OK | Ground clear controls. | 76 | 37.8 | 748.56
5223 | TIN-INTERP | Interpolated Ground | 33344.12 | -4.75 | 726.47 | 0 | 27.41 | 0 | OK | Ground clear controls. | 76 | 37.8 | 753.88
5224 | TIN-INTERP | Interpolated Ground | 33383.94 | -6.7 | 726.36 | 0 | 24.49 | 0 | OK | Ground clear controls. | 76 | 37.8 | 750.85
5225 | TIN-INTERP | Interpolated Ground | 33384.01 | 5.06 | 726.21 | 0 | 30.11 | 0 | OK | Ground clear controls. | 76 | 37.8 | 756.32
5226 | TIN-INTERP | Interpolated Ground | 33384.03 | -5.19 | 726.38 | 0 | 19.01 | 0 | OK | Ground clear controls. | 76 | 37.8 | 745.39
5227 | TIN-INTERP | Interpolated Ground | 33384.03 | 5.49 | 726.22 | 0 | 19.17 | 0 | OK | Ground clear controls. | 76 | 37.8 | 745.39
5228 | TIN-INTERP | Interpolated Ground | 33384.05 | 6.99 | 726.18 | 0 | 24.98 | 0 | OK | Ground clear controls. | 76 | 37.8 | 751.16
5229 | TIN-INTERP | Interpolated Ground | 33384.12 | -4.77 | 726.39 | 0 | 30.17 | 0 | OK | Ground clear controls. | 76 | 37.8 | 756.56
5230 | TIN-INTERP | Interpolated Ground | 33423.94 | -6.7 | 726.66 | 0 | 27.73 | 0 | OK | Ground clear controls. | 76 | 37.8 | 754.39
5231 | TIN-INTERP | Interpolated Ground | 33424.01 | 5.11 | 726.78 | 0 | 33.17 | 0 | OK | Ground clear controls. | 76 | 37.8 | 759.95
5232 | TIN-INTERP | Interpolated Ground | 33424.03 | -5.2 | 726.69 | 0 | 22.23 | 0 | OK | Ground clear controls. | 76 | 37.8 | 748.92
5233 | TIN-INTERP | Interpolated Ground | 33424.03 | 5.53 | 726.77 | 0 | 22.16 | 0 | OK | Ground clear controls. | 76 | 37.8 | 748.93
5234 | TIN-INTERP | Interpolated Ground | 33424.05 | 7.03 | 726.79 | 0 | 27.85 | 0 | OK | Ground clear controls. | 76 | 37.8 | 754.64
5235 | TIN-INTERP | Interpolated Ground | 33424.12 | -4.78 | 726.7 | 0 | 33.44 | 0 | OK | Ground clear controls. | 76 | 37.8 | 760.14
5236 | TIN-INTERP | Interpolated Ground | 33463.94 | -6.71 | 726.75 | 0 | 32.09 | 0 | OK | Ground clear controls. | 76 | 37.8 | 758.84
5237 | TIN-INTERP | Interpolated Ground | 33464.01 | 5.16 | 726.89 | 0 | 37.62 | 0 | OK | Ground clear controls. | 76 | 37.8 | 764.51
5238 | TIN-INTERP | Interpolated Ground | 33464.03 | -5.21 | 726.82 | 0 | 26.54 | 0 | OK | Ground clear controls. | 76 | 37.8 | 753.36
5239 | TIN-INTERP | Interpolated Ground | 33464.03 | 5.57 | 726.91 | 0 | 26.47 | 0 | OK | Ground clear controls. | 76 | 37.8 | 753.38
5240 | TIN-INTERP | Interpolated Ground | 33464.05 | 7.07 | 726.89 | 0 | 32.1 | 0 | OK | Ground clear controls. | 76 | 37.8 | 758.99
5241 | TIN-INTERP | Interpolated Ground | 33464.12 | -4.8 | 726.82 | 0 | 37.8 | 0 | OK | Ground clear controls. | 76 | 37.8 | 764.62
5242 | TIN-INTERP | Interpolated Ground | 33502.29 | 7.11 | 726.85 | 0 | 37.12 | 0 | OK | Ground clear controls. | 77 | 43.11 | 763.97
5243 | TIN-INTERP | Interpolated Ground | 33502.34 | 5.61 | 726.82 | 0 | 31.65 | 0 | OK | Ground clear controls. | 77 | 43.11 | 758.47
5244 | TIN-INTERP | Interpolated Ground | 33502.46 | -5.22 | 726.65 | 0 | 31.82 | 0 | OK | Ground clear controls. | 77 | 43.11 | 758.47
5245 | TIN-INTERP | Interpolated Ground | 33502.47 | -6.72 | 726.64 | 0 | 37.33 | 0 | OK | Ground clear controls. | 77 | 43.11 | 763.97
5246 | TIN-INTERP | Interpolated Ground | 33502.52 | -4.81 | 726.65 | 0 | 43.11 | 0 | OK | Ground clear controls. | 77 | 43.11 | 769.76
5247 | TIN-INTERP | Interpolated Ground | 33502.53 | 5.2 | 726.83 | 0 | 42.93 | 0 | OK | Ground clear controls. | 77 | 42.93 | 769.76
5248 | TIN-INTERP | Interpolated Ground | 33542.33 | -6.68 | 726.56 | 0 | 32.08 | 0 | OK | Ground clear controls. | 77 | 39.02 | 758.64
5249 | TIN-INTERP | Interpolated Ground | 33542.35 | -5.17 | 726.53 | 0 | 26.59 | 0 | OK | Ground clear controls. | 77 | 39.02 | 753.12
5250 | TIN-INTERP | Interpolated Ground | 33542.41 | -4.75 | 726.53 | 0 | 37.97 | 0 | OK | Ground clear controls. | 77 | 39.02 | 764.5
5251 | TIN-INTERP | Interpolated Ground | 33542.45 | 7.32 | 726.57 | 0 | 32.14 | 0 | OK | Ground clear controls. | 77 | 39.02 | 758.71
5252 | TIN-INTERP | Interpolated Ground | 33542.47 | 5.82 | 726.59 | 0 | 26.52 | 0 | OK | Ground clear controls. | 77 | 39.02 | 753.11
5253 | TIN-INTERP | Interpolated Ground | 33542.64 | 5.39 | 726.59 | 0 | 37.87 | 0 | OK | Ground clear controls. | 77 | 39.02 | 764.46
5254 | TIN-INTERP | Interpolated Ground | 33582.33 | -6.65 | 726.43 | 0 | 27.8 | 0 | OK | Ground clear controls. | 77 | 39.02 | 754.23
5255 | TIN-INTERP | Interpolated Ground | 33582.35 | -5.13 | 726.42 | 0 | 22.28 | 0 | OK | Ground clear controls. | 77 | 39.02 | 748.7
5256 | TIN-INTERP | Interpolated Ground | 33582.41 | -4.69 | 726.44 | 0 | 33.71 | 0 | OK | Ground clear controls. | 77 | 39.02 | 760.15
5257 | TIN-INTERP | Interpolated Ground | 33582.45 | 7.53 | 726.51 | 0 | 27.85 | 0 | OK | Ground clear controls. | 77 | 39.02 | 754.36
5258 | TIN-INTERP | Interpolated Ground | 33582.46 | 6.03 | 726.48 | 0 | 22.18 | 0 | OK | Ground clear controls. | 77 | 39.02 | 748.66
5259 | TIN-INTERP | Interpolated Ground | 33582.64 | 5.57 | 726.5 | 0 | 33.59 | 0 | OK | Ground clear controls. | 77 | 39.02 | 760.09
5260 | TIN-INTERP | Interpolated Ground | 33622.33 | -6.62 | 726.43 | 0 | 24.3 | 0 | OK | Ground clear controls. | 77 | 39.02 | 750.73
5261 | TIN-INTERP | Interpolated Ground | 33622.35 | -5.09 | 726.39 | 0 | 18.79 | 0 | OK | Ground clear controls. | 77 | 39.02 | 745.18
5262 | TIN-INTERP | Interpolated Ground | 33622.41 | -4.63 | 726.44 | 0 | 30.27 | 0 | OK | Ground clear controls. | 77 | 39.02 | 756.71
5263 | TIN-INTERP | Interpolated Ground | 33622.45 | 7.74 | 726.54 | 0 | 24.38 | 0 | OK | Ground clear controls. | 77 | 39.02 | 750.92
5264 | TIN-INTERP | Interpolated Ground | 33622.46 | 6.24 | 726.62 | 0 | 18.51 | 0 | OK | Ground clear controls. | 77 | 39.02 | 745.13
5265 | TIN-INTERP | Interpolated Ground | 33622.64 | 5.76 | 726.63 | 0 | 30.01 | 0 | OK | Ground clear controls. | 77 | 39.02 | 756.64
5266 | TIN-INTERP | Interpolated Ground | 33662.33 | -6.59 | 726.66 | 0 | 21.48 | 0 | OK | Ground clear controls. | 77 | 39.02 | 748.14
5267 | TIN-INTERP | Interpolated Ground | 33662.35 | -5.05 | 726.68 | 0 | 15.9 | 0 | OK | Ground clear controls. | 77 | 39.02 | 742.58
5268 | TIN-INTERP | Interpolated Ground | 33662.41 | -4.57 | 726.68 | 0 | 27.5 | 0 | OK | Ground clear controls. | 77 | 39.02 | 754.18
5269 | TIN-INTERP | Interpolated Ground | 33662.45 | 7.95 | 726.55 | 0 | 21.83 | 0 | OK | Ground clear controls. | 77 | 39.02 | 748.38
5270 | TIN-INTERP | Interpolated Ground | 33662.46 | 6.45 | 726.53 | 0 | 16 | 0 | OK | Ground clear controls. | 77 | 39.02 | 742.53
5271 | TIN-INTERP | Interpolated Ground | 33662.64 | 5.95 | 726.58 | 0 | 27.51 | 0 | OK | Ground clear controls. | 77 | 39.02 | 754.09
5272 | TIN-INTERP | Interpolated Ground | 33702.33 | -6.55 | 726.62 | 0 | 19.86 | 0 | OK | Ground clear controls. | 77 | 39.02 | 746.48
5273 | TIN-INTERP | Interpolated Ground | 33702.35 | -5.01 | 726.54 | 0 | 14.34 | 0 | OK | Ground clear controls. | 77 | 39.02 | 740.88
5274 | TIN-INTERP | Interpolated Ground | 33702.41 | -4.51 | 726.51 | 0 | 26.04 | 0 | OK | Ground clear controls. | 77 | 39.02 | 752.55
5275 | TIN-INTERP | Interpolated Ground | 33702.45 | 8.15 | 726.37 | 0 | 20.36 | 0 | OK | Ground clear controls. | 77 | 39.02 | 746.73
5276 | TIN-INTERP | Interpolated Ground | 33702.46 | 6.66 | 726.35 | 0 | 14.48 | 0 | OK | Ground clear controls. | 77 | 39.02 | 740.83
5277 | TIN-INTERP | Interpolated Ground | 33702.64 | 6.13 | 726.35 | 0 | 26.12 | 0 | OK | Ground clear controls. | 77 | 39.02 | 752.47
5278 | TIN-INTERP | Interpolated Ground | 33742.33 | -6.52 | 726.21 | 0 | 19.5 | 0 | OK | Ground clear controls. | 77 | 39.02 | 745.71
5279 | TIN-INTERP | Interpolated Ground | 33742.35 | -4.97 | 726.35 | 0 | 13.75 | 0 | OK | Ground clear controls. | 77 | 39.02 | 740.1
5280 | TIN-INTERP | Interpolated Ground | 33742.41 | -4.45 | 726.36 | 0 | 25.47 | 0 | OK | Ground clear controls. | 77 | 39.02 | 751.83
5281 | TIN-INTERP | Interpolated Ground | 33742.45 | 8.36 | 726.76 | 0 | 19.23 | 0 | OK | Ground clear controls. | 77 | 39.02 | 745.99
5282 | TIN-INTERP | Interpolated Ground | 33742.46 | 6.87 | 726.73 | 0 | 13.33 | 0 | OK | Ground clear controls. | 77 | 39.02 | 740.06
5283 | TIN-INTERP | Interpolated Ground | 33742.64 | 6.32 | 726.69 | 0 | 25.07 | 0 | OK | Ground clear controls. | 77 | 39.02 | 751.76
5284 | TIN-INTERP | Interpolated Ground | 33782.33 | -6.49 | 727.15 | 0 | 18.71 | 0 | OK | Ground clear controls. | 77 | 39.02 | 745.86
5285 | TIN-INTERP | Interpolated Ground | 33782.35 | -4.93 | 727.17 | 0 | 13.05 | 0 | OK | Ground clear controls. | 77 | 39.02 | 740.22
5286 | TIN-INTERP | Interpolated Ground | 33782.41 | -4.38 | 727.22 | 0 | 24.8 | 0 | OK | Ground clear controls. | 77 | 39.02 | 752.02
5287 | TIN-INTERP | Interpolated Ground | 33782.44 | 8.57 | 727.84 | 0 | 18.32 | 0 | OK | Ground clear controls. | 77 | 39.02 | 746.16
5288 | TIN-INTERP | Interpolated Ground | 33782.46 | 7.08 | 727.77 | 0 | 12.43 | 0 | OK | Ground clear controls. | 77 | 39.02 | 740.2
5289 | TIN-INTERP | Interpolated Ground | 33782.64 | 6.51 | 727.77 | 0 | 24.2 | 0 | OK | Ground clear controls. | 77 | 39.02 | 751.97
5290 | TIN-INTERP | Interpolated Ground | 33822.33 | -6.46 | 727.96 | 0 | 18.96 | 0 | OK | Ground clear controls. | 77 | 39.02 | 746.92
5291 | TIN-INTERP | Interpolated Ground | 33822.35 | -4.89 | 728.01 | 0 | 13.26 | 0 | OK | Ground clear controls. | 77 | 39.02 | 741.27
5292 | TIN-INTERP | Interpolated Ground | 33822.41 | -4.32 | 728.01 | 0 | 25.11 | 0 | OK | Ground clear controls. | 77 | 39.02 | 753.12
5293 | TIN-INTERP | Interpolated Ground | 33822.44 | 8.78 | 727.97 | 0 | 19.26 | 0 | OK | Ground clear controls. | 77 | 39.02 | 747.23
5294 | TIN-INTERP | Interpolated Ground | 33822.46 | 7.29 | 727.94 | 0 | 13.33 | 0 | OK | Ground clear controls. | 77 | 39.02 | 741.27
5295 | TIN-INTERP | Interpolated Ground | 33822.64 | 6.69 | 727.93 | 0 | 25.17 | 0 | OK | Ground clear controls. | 77 | 39.02 | 753.1
5296 | TIN-INTERP | Interpolated Ground | 33862.33 | -6.43 | 728.03 | 0 | 20.86 | 0 | OK | Ground clear controls. | 77 | 39.02 | 748.89
5297 | TIN-INTERP | Interpolated Ground | 33862.35 | -4.85 | 728.08 | 0 | 15.13 | 0 | OK | Ground clear controls. | 77 | 39.02 | 743.21
5298 | TIN-INTERP | Interpolated Ground | 33862.41 | -4.26 | 728.09 | 0 | 27.04 | 0 | OK | Ground clear controls. | 77 | 39.02 | 755.13
5299 | TIN-INTERP | Interpolated Ground | 33862.44 | 8.99 | 728.47 | 0 | 20.72 | 0 | OK | Ground clear controls. | 77 | 39.02 | 749.19
5300 | TIN-INTERP | Interpolated Ground | 33862.46 | 7.49 | 728.43 | 0 | 14.8 | 0 | OK | Ground clear controls. | 77 | 39.02 | 743.23
5301 | TIN-INTERP | Interpolated Ground | 33862.64 | 6.88 | 728.43 | 0 | 26.7 | 0 | OK | Ground clear controls. | 77 | 39.02 | 755.13
5302 | TIN-INTERP | Interpolated Ground | 33902.33 | -6.39 | 728.59 | 0 | 23.18 | 0 | OK | Ground clear controls. | 77 | 39.02 | 751.77
5303 | TIN-INTERP | Interpolated Ground | 33902.35 | -4.81 | 728.56 | 0 | 17.5 | 0 | OK | Ground clear controls. | 77 | 39.02 | 746.06
5304 | TIN-INTERP | Interpolated Ground | 33902.41 | -4.2 | 728.61 | 0 | 29.42 | 0 | OK | Ground clear controls. | 77 | 39.02 | 758.03
5305 | TIN-INTERP | Interpolated Ground | 33902.44 | 9.19 | 728.64 | 0 | 23.42 | 0 | OK | Ground clear controls. | 77 | 39.02 | 752.06
5306 | TIN-INTERP | Interpolated Ground | 33902.46 | 7.7 | 728.59 | 0 | 17.53 | 0 | OK | Ground clear controls. | 77 | 39.02 | 746.12
5307 | TIN-INTERP | Interpolated Ground | 33902.64 | 7.07 | 728.61 | 0 | 29.48 | 0 | OK | Ground clear controls. | 77 | 39.02 | 758.09
5308 | TIN-INTERP | Interpolated Ground | 33942.33 | -6.36 | 729.96 | 0 | 25.6 | 0 | OK | Ground clear controls. | 77 | 39.02 | 755.56
5309 | TIN-INTERP | Interpolated Ground | 33942.35 | -4.77 | 729.95 | 0 | 19.88 | 0 | OK | Ground clear controls. | 77 | 39.02 | 749.83
5310 | TIN-INTERP | Interpolated Ground | 33942.41 | -4.14 | 729.87 | 0 | 31.98 | 0 | OK | Ground clear controls. | 77 | 39.02 | 761.85
5311 | TIN-INTERP | Interpolated Ground | 33942.44 | 9.4 | 728.8 | 0 | 27.04 | 0 | OK | Ground clear controls. | 77 | 39.02 | 755.84
5312 | TIN-INTERP | Interpolated Ground | 33942.46 | 7.91 | 728.93 | 0 | 21.01 | 0 | OK | Ground clear controls. | 77 | 39.02 | 749.94
5313 | TIN-INTERP | Interpolated Ground | 33942.64 | 7.25 | 729.02 | 0 | 32.94 | 0 | OK | Ground clear controls. | 77 | 39.02 | 761.96
5314 | TIN-INTERP | Interpolated Ground | 33982.33 | -6.33 | 728.18 | 0 | 32.09 | 0 | OK | Ground clear controls. | 77 | 39.02 | 760.27
5315 | TIN-INTERP | Interpolated Ground | 33982.35 | -4.73 | 728.14 | 0 | 26.37 | 0 | OK | Ground clear controls. | 77 | 39.02 | 754.51
5316 | TIN-INTERP | Interpolated Ground | 33982.41 | -4.08 | 728.09 | 0 | 38.5 | 0 | OK | Ground clear controls. | 77 | 39.02 | 766.59
5317 | TIN-INTERP | Interpolated Ground | 33982.44 | 9.61 | 727.8 | 0 | 32.71 | 0 | OK | Ground clear controls. | 77 | 39.02 | 760.51
5318 | TIN-INTERP | Interpolated Ground | 33982.46 | 8.12 | 727.79 | 0 | 26.88 | 0 | OK | Ground clear controls. | 77 | 39.02 | 754.67
5319 | TIN-INTERP | Interpolated Ground | 33982.64 | 7.44 | 727.74 | 0 | 39.02 | 0 | OK | Ground clear controls. | 77 | 39.02 | 766.76
5320 | TIN-INTERP | Interpolated Ground | 33990.75 | 9.65 | 727.27 | 0 | 34.33 | 0 | OK | Ground clear controls. | 78 | 42.13 | 761.6
5321 | TIN-INTERP | Interpolated Ground | 33991 | 8.17 | 727.32 | 0 | 28.48 | 0 | OK | Ground clear controls. | 78 | 42.13 | 755.8
5322 | TIN-INTERP | Interpolated Ground | 33991.15 | 7.48 | 727.37 | 0 | 40.52 | 0 | OK | Ground clear controls. | 78 | 42.13 | 767.89
5323 | TIN-INTERP | Interpolated Ground | 33992.03 | -6.35 | 727.67 | 0 | 33.96 | 0 | OK | Ground clear controls. | 78 | 42.13 | 761.63
5324 | TIN-INTERP | Interpolated Ground | 33992.03 | -4.74 | 727.66 | 0 | 28.17 | 0 | OK | Ground clear controls. | 78 | 42.13 | 755.83
5325 | TIN-INTERP | Interpolated Ground | 33992.03 | -4.09 | 727.55 | 0 | 40.37 | 0 | OK | Ground clear controls. | 78 | 42.13 | 767.92
5326 | TIN-INTERP | Interpolated Ground | 34031.11 | -6.31 | 723.78 | 0 | 33.09 | 0 | OK | Ground clear controls. | 78 | 42.13 | 756.87
5327 | TIN-INTERP | Interpolated Ground | 34031.32 | -4.73 | 723.74 | 0 | 27.38 | 0 | OK | Ground clear controls. | 78 | 42.13 | 751.12
5328 | TIN-INTERP | Interpolated Ground | 34031.49 | -4.1 | 723.81 | 0 | 39.41 | 0 | OK | Ground clear controls. | 78 | 42.13 | 763.22
5329 | TIN-INTERP | Interpolated Ground | 34032.89 | 7.24 | 725.87 | 0 | 37.33 | 0 | OK | Ground clear controls. | 78 | 42.13 | 763.2
5330 | TIN-INTERP | Interpolated Ground | 34032.9 | 7.93 | 725.87 | 0 | 25.26 | 0 | OK | Ground clear controls. | 78 | 42.13 | 751.13
5331 | TIN-INTERP | Interpolated Ground | 34032.99 | 9.43 | 725.96 | 0 | 30.98 | 0 | OK | Ground clear controls. | 78 | 42.13 | 756.94
5332 | TIN-INTERP | Interpolated Ground | 34071.11 | -6.35 | 725.46 | 0 | 27.58 | 0 | OK | Ground clear controls. | 78 | 42.13 | 753.04
5333 | TIN-INTERP | Interpolated Ground | 34071.32 | -4.77 | 725.5 | 0 | 21.84 | 0 | OK | Ground clear controls. | 78 | 42.13 | 747.34
5334 | TIN-INTERP | Interpolated Ground | 34071.49 | -4.16 | 725.54 | 0 | 33.89 | 0 | OK | Ground clear controls. | 78 | 42.13 | 759.43
5335 | TIN-INTERP | Interpolated Ground | 34072.89 | 7 | 725.5 | 0 | 33.93 | 0 | OK | Ground clear controls. | 78 | 42.13 | 759.43
5336 | TIN-INTERP | Interpolated Ground | 34072.9 | 7.68 | 725.49 | 0 | 21.91 | 0 | OK | Ground clear controls. | 78 | 42.13 | 747.4
5337 | TIN-INTERP | Interpolated Ground | 34072.99 | 9.18 | 725.58 | 0 | 27.63 | 0 | OK | Ground clear controls. | 78 | 42.13 | 753.21
5338 | TIN-INTERP | Interpolated Ground | 34111.11 | -6.38 | 726.32 | 0 | 23.83 | 0 | OK | Ground clear controls. | 78 | 42.13 | 750.15
5339 | TIN-INTERP | Interpolated Ground | 34111.32 | -4.81 | 726.4 | 0 | 18.11 | 0 | OK | Ground clear controls. | 78 | 42.13 | 744.51
5340 | TIN-INTERP | Interpolated Ground | 34111.49 | -4.21 | 726.47 | 0 | 30.09 | 0 | OK | Ground clear controls. | 78 | 42.13 | 756.56
5341 | TIN-INTERP | Interpolated Ground | 34112.89 | 6.77 | 726.82 | 0 | 29.75 | 0 | OK | Ground clear controls. | 78 | 42.13 | 756.57
5342 | TIN-INTERP | Interpolated Ground | 34112.9 | 7.42 | 726.8 | 0 | 17.8 | 0 | OK | Ground clear controls. | 78 | 42.13 | 744.6
5343 | TIN-INTERP | Interpolated Ground | 34112.99 | 8.92 | 726.85 | 0 | 23.55 | 0 | OK | Ground clear controls. | 78 | 42.13 | 750.4
5344 | TIN-INTERP | Interpolated Ground | 34151.11 | -6.41 | 727.5 | 0 | 20.7 | 0 | OK | Ground clear controls. | 78 | 42.13 | 748.2
5345 | TIN-INTERP | Interpolated Ground | 34151.32 | -4.85 | 727.56 | 0 | 15.03 | 0 | OK | Ground clear controls. | 78 | 42.13 | 742.59
5346 | TIN-INTERP | Interpolated Ground | 34151.49 | -4.26 | 727.59 | 0 | 27.01 | 0 | OK | Ground clear controls. | 78 | 42.13 | 754.6
5347 | TIN-INTERP | Interpolated Ground | 34152.89 | 6.53 | 728.07 | 0 | 26.57 | 0 | OK | Ground clear controls. | 78 | 42.13 | 754.64
5348 | TIN-INTERP | Interpolated Ground | 34152.9 | 7.17 | 728.06 | 0 | 14.66 | 0 | OK | Ground clear controls. | 78 | 42.13 | 742.72
5349 | TIN-INTERP | Interpolated Ground | 34152.99 | 8.67 | 728.14 | 0 | 20.37 | 0 | OK | Ground clear controls. | 78 | 42.13 | 748.51
5350 | TIN-INTERP | Interpolated Ground | 34191.11 | -6.45 | 727.91 | 0 | 19.28 | 0 | OK | Ground clear controls. | 78 | 42.13 | 747.19
5351 | TIN-INTERP | Interpolated Ground | 34191.32 | -4.89 | 727.98 | 0 | 13.64 | 0 | OK | Ground clear controls. | 78 | 42.13 | 741.62
5352 | TIN-INTERP | Interpolated Ground | 34191.49 | -4.31 | 728.02 | 0 | 25.55 | 0 | OK | Ground clear controls. | 78 | 42.13 | 753.57
5353 | TIN-INTERP | Interpolated Ground | 34192.88 | 6.29 | 728.44 | 0 | 25.18 | 0 | OK | Ground clear controls. | 78 | 42.13 | 753.62
5354 | TIN-INTERP | Interpolated Ground | 34192.9 | 6.91 | 728.44 | 0 | 13.34 | 0 | OK | Ground clear controls. | 78 | 42.13 | 741.78
5355 | TIN-INTERP | Interpolated Ground | 34192.99 | 8.41 | 728.47 | 0 | 19.07 | 0 | OK | Ground clear controls. | 78 | 42.13 | 747.54
5356 | TIN-INTERP | Interpolated Ground | 34231.11 | -6.48 | 728.1 | 0 | 19.01 | 0 | OK | Ground clear controls. | 78 | 42.13 | 747.11
5357 | TIN-INTERP | Interpolated Ground | 34231.32 | -4.93 | 728.1 | 0 | 13.47 | 0 | OK | Ground clear controls. | 78 | 42.13 | 741.57
5358 | TIN-INTERP | Interpolated Ground | 34231.49 | -4.36 | 728.18 | 0 | 25.27 | 0 | OK | Ground clear controls. | 78 | 42.13 | 753.45
5359 | TIN-INTERP | Interpolated Ground | 34232.88 | 6.05 | 728.51 | 0 | 25.01 | 0 | OK | Ground clear controls. | 78 | 42.13 | 753.52
5360 | TIN-INTERP | Interpolated Ground | 34232.9 | 6.66 | 728.51 | 0 | 13.25 | 0 | OK | Ground clear controls. | 78 | 42.13 | 741.76
5361 | TIN-INTERP | Interpolated Ground | 34232.99 | 8.16 | 728.58 | 0 | 18.92 | 0 | OK | Ground clear controls. | 78 | 42.13 | 747.5
5362 | TIN-INTERP | Interpolated Ground | 34271.11 | -6.51 | 729.34 | 0 | 18.63 | 0 | OK | Ground clear controls. | 78 | 42.13 | 747.97
5363 | TIN-INTERP | Interpolated Ground | 34271.32 | -4.97 | 729.3 | 0 | 13.15 | 0 | OK | Ground clear controls. | 78 | 42.13 | 742.45
5364 | TIN-INTERP | Interpolated Ground | 34271.49 | -4.41 | 729.29 | 0 | 24.95 | 0 | OK | Ground clear controls. | 78 | 42.13 | 754.24
5365 | TIN-INTERP | Interpolated Ground | 34272.88 | 5.81 | 728.98 | 0 | 25.35 | 0 | OK | Ground clear controls. | 78 | 42.13 | 754.33
5366 | TIN-INTERP | Interpolated Ground | 34272.89 | 6.4 | 728.93 | 0 | 13.73 | 0 | OK | Ground clear controls. | 78 | 42.13 | 742.66
5367 | TIN-INTERP | Interpolated Ground | 34272.99 | 7.91 | 728.81 | 0 | 19.57 | 0 | OK | Ground clear controls. | 78 | 42.13 | 748.38
5368 | TIN-INTERP | Interpolated Ground | 34311.11 | -6.55 | 725.38 | 0 | 24.39 | 0 | OK | Ground clear controls. | 78 | 42.13 | 749.77
5369 | TIN-INTERP | Interpolated Ground | 34311.32 | -5.01 | 725.39 | 0 | 18.88 | 0 | OK | Ground clear controls. | 78 | 42.13 | 744.27
5370 | TIN-INTERP | Interpolated Ground | 34311.49 | -4.46 | 725.38 | 0 | 30.57 | 0 | OK | Ground clear controls. | 78 | 42.13 | 755.95
5371 | TIN-INTERP | Interpolated Ground | 34312.88 | 5.58 | 726.73 | 0 | 29.33 | 0 | OK | Ground clear controls. | 78 | 42.13 | 756.06
5372 | TIN-INTERP | Interpolated Ground | 34312.89 | 6.15 | 726.69 | 0 | 17.8 | 0 | OK | Ground clear controls. | 78 | 42.13 | 744.49
5373 | TIN-INTERP | Interpolated Ground | 34312.99 | 7.65 | 726.53 | 0 | 23.66 | 0 | OK | Ground clear controls. | 78 | 42.13 | 750.19
5374 | TIN-INTERP | Interpolated Ground | 34351.11 | -6.58 | 728.21 | 0 | 24.29 | 0 | OK | Ground clear controls. | 78 | 42.13 | 752.5
5375 | TIN-INTERP | Interpolated Ground | 34351.32 | -5.05 | 728.23 | 0 | 18.79 | 0 | OK | Ground clear controls. | 78 | 42.13 | 747.02
5376 | TIN-INTERP | Interpolated Ground | 34351.49 | -4.52 | 728.23 | 0 | 30.34 | 0 | OK | Ground clear controls. | 78 | 42.13 | 758.57
5377 | TIN-INTERP | Interpolated Ground | 34352.88 | 5.34 | 728.61 | 0 | 30.1 | 0 | OK | Ground clear controls. | 78 | 42.13 | 758.71
5378 | TIN-INTERP | Interpolated Ground | 34352.89 | 5.9 | 728.62 | 0 | 18.64 | 0 | OK | Ground clear controls. | 78 | 42.13 | 747.26
5379 | TIN-INTERP | Interpolated Ground | 34352.99 | 7.4 | 728.65 | 0 | 24.26 | 0 | OK | Ground clear controls. | 78 | 42.13 | 752.91
5380 | TIN-INTERP | Interpolated Ground | 34391.11 | -6.61 | 728.88 | 0 | 27.29 | 0 | OK | Ground clear controls. | 78 | 42.13 | 756.17
5381 | TIN-INTERP | Interpolated Ground | 34391.32 | -5.09 | 728.91 | 0 | 21.79 | 0 | OK | Ground clear controls. | 78 | 42.13 | 750.7
5382 | TIN-INTERP | Interpolated Ground | 34391.49 | -4.57 | 728.9 | 0 | 33.22 | 0 | OK | Ground clear controls. | 78 | 42.13 | 762.12
5383 | TIN-INTERP | Interpolated Ground | 34392.88 | 5.1 | 729.06 | 0 | 33.21 | 0 | OK | Ground clear controls. | 78 | 42.13 | 762.27
5384 | TIN-INTERP | Interpolated Ground | 34392.89 | 5.64 | 729.07 | 0 | 21.88 | 0 | OK | Ground clear controls. | 78 | 42.13 | 750.95
5385 | TIN-INTERP | Interpolated Ground | 34392.99 | 7.14 | 729 | 0 | 27.57 | 0 | OK | Ground clear controls. | 78 | 42.13 | 756.57
5386 | TIN-INTERP | Interpolated Ground | 34431.11 | -6.65 | 729.76 | 0 | 31.03 | 0 | OK | Ground clear controls. | 78 | 42.13 | 760.79
5387 | TIN-INTERP | Interpolated Ground | 34431.32 | -5.13 | 729.79 | 0 | 25.53 | 0 | OK | Ground clear controls. | 78 | 42.13 | 755.32
5388 | TIN-INTERP | Interpolated Ground | 34431.49 | -4.62 | 729.8 | 0 | 36.79 | 0 | OK | Ground clear controls. | 78 | 42.13 | 766.59
5389 | TIN-INTERP | Interpolated Ground | 34432.88 | 4.86 | 730.07 | 0 | 36.69 | 0 | OK | Ground clear controls. | 78 | 42.13 | 766.76
5390 | TIN-INTERP | Interpolated Ground | 34432.89 | 5.39 | 730.08 | 0 | 25.49 | 0 | OK | Ground clear controls. | 78 | 42.13 | 755.57
5391 | TIN-INTERP | Interpolated Ground | 34432.99 | 6.89 | 730.07 | 0 | 31.08 | 0 | OK | Ground clear controls. | 78 | 42.13 | 761.15
5392 | TIN-INTERP | Interpolated Ground | 34471.11 | -6.68 | 729.8 | 0 | 36.54 | 0 | OK | Ground clear controls. | 78 | 42.13 | 766.34
5393 | TIN-INTERP | Interpolated Ground | 34471.32 | -5.18 | 729.78 | 0 | 31.1 | 0 | OK | Ground clear controls. | 78 | 42.13 | 760.88
5394 | TIN-INTERP | Interpolated Ground | 34471.49 | -4.67 | 729.85 | 0 | 42.13 | 0 | OK | Ground clear controls. | 78 | 42.13 | 771.98
5395 | TIN-INTERP | Interpolated Ground | 34472.88 | 4.63 | 730.07 | 0 | 42.1 | 0 | OK | Ground clear controls. | 78 | 42.1 | 772.17
5396 | TIN-INTERP | Interpolated Ground | 34472.89 | 5.13 | 730.08 | 0 | 31.05 | 0 | OK | Ground clear controls. | 78 | 36.45 | 761.13
5397 | TIN-INTERP | Interpolated Ground | 34472.99 | 6.63 | 730.21 | 0 | 36.45 | 0 | OK | Ground clear controls. | 78 | 36.45 | 766.66
5398 | TIN-INTERP | Interpolated Ground | 34485.02 | -4.69 | 729.7 | 0 | 44.3 | 0 | OK | Ground clear controls. | 79 | 44.3 | 774
5399 | TIN-INTERP | Interpolated Ground | 34485.04 | 6.56 | 730.22 | 0 | 38.28 | 0 | OK | Ground clear controls. | 79 | 43.79 | 768.5
5400 | TIN-INTERP | Interpolated Ground | 34485.07 | -5.19 | 729.69 | 0 | 33.31 | 0 | OK | Ground clear controls. | 79 | 43.79 | 763
5401 | TIN-INTERP | Interpolated Ground | 34485.07 | 4.55 | 730.21 | 0 | 43.79 | 0 | OK | Ground clear controls. | 79 | 43.79 | 774
5402 | TIN-INTERP | Interpolated Ground | 34485.07 | -6.69 | 729.67 | 0 | 38.83 | 0 | OK | Ground clear controls. | 79 | 38.83 | 768.5
5403 | TIN-INTERP | Interpolated Ground | 34485.1 | 5.06 | 730.28 | 0 | 32.72 | 0 | OK | Ground clear controls. | 79 | 38.21 | 763
5404 | TIN-INTERP | Interpolated Ground | 34525.02 | -4.68 | 730.64 | 0 | 38.21 | 0 | OK | Ground clear controls. | 79 | 38.21 | 768.85
5405 | TIN-INTERP | Interpolated Ground | 34525.04 | 6.56 | 731.15 | 0 | 32.18 | 0 | OK | Ground clear controls. | 79 | 37.83 | 763.33
5406 | TIN-INTERP | Interpolated Ground | 34525.07 | -5.19 | 730.62 | 0 | 27.17 | 0 | OK | Ground clear controls. | 79 | 37.83 | 757.79
5407 | TIN-INTERP | Interpolated Ground | 34525.07 | 4.55 | 731.05 | 0 | 37.83 | 0 | OK | Ground clear controls. | 79 | 37.83 | 768.88
5408 | TIN-INTERP | Interpolated Ground | 34525.07 | -6.69 | 730.59 | 0 | 32.68 | 0 | OK | Ground clear controls. | 79 | 33.11 | 763.27
5409 | TIN-INTERP | Interpolated Ground | 34525.1 | 5.06 | 731.05 | 0 | 26.79 | 0 | OK | Ground clear controls. | 79 | 33.11 | 757.84
5410 | TIN-INTERP | Interpolated Ground | 34565.02 | -4.68 | 731.95 | 0 | 32.68 | 0 | OK | Ground clear controls. | 79 | 33.11 | 764.63
5411 | TIN-INTERP | Interpolated Ground | 34565.04 | 6.56 | 732.43 | 0 | 26.65 | 0 | OK | Ground clear controls. | 79 | 33.11 | 759.08
5412 | TIN-INTERP | Interpolated Ground | 34565.07 | -5.18 | 731.92 | 0 | 21.6 | 0 | OK | Ground clear controls. | 79 | 33.11 | 753.52
5413 | TIN-INTERP | Interpolated Ground | 34565.07 | 4.55 | 732.46 | 0 | 32.22 | 0 | OK | Ground clear controls. | 79 | 33.11 | 764.68
5414 | TIN-INTERP | Interpolated Ground | 34565.07 | -6.68 | 731.84 | 0 | 27.14 | 0 | OK | Ground clear controls. | 79 | 33.11 | 758.98
5415 | TIN-INTERP | Interpolated Ground | 34565.1 | 5.06 | 732.47 | 0 | 21.14 | 0 | OK | Ground clear controls. | 79 | 33.11 | 753.61
5416 | TIN-INTERP | Interpolated Ground | 34605.02 | -4.68 | 731.81 | 0 | 29.53 | 0 | OK | Ground clear controls. | 79 | 33.11 | 761.34
5417 | TIN-INTERP | Interpolated Ground | 34605.04 | 6.56 | 732.21 | 0 | 23.56 | 0 | OK | Ground clear controls. | 79 | 33.11 | 755.77
5418 | TIN-INTERP | Interpolated Ground | 34605.07 | -5.18 | 731.81 | 0 | 18.38 | 0 | OK | Ground clear controls. | 79 | 33.11 | 750.19
5419 | TIN-INTERP | Interpolated Ground | 34605.07 | 4.55 | 732.19 | 0 | 29.21 | 0 | OK | Ground clear controls. | 79 | 33.11 | 761.4
5420 | TIN-INTERP | Interpolated Ground | 34605.07 | -6.68 | 731.77 | 0 | 23.86 | 0 | OK | Ground clear controls. | 79 | 33.11 | 755.63
5421 | TIN-INTERP | Interpolated Ground | 34605.1 | 5.06 | 732.19 | 0 | 18.11 | 0 | OK | Ground clear controls. | 79 | 33.11 | 750.3
5422 | TIN-INTERP | Interpolated Ground | 34645.02 | -4.67 | 731.01 | 0 | 27.95 | 0 | OK | Ground clear controls. | 79 | 33.11 | 758.96
5423 | TIN-INTERP | Interpolated Ground | 34645.04 | 6.56 | 731.19 | 0 | 22.18 | 0 | OK | Ground clear controls. | 79 | 33.11 | 753.37
5424 | TIN-INTERP | Interpolated Ground | 34645.07 | -5.17 | 731 | 0 | 16.78 | 0 | OK | Ground clear controls. | 79 | 33.11 | 747.78
5425 | TIN-INTERP | Interpolated Ground | 34645.07 | 4.56 | 731.17 | 0 | 27.85 | 0 | OK | Ground clear controls. | 79 | 33.11 | 759.02
5426 | TIN-INTERP | Interpolated Ground | 34645.07 | -6.67 | 731.02 | 0 | 22.2 | 0 | OK | Ground clear controls. | 79 | 33.11 | 753.22
5427 | TIN-INTERP | Interpolated Ground | 34645.1 | 5.06 | 731.17 | 0 | 16.75 | 0 | OK | Ground clear controls. | 79 | 33.11 | 747.92
5428 | TIN-INTERP | Interpolated Ground | 34685.02 | -4.67 | 729.61 | 0 | 27.89 | 0 | OK | Ground clear controls. | 79 | 33.11 | 757.5
5429 | TIN-INTERP | Interpolated Ground | 34685.04 | 6.56 | 730.15 | 0 | 21.75 | 0 | OK | Ground clear controls. | 79 | 33.11 | 751.9
5430 | TIN-INTERP | Interpolated Ground | 34685.07 | -5.17 | 729.62 | 0 | 16.69 | 0 | OK | Ground clear controls. | 79 | 33.11 | 746.31
5431 | TIN-INTERP | Interpolated Ground | 34685.07 | 4.56 | 729.95 | 0 | 27.62 | 0 | OK | Ground clear controls. | 79 | 33.11 | 757.57
5432 | TIN-INTERP | Interpolated Ground | 34685.07 | -6.67 | 729.59 | 0 | 22.15 | 0 | OK | Ground clear controls. | 79 | 33.11 | 751.74
5433 | TIN-INTERP | Interpolated Ground | 34685.1 | 5.06 | 729.99 | 0 | 16.47 | 0 | OK | Ground clear controls. | 79 | 33.11 | 746.46
5434 | TIN-INTERP | Interpolated Ground | 34725.02 | -4.66 | 732.61 | 0 | 24.34 | 0 | OK | Ground clear controls. | 79 | 33.11 | 756.95
5435 | TIN-INTERP | Interpolated Ground | 34725.04 | 6.56 | 732.54 | 0 | 18.82 | 0 | OK | Ground clear controls. | 79 | 33.11 | 751.36
5436 | TIN-INTERP | Interpolated Ground | 34725.07 | -5.16 | 732.61 | 0 | 13.15 | 0 | OK | Ground clear controls. | 79 | 33.11 | 745.76
5437 | TIN-INTERP | Interpolated Ground | 34725.07 | 4.56 | 732.7 | 0 | 24.32 | 0 | OK | Ground clear controls. | 79 | 33.11 | 757.02
5438 | TIN-INTERP | Interpolated Ground | 34725.07 | -6.67 | 732.52 | 0 | 18.67 | 0 | OK | Ground clear controls. | 79 | 33.11 | 751.19
5439 | TIN-INTERP | Interpolated Ground | 34725.1 | 5.06 | 732.67 | 0 | 13.24 | 0 | OK | Ground clear controls. | 79 | 33.11 | 745.91
5440 | TIN-INTERP | Interpolated Ground | 34765.02 | -4.66 | 733.16 | 0 | 24.16 | 0 | OK | Ground clear controls. | 79 | 33.11 | 757.32
5441 | TIN-INTERP | Interpolated Ground | 34765.04 | 6.56 | 733.39 | 0 | 18.36 | 0 | OK | Ground clear controls. | 79 | 33.11 | 751.75
5442 | TIN-INTERP | Interpolated Ground | 34765.07 | -5.16 | 733.16 | 0 | 12.98 | 0 | OK | Ground clear controls. | 79 | 33.11 | 746.14
5443 | TIN-INTERP | Interpolated Ground | 34765.07 | 4.56 | 733.38 | 0 | 24.02 | 0 | OK | Ground clear controls. | 79 | 33.11 | 757.4
5444 | TIN-INTERP | Interpolated Ground | 34765.07 | -6.66 | 733.17 | 0 | 18.4 | 0 | OK | Ground clear controls. | 79 | 33.11 | 751.57
5445 | TIN-INTERP | Interpolated Ground | 34765.1 | 5.06 | 733.36 | 0 | 12.93 | 0 | OK | Ground clear controls. | 79 | 33.11 | 746.29
5446 | TIN-INTERP | Interpolated Ground | 34805.02 | -4.66 | 733.09 | 0 | 25.53 | 0 | OK | Ground clear controls. | 79 | 33.11 | 758.62
5447 | TIN-INTERP | Interpolated Ground | 34805.04 | 6.56 | 733.98 | 0 | 19.06 | 0 | OK | Ground clear controls. | 79 | 33.11 | 753.04
5448 | TIN-INTERP | Interpolated Ground | 34805.07 | -5.16 | 733.04 | 0 | 14.41 | 0 | OK | Ground clear controls. | 79 | 33.11 | 747.45
5449 | TIN-INTERP | Interpolated Ground | 34805.07 | 4.56 | 733.85 | 0 | 24.84 | 0 | OK | Ground clear controls. | 79 | 33.11 | 758.69
5450 | TIN-INTERP | Interpolated Ground | 34805.07 | -6.66 | 732.98 | 0 | 19.89 | 0 | OK | Ground clear controls. | 79 | 33.11 | 752.87
5451 | TIN-INTERP | Interpolated Ground | 34805.1 | 5.06 | 733.88 | 0 | 13.7 | 0 | OK | Ground clear controls. | 79 | 33.11 | 747.58
5452 | TIN-INTERP | Interpolated Ground | 34845.02 | -4.65 | 731.62 | 0 | 29.21 | 0 | OK | Ground clear controls. | 79 | 33.11 | 760.83
5453 | TIN-INTERP | Interpolated Ground | 34845.04 | 6.56 | 730.96 | 0 | 24.3 | 0 | OK | Ground clear controls. | 79 | 33.11 | 755.26
5454 | TIN-INTERP | Interpolated Ground | 34845.07 | -5.15 | 731.65 | 0 | 18.03 | 0 | OK | Ground clear controls. | 79 | 33.11 | 749.68
5455 | TIN-INTERP | Interpolated Ground | 34845.07 | 4.56 | 731.11 | 0 | 29.78 | 0 | OK | Ground clear controls. | 79 | 33.11 | 760.89
5456 | TIN-INTERP | Interpolated Ground | 34845.07 | -6.65 | 731.83 | 0 | 23.3 | 0 | OK | Ground clear controls. | 79 | 33.11 | 755.13
5457 | TIN-INTERP | Interpolated Ground | 34845.1 | 5.06 | 731.06 | 0 | 18.74 | 0 | OK | Ground clear controls. | 79 | 33.11 | 749.8
5458 | TIN-INTERP | Interpolated Ground | 34885.02 | -4.65 | 732 | 0 | 31.96 | 0 | OK | Ground clear controls. | 79 | 33.11 | 763.96
5459 | TIN-INTERP | Interpolated Ground | 34885.04 | 6.56 | 732.8 | 0 | 25.61 | 0 | OK | Ground clear controls. | 79 | 33.11 | 758.41
5460 | TIN-INTERP | Interpolated Ground | 34885.07 | -5.15 | 731.95 | 0 | 20.9 | 0 | OK | Ground clear controls. | 79 | 33.11 | 752.85
5461 | TIN-INTERP | Interpolated Ground | 34885.07 | 4.56 | 732.79 | 0 | 31.21 | 0 | OK | Ground clear controls. | 79 | 33.11 | 764
5462 | TIN-INTERP | Interpolated Ground | 34885.07 | -6.65 | 731.83 | 0 | 26.48 | 0 | OK | Ground clear controls. | 79 | 33.11 | 758.31
5463 | TIN-INTERP | Interpolated Ground | 34885.1 | 5.06 | 732.78 | 0 | 20.16 | 0 | OK | Ground clear controls. | 79 | 33.11 | 752.94
5464 | TIN-INTERP | Interpolated Ground | 34925.02 | -4.64 | 734.89 | 0 | 33.11 | 0 | OK | Ground clear controls. | 79 | 33.11 | 768
5465 | TIN-INTERP | Interpolated Ground | 34925.04 | 6.56 | 735.53 | 0 | 26.96 | 0 | OK | Ground clear controls. | 79 | 32.66 | 762.49
5466 | TIN-INTERP | Interpolated Ground | 34925.07 | -5.14 | 734.85 | 0 | 22.1 | 0 | OK | Ground clear controls. | 79 | 32.66 | 756.95
5467 | TIN-INTERP | Interpolated Ground | 34925.07 | 4.56 | 735.38 | 0 | 32.66 | 0 | OK | Ground clear controls. | 79 | 32.66 | 768.04
5468 | TIN-INTERP | Interpolated Ground | 34925.07 | -6.64 | 734.66 | 0 | 27.76 | 0 | OK | Ground clear controls. | 79 | 27.76 | 762.42
5469 | TIN-INTERP | Interpolated Ground | 34925.1 | 5.06 | 735.39 | 0 | 21.61 | 0 | OK | Ground clear controls. | 79 | 21.61 | 757
5470 | TIN-INTERP | Interpolated Ground | 34964 | 6.56 | 737.33 | 0 | 30.02 | 0 | OK | Ground clear controls. | 80 | 39.68 | 767.35
5471 | TIN-INTERP | Interpolated Ground | 34964.02 | 4.56 | 737.14 | 0 | 35.71 | 0 | OK | Ground clear controls. | 80 | 39.68 | 772.85
5472 | TIN-INTERP | Interpolated Ground | 34964.04 | 5.06 | 737.23 | 0 | 24.62 | 0 | OK | Ground clear controls. | 80 | 39.68 | 761.85
5473 | TIN-INTERP | Interpolated Ground | 34964.08 | -5.14 | 735.97 | 0 | 25.87 | 0 | OK | Ground clear controls. | 80 | 39.68 | 761.84
5474 | TIN-INTERP | Interpolated Ground | 34964.09 | -4.64 | 735.99 | 0 | 36.86 | 0 | OK | Ground clear controls. | 80 | 39.68 | 772.85
5475 | TIN-INTERP | Interpolated Ground | 34964.12 | -6.64 | 735.67 | 0 | 31.68 | 0 | OK | Ground clear controls. | 80 | 39.68 | 767.35
5476 | TIN-INTERP | Interpolated Ground | 35004 | 6.56 | 735.86 | 0 | 25.69 | 0 | OK | Ground clear controls. | 80 | 39.68 | 761.55
5477 | TIN-INTERP | Interpolated Ground | 35004.02 | 4.56 | 735.77 | 0 | 31.35 | 0 | OK | Ground clear controls. | 80 | 39.68 | 767.12
5478 | TIN-INTERP | Interpolated Ground | 35004.04 | 5.06 | 735.8 | 0 | 20.29 | 0 | OK | Ground clear controls. | 80 | 39.68 | 756.09
5479 | TIN-INTERP | Interpolated Ground | 35004.08 | -5.14 | 734.86 | 0 | 21.21 | 0 | OK | Ground clear controls. | 80 | 39.68 | 756.07
5480 | TIN-INTERP | Interpolated Ground | 35004.09 | -4.64 | 734.89 | 0 | 32.24 | 0 | OK | Ground clear controls. | 80 | 39.68 | 767.13
5481 | TIN-INTERP | Interpolated Ground | 35004.12 | -6.64 | 734.83 | 0 | 26.74 | 0 | OK | Ground clear controls. | 80 | 39.68 | 761.57
5482 | TIN-INTERP | Interpolated Ground | 35044 | 6.56 | 732.83 | 0 | 23.86 | 0 | OK | Ground clear controls. | 80 | 39.68 | 756.69
5483 | TIN-INTERP | Interpolated Ground | 35044.02 | 4.56 | 732.61 | 0 | 29.69 | 0 | OK | Ground clear controls. | 80 | 39.68 | 762.3
5484 | TIN-INTERP | Interpolated Ground | 35044.04 | 5.06 | 732.65 | 0 | 18.61 | 0 | OK | Ground clear controls. | 80 | 39.68 | 751.26
5485 | TIN-INTERP | Interpolated Ground | 35044.08 | -5.14 | 732.74 | 0 | 18.48 | 0 | OK | Ground clear controls. | 80 | 39.68 | 751.22
5486 | TIN-INTERP | Interpolated Ground | 35044.09 | -4.64 | 732.74 | 0 | 29.61 | 0 | OK | Ground clear controls. | 80 | 39.68 | 762.35
5487 | TIN-INTERP | Interpolated Ground | 35044.12 | -6.64 | 732.77 | 0 | 23.95 | 0 | OK | Ground clear controls. | 80 | 39.68 | 756.72
5488 | TIN-INTERP | Interpolated Ground | 35084 | 6.57 | 732.04 | 0 | 20.73 | 0 | OK | Ground clear controls. | 80 | 39.68 | 752.77
5489 | TIN-INTERP | Interpolated Ground | 35084.02 | 4.57 | 731.88 | 0 | 26.54 | 0 | OK | Ground clear controls. | 80 | 39.68 | 758.42
5490 | TIN-INTERP | Interpolated Ground | 35084.04 | 5.07 | 731.91 | 0 | 15.45 | 0 | OK | Ground clear controls. | 80 | 39.68 | 747.36
5491 | TIN-INTERP | Interpolated Ground | 35084.08 | -5.13 | 731.6 | 0 | 15.71 | 0 | OK | Ground clear controls. | 80 | 39.68 | 747.31
5492 | TIN-INTERP | Interpolated Ground | 35084.09 | -4.63 | 731.61 | 0 | 26.88 | 0 | OK | Ground clear controls. | 80 | 39.68 | 758.49
5493 | TIN-INTERP | Interpolated Ground | 35084.12 | -6.63 | 731.5 | 0 | 21.32 | 0 | OK | Ground clear controls. | 80 | 39.68 | 752.82
5494 | TIN-INTERP | Interpolated Ground | 35124 | 6.57 | 731.49 | 0 | 18.29 | 0 | OK | Ground clear controls. | 80 | 39.68 | 749.78
5495 | TIN-INTERP | Interpolated Ground | 35124.02 | 4.57 | 731.33 | 0 | 24.13 | 0 | OK | Ground clear controls. | 80 | 39.68 | 755.46
5496 | TIN-INTERP | Interpolated Ground | 35124.04 | 5.07 | 731.36 | 0 | 13.04 | 0 | OK | Ground clear controls. | 80 | 39.68 | 744.4
5497 | TIN-INTERP | Interpolated Ground | 35124.08 | -5.13 | 731.11 | 0 | 13.22 | 0 | OK | Ground clear controls. | 80 | 39.68 | 744.33
5498 | TIN-INTERP | Interpolated Ground | 35124.09 | -4.63 | 731.09 | 0 | 24.45 | 0 | OK | Ground clear controls. | 80 | 39.68 | 755.54
5499 | TIN-INTERP | Interpolated Ground | 35124.12 | -6.63 | 730.94 | 0 | 18.9 | 0 | OK | Ground clear controls. | 80 | 39.68 | 749.84
5500 | TIN-INTERP | Interpolated Ground | 35164 | 6.57 | 730.59 | 0 | 17.13 | 0 | OK | Ground clear controls. | 80 | 39.68 | 747.72
5501 | TIN-INTERP | Interpolated Ground | 35164.02 | 4.57 | 730.4 | 0 | 23.02 | 0 | OK | Ground clear controls. | 80 | 39.68 | 753.42
5502 | TIN-INTERP | Interpolated Ground | 35164.04 | 5.07 | 730.47 | 0 | 11.88 | 0 | OK | Ground clear controls. | 80 | 39.68 | 742.35
5503 | TIN-INTERP | Interpolated Ground | 35164.08 | -5.13 | 729.84 | 0 | 12.44 | 0 | OK | Ground clear controls. | 80 | 39.68 | 742.28
5504 | TIN-INTERP | Interpolated Ground | 35164.09 | -4.63 | 729.87 | 0 | 23.63 | 0 | OK | Ground clear controls. | 80 | 39.68 | 753.5
5505 | TIN-INTERP | Interpolated Ground | 35164.12 | -6.63 | 729.78 | 0 | 18.01 | 0 | OK | Ground clear controls. | 80 | 39.68 | 747.79
5506 | TIN-INTERP | Interpolated Ground | 35204 | 6.57 | 729.8 | 0 | 16.81 | 0 | OK | Ground clear controls. | 80 | 39.68 | 746.61
5507 | TIN-INTERP | Interpolated Ground | 35204.02 | 4.57 | 729.64 | 0 | 22.67 | 0 | OK | Ground clear controls. | 80 | 39.68 | 752.31
5508 | TIN-INTERP | Interpolated Ground | 35204.04 | 5.07 | 729.66 | 0 | 11.57 | 0 | OK | Ground clear controls. | 80 | 39.68 | 741.23
5509 | TIN-INTERP | Interpolated Ground | 35204.08 | -5.13 | 729.13 | 0 | 12.03 | 0 | OK | Ground clear controls. | 80 | 39.68 | 741.16
5510 | TIN-INTERP | Interpolated Ground | 35204.09 | -4.63 | 729.14 | 0 | 23.25 | 0 | OK | Ground clear controls. | 80 | 39.68 | 752.39
5511 | TIN-INTERP | Interpolated Ground | 35204.12 | -6.63 | 729.1 | 0 | 17.57 | 0 | OK | Ground clear controls. | 80 | 39.68 | 746.67
5512 | TIN-INTERP | Interpolated Ground | 35244 | 6.57 | 728.98 | 0 | 17.44 | 0 | OK | Ground clear controls. | 80 | 39.68 | 746.42
5513 | TIN-INTERP | Interpolated Ground | 35244.02 | 4.57 | 728.79 | 0 | 23.33 | 0 | OK | Ground clear controls. | 80 | 39.68 | 752.12
5514 | TIN-INTERP | Interpolated Ground | 35244.04 | 5.07 | 728.83 | 0 | 12.22 | 0 | OK | Ground clear controls. | 80 | 39.68 | 741.05
5515 | TIN-INTERP | Interpolated Ground | 35244.08 | -5.13 | 728.51 | 0 | 12.46 | 0 | OK | Ground clear controls. | 80 | 39.68 | 740.97
5516 | TIN-INTERP | Interpolated Ground | 35244.09 | -4.63 | 728.53 | 0 | 23.67 | 0 | OK | Ground clear controls. | 80 | 39.68 | 752.2
5517 | TIN-INTERP | Interpolated Ground | 35244.12 | -6.63 | 728.57 | 0 | 17.91 | 0 | OK | Ground clear controls. | 80 | 39.68 | 746.48
5518 | TIN-INTERP | Interpolated Ground | 35284 | 6.57 | 727.91 | 0 | 19.25 | 0 | OK | Ground clear controls. | 80 | 39.68 | 747.16
5519 | TIN-INTERP | Interpolated Ground | 35284.02 | 4.57 | 727.88 | 0 | 24.97 | 0 | OK | Ground clear controls. | 80 | 39.68 | 752.85
5520 | TIN-INTERP | Interpolated Ground | 35284.04 | 5.07 | 727.88 | 0 | 13.9 | 0 | OK | Ground clear controls. | 80 | 39.68 | 741.78
5521 | TIN-INTERP | Interpolated Ground | 35284.08 | -5.13 | 727.66 | 0 | 14.06 | 0 | OK | Ground clear controls. | 80 | 39.68 | 741.72
5522 | TIN-INTERP | Interpolated Ground | 35284.09 | -4.63 | 727.64 | 0 | 25.3 | 0 | OK | Ground clear controls. | 80 | 39.68 | 752.94
5523 | TIN-INTERP | Interpolated Ground | 35284.12 | -6.63 | 727.65 | 0 | 19.58 | 0 | OK | Ground clear controls. | 80 | 39.68 | 747.23
5524 | TIN-INTERP | Interpolated Ground | 35324 | 6.58 | 728.1 | 0 | 20.74 | 0 | OK | Ground clear controls. | 80 | 39.68 | 748.84
5525 | TIN-INTERP | Interpolated Ground | 35324.02 | 4.58 | 727.93 | 0 | 26.57 | 0 | OK | Ground clear controls. | 80 | 39.68 | 754.5
5526 | TIN-INTERP | Interpolated Ground | 35324.04 | 5.08 | 727.95 | 0 | 15.49 | 0 | OK | Ground clear controls. | 80 | 39.68 | 743.44
5527 | TIN-INTERP | Interpolated Ground | 35324.08 | -5.12 | 727.68 | 0 | 15.71 | 0 | OK | Ground clear controls. | 80 | 39.68 | 743.39
5528 | TIN-INTERP | Interpolated Ground | 35324.09 | -4.62 | 727.71 | 0 | 26.87 | 0 | OK | Ground clear controls. | 80 | 39.68 | 754.58
5529 | TIN-INTERP | Interpolated Ground | 35324.12 | -6.62 | 727.64 | 0 | 21.26 | 0 | OK | Ground clear controls. | 80 | 39.68 | 748.9
5530 | TIN-INTERP | Interpolated Ground | 35364 | 6.58 | 727.34 | 0 | 24.11 | 0 | OK | Ground clear controls. | 80 | 39.68 | 751.45
5531 | TIN-INTERP | Interpolated Ground | 35364.02 | 4.58 | 727.34 | 0 | 29.74 | 0 | OK | Ground clear controls. | 80 | 39.68 | 757.08
5532 | TIN-INTERP | Interpolated Ground | 35364.04 | 5.08 | 727.3 | 0 | 18.73 | 0 | OK | Ground clear controls. | 80 | 39.68 | 746.03
5533 | TIN-INTERP | Interpolated Ground | 35364.08 | -5.12 | 727.11 | 0 | 18.88 | 0 | OK | Ground clear controls. | 80 | 39.68 | 745.99
5534 | TIN-INTERP | Interpolated Ground | 35364.09 | -4.62 | 727.14 | 0 | 30 | 0 | OK | Ground clear controls. | 80 | 39.68 | 757.14
5535 | TIN-INTERP | Interpolated Ground | 35364.12 | -6.62 | 727.11 | 0 | 24.39 | 0 | OK | Ground clear controls. | 80 | 39.68 | 751.5
5536 | TIN-INTERP | Interpolated Ground | 35404 | 6.58 | 726.71 | 0 | 28.28 | 0 | OK | Ground clear controls. | 80 | 39.68 | 754.99
5537 | TIN-INTERP | Interpolated Ground | 35404.02 | 4.58 | 726.72 | 0 | 33.85 | 0 | OK | Ground clear controls. | 80 | 39.68 | 760.57
5538 | TIN-INTERP | Interpolated Ground | 35404.04 | 5.08 | 726.72 | 0 | 22.82 | 0 | OK | Ground clear controls. | 80 | 39.68 | 749.54
5539 | TIN-INTERP | Interpolated Ground | 35404.08 | -5.12 | 726.73 | 0 | 22.8 | 0 | OK | Ground clear controls. | 80 | 39.68 | 749.53
5540 | TIN-INTERP | Interpolated Ground | 35404.09 | -4.62 | 726.75 | 0 | 33.87 | 0 | OK | Ground clear controls. | 80 | 39.68 | 760.62
5541 | TIN-INTERP | Interpolated Ground | 35404.12 | -6.62 | 726.35 | 0 | 28.69 | 0 | OK | Ground clear controls. | 80 | 39.68 | 755.04
5542 | TIN-INTERP | Interpolated Ground | 35444 | 6.58 | 726.07 | 0 | 33.41 | 0 | OK | Ground clear controls. | 80 | 39.68 | 759.48
5543 | TIN-INTERP | Interpolated Ground | 35444.02 | 4.58 | 725.71 | 0 | 39.29 | 0 | OK | Ground clear controls. | 80 | 39.68 | 765
5544 | TIN-INTERP | Interpolated Ground | 35444.04 | 5.08 | 725.83 | 0 | 28.16 | 0 | OK | Ground clear controls. | 80 | 39.68 | 753.99
5545 | TIN-INTERP | Interpolated Ground | 35444.08 | -5.12 | 725.3 | 0 | 28.69 | 0 | OK | Ground clear controls. | 80 | 39.68 | 753.99
5546 | TIN-INTERP | Interpolated Ground | 35444.09 | -4.62 | 725.35 | 0 | 39.68 | 0 | OK | Ground clear controls. | 80 | 39.68 | 765.03
5547 | TIN-INTERP | Interpolated Ground | 35444.12 | -6.62 | 725.23 | 0 | 34.28 | 0 | OK | Ground clear controls. | 80 | 34.28 | 759.51
5548 | TIN-INTERP | Interpolated Ground | 35454.19 | -4.62 | 725.3 | 0 | 40.98 | 0 | OK | Ground clear controls. | 81 | 40.98 | 766.28
5549 | TIN-INTERP | Interpolated Ground | 35454.25 | -6.62 | 725.33 | 0 | 35.45 | 0 | OK | Ground clear controls. | 81 | 40.69 | 760.78
5550 | TIN-INTERP | Interpolated Ground | 35454.25 | -5.12 | 725.33 | 0 | 29.95 | 0 | OK | Ground clear controls. | 81 | 40.69 | 755.28
5551 | TIN-INTERP | Interpolated Ground | 35454.27 | 4.58 | 725.59 | 0 | 40.69 | 0 | OK | Ground clear controls. | 81 | 40.69 | 766.28
5552 | TIN-INTERP | Interpolated Ground | 35454.29 | 6.58 | 725.87 | 0 | 34.91 | 0 | OK | Ground clear controls. | 81 | 39.8 | 760.78
5553 | TIN-INTERP | Interpolated Ground | 35454.3 | 5.08 | 725.66 | 0 | 29.62 | 0 | OK | Ground clear controls. | 81 | 39.8 | 755.28
5554 | TIN-INTERP | Interpolated Ground | 35494.19 | -4.62 | 725.27 | 0 | 36.12 | 0 | OK | Ground clear controls. | 81 | 39.8 | 761.39
5555 | TIN-INTERP | Interpolated Ground | 35494.25 | -6.62 | 725.27 | 0 | 30.59 | 0 | OK | Ground clear controls. | 81 | 39.8 | 755.86
5556 | TIN-INTERP | Interpolated Ground | 35494.25 | -5.12 | 725.27 | 0 | 25.08 | 0 | OK | Ground clear controls. | 81 | 39.8 | 750.35
5557 | TIN-INTERP | Interpolated Ground | 35494.27 | 4.58 | 725.97 | 0 | 35.43 | 0 | OK | Ground clear controls. | 81 | 39.8 | 761.4
5558 | TIN-INTERP | Interpolated Ground | 35494.29 | 6.58 | 725.64 | 0 | 30.2 | 0 | OK | Ground clear controls. | 81 | 39.8 | 755.84
5559 | TIN-INTERP | Interpolated Ground | 35494.3 | 5.08 | 725.92 | 0 | 24.47 | 0 | OK | Ground clear controls. | 81 | 39.8 | 750.39
5560 | TIN-INTERP | Interpolated Ground | 35534.19 | -4.62 | 725.69 | 0 | 31.75 | 0 | OK | Ground clear controls. | 81 | 39.8 | 757.44
5561 | TIN-INTERP | Interpolated Ground | 35534.25 | -6.62 | 725.63 | 0 | 26.24 | 0 | OK | Ground clear controls. | 81 | 39.8 | 751.87
5562 | TIN-INTERP | Interpolated Ground | 35534.25 | -5.12 | 725.67 | 0 | 20.7 | 0 | OK | Ground clear controls. | 81 | 39.8 | 746.37
5563 | TIN-INTERP | Interpolated Ground | 35534.27 | 4.58 | 725.69 | 0 | 31.76 | 0 | OK | Ground clear controls. | 81 | 39.8 | 757.45
5564 | TIN-INTERP | Interpolated Ground | 35534.29 | 6.58 | 725.49 | 0 | 26.35 | 0 | OK | Ground clear controls. | 81 | 39.8 | 751.84
5565 | TIN-INTERP | Interpolated Ground | 35534.3 | 5.08 | 725.61 | 0 | 20.81 | 0 | OK | Ground clear controls. | 81 | 39.8 | 746.42
5566 | TIN-INTERP | Interpolated Ground | 35574.19 | -4.62 | 725.68 | 0 | 28.73 | 0 | OK | Ground clear controls. | 81 | 39.8 | 754.41
5567 | TIN-INTERP | Interpolated Ground | 35574.25 | -6.62 | 725.7 | 0 | 23.13 | 0 | OK | Ground clear controls. | 81 | 39.8 | 748.83
5568 | TIN-INTERP | Interpolated Ground | 35574.25 | -5.12 | 725.69 | 0 | 17.63 | 0 | OK | Ground clear controls. | 81 | 39.8 | 743.32
5569 | TIN-INTERP | Interpolated Ground | 35574.27 | 4.58 | 725.92 | 0 | 28.5 | 0 | OK | Ground clear controls. | 81 | 39.8 | 754.42
5570 | TIN-INTERP | Interpolated Ground | 35574.29 | 6.58 | 725.7 | 0 | 23.07 | 0 | OK | Ground clear controls. | 81 | 39.8 | 748.77
5571 | TIN-INTERP | Interpolated Ground | 35574.3 | 5.08 | 725.87 | 0 | 17.53 | 0 | OK | Ground clear controls. | 81 | 39.8 | 743.4
5572 | TIN-INTERP | Interpolated Ground | 35614.19 | -4.62 | 726.59 | 0 | 25.73 | 0 | OK | Ground clear controls. | 81 | 39.8 | 752.32
5573 | TIN-INTERP | Interpolated Ground | 35614.25 | -6.62 | 726.59 | 0 | 20.13 | 0 | OK | Ground clear controls. | 81 | 39.8 | 746.72
5574 | TIN-INTERP | Interpolated Ground | 35614.25 | -5.12 | 726.59 | 0 | 14.62 | 0 | OK | Ground clear controls. | 81 | 39.8 | 741.21
5575 | TIN-INTERP | Interpolated Ground | 35614.27 | 4.58 | 726.95 | 0 | 25.39 | 0 | OK | Ground clear controls. | 81 | 39.8 | 752.34
5576 | TIN-INTERP | Interpolated Ground | 35614.29 | 6.58 | 726.71 | 0 | 19.95 | 0 | OK | Ground clear controls. | 81 | 39.8 | 746.66
5577 | TIN-INTERP | Interpolated Ground | 35614.3 | 5.08 | 726.82 | 0 | 14.49 | 0 | OK | Ground clear controls. | 81 | 39.8 | 741.31
5578 | TIN-INTERP | Interpolated Ground | 35654.19 | -4.62 | 727.47 | 0 | 23.7 | 0 | OK | Ground clear controls. | 81 | 39.8 | 751.17
5579 | TIN-INTERP | Interpolated Ground | 35654.25 | -6.62 | 727.44 | 0 | 18.12 | 0 | OK | Ground clear controls. | 81 | 39.8 | 745.56
5580 | TIN-INTERP | Interpolated Ground | 35654.25 | -5.12 | 727.44 | 0 | 12.6 | 0 | OK | Ground clear controls. | 81 | 39.8 | 740.04
5581 | TIN-INTERP | Interpolated Ground | 35654.27 | 4.58 | 727.79 | 0 | 23.4 | 0 | OK | Ground clear controls. | 81 | 39.8 | 751.19
5582 | TIN-INTERP | Interpolated Ground | 35654.29 | 6.58 | 727.71 | 0 | 17.78 | 0 | OK | Ground clear controls. | 81 | 39.8 | 745.49
5583 | TIN-INTERP | Interpolated Ground | 35654.3 | 5.08 | 727.75 | 0 | 12.4 | 0 | OK | Ground clear controls. | 81 | 39.8 | 740.15
5584 | TIN-INTERP | Interpolated Ground | 35694.19 | -4.62 | 728.13 | 0 | 22.81 | 0 | OK | Ground clear controls. | 81 | 39.8 | 750.94
5585 | TIN-INTERP | Interpolated Ground | 35694.25 | -6.62 | 728.19 | 0 | 17.13 | 0 | OK | Ground clear controls. | 81 | 39.8 | 745.32
5586 | TIN-INTERP | Interpolated Ground | 35694.25 | -5.12 | 728.13 | 0 | 11.68 | 0 | OK | Ground clear controls. | 81 | 39.8 | 739.81
5587 | TIN-INTERP | Interpolated Ground | 35694.27 | 4.58 | 728.15 | 0 | 22.81 | 0 | OK | Ground clear controls. | 81 | 39.8 | 750.96
5588 | TIN-INTERP | Interpolated Ground | 35694.29 | 6.58 | 728.03 | 0 | 17.21 | 0 | OK | Ground clear controls. | 81 | 39.8 | 745.24
5589 | TIN-INTERP | Interpolated Ground | 35694.3 | 5.08 | 728.09 | 0 | 11.82 | 0 | OK | Ground clear controls. | 81 | 39.8 | 739.91
5590 | TIN-INTERP | Interpolated Ground | 35734.19 | -4.62 | 728.47 | 0 | 23.17 | 0 | OK | Ground clear controls. | 81 | 39.8 | 751.64
5591 | TIN-INTERP | Interpolated Ground | 35734.25 | -6.62 | 728.45 | 0 | 17.58 | 0 | OK | Ground clear controls. | 81 | 39.8 | 746.03
5592 | TIN-INTERP | Interpolated Ground | 35734.25 | -5.12 | 728.48 | 0 | 12.04 | 0 | OK | Ground clear controls. | 81 | 39.8 | 740.52
5593 | TIN-INTERP | Interpolated Ground | 35734.27 | 4.58 | 728.5 | 0 | 23.16 | 0 | OK | Ground clear controls. | 81 | 39.8 | 751.66
5594 | TIN-INTERP | Interpolated Ground | 35734.29 | 6.58 | 728.54 | 0 | 17.41 | 0 | OK | Ground clear controls. | 81 | 39.8 | 745.95
5595 | TIN-INTERP | Interpolated Ground | 35734.3 | 5.08 | 728.43 | 0 | 12.2 | 0 | OK | Ground clear controls. | 81 | 39.8 | 740.63
5596 | TIN-INTERP | Interpolated Ground | 35774.19 | -4.62 | 728.77 | 0 | 24.5 | 0 | OK | Ground clear controls. | 81 | 39.8 | 753.27
5597 | TIN-INTERP | Interpolated Ground | 35774.25 | -6.62 | 728.84 | 0 | 18.82 | 0 | OK | Ground clear controls. | 81 | 39.8 | 747.66
5598 | TIN-INTERP | Interpolated Ground | 35774.25 | -5.12 | 728.79 | 0 | 13.36 | 0 | OK | Ground clear controls. | 81 | 39.8 | 742.15
5599 | TIN-INTERP | Interpolated Ground | 35774.27 | 4.58 | 728.91 | 0 | 24.38 | 0 | OK | Ground clear controls. | 81 | 39.8 | 753.29
5600 | TIN-INTERP | Interpolated Ground | 35774.29 | 6.58 | 728.89 | 0 | 18.71 | 0 | OK | Ground clear controls. | 81 | 39.8 | 747.6
5601 | TIN-INTERP | Interpolated Ground | 35774.3 | 5.08 | 728.84 | 0 | 13.41 | 0 | OK | Ground clear controls. | 81 | 39.8 | 742.25
5602 | TIN-INTERP | Interpolated Ground | 35814.19 | -4.62 | 729.03 | 0 | 26.81 | 0 | OK | Ground clear controls. | 81 | 39.8 | 755.84
5603 | TIN-INTERP | Interpolated Ground | 35814.25 | -6.62 | 729.14 | 0 | 21.1 | 0 | OK | Ground clear controls. | 81 | 39.8 | 750.24
5604 | TIN-INTERP | Interpolated Ground | 35814.25 | -5.12 | 729.05 | 0 | 15.68 | 0 | OK | Ground clear controls. | 81 | 39.8 | 744.73
5605 | TIN-INTERP | Interpolated Ground | 35814.27 | 4.58 | 729.11 | 0 | 26.75 | 0 | OK | Ground clear controls. | 81 | 39.8 | 755.86
5606 | TIN-INTERP | Interpolated Ground | 35814.29 | 6.58 | 729.08 | 0 | 21.1 | 0 | OK | Ground clear controls. | 81 | 39.8 | 750.18
5607 | TIN-INTERP | Interpolated Ground | 35814.3 | 5.08 | 729.07 | 0 | 15.76 | 0 | OK | Ground clear controls. | 81 | 39.8 | 744.83
5608 | TIN-INTERP | Interpolated Ground | 35854.19 | -4.62 | 729.12 | 0 | 30.21 | 0 | OK | Ground clear controls. | 81 | 39.8 | 759.33
5609 | TIN-INTERP | Interpolated Ground | 35854.25 | -6.62 | 729.25 | 0 | 24.51 | 0 | OK | Ground clear controls. | 81 | 39.8 | 753.76
5610 | TIN-INTERP | Interpolated Ground | 35854.25 | -5.12 | 729.11 | 0 | 19.15 | 0 | OK | Ground clear controls. | 81 | 39.8 | 748.26
5611 | TIN-INTERP | Interpolated Ground | 35854.27 | 4.58 | 729.29 | 0 | 30.07 | 0 | OK | Ground clear controls. | 81 | 39.8 | 759.36
5612 | TIN-INTERP | Interpolated Ground | 35854.29 | 6.58 | 729.25 | 0 | 24.46 | 0 | OK | Ground clear controls. | 81 | 39.8 | 753.71
5613 | TIN-INTERP | Interpolated Ground | 35854.3 | 5.08 | 729.26 | 0 | 19.07 | 0 | OK | Ground clear controls. | 81 | 39.8 | 748.33
5614 | TIN-INTERP | Interpolated Ground | 35894.19 | -4.62 | 729.05 | 0 | 34.72 | 0 | OK | Ground clear controls. | 81 | 39.8 | 763.77
5615 | TIN-INTERP | Interpolated Ground | 35894.25 | -6.62 | 729.04 | 0 | 29.17 | 0 | OK | Ground clear controls. | 81 | 39.8 | 758.21
5616 | TIN-INTERP | Interpolated Ground | 35894.25 | -5.12 | 729.07 | 0 | 23.64 | 0 | OK | Ground clear controls. | 81 | 39.8 | 752.71
5617 | TIN-INTERP | Interpolated Ground | 35894.27 | 4.58 | 729.58 | 0 | 34.21 | 0 | OK | Ground clear controls. | 81 | 39.8 | 763.79
5618 | TIN-INTERP | Interpolated Ground | 35894.29 | 6.58 | 729.43 | 0 | 28.75 | 0 | OK | Ground clear controls. | 81 | 39.8 | 758.18
5619 | TIN-INTERP | Interpolated Ground | 35894.3 | 5.08 | 729.56 | 0 | 23.2 | 0 | OK | Ground clear controls. | 81 | 39.8 | 752.76
5620 | TIN-INTERP | Interpolated Ground | 35934.19 | -4.62 | 729.34 | 0 | 39.8 | 0 | OK | Ground clear controls. | 81 | 39.8 | 769.14
5621 | TIN-INTERP | Interpolated Ground | 35934.25 | -6.62 | 729.4 | 0 | 34.21 | 0 | OK | Ground clear controls. | 81 | 39.59 | 763.61
5622 | TIN-INTERP | Interpolated Ground | 35934.25 | -5.12 | 729.34 | 0 | 28.77 | 0 | OK | Ground clear controls. | 81 | 39.59 | 758.11
5623 | TIN-INTERP | Interpolated Ground | 35934.27 | 4.58 | 729.57 | 0 | 39.59 | 0 | OK | Ground clear controls. | 81 | 39.59 | 769.16
5624 | TIN-INTERP | Interpolated Ground | 35934.29 | 6.58 | 729.68 | 0 | 33.92 | 0 | OK | Ground clear controls. | 81 | 33.92 | 763.6
5625 | TIN-INTERP | Interpolated Ground | 35934.3 | 5.08 | 729.63 | 0 | 28.51 | 0 | OK | Ground clear controls. | 81 | 28.51 | 758.14
5626 | TIN-INTERP | Interpolated Ground | 35962.35 | 4.58 | 729.57 | 0 | 43.91 | 0 | OK | Ground clear controls. | 82 | 43.98 | 773.48
5627 | TIN-INTERP | Interpolated Ground | 35962.36 | -4.62 | 729.5 | 0 | 43.98 | 0 | OK | Ground clear controls. | 82 | 43.98 | 773.48
5628 | TIN-INTERP | Interpolated Ground | 35962.38 | 5.08 | 729.62 | 0 | 32.86 | 0 | OK | Ground clear controls. | 82 | 41.5 | 762.48
5629 | TIN-INTERP | Interpolated Ground | 35962.39 | -5.12 | 729.53 | 0 | 32.95 | 0 | OK | Ground clear controls. | 82 | 41.5 | 762.48
5630 | TIN-INTERP | Interpolated Ground | 35962.42 | 6.58 | 729.71 | 0 | 38.27 | 0 | OK | Ground clear controls. | 82 | 41.5 | 767.98
5631 | TIN-INTERP | Interpolated Ground | 35962.43 | -6.62 | 729.61 | 0 | 38.37 | 0 | OK | Ground clear controls. | 82 | 41.5 | 767.98
5632 | TIN-INTERP | Interpolated Ground | 36002.35 | 4.58 | 730.15 | 0 | 37.5 | 0 | OK | Ground clear controls. | 82 | 41.5 | 767.65
5633 | TIN-INTERP | Interpolated Ground | 36002.37 | -4.62 | 729.81 | 0 | 37.84 | 0 | OK | Ground clear controls. | 82 | 41.5 | 767.65
5634 | TIN-INTERP | Interpolated Ground | 36002.38 | 5.08 | 730.12 | 0 | 26.53 | 0 | OK | Ground clear controls. | 82 | 41.5 | 756.65
5635 | TIN-INTERP | Interpolated Ground | 36002.4 | -5.12 | 729.81 | 0 | 26.82 | 0 | OK | Ground clear controls. | 82 | 41.5 | 756.63
5636 | TIN-INTERP | Interpolated Ground | 36002.41 | 6.58 | 730.07 | 0 | 32.05 | 0 | OK | Ground clear controls. | 82 | 41.5 | 762.12
5637 | TIN-INTERP | Interpolated Ground | 36002.43 | -6.62 | 729.83 | 0 | 32.33 | 0 | OK | Ground clear controls. | 82 | 41.5 | 762.16
5638 | TIN-INTERP | Interpolated Ground | 36042.35 | 4.58 | 729.95 | 0 | 32.8 | 0 | OK | Ground clear controls. | 82 | 41.5 | 762.75
5639 | TIN-INTERP | Interpolated Ground | 36042.37 | -4.62 | 729.88 | 0 | 32.88 | 0 | OK | Ground clear controls. | 82 | 41.5 | 762.76
5640 | TIN-INTERP | Interpolated Ground | 36042.38 | 5.08 | 729.92 | 0 | 21.84 | 0 | OK | Ground clear controls. | 82 | 41.5 | 751.76
5641 | TIN-INTERP | Interpolated Ground | 36042.4 | -5.12 | 729.84 | 0 | 21.88 | 0 | OK | Ground clear controls. | 82 | 41.5 | 751.72
5642 | TIN-INTERP | Interpolated Ground | 36042.41 | 6.58 | 729.89 | 0 | 27.32 | 0 | OK | Ground clear controls. | 82 | 41.5 | 757.21
5643 | TIN-INTERP | Interpolated Ground | 36042.43 | -6.62 | 729.82 | 0 | 27.46 | 0 | OK | Ground clear controls. | 82 | 41.5 | 757.28
5644 | TIN-INTERP | Interpolated Ground | 36082.35 | 4.58 | 729.65 | 0 | 29.14 | 0 | OK | Ground clear controls. | 82 | 41.5 | 758.79
5645 | TIN-INTERP | Interpolated Ground | 36082.37 | -4.62 | 729.54 | 0 | 29.28 | 0 | OK | Ground clear controls. | 82 | 41.5 | 758.82
5646 | TIN-INTERP | Interpolated Ground | 36082.38 | 5.08 | 729.64 | 0 | 18.18 | 0 | OK | Ground clear controls. | 82 | 41.5 | 747.82
5647 | TIN-INTERP | Interpolated Ground | 36082.4 | -5.12 | 729.51 | 0 | 18.25 | 0 | OK | Ground clear controls. | 82 | 41.5 | 747.76
5648 | TIN-INTERP | Interpolated Ground | 36082.41 | 6.58 | 729.61 | 0 | 23.63 | 0 | OK | Ground clear controls. | 82 | 41.5 | 753.24
5649 | TIN-INTERP | Interpolated Ground | 36082.43 | -6.62 | 729.62 | 0 | 23.72 | 0 | OK | Ground clear controls. | 82 | 41.5 | 753.34
5650 | TIN-INTERP | Interpolated Ground | 36122.35 | 4.59 | 729.4 | 0 | 26.39 | 0 | OK | Ground clear controls. | 82 | 41.5 | 755.79
5651 | TIN-INTERP | Interpolated Ground | 36122.37 | -4.61 | 729.08 | 0 | 26.73 | 0 | OK | Ground clear controls. | 82 | 41.5 | 755.81
5652 | TIN-INTERP | Interpolated Ground | 36122.38 | 5.09 | 729.38 | 0 | 15.43 | 0 | OK | Ground clear controls. | 82 | 41.5 | 744.81
5653 | TIN-INTERP | Interpolated Ground | 36122.4 | -5.11 | 729.09 | 0 | 15.67 | 0 | OK | Ground clear controls. | 82 | 41.5 | 744.76
5654 | TIN-INTERP | Interpolated Ground | 36122.41 | 6.59 | 729.32 | 0 | 20.91 | 0 | OK | Ground clear controls. | 82 | 41.5 | 750.23
5655 | TIN-INTERP | Interpolated Ground | 36122.43 | -6.61 | 729.21 | 0 | 21.14 | 0 | OK | Ground clear controls. | 82 | 41.5 | 750.35
5656 | TIN-INTERP | Interpolated Ground | 36162.35 | 4.59 | 729.02 | 0 | 24.69 | 0 | OK | Ground clear controls. | 82 | 41.5 | 753.71
5657 | TIN-INTERP | Interpolated Ground | 36162.37 | -4.61 | 728.51 | 0 | 25.23 | 0 | OK | Ground clear controls. | 82 | 41.5 | 753.74
5658 | TIN-INTERP | Interpolated Ground | 36162.38 | 5.09 | 729 | 0 | 13.75 | 0 | OK | Ground clear controls. | 82 | 41.5 | 742.75
5659 | TIN-INTERP | Interpolated Ground | 36162.4 | -5.11 | 728.48 | 0 | 14.2 | 0 | OK | Ground clear controls. | 82 | 41.5 | 742.68
5660 | TIN-INTERP | Interpolated Ground | 36162.41 | 6.59 | 728.89 | 0 | 19.26 | 0 | OK | Ground clear controls. | 82 | 41.5 | 748.15
5661 | TIN-INTERP | Interpolated Ground | 36162.43 | -6.61 | 728.54 | 0 | 19.74 | 0 | OK | Ground clear controls. | 82 | 41.5 | 748.28
5662 | TIN-INTERP | Interpolated Ground | 36202.35 | 4.59 | 728.81 | 0 | 23.77 | 0 | OK | Ground clear controls. | 82 | 41.5 | 752.58
5663 | TIN-INTERP | Interpolated Ground | 36202.37 | -4.61 | 728.39 | 0 | 24.22 | 0 | OK | Ground clear controls. | 82 | 41.5 | 752.61
5664 | TIN-INTERP | Interpolated Ground | 36202.38 | 5.09 | 728.79 | 0 | 12.84 | 0 | OK | Ground clear controls. | 82 | 41.5 | 741.63
5665 | TIN-INTERP | Interpolated Ground | 36202.4 | -5.11 | 728.38 | 0 | 13.17 | 0 | OK | Ground clear controls. | 82 | 41.5 | 741.55
5666 | TIN-INTERP | Interpolated Ground | 36202.41 | 6.59 | 728.74 | 0 | 18.29 | 0 | OK | Ground clear controls. | 82 | 41.5 | 747.03
5667 | TIN-INTERP | Interpolated Ground | 36202.43 | -6.61 | 728.35 | 0 | 18.8 | 0 | OK | Ground clear controls. | 82 | 41.5 | 747.15
5668 | TIN-INTERP | Interpolated Ground | 36242.35 | 4.59 | 728.77 | 0 | 23.63 | 0 | OK | Ground clear controls. | 82 | 41.5 | 752.4
5669 | TIN-INTERP | Interpolated Ground | 36242.37 | -4.61 | 728.19 | 0 | 24.24 | 0 | OK | Ground clear controls. | 82 | 41.5 | 752.43
5670 | TIN-INTERP | Interpolated Ground | 36242.38 | 5.09 | 728.73 | 0 | 12.7 | 0 | OK | Ground clear controls. | 82 | 41.5 | 741.43
5671 | TIN-INTERP | Interpolated Ground | 36242.4 | -5.11 | 728.18 | 0 | 13.19 | 0 | OK | Ground clear controls. | 82 | 41.5 | 741.37
5672 | TIN-INTERP | Interpolated Ground | 36242.41 | 6.59 | 728.65 | 0 | 18.18 | 0 | OK | Ground clear controls. | 82 | 41.5 | 746.83
5673 | TIN-INTERP | Interpolated Ground | 36242.43 | -6.61 | 728.11 | 0 | 18.86 | 0 | OK | Ground clear controls. | 82 | 41.5 | 746.97
5674 | TIN-INTERP | Interpolated Ground | 36282.35 | 4.59 | 728.83 | 0 | 24.31 | 0 | OK | Ground clear controls. | 82 | 41.5 | 753.14
5675 | TIN-INTERP | Interpolated Ground | 36282.37 | -4.61 | 728.15 | 0 | 25.02 | 0 | OK | Ground clear controls. | 82 | 41.5 | 753.17
5676 | TIN-INTERP | Interpolated Ground | 36282.38 | 5.09 | 728.8 | 0 | 13.38 | 0 | OK | Ground clear controls. | 82 | 41.5 | 742.18
5677 | TIN-INTERP | Interpolated Ground | 36282.4 | -5.11 | 728.12 | 0 | 14 | 0 | OK | Ground clear controls. | 82 | 41.5 | 742.12
5678 | TIN-INTERP | Interpolated Ground | 36282.41 | 6.59 | 728.79 | 0 | 18.79 | 0 | OK | Ground clear controls. | 82 | 41.5 | 747.58
5679 | TIN-INTERP | Interpolated Ground | 36282.43 | -6.61 | 728.08 | 0 | 19.63 | 0 | OK | Ground clear controls. | 82 | 41.5 | 747.71
5680 | TIN-INTERP | Interpolated Ground | 36322.35 | 4.59 | 728.89 | 0 | 25.94 | 0 | OK | Ground clear controls. | 82 | 41.5 | 754.83
5681 | TIN-INTERP | Interpolated Ground | 36322.37 | -4.61 | 728.04 | 0 | 26.83 | 0 | OK | Ground clear controls. | 82 | 41.5 | 754.87
5682 | TIN-INTERP | Interpolated Ground | 36322.38 | 5.09 | 728.87 | 0 | 14.99 | 0 | OK | Ground clear controls. | 82 | 41.5 | 743.86
5683 | TIN-INTERP | Interpolated Ground | 36322.4 | -5.11 | 728 | 0 | 15.81 | 0 | OK | Ground clear controls. | 82 | 41.5 | 743.81
5684 | TIN-INTERP | Interpolated Ground | 36322.41 | 6.59 | 728.81 | 0 | 20.46 | 0 | OK | Ground clear controls. | 82 | 41.5 | 749.27
5685 | TIN-INTERP | Interpolated Ground | 36322.43 | -6.61 | 727.89 | 0 | 21.52 | 0 | OK | Ground clear controls. | 82 | 41.5 | 749.41
5686 | TIN-INTERP | Interpolated Ground | 36362.35 | 4.6 | 729.1 | 0 | 28.36 | 0 | OK | Ground clear controls. | 82 | 41.5 | 757.46
5687 | TIN-INTERP | Interpolated Ground | 36362.37 | -4.6 | 728.87 | 0 | 28.62 | 0 | OK | Ground clear controls. | 82 | 41.5 | 757.49
5688 | TIN-INTERP | Interpolated Ground | 36362.38 | 5.1 | 729.07 | 0 | 17.42 | 0 | OK | Ground clear controls. | 82 | 41.5 | 746.49
5689 | TIN-INTERP | Interpolated Ground | 36362.4 | -5.1 | 728.87 | 0 | 17.57 | 0 | OK | Ground clear controls. | 82 | 41.5 | 746.44
5690 | TIN-INTERP | Interpolated Ground | 36362.41 | 6.59 | 729.12 | 0 | 22.79 | 0 | OK | Ground clear controls. | 82 | 41.5 | 751.91
5691 | TIN-INTERP | Interpolated Ground | 36362.43 | -6.6 | 728.94 | 0 | 23.09 | 0 | OK | Ground clear controls. | 82 | 41.5 | 752.03
5692 | TIN-INTERP | Interpolated Ground | 36402.35 | 4.6 | 729.27 | 0 | 31.75 | 0 | OK | Ground clear controls. | 82 | 41.5 | 761.02
5693 | TIN-INTERP | Interpolated Ground | 36402.37 | -4.6 | 729.02 | 0 | 32.04 | 0 | OK | Ground clear controls. | 82 | 41.5 | 761.06
5694 | TIN-INTERP | Interpolated Ground | 36402.38 | 5.1 | 729.26 | 0 | 20.79 | 0 | OK | Ground clear controls. | 82 | 41.5 | 750.05
5695 | TIN-INTERP | Interpolated Ground | 36402.4 | -5.1 | 729 | 0 | 21.02 | 0 | OK | Ground clear controls. | 82 | 41.5 | 750.02
5696 | TIN-INTERP | Interpolated Ground | 36402.41 | 6.6 | 729.33 | 0 | 26.15 | 0 | OK | Ground clear controls. | 82 | 41.5 | 755.48
5697 | TIN-INTERP | Interpolated Ground | 36402.43 | -6.6 | 729 | 0 | 26.59 | 0 | OK | Ground clear controls. | 82 | 41.5 | 755.59
5698 | TIN-INTERP | Interpolated Ground | 36442.35 | 4.6 | 729.3 | 0 | 36.24 | 0 | OK | Ground clear controls. | 82 | 41.5 | 765.54
5699 | TIN-INTERP | Interpolated Ground | 36442.37 | -4.6 | 729.3 | 0 | 36.27 | 0 | OK | Ground clear controls. | 82 | 41.5 | 765.57
5700 | TIN-INTERP | Interpolated Ground | 36442.38 | 5.1 | 729.31 | 0 | 25.25 | 0 | OK | Ground clear controls. | 82 | 41.5 | 754.56
5701 | TIN-INTERP | Interpolated Ground | 36442.4 | -5.1 | 729.26 | 0 | 25.28 | 0 | OK | Ground clear controls. | 82 | 41.5 | 754.54
5702 | TIN-INTERP | Interpolated Ground | 36442.41 | 6.6 | 729.33 | 0 | 30.68 | 0 | OK | Ground clear controls. | 82 | 41.5 | 760.01
5703 | TIN-INTERP | Interpolated Ground | 36442.43 | -6.6 | 729.23 | 0 | 30.86 | 0 | OK | Ground clear controls. | 82 | 41.5 | 760.09
5704 | TIN-INTERP | Interpolated Ground | 36482.35 | 4.6 | 729.91 | 0 | 41.1 | 0 | OK | Ground clear controls. | 82 | 41.5 | 771.01
5705 | TIN-INTERP | Interpolated Ground | 36482.37 | -4.6 | 729.52 | 0 | 41.5 | 0 | OK | Ground clear controls. | 82 | 41.5 | 771.02
5706 | TIN-INTERP | Interpolated Ground | 36482.38 | 5.1 | 729.91 | 0 | 30.1 | 0 | OK | Ground clear controls. | 82 | 36.07 | 760.01
5707 | TIN-INTERP | Interpolated Ground | 36482.4 | -5.1 | 729.51 | 0 | 30.5 | 0 | OK | Ground clear controls. | 82 | 36.07 | 760.01
5708 | TIN-INTERP | Interpolated Ground | 36482.41 | 6.6 | 729.93 | 0 | 35.56 | 0 | OK | Ground clear controls. | 82 | 36.07 | 765.49
5709 | TIN-INTERP | Interpolated Ground | 36482.43 | -6.6 | 729.47 | 0 | 36.07 | 0 | OK | Ground clear controls. | 82 | 36.07 | 765.54
5710 | TIN-INTERP | Interpolated Ground | 36503.98 | -6.6 | 730.24 | 0 | 38.62 | 0 | OK | Ground clear controls. | 83 | 44.13 | 768.86
5711 | TIN-INTERP | Interpolated Ground | 36503.99 | -4.6 | 730.23 | 0 | 44.13 | 0 | OK | Ground clear controls. | 83 | 44.13 | 774.36
5712 | TIN-INTERP | Interpolated Ground | 36504.02 | -5.1 | 730.34 | 0 | 33.02 | 0 | OK | Ground clear controls. | 83 | 43.69 | 763.36
5713 | TIN-INTERP | Interpolated Ground | 36504.06 | 4.6 | 730.68 | 0 | 43.69 | 0 | OK | Ground clear controls. | 83 | 43.69 | 774.37
5714 | TIN-INTERP | Interpolated Ground | 36504.13 | 5.1 | 730.75 | 0 | 32.61 | 0 | OK | Ground clear controls. | 83 | 39.52 | 763.36
5715 | TIN-INTERP | Interpolated Ground | 36504.17 | 6.6 | 730.8 | 0 | 38.06 | 0 | OK | Ground clear controls. | 83 | 39.52 | 768.86
5716 | TIN-INTERP | Interpolated Ground | 36543.97 | -6.61 | 729.04 | 0 | 33.36 | 0 | OK | Ground clear controls. | 83 | 39.52 | 762.4
5717 | TIN-INTERP | Interpolated Ground | 36543.99 | -4.61 | 729.02 | 0 | 38.87 | 0 | OK | Ground clear controls. | 83 | 39.52 | 767.89
5718 | TIN-INTERP | Interpolated Ground | 36544.01 | -5.11 | 729.02 | 0 | 27.87 | 0 | OK | Ground clear controls. | 83 | 39.52 | 756.89
5719 | TIN-INTERP | Interpolated Ground | 36544.07 | 4.59 | 728.97 | 0 | 38.9 | 0 | OK | Ground clear controls. | 83 | 39.52 | 767.87
5720 | TIN-INTERP | Interpolated Ground | 36544.13 | 5.09 | 728.98 | 0 | 27.96 | 0 | OK | Ground clear controls. | 83 | 39.52 | 756.94
5721 | TIN-INTERP | Interpolated Ground | 36544.17 | 6.59 | 728.96 | 0 | 33.47 | 0 | OK | Ground clear controls. | 83 | 39.52 | 762.43
5722 | TIN-INTERP | Interpolated Ground | 36583.97 | -6.62 | 729 | 0 | 27.89 | 0 | OK | Ground clear controls. | 83 | 39.52 | 756.89
5723 | TIN-INTERP | Interpolated Ground | 36583.99 | -4.62 | 729.04 | 0 | 33.32 | 0 | OK | Ground clear controls. | 83 | 39.52 | 762.36
5724 | TIN-INTERP | Interpolated Ground | 36584.01 | -5.12 | 729.01 | 0 | 22.36 | 0 | OK | Ground clear controls. | 83 | 39.52 | 751.37
5725 | TIN-INTERP | Interpolated Ground | 36584.07 | 4.58 | 728.73 | 0 | 33.61 | 0 | OK | Ground clear controls. | 83 | 39.52 | 762.34
5726 | TIN-INTERP | Interpolated Ground | 36584.13 | 5.08 | 728.69 | 0 | 22.76 | 0 | OK | Ground clear controls. | 83 | 39.52 | 751.45
5727 | TIN-INTERP | Interpolated Ground | 36584.17 | 6.58 | 728.61 | 0 | 28.33 | 0 | OK | Ground clear controls. | 83 | 39.52 | 756.94
5728 | TIN-INTERP | Interpolated Ground | 36623.97 | -6.62 | 728.13 | 0 | 24.18 | 0 | OK | Ground clear controls. | 83 | 39.52 | 752.31
5729 | TIN-INTERP | Interpolated Ground | 36623.99 | -4.62 | 728.33 | 0 | 29.46 | 0 | OK | Ground clear controls. | 83 | 39.52 | 757.79
5730 | TIN-INTERP | Interpolated Ground | 36624.01 | -5.12 | 728.3 | 0 | 18.5 | 0 | OK | Ground clear controls. | 83 | 39.52 | 746.8
5731 | TIN-INTERP | Interpolated Ground | 36624.07 | 4.58 | 728.49 | 0 | 29.27 | 0 | OK | Ground clear controls. | 83 | 39.52 | 757.76
5732 | TIN-INTERP | Interpolated Ground | 36624.13 | 5.08 | 728.5 | 0 | 18.41 | 0 | OK | Ground clear controls. | 83 | 39.52 | 746.91
5733 | TIN-INTERP | Interpolated Ground | 36624.17 | 6.58 | 728.47 | 0 | 23.92 | 0 | OK | Ground clear controls. | 83 | 39.52 | 752.39
5734 | TIN-INTERP | Interpolated Ground | 36663.97 | -6.63 | 727.52 | 0 | 21.19 | 0 | OK | Ground clear controls. | 83 | 39.52 | 748.71
5735 | TIN-INTERP | Interpolated Ground | 36663.99 | -4.63 | 727.74 | 0 | 26.44 | 0 | OK | Ground clear controls. | 83 | 39.52 | 754.18
5736 | TIN-INTERP | Interpolated Ground | 36664.01 | -5.13 | 727.68 | 0 | 15.5 | 0 | OK | Ground clear controls. | 83 | 39.52 | 743.18
5737 | TIN-INTERP | Interpolated Ground | 36664.07 | 4.57 | 728.3 | 0 | 25.85 | 0 | OK | Ground clear controls. | 83 | 39.52 | 754.15
5738 | TIN-INTERP | Interpolated Ground | 36664.13 | 5.07 | 728.32 | 0 | 15.02 | 0 | OK | Ground clear controls. | 83 | 39.52 | 743.34
5739 | TIN-INTERP | Interpolated Ground | 36664.17 | 6.57 | 728.39 | 0 | 20.41 | 0 | OK | Ground clear controls. | 83 | 39.52 | 748.8
5740 | TIN-INTERP | Interpolated Ground | 36703.97 | -6.64 | 727.07 | 0 | 18.98 | 0 | OK | Ground clear controls. | 83 | 39.52 | 746.05
5741 | TIN-INTERP | Interpolated Ground | 36703.99 | -4.64 | 727.42 | 0 | 24.09 | 0 | OK | Ground clear controls. | 83 | 39.52 | 751.51
5742 | TIN-INTERP | Interpolated Ground | 36704.01 | -5.14 | 727.35 | 0 | 13.18 | 0 | OK | Ground clear controls. | 83 | 39.52 | 740.53
5743 | TIN-INTERP | Interpolated Ground | 36704.07 | 4.56 | 727.72 | 0 | 23.76 | 0 | OK | Ground clear controls. | 83 | 39.52 | 751.48
5744 | TIN-INTERP | Interpolated Ground | 36704.13 | 5.06 | 727.73 | 0 | 12.97 | 0 | OK | Ground clear controls. | 83 | 39.52 | 740.7
5745 | TIN-INTERP | Interpolated Ground | 36704.17 | 6.56 | 727.81 | 0 | 18.35 | 0 | OK | Ground clear controls. | 83 | 39.52 | 746.16
5746 | TIN-INTERP | Interpolated Ground | 36743.97 | -6.65 | 726.4 | 0 | 17.94 | 0 | OK | Ground clear controls. | 83 | 39.52 | 744.34
5747 | TIN-INTERP | Interpolated Ground | 36743.99 | -4.65 | 726.65 | 0 | 23.14 | 0 | OK | Ground clear controls. | 83 | 39.52 | 749.79
5748 | TIN-INTERP | Interpolated Ground | 36744.01 | -5.15 | 726.6 | 0 | 12.22 | 0 | OK | Ground clear controls. | 83 | 39.52 | 738.82
5749 | TIN-INTERP | Interpolated Ground | 36744.07 | 4.55 | 726.68 | 0 | 23.08 | 0 | OK | Ground clear controls. | 83 | 39.52 | 749.76
5750 | TIN-INTERP | Interpolated Ground | 36744.13 | 5.05 | 726.69 | 0 | 12.3 | 0 | OK | Ground clear controls. | 83 | 39.52 | 738.99
5751 | TIN-INTERP | Interpolated Ground | 36744.17 | 6.55 | 726.68 | 0 | 17.77 | 0 | OK | Ground clear controls. | 83 | 39.52 | 744.45
5752 | TIN-INTERP | Interpolated Ground | 36783.97 | -6.66 | 725.97 | 0 | 17.6 | 0 | OK | Ground clear controls. | 83 | 39.52 | 743.57
5753 | TIN-INTERP | Interpolated Ground | 36783.99 | -4.66 | 726.07 | 0 | 22.95 | 0 | OK | Ground clear controls. | 83 | 39.52 | 749.02
5754 | TIN-INTERP | Interpolated Ground | 36784.01 | -5.16 | 726.02 | 0 | 12.02 | 0 | OK | Ground clear controls. | 83 | 39.52 | 738.04
5755 | TIN-INTERP | Interpolated Ground | 36784.07 | 4.54 | 726.01 | 0 | 22.98 | 0 | OK | Ground clear controls. | 83 | 39.52 | 748.99
5756 | TIN-INTERP | Interpolated Ground | 36784.13 | 5.04 | 726.05 | 0 | 12.17 | 0 | OK | Ground clear controls. | 83 | 39.52 | 738.22
5757 | TIN-INTERP | Interpolated Ground | 36784.17 | 6.54 | 726.08 | 0 | 17.61 | 0 | OK | Ground clear controls. | 83 | 39.52 | 743.69
5758 | TIN-INTERP | Interpolated Ground | 36823.97 | -6.66 | 725.81 | 0 | 17.94 | 0 | OK | Ground clear controls. | 83 | 39.52 | 743.75
5759 | TIN-INTERP | Interpolated Ground | 36823.99 | -4.66 | 725.86 | 0 | 23.35 | 0 | OK | Ground clear controls. | 83 | 39.52 | 749.21
5760 | TIN-INTERP | Interpolated Ground | 36824.01 | -5.16 | 725.85 | 0 | 12.37 | 0 | OK | Ground clear controls. | 83 | 39.52 | 738.22
5761 | TIN-INTERP | Interpolated Ground | 36824.07 | 4.54 | 725.93 | 0 | 23.25 | 0 | OK | Ground clear controls. | 83 | 39.52 | 749.18
5762 | TIN-INTERP | Interpolated Ground | 36824.13 | 5.04 | 725.93 | 0 | 12.47 | 0 | OK | Ground clear controls. | 83 | 39.52 | 738.4
5763 | TIN-INTERP | Interpolated Ground | 36824.17 | 6.54 | 725.99 | 0 | 17.88 | 0 | OK | Ground clear controls. | 83 | 39.52 | 743.87
5764 | TIN-INTERP | Interpolated Ground | 36863.97 | -6.67 | 725.86 | 0 | 19.02 | 0 | OK | Ground clear controls. | 83 | 39.52 | 744.88
5765 | TIN-INTERP | Interpolated Ground | 36863.99 | -4.67 | 725.86 | 0 | 24.47 | 0 | OK | Ground clear controls. | 83 | 39.52 | 750.33
5766 | TIN-INTERP | Interpolated Ground | 36864.01 | -5.17 | 725.86 | 0 | 13.49 | 0 | OK | Ground clear controls. | 83 | 39.52 | 739.35
5767 | TIN-INTERP | Interpolated Ground | 36864.07 | 4.53 | 725.91 | 0 | 24.4 | 0 | OK | Ground clear controls. | 83 | 39.52 | 750.31
5768 | TIN-INTERP | Interpolated Ground | 36864.13 | 5.03 | 725.93 | 0 | 13.59 | 0 | OK | Ground clear controls. | 83 | 39.52 | 739.52
5769 | TIN-INTERP | Interpolated Ground | 36864.17 | 6.53 | 725.9 | 0 | 19.09 | 0 | OK | Ground clear controls. | 83 | 39.52 | 744.99
5770 | TIN-INTERP | Interpolated Ground | 36903.97 | -6.68 | 725.58 | 0 | 21.37 | 0 | OK | Ground clear controls. | 83 | 39.52 | 746.95
5771 | TIN-INTERP | Interpolated Ground | 36903.99 | -4.68 | 725.55 | 0 | 26.86 | 0 | OK | Ground clear controls. | 83 | 39.52 | 752.41
5772 | TIN-INTERP | Interpolated Ground | 36904.01 | -5.18 | 725.56 | 0 | 15.87 | 0 | OK | Ground clear controls. | 83 | 39.52 | 741.43
5773 | TIN-INTERP | Interpolated Ground | 36904.07 | 4.52 | 725.48 | 0 | 26.91 | 0 | OK | Ground clear controls. | 83 | 39.52 | 752.39
5774 | TIN-INTERP | Interpolated Ground | 36904.13 | 5.02 | 725.49 | 0 | 16.09 | 0 | OK | Ground clear controls. | 83 | 39.52 | 741.58
5775 | TIN-INTERP | Interpolated Ground | 36904.17 | 6.52 | 725.51 | 0 | 21.54 | 0 | OK | Ground clear controls. | 83 | 39.52 | 747.05
5776 | TIN-INTERP | Interpolated Ground | 36943.97 | -6.69 | 725.02 | 0 | 24.95 | 0 | OK | Ground clear controls. | 83 | 39.52 | 749.97
5777 | TIN-INTERP | Interpolated Ground | 36943.99 | -4.69 | 725.01 | 0 | 30.43 | 0 | OK | Ground clear controls. | 83 | 39.52 | 755.44
5778 | TIN-INTERP | Interpolated Ground | 36944.01 | -5.19 | 724.99 | 0 | 19.46 | 0 | OK | Ground clear controls. | 83 | 39.52 | 744.45
5779 | TIN-INTERP | Interpolated Ground | 36944.07 | 4.51 | 725.05 | 0 | 30.37 | 0 | OK | Ground clear controls. | 83 | 39.52 | 755.42
5780 | TIN-INTERP | Interpolated Ground | 36944.13 | 5.01 | 725.05 | 0 | 19.53 | 0 | OK | Ground clear controls. | 83 | 39.52 | 744.58
5781 | TIN-INTERP | Interpolated Ground | 36944.17 | 6.51 | 725.01 | 0 | 25.05 | 0 | OK | Ground clear controls. | 83 | 39.52 | 750.06
5782 | TIN-INTERP | Interpolated Ground | 36983.97 | -6.7 | 724.83 | 0 | 29.12 | 0 | OK | Ground clear controls. | 83 | 39.52 | 753.95
5783 | TIN-INTERP | Interpolated Ground | 36983.99 | -4.7 | 724.79 | 0 | 34.63 | 0 | OK | Ground clear controls. | 83 | 39.52 | 759.42
5784 | TIN-INTERP | Interpolated Ground | 36984.01 | -5.2 | 724.78 | 0 | 23.65 | 0 | OK | Ground clear controls. | 83 | 39.52 | 748.43
5785 | TIN-INTERP | Interpolated Ground | 36984.07 | 4.5 | 724.71 | 0 | 34.71 | 0 | OK | Ground clear controls. | 83 | 39.52 | 759.42
5786 | TIN-INTERP | Interpolated Ground | 36984.13 | 5 | 724.67 | 0 | 23.85 | 0 | OK | Ground clear controls. | 83 | 39.52 | 748.52
5787 | TIN-INTERP | Interpolated Ground | 36984.17 | 6.5 | 724.77 | 0 | 29.25 | 0 | OK | Ground clear controls. | 83 | 39.52 | 754.02
5788 | TIN-INTERP | Interpolated Ground | 37023.97 | -6.71 | 724.85 | 0 | 34.02 | 0 | OK | Ground clear controls. | 83 | 39.52 | 758.87
5789 | TIN-INTERP | Interpolated Ground | 37023.99 | -4.71 | 724.84 | 0 | 39.52 | 0 | OK | Ground clear controls. | 83 | 39.52 | 764.36
5790 | TIN-INTERP | Interpolated Ground | 37024.01 | -5.21 | 724.84 | 0 | 28.51 | 0 | OK | Ground clear controls. | 83 | 39.51 | 753.35
5791 | TIN-INTERP | Interpolated Ground | 37024.07 | 4.49 | 724.85 | 0 | 39.51 | 0 | OK | Ground clear controls. | 83 | 39.51 | 764.36
5792 | TIN-INTERP | Interpolated Ground | 37024.13 | 4.99 | 724.86 | 0 | 28.55 | 0 | OK | Ground clear controls. | 83 | 34.04 | 753.41
5793 | TIN-INTERP | Interpolated Ground | 37024.17 | 6.49 | 724.87 | 0 | 34.04 | 0 | OK | Ground clear controls. | 83 | 34.04 | 758.91
5794 | TIN-INTERP | Interpolated Ground | 37054.07 | 4.49 | 724.84 | 0 | 43.86 | 0 | OK | Ground clear controls. | 84 | 43.86 | 768.7
5795 | TIN-INTERP | Interpolated Ground | 37054.1 | -6.71 | 724.88 | 0 | 38.32 | 0 | OK | Ground clear controls. | 84 | 43.82 | 763.2
5796 | TIN-INTERP | Interpolated Ground | 37054.1 | -4.71 | 724.88 | 0 | 43.82 | 0 | OK | Ground clear controls. | 84 | 43.82 | 768.7
5797 | TIN-INTERP | Interpolated Ground | 37054.14 | 4.99 | 724.87 | 0 | 32.83 | 0 | OK | Ground clear controls. | 84 | 39.16 | 757.7
5798 | TIN-INTERP | Interpolated Ground | 37054.16 | 6.49 | 724.96 | 0 | 38.24 | 0 | OK | Ground clear controls. | 84 | 39.16 | 763.2
5799 | TIN-INTERP | Interpolated Ground | 37054.2 | -5.21 | 724.91 | 0 | 32.79 | 0 | OK | Ground clear controls. | 84 | 39.16 | 757.7
5800 | TIN-INTERP | Interpolated Ground | 37094.07 | 4.49 | 724.8 | 0 | 38.15 | 0 | OK | Ground clear controls. | 84 | 39.16 | 762.95
5801 | TIN-INTERP | Interpolated Ground | 37094.1 | -6.71 | 724.78 | 0 | 32.72 | 0 | OK | Ground clear controls. | 84 | 39.16 | 757.5
5802 | TIN-INTERP | Interpolated Ground | 37094.1 | -4.71 | 724.81 | 0 | 38.18 | 0 | OK | Ground clear controls. | 84 | 39.16 | 762.99
5803 | TIN-INTERP | Interpolated Ground | 37094.14 | 4.99 | 724.79 | 0 | 27.26 | 0 | OK | Ground clear controls. | 84 | 39.16 | 752.05
5804 | TIN-INTERP | Interpolated Ground | 37094.16 | 6.49 | 724.82 | 0 | 32.74 | 0 | OK | Ground clear controls. | 84 | 39.16 | 757.56
5805 | TIN-INTERP | Interpolated Ground | 37094.2 | -5.21 | 724.8 | 0 | 27.26 | 0 | OK | Ground clear controls. | 84 | 39.16 | 752.06
5806 | TIN-INTERP | Interpolated Ground | 37134.07 | 4.5 | 724.58 | 0 | 33.57 | 0 | OK | Ground clear controls. | 84 | 39.16 | 758.15
5807 | TIN-INTERP | Interpolated Ground | 37134.1 | -6.7 | 724.72 | 0 | 28.01 | 0 | OK | Ground clear controls. | 84 | 39.16 | 752.73
5808 | TIN-INTERP | Interpolated Ground | 37134.1 | -4.7 | 724.7 | 0 | 33.51 | 0 | OK | Ground clear controls. | 84 | 39.16 | 758.21
5809 | TIN-INTERP | Interpolated Ground | 37134.14 | 5 | 724.61 | 0 | 22.74 | 0 | OK | Ground clear controls. | 84 | 39.16 | 747.35
5810 | TIN-INTERP | Interpolated Ground | 37134.16 | 6.5 | 724.6 | 0 | 28.25 | 0 | OK | Ground clear controls. | 84 | 39.16 | 752.85
5811 | TIN-INTERP | Interpolated Ground | 37134.2 | -5.2 | 724.7 | 0 | 22.65 | 0 | OK | Ground clear controls. | 84 | 39.16 | 747.35
5812 | TIN-INTERP | Interpolated Ground | 37174.07 | 4.51 | 724.8 | 0 | 29.51 | 0 | OK | Ground clear controls. | 84 | 39.16 | 754.31
5813 | TIN-INTERP | Interpolated Ground | 37174.1 | -6.69 | 724.53 | 0 | 24.39 | 0 | OK | Ground clear controls. | 84 | 39.16 | 748.92
5814 | TIN-INTERP | Interpolated Ground | 37174.1 | -4.69 | 724.73 | 0 | 29.66 | 0 | OK | Ground clear controls. | 84 | 39.16 | 754.39
5815 | TIN-INTERP | Interpolated Ground | 37174.14 | 5.01 | 724.81 | 0 | 18.76 | 0 | OK | Ground clear controls. | 84 | 39.16 | 743.57
5816 | TIN-INTERP | Interpolated Ground | 37174.16 | 6.51 | 724.88 | 0 | 24.21 | 0 | OK | Ground clear controls. | 84 | 39.16 | 749.09
5817 | TIN-INTERP | Interpolated Ground | 37174.2 | -5.19 | 724.67 | 0 | 18.91 | 0 | OK | Ground clear controls. | 84 | 39.16 | 743.58
5818 | TIN-INTERP | Interpolated Ground | 37214.07 | 4.51 | 724.82 | 0 | 26.61 | 0 | OK | Ground clear controls. | 84 | 39.16 | 751.43
5819 | TIN-INTERP | Interpolated Ground | 37214.1 | -6.69 | 724.79 | 0 | 21.27 | 0 | OK | Ground clear controls. | 84 | 39.16 | 746.06
5820 | TIN-INTERP | Interpolated Ground | 37214.1 | -4.69 | 724.84 | 0 | 26.68 | 0 | OK | Ground clear controls. | 84 | 39.16 | 751.52
5821 | TIN-INTERP | Interpolated Ground | 37214.14 | 5.01 | 724.83 | 0 | 15.91 | 0 | OK | Ground clear controls. | 84 | 39.16 | 740.74
5822 | TIN-INTERP | Interpolated Ground | 37214.16 | 6.51 | 724.85 | 0 | 21.41 | 0 | OK | Ground clear controls. | 84 | 39.16 | 746.26
5823 | TIN-INTERP | Interpolated Ground | 37214.2 | -5.19 | 724.83 | 0 | 15.92 | 0 | OK | Ground clear controls. | 84 | 39.16 | 740.75
5824 | TIN-INTERP | Interpolated Ground | 37254.07 | 4.52 | 725.03 | 0 | 24.47 | 0 | OK | Ground clear controls. | 84 | 39.16 | 749.5
5825 | TIN-INTERP | Interpolated Ground | 37254.1 | -6.68 | 725.01 | 0 | 19.13 | 0 | OK | Ground clear controls. | 84 | 39.16 | 744.14
5826 | TIN-INTERP | Interpolated Ground | 37254.1 | -4.68 | 725.01 | 0 | 24.6 | 0 | OK | Ground clear controls. | 84 | 39.16 | 749.61
5827 | TIN-INTERP | Interpolated Ground | 37254.14 | 5.02 | 725.02 | 0 | 13.83 | 0 | OK | Ground clear controls. | 84 | 39.16 | 738.85
5828 | TIN-INTERP | Interpolated Ground | 37254.16 | 6.52 | 724.99 | 0 | 19.38 | 0 | OK | Ground clear controls. | 84 | 39.16 | 744.37
5829 | TIN-INTERP | Interpolated Ground | 37254.2 | -5.18 | 725 | 0 | 13.85 | 0 | OK | Ground clear controls. | 84 | 39.16 | 738.85
5830 | TIN-INTERP | Interpolated Ground | 37294.07 | 4.52 | 725.07 | 0 | 23.45 | 0 | OK | Ground clear controls. | 84 | 39.16 | 748.52
5831 | TIN-INTERP | Interpolated Ground | 37294.1 | -6.68 | 724.99 | 0 | 18.19 | 0 | OK | Ground clear controls. | 84 | 39.16 | 743.18
5832 | TIN-INTERP | Interpolated Ground | 37294.1 | -4.68 | 725 | 0 | 23.64 | 0 | OK | Ground clear controls. | 84 | 39.16 | 748.64
5833 | TIN-INTERP | Interpolated Ground | 37294.14 | 5.02 | 725.1 | 0 | 12.79 | 0 | OK | Ground clear controls. | 84 | 39.16 | 737.89
5834 | TIN-INTERP | Interpolated Ground | 37294.16 | 6.52 | 725.07 | 0 | 18.34 | 0 | OK | Ground clear controls. | 84 | 39.16 | 743.41
5835 | TIN-INTERP | Interpolated Ground | 37294.2 | -5.18 | 725 | 0 | 12.9 | 0 | OK | Ground clear controls. | 84 | 39.16 | 737.9
5836 | TIN-INTERP | Interpolated Ground | 37334.07 | 4.53 | 724.81 | 0 | 23.68 | 0 | OK | Ground clear controls. | 84 | 39.16 | 748.49
5837 | TIN-INTERP | Interpolated Ground | 37334.1 | -6.67 | 724.79 | 0 | 18.36 | 0 | OK | Ground clear controls. | 84 | 39.16 | 743.15
5838 | TIN-INTERP | Interpolated Ground | 37334.1 | -4.67 | 724.82 | 0 | 23.79 | 0 | OK | Ground clear controls. | 84 | 39.16 | 748.61
5839 | TIN-INTERP | Interpolated Ground | 37334.14 | 5.03 | 724.83 | 0 | 13.03 | 0 | OK | Ground clear controls. | 84 | 39.16 | 737.86
5840 | TIN-INTERP | Interpolated Ground | 37334.16 | 6.53 | 724.87 | 0 | 18.51 | 0 | OK | Ground clear controls. | 84 | 39.16 | 743.38
5841 | TIN-INTERP | Interpolated Ground | 37334.2 | -5.17 | 724.82 | 0 | 13.05 | 0 | OK | Ground clear controls. | 84 | 39.16 | 737.87
5842 | TIN-INTERP | Interpolated Ground | 37374.07 | 4.53 | 724.71 | 0 | 24.71 | 0 | OK | Ground clear controls. | 84 | 39.16 | 749.42
5843 | TIN-INTERP | Interpolated Ground | 37374.1 | -6.67 | 724.86 | 0 | 19.21 | 0 | OK | Ground clear controls. | 84 | 39.16 | 744.07
5844 | TIN-INTERP | Interpolated Ground | 37374.1 | -4.67 | 724.85 | 0 | 24.69 | 0 | OK | Ground clear controls. | 84 | 39.16 | 749.54
5845 | TIN-INTERP | Interpolated Ground | 37374.14 | 5.03 | 724.73 | 0 | 14.04 | 0 | OK | Ground clear controls. | 84 | 39.16 | 738.77
5846 | TIN-INTERP | Interpolated Ground | 37374.16 | 6.53 | 724.73 | 0 | 19.57 | 0 | OK | Ground clear controls. | 84 | 39.16 | 744.3
5847 | TIN-INTERP | Interpolated Ground | 37374.2 | -5.17 | 724.85 | 0 | 13.93 | 0 | OK | Ground clear controls. | 84 | 39.16 | 738.78
5848 | TIN-INTERP | Interpolated Ground | 37414.07 | 4.54 | 724.74 | 0 | 26.56 | 0 | OK | Ground clear controls. | 84 | 39.16 | 751.3
5849 | TIN-INTERP | Interpolated Ground | 37414.1 | -6.66 | 724.7 | 0 | 21.24 | 0 | OK | Ground clear controls. | 84 | 39.16 | 745.94
5850 | TIN-INTERP | Interpolated Ground | 37414.1 | -4.66 | 724.74 | 0 | 26.66 | 0 | OK | Ground clear controls. | 84 | 39.16 | 751.4
5851 | TIN-INTERP | Interpolated Ground | 37414.14 | 5.04 | 724.75 | 0 | 15.87 | 0 | OK | Ground clear controls. | 84 | 39.16 | 740.62
5852 | TIN-INTERP | Interpolated Ground | 37414.16 | 6.54 | 724.75 | 0 | 21.39 | 0 | OK | Ground clear controls. | 84 | 39.16 | 746.14
5853 | TIN-INTERP | Interpolated Ground | 37414.2 | -5.16 | 724.74 | 0 | 15.89 | 0 | OK | Ground clear controls. | 84 | 39.16 | 740.63
5854 | TIN-INTERP | Interpolated Ground | 37454.07 | 4.55 | 724.66 | 0 | 29.48 | 0 | OK | Ground clear controls. | 84 | 39.16 | 754.14
5855 | TIN-INTERP | Interpolated Ground | 37454.1 | -6.65 | 724.57 | 0 | 24.18 | 0 | OK | Ground clear controls. | 84 | 39.16 | 748.75
5856 | TIN-INTERP | Interpolated Ground | 37454.1 | -4.65 | 724.57 | 0 | 29.65 | 0 | OK | Ground clear controls. | 84 | 39.16 | 754.22
5857 | TIN-INTERP | Interpolated Ground | 37454.14 | 5.05 | 724.68 | 0 | 18.72 | 0 | OK | Ground clear controls. | 84 | 39.16 | 743.4
5858 | TIN-INTERP | Interpolated Ground | 37454.16 | 6.55 | 724.72 | 0 | 24.19 | 0 | OK | Ground clear controls. | 84 | 39.16 | 748.91
5859 | TIN-INTERP | Interpolated Ground | 37454.2 | -5.15 | 724.58 | 0 | 18.84 | 0 | OK | Ground clear controls. | 84 | 39.16 | 743.42
5860 | TIN-INTERP | Interpolated Ground | 37494.07 | 4.55 | 724.51 | 0 | 33.41 | 0 | OK | Ground clear controls. | 84 | 39.16 | 757.92
5861 | TIN-INTERP | Interpolated Ground | 37494.1 | -6.65 | 724.15 | 0 | 28.35 | 0 | OK | Ground clear controls. | 84 | 39.16 | 752.5
5862 | TIN-INTERP | Interpolated Ground | 37494.1 | -4.65 | 724.28 | 0 | 33.71 | 0 | OK | Ground clear controls. | 84 | 39.16 | 757.99
5863 | TIN-INTERP | Interpolated Ground | 37494.14 | 5.05 | 724.5 | 0 | 22.61 | 0 | OK | Ground clear controls. | 84 | 39.16 | 747.11
5864 | TIN-INTERP | Interpolated Ground | 37494.16 | 6.55 | 724.55 | 0 | 28.08 | 0 | OK | Ground clear controls. | 84 | 39.16 | 752.63
5865 | TIN-INTERP | Interpolated Ground | 37494.2 | -5.15 | 724.28 | 0 | 22.84 | 0 | OK | Ground clear controls. | 84 | 39.16 | 747.12
5866 | TIN-INTERP | Interpolated Ground | 37534.07 | 4.56 | 723.55 | 0 | 39.12 | 0 | OK | Ground clear controls. | 84 | 39.16 | 762.67
5867 | TIN-INTERP | Interpolated Ground | 37534.1 | -6.64 | 723.49 | 0 | 33.74 | 0 | OK | Ground clear controls. | 84 | 39.16 | 757.23
5868 | TIN-INTERP | Interpolated Ground | 37534.1 | -4.64 | 723.55 | 0 | 39.16 | 0 | OK | Ground clear controls. | 84 | 39.16 | 762.71
5869 | TIN-INTERP | Interpolated Ground | 37534.14 | 5.06 | 723.55 | 0 | 28.23 | 0 | OK | Ground clear controls. | 84 | 33.73 | 751.78
5870 | TIN-INTERP | Interpolated Ground | 37534.16 | 6.56 | 723.55 | 0 | 33.73 | 0 | OK | Ground clear controls. | 84 | 33.73 | 757.28
5871 | TIN-INTERP | Interpolated Ground | 37534.2 | -5.14 | 723.53 | 0 | 28.26 | 0 | OK | Ground clear controls. | 84 | 28.26 | 751.79
5872 | TIN-INTERP | Interpolated Ground | 37572.45 | -6.64 | 724.38 | 0 | 38.25 | 0 | OK | Ground clear controls. | 85 | 44.36 | 762.63
5873 | TIN-INTERP | Interpolated Ground | 37572.47 | -4.64 | 724.3 | 0 | 43.83 | 0 | OK | Ground clear controls. | 85 | 44.36 | 768.13
5874 | TIN-INTERP | Interpolated Ground | 37572.47 | -5.14 | 724.3 | 0 | 32.83 | 0 | OK | Ground clear controls. | 85 | 44.36 | 757.13
5875 | TIN-INTERP | Interpolated Ground | 37572.5 | 4.56 | 723.77 | 0 | 44.36 | 0 | OK | Ground clear controls. | 85 | 44.36 | 768.13
5876 | TIN-INTERP | Interpolated Ground | 37572.55 | 5.06 | 723.79 | 0 | 33.34 | 0 | OK | Ground clear controls. | 85 | 39.19 | 757.13
5877 | TIN-INTERP | Interpolated Ground | 37572.57 | 6.56 | 723.7 | 0 | 38.93 | 0 | OK | Ground clear controls. | 85 | 39.19 | 762.63
5878 | TIN-INTERP | Interpolated Ground | 37612.45 | -6.64 | 724.48 | 0 | 32.57 | 0 | OK | Ground clear controls. | 85 | 39.19 | 757.05
5879 | TIN-INTERP | Interpolated Ground | 37612.47 | -5.14 | 724.5 | 0 | 27.12 | 0 | OK | Ground clear controls. | 85 | 39.19 | 751.62
5880 | TIN-INTERP | Interpolated Ground | 37612.47 | -4.64 | 724.51 | 0 | 38.03 | 0 | OK | Ground clear controls. | 85 | 39.19 | 762.54
5881 | TIN-INTERP | Interpolated Ground | 37612.5 | 4.56 | 724.49 | 0 | 37.98 | 0 | OK | Ground clear controls. | 85 | 39.19 | 762.47
5882 | TIN-INTERP | Interpolated Ground | 37612.55 | 5.06 | 724.51 | 0 | 27.1 | 0 | OK | Ground clear controls. | 85 | 39.19 | 751.61
5883 | TIN-INTERP | Interpolated Ground | 37612.57 | 6.56 | 724.51 | 0 | 32.61 | 0 | OK | Ground clear controls. | 85 | 39.19 | 757.12
5884 | TIN-INTERP | Interpolated Ground | 37652.45 | -6.64 | 724.83 | 0 | 27.59 | 0 | OK | Ground clear controls. | 85 | 39.19 | 752.42
5885 | TIN-INTERP | Interpolated Ground | 37652.47 | -5.14 | 724.81 | 0 | 22.23 | 0 | OK | Ground clear controls. | 85 | 39.19 | 747.04
5886 | TIN-INTERP | Interpolated Ground | 37652.47 | -4.64 | 724.82 | 0 | 33.07 | 0 | OK | Ground clear controls. | 85 | 39.19 | 757.89
5887 | TIN-INTERP | Interpolated Ground | 37652.5 | 4.56 | 724.95 | 0 | 32.82 | 0 | OK | Ground clear controls. | 85 | 39.19 | 757.77
5888 | TIN-INTERP | Interpolated Ground | 37652.55 | 5.06 | 724.96 | 0 | 22.07 | 0 | OK | Ground clear controls. | 85 | 39.19 | 747.03
5889 | TIN-INTERP | Interpolated Ground | 37652.57 | 6.56 | 724.96 | 0 | 27.59 | 0 | OK | Ground clear controls. | 85 | 39.19 | 752.55
5890 | TIN-INTERP | Interpolated Ground | 37692.45 | -6.63 | 724.94 | 0 | 23.79 | 0 | OK | Ground clear controls. | 85 | 39.19 | 748.73
5891 | TIN-INTERP | Interpolated Ground | 37692.47 | -5.13 | 724.93 | 0 | 18.47 | 0 | OK | Ground clear controls. | 85 | 39.19 | 743.4
5892 | TIN-INTERP | Interpolated Ground | 37692.47 | -4.63 | 724.94 | 0 | 29.26 | 0 | OK | Ground clear controls. | 85 | 39.19 | 754.2
5893 | TIN-INTERP | Interpolated Ground | 37692.5 | 4.57 | 724.91 | 0 | 29.11 | 0 | OK | Ground clear controls. | 85 | 39.19 | 754.02
5894 | TIN-INTERP | Interpolated Ground | 37692.55 | 5.07 | 724.94 | 0 | 18.44 | 0 | OK | Ground clear controls. | 85 | 39.19 | 743.38
5895 | TIN-INTERP | Interpolated Ground | 37692.57 | 6.57 | 724.98 | 0 | 23.93 | 0 | OK | Ground clear controls. | 85 | 39.19 | 748.91
5896 | TIN-INTERP | Interpolated Ground | 37732.45 | -6.63 | 725.07 | 0 | 20.91 | 0 | OK | Ground clear controls. | 85 | 39.19 | 745.98
5897 | TIN-INTERP | Interpolated Ground | 37732.47 | -5.13 | 725.05 | 0 | 15.64 | 0 | OK | Ground clear controls. | 85 | 39.19 | 740.69
5898 | TIN-INTERP | Interpolated Ground | 37732.47 | -4.63 | 725.07 | 0 | 26.38 | 0 | OK | Ground clear controls. | 85 | 39.19 | 751.45
5899 | TIN-INTERP | Interpolated Ground | 37732.5 | 4.57 | 724.96 | 0 | 26.27 | 0 | OK | Ground clear controls. | 85 | 39.19 | 751.23
5900 | TIN-INTERP | Interpolated Ground | 37732.55 | 5.07 | 724.95 | 0 | 15.72 | 0 | OK | Ground clear controls. | 85 | 39.19 | 740.67
5901 | TIN-INTERP | Interpolated Ground | 37732.57 | 6.57 | 725.02 | 0 | 21.18 | 0 | OK | Ground clear controls. | 85 | 39.19 | 746.2
5902 | TIN-INTERP | Interpolated Ground | 37772.45 | -6.63 | 725.29 | 0 | 18.89 | 0 | OK | Ground clear controls. | 85 | 39.19 | 744.18
5903 | TIN-INTERP | Interpolated Ground | 37772.47 | -5.13 | 725.19 | 0 | 13.72 | 0 | OK | Ground clear controls. | 85 | 39.19 | 738.91
5904 | TIN-INTERP | Interpolated Ground | 37772.47 | -4.63 | 725.21 | 0 | 24.44 | 0 | OK | Ground clear controls. | 85 | 39.19 | 749.65
5905 | TIN-INTERP | Interpolated Ground | 37772.5 | 4.57 | 725.3 | 0 | 24.11 | 0 | OK | Ground clear controls. | 85 | 39.19 | 749.41
5906 | TIN-INTERP | Interpolated Ground | 37772.55 | 5.07 | 725.28 | 0 | 13.62 | 0 | OK | Ground clear controls. | 85 | 39.19 | 738.9
5907 | TIN-INTERP | Interpolated Ground | 37772.57 | 6.57 | 725.31 | 0 | 19.13 | 0 | OK | Ground clear controls. | 85 | 39.19 | 744.44
5908 | TIN-INTERP | Interpolated Ground | 37812.45 | -6.63 | 725.27 | 0 | 18.05 | 0 | OK | Ground clear controls. | 85 | 39.19 | 743.32
5909 | TIN-INTERP | Interpolated Ground | 37812.47 | -5.13 | 725.33 | 0 | 12.74 | 0 | OK | Ground clear controls. | 85 | 39.19 | 738.07
5910 | TIN-INTERP | Interpolated Ground | 37812.47 | -4.63 | 725.34 | 0 | 23.45 | 0 | OK | Ground clear controls. | 85 | 39.19 | 748.79
5911 | TIN-INTERP | Interpolated Ground | 37812.5 | 4.57 | 725.33 | 0 | 23.21 | 0 | OK | Ground clear controls. | 85 | 39.19 | 748.54
5912 | TIN-INTERP | Interpolated Ground | 37812.55 | 5.07 | 725.33 | 0 | 12.73 | 0 | OK | Ground clear controls. | 85 | 39.19 | 738.06
5913 | TIN-INTERP | Interpolated Ground | 37812.57 | 6.57 | 725.35 | 0 | 18.25 | 0 | OK | Ground clear controls. | 85 | 39.19 | 743.6
5914 | TIN-INTERP | Interpolated Ground | 37852.45 | -6.63 | 724.98 | 0 | 18.43 | 0 | OK | Ground clear controls. | 85 | 39.19 | 743.41
5915 | TIN-INTERP | Interpolated Ground | 37852.47 | -5.13 | 724.93 | 0 | 13.23 | 0 | OK | Ground clear controls. | 85 | 39.19 | 738.16
5916 | TIN-INTERP | Interpolated Ground | 37852.47 | -4.63 | 724.93 | 0 | 23.94 | 0 | OK | Ground clear controls. | 85 | 39.19 | 748.87
5917 | TIN-INTERP | Interpolated Ground | 37852.5 | 4.57 | 725.25 | 0 | 23.36 | 0 | OK | Ground clear controls. | 85 | 39.19 | 748.61
5918 | TIN-INTERP | Interpolated Ground | 37852.55 | 5.07 | 725.26 | 0 | 12.88 | 0 | OK | Ground clear controls. | 85 | 39.19 | 738.14
5919 | TIN-INTERP | Interpolated Ground | 37852.57 | 6.57 | 725.32 | 0 | 18.36 | 0 | OK | Ground clear controls. | 85 | 39.19 | 743.68
5920 | TIN-INTERP | Interpolated Ground | 37892.45 | -6.63 | 725.62 | 0 | 18.82 | 0 | OK | Ground clear controls. | 85 | 39.19 | 744.44
5921 | TIN-INTERP | Interpolated Ground | 37892.47 | -5.13 | 725.49 | 0 | 13.69 | 0 | OK | Ground clear controls. | 85 | 39.19 | 739.18
5922 | TIN-INTERP | Interpolated Ground | 37892.47 | -4.63 | 725.51 | 0 | 24.39 | 0 | OK | Ground clear controls. | 85 | 39.19 | 749.9
5923 | TIN-INTERP | Interpolated Ground | 37892.5 | 4.57 | 725.58 | 0 | 24.07 | 0 | OK | Ground clear controls. | 85 | 39.19 | 749.65
5924 | TIN-INTERP | Interpolated Ground | 37892.55 | 5.07 | 725.56 | 0 | 13.61 | 0 | OK | Ground clear controls. | 85 | 39.19 | 739.17
5925 | TIN-INTERP | Interpolated Ground | 37892.57 | 6.57 | 725.54 | 0 | 19.17 | 0 | OK | Ground clear controls. | 85 | 39.19 | 744.71
5926 | TIN-INTERP | Interpolated Ground | 37932.45 | -6.63 | 725.68 | 0 | 20.73 | 0 | OK | Ground clear controls. | 85 | 39.19 | 746.41
5927 | TIN-INTERP | Interpolated Ground | 37932.47 | -5.13 | 725.63 | 0 | 15.51 | 0 | OK | Ground clear controls. | 85 | 39.19 | 741.14
5928 | TIN-INTERP | Interpolated Ground | 37932.47 | -4.63 | 725.68 | 0 | 26.2 | 0 | OK | Ground clear controls. | 85 | 39.19 | 751.88
5929 | TIN-INTERP | Interpolated Ground | 37932.5 | 4.57 | 725.79 | 0 | 25.85 | 0 | OK | Ground clear controls. | 85 | 39.19 | 751.64
5930 | TIN-INTERP | Interpolated Ground | 37932.55 | 5.07 | 725.75 | 0 | 15.37 | 0 | OK | Ground clear controls. | 85 | 39.19 | 741.12
5931 | TIN-INTERP | Interpolated Ground | 37932.57 | 6.57 | 725.79 | 0 | 20.87 | 0 | OK | Ground clear controls. | 85 | 39.19 | 746.66
5932 | TIN-INTERP | Interpolated Ground | 37972.45 | -6.63 | 725.88 | 0 | 23.44 | 0 | OK | Ground clear controls. | 85 | 39.19 | 749.32
5933 | TIN-INTERP | Interpolated Ground | 37972.47 | -5.13 | 725.91 | 0 | 18.11 | 0 | OK | Ground clear controls. | 85 | 39.19 | 744.02
5934 | TIN-INTERP | Interpolated Ground | 37972.47 | -4.63 | 725.92 | 0 | 28.88 | 0 | OK | Ground clear controls. | 85 | 39.19 | 754.8
5935 | TIN-INTERP | Interpolated Ground | 37972.5 | 4.57 | 725.89 | 0 | 28.7 | 0 | OK | Ground clear controls. | 85 | 39.19 | 754.59
5936 | TIN-INTERP | Interpolated Ground | 37972.55 | 5.07 | 725.88 | 0 | 18.13 | 0 | OK | Ground clear controls. | 85 | 39.19 | 744.01
5937 | TIN-INTERP | Interpolated Ground | 37972.57 | 6.57 | 725.95 | 0 | 23.59 | 0 | OK | Ground clear controls. | 85 | 39.19 | 749.54
5938 | TIN-INTERP | Interpolated Ground | 38012.45 | -6.63 | 727.66 | 0 | 25.52 | 0 | OK | Ground clear controls. | 85 | 39.19 | 753.18
5939 | TIN-INTERP | Interpolated Ground | 38012.47 | -5.13 | 727.66 | 0 | 20.18 | 0 | OK | Ground clear controls. | 85 | 39.19 | 747.84
5940 | TIN-INTERP | Interpolated Ground | 38012.47 | -4.63 | 727.67 | 0 | 30.99 | 0 | OK | Ground clear controls. | 85 | 39.19 | 758.66
5941 | TIN-INTERP | Interpolated Ground | 38012.5 | 4.57 | 727.17 | 0 | 31.32 | 0 | OK | Ground clear controls. | 85 | 39.19 | 758.49
5942 | TIN-INTERP | Interpolated Ground | 38012.55 | 5.07 | 727.14 | 0 | 20.7 | 0 | OK | Ground clear controls. | 85 | 39.19 | 747.84
5943 | TIN-INTERP | Interpolated Ground | 38012.57 | 6.57 | 727.02 | 0 | 26.34 | 0 | OK | Ground clear controls. | 85 | 39.19 | 753.36
5944 | TIN-INTERP | Interpolated Ground | 38052.45 | -6.62 | 728.69 | 0 | 29.3 | 0 | OK | Ground clear controls. | 85 | 39.19 | 757.99
5945 | TIN-INTERP | Interpolated Ground | 38052.47 | -5.12 | 728.67 | 0 | 23.93 | 0 | OK | Ground clear controls. | 85 | 39.19 | 752.6
5946 | TIN-INTERP | Interpolated Ground | 38052.47 | -4.62 | 728.65 | 0 | 34.83 | 0 | OK | Ground clear controls. | 85 | 39.19 | 763.48
5947 | TIN-INTERP | Interpolated Ground | 38052.5 | 4.58 | 728.58 | 0 | 34.78 | 0 | OK | Ground clear controls. | 85 | 39.19 | 763.36
5948 | TIN-INTERP | Interpolated Ground | 38052.55 | 5.08 | 728.56 | 0 | 24.03 | 0 | OK | Ground clear controls. | 85 | 39.19 | 752.59
5949 | TIN-INTERP | Interpolated Ground | 38052.57 | 6.58 | 728.53 | 0 | 29.6 | 0 | OK | Ground clear controls. | 85 | 39.19 | 758.13
5950 | TIN-INTERP | Interpolated Ground | 38092.45 | -6.62 | 730.03 | 0 | 33.72 | 0 | OK | Ground clear controls. | 85 | 39.19 | 763.75
5951 | TIN-INTERP | Interpolated Ground | 38092.47 | -5.12 | 730.06 | 0 | 28.25 | 0 | OK | Ground clear controls. | 85 | 39.19 | 758.31
5952 | TIN-INTERP | Interpolated Ground | 38092.47 | -4.62 | 730.05 | 0 | 39.19 | 0 | OK | Ground clear controls. | 85 | 39.19 | 769.24
5953 | TIN-INTERP | Interpolated Ground | 38092.5 | 4.58 | 730.01 | 0 | 39.18 | 0 | OK | Ground clear controls. | 85 | 39.18 | 769.19
5954 | TIN-INTERP | Interpolated Ground | 38092.55 | 5.08 | 730 | 0 | 28.3 | 0 | OK | Ground clear controls. | 85 | 33.82 | 758.3
5955 | TIN-INTERP | Interpolated Ground | 38092.57 | 6.58 | 730 | 0 | 33.82 | 0 | OK | Ground clear controls. | 85 | 33.82 | 763.82
5956 | TIN-INTERP | Interpolated Ground | 38125.37 | -4.62 | 730.49 | 0 | 44.21 | 0 | OK | Ground clear controls. | 86 | 44.24 | 774.7
5957 | TIN-INTERP | Interpolated Ground | 38125.4 | 4.58 | 730.46 | 0 | 44.24 | 0 | OK | Ground clear controls. | 86 | 44.24 | 774.7
5958 | TIN-INTERP | Interpolated Ground | 38125.41 | -6.62 | 730.67 | 0 | 38.53 | 0 | OK | Ground clear controls. | 86 | 40.27 | 769.2
5959 | TIN-INTERP | Interpolated Ground | 38125.44 | 6.58 | 730.54 | 0 | 38.66 | 0 | OK | Ground clear controls. | 86 | 40.27 | 769.2
5960 | TIN-INTERP | Interpolated Ground | 38125.45 | -5.12 | 730.59 | 0 | 33.11 | 0 | OK | Ground clear controls. | 86 | 40.27 | 763.7
5961 | TIN-INTERP | Interpolated Ground | 38125.49 | 5.08 | 730.52 | 0 | 33.18 | 0 | OK | Ground clear controls. | 86 | 40.27 | 763.7
5962 | TIN-INTERP | Interpolated Ground | 38165.37 | -4.62 | 730.93 | 0 | 38.27 | 0 | OK | Ground clear controls. | 86 | 40.27 | 769.2
5963 | TIN-INTERP | Interpolated Ground | 38165.4 | 4.58 | 731.09 | 0 | 38.09 | 0 | OK | Ground clear controls. | 86 | 40.27 | 769.18
5964 | TIN-INTERP | Interpolated Ground | 38165.41 | -6.62 | 730.82 | 0 | 32.94 | 0 | OK | Ground clear controls. | 86 | 40.27 | 763.76
5965 | TIN-INTERP | Interpolated Ground | 38165.44 | 6.58 | 731.11 | 0 | 32.74 | 0 | OK | Ground clear controls. | 86 | 40.27 | 763.85
5966 | TIN-INTERP | Interpolated Ground | 38165.45 | -5.12 | 730.89 | 0 | 27.46 | 0 | OK | Ground clear controls. | 86 | 40.27 | 758.35
5967 | TIN-INTERP | Interpolated Ground | 38165.49 | 5.08 | 731.09 | 0 | 27.29 | 0 | OK | Ground clear controls. | 86 | 40.27 | 758.38
5968 | TIN-INTERP | Interpolated Ground | 38205.37 | -4.62 | 730.41 | 0 | 34.23 | 0 | OK | Ground clear controls. | 86 | 40.27 | 764.64
5969 | TIN-INTERP | Interpolated Ground | 38205.4 | 4.58 | 730.63 | 0 | 33.97 | 0 | OK | Ground clear controls. | 86 | 40.27 | 764.6
5970 | TIN-INTERP | Interpolated Ground | 38205.41 | -6.62 | 730.32 | 0 | 28.94 | 0 | OK | Ground clear controls. | 86 | 40.27 | 759.26
5971 | TIN-INTERP | Interpolated Ground | 38205.44 | 6.58 | 730.66 | 0 | 28.76 | 0 | OK | Ground clear controls. | 86 | 40.27 | 759.42
5972 | TIN-INTERP | Interpolated Ground | 38205.45 | -5.12 | 730.39 | 0 | 23.54 | 0 | OK | Ground clear controls. | 86 | 40.27 | 753.93
5973 | TIN-INTERP | Interpolated Ground | 38205.49 | 5.08 | 730.63 | 0 | 23.35 | 0 | OK | Ground clear controls. | 86 | 40.27 | 753.98
5974 | TIN-INTERP | Interpolated Ground | 38245.37 | -4.62 | 731.29 | 0 | 29.75 | 0 | OK | Ground clear controls. | 86 | 40.27 | 761.04
5975 | TIN-INTERP | Interpolated Ground | 38245.4 | 4.58 | 731.41 | 0 | 29.57 | 0 | OK | Ground clear controls. | 86 | 40.27 | 760.98
5976 | TIN-INTERP | Interpolated Ground | 38245.41 | -6.62 | 731.22 | 0 | 24.48 | 0 | OK | Ground clear controls. | 86 | 40.27 | 755.7
5977 | TIN-INTERP | Interpolated Ground | 38245.44 | 6.58 | 731.41 | 0 | 24.53 | 0 | OK | Ground clear controls. | 86 | 40.27 | 755.94
5978 | TIN-INTERP | Interpolated Ground | 38245.45 | -5.12 | 731.27 | 0 | 19.16 | 0 | OK | Ground clear controls. | 86 | 40.27 | 750.43
5979 | TIN-INTERP | Interpolated Ground | 38245.49 | 5.08 | 731.39 | 0 | 19.11 | 0 | OK | Ground clear controls. | 86 | 40.27 | 750.5
5980 | TIN-INTERP | Interpolated Ground | 38285.37 | -4.62 | 731.45 | 0 | 26.93 | 0 | OK | Ground clear controls. | 86 | 40.27 | 758.38
5981 | TIN-INTERP | Interpolated Ground | 38285.4 | 4.58 | 731.66 | 0 | 26.67 | 0 | OK | Ground clear controls. | 86 | 40.27 | 758.33
5982 | TIN-INTERP | Interpolated Ground | 38285.41 | -6.62 | 731.5 | 0 | 21.6 | 0 | OK | Ground clear controls. | 86 | 40.27 | 753.1
5983 | TIN-INTERP | Interpolated Ground | 38285.44 | 6.58 | 731.77 | 0 | 21.6 | 0 | OK | Ground clear controls. | 86 | 40.27 | 753.37
5984 | TIN-INTERP | Interpolated Ground | 38285.45 | -5.12 | 731.46 | 0 | 16.42 | 0 | OK | Ground clear controls. | 86 | 40.27 | 747.88
5985 | TIN-INTERP | Interpolated Ground | 38285.49 | 5.08 | 731.69 | 0 | 16.26 | 0 | OK | Ground clear controls. | 86 | 40.27 | 747.95
5986 | TIN-INTERP | Interpolated Ground | 38325.37 | -4.61 | 732.58 | 0 | 24.09 | 0 | OK | Ground clear controls. | 86 | 40.27 | 756.67
5987 | TIN-INTERP | Interpolated Ground | 38325.4 | 4.59 | 732.63 | 0 | 24 | 0 | OK | Ground clear controls. | 86 | 40.27 | 756.63
5988 | TIN-INTERP | Interpolated Ground | 38325.41 | -6.61 | 732.38 | 0 | 19.03 | 0 | OK | Ground clear controls. | 86 | 40.27 | 751.41
5989 | TIN-INTERP | Interpolated Ground | 38325.44 | 6.59 | 732.61 | 0 | 19.12 | 0 | OK | Ground clear controls. | 86 | 40.27 | 751.73
5990 | TIN-INTERP | Interpolated Ground | 38325.45 | -5.11 | 732.54 | 0 | 13.69 | 0 | OK | Ground clear controls. | 86 | 40.27 | 746.23
5991 | TIN-INTERP | Interpolated Ground | 38325.49 | 5.09 | 732.58 | 0 | 13.74 | 0 | OK | Ground clear controls. | 86 | 40.27 | 746.32
5992 | TIN-INTERP | Interpolated Ground | 38365.37 | -4.61 | 733.05 | 0 | 22.86 | 0 | OK | Ground clear controls. | 86 | 40.27 | 755.91
5993 | TIN-INTERP | Interpolated Ground | 38365.4 | 4.59 | 732.49 | 0 | 23.39 | 0 | OK | Ground clear controls. | 86 | 40.27 | 755.88
5994 | TIN-INTERP | Interpolated Ground | 38365.41 | -6.61 | 733.09 | 0 | 17.6 | 0 | OK | Ground clear controls. | 86 | 40.27 | 750.69
5995 | TIN-INTERP | Interpolated Ground | 38365.44 | 6.59 | 732.46 | 0 | 18.56 | 0 | OK | Ground clear controls. | 86 | 40.27 | 751.02
5996 | TIN-INTERP | Interpolated Ground | 38365.45 | -5.11 | 733.06 | 0 | 12.46 | 0 | OK | Ground clear controls. | 86 | 40.27 | 745.52
5997 | TIN-INTERP | Interpolated Ground | 38365.49 | 5.09 | 732.49 | 0 | 13.13 | 0 | OK | Ground clear controls. | 86 | 40.27 | 745.62
5998 | TIN-INTERP | Interpolated Ground | 38405.37 | -4.61 | 732.66 | 0 | 23.43 | 0 | OK | Ground clear controls. | 86 | 40.27 | 756.09
5999 | TIN-INTERP | Interpolated Ground | 38405.4 | 4.59 | 732.5 | 0 | 23.58 | 0 | OK | Ground clear controls. | 86 | 40.27 | 756.08
6000 | TIN-INTERP | Interpolated Ground | 38405.41 | -6.61 | 732.67 | 0 | 18.23 | 0 | OK | Ground clear controls. | 86 | 40.27 | 750.9
6001 | TIN-INTERP | Interpolated Ground | 38405.44 | 6.59 | 732.54 | 0 | 18.69 | 0 | OK | Ground clear controls. | 86 | 40.27 | 751.23
6002 | TIN-INTERP | Interpolated Ground | 38405.45 | -5.11 | 732.67 | 0 | 13.06 | 0 | OK | Ground clear controls. | 86 | 40.27 | 745.73
6003 | TIN-INTERP | Interpolated Ground | 38405.49 | 5.09 | 732.48 | 0 | 13.35 | 0 | OK | Ground clear controls. | 86 | 40.27 | 745.83
6004 | TIN-INTERP | Interpolated Ground | 38445.37 | -4.61 | 732.94 | 0 | 24.27 | 0 | OK | Ground clear controls. | 86 | 40.27 | 757.21
6005 | TIN-INTERP | Interpolated Ground | 38445.4 | 4.59 | 732.8 | 0 | 24.43 | 0 | OK | Ground clear controls. | 86 | 40.27 | 757.23
6006 | TIN-INTERP | Interpolated Ground | 38445.41 | -6.61 | 732.94 | 0 | 19.09 | 0 | OK | Ground clear controls. | 86 | 40.27 | 752.03
6007 | TIN-INTERP | Interpolated Ground | 38445.44 | 6.59 | 732.81 | 0 | 19.55 | 0 | OK | Ground clear controls. | 86 | 40.27 | 752.36
6008 | TIN-INTERP | Interpolated Ground | 38445.45 | -5.11 | 732.95 | 0 | 13.91 | 0 | OK | Ground clear controls. | 86 | 40.27 | 746.86
6009 | TIN-INTERP | Interpolated Ground | 38445.49 | 5.09 | 732.79 | 0 | 14.17 | 0 | OK | Ground clear controls. | 86 | 40.27 | 746.96
6010 | TIN-INTERP | Interpolated Ground | 38485.37 | -4.61 | 734.15 | 0 | 25.15 | 0 | OK | Ground clear controls. | 86 | 40.27 | 759.3
6011 | TIN-INTERP | Interpolated Ground | 38485.4 | 4.59 | 733.79 | 0 | 25.55 | 0 | OK | Ground clear controls. | 86 | 40.27 | 759.34
6012 | TIN-INTERP | Interpolated Ground | 38485.41 | -6.61 | 734.17 | 0 | 19.95 | 0 | OK | Ground clear controls. | 86 | 40.27 | 754.12
6013 | TIN-INTERP | Interpolated Ground | 38485.44 | 6.59 | 733.74 | 0 | 20.68 | 0 | OK | Ground clear controls. | 86 | 40.27 | 754.42
6014 | TIN-INTERP | Interpolated Ground | 38485.45 | -5.11 | 734.15 | 0 | 14.78 | 0 | OK | Ground clear controls. | 86 | 40.27 | 748.93
6015 | TIN-INTERP | Interpolated Ground | 38485.49 | 5.09 | 733.78 | 0 | 15.24 | 0 | OK | Ground clear controls. | 86 | 40.27 | 749.02
6016 | TIN-INTERP | Interpolated Ground | 38525.37 | -4.6 | 734.57 | 0 | 27.76 | 0 | OK | Ground clear controls. | 86 | 40.27 | 762.33
6017 | TIN-INTERP | Interpolated Ground | 38525.4 | 4.6 | 734.58 | 0 | 27.83 | 0 | OK | Ground clear controls. | 86 | 40.27 | 762.41
6018 | TIN-INTERP | Interpolated Ground | 38525.41 | -6.6 | 734.59 | 0 | 22.56 | 0 | OK | Ground clear controls. | 86 | 40.27 | 757.15
6019 | TIN-INTERP | Interpolated Ground | 38525.44 | 6.6 | 734.64 | 0 | 22.78 | 0 | OK | Ground clear controls. | 86 | 40.27 | 757.42
6020 | TIN-INTERP | Interpolated Ground | 38525.45 | -5.1 | 734.57 | 0 | 17.34 | 0 | OK | Ground clear controls. | 86 | 40.27 | 751.91
6021 | TIN-INTERP | Interpolated Ground | 38525.49 | 5.1 | 734.58 | 0 | 17.42 | 0 | OK | Ground clear controls. | 86 | 40.27 | 752
6022 | TIN-INTERP | Interpolated Ground | 38565.37 | -4.6 | 735.39 | 0 | 30.9 | 0 | OK | Ground clear controls. | 86 | 40.27 | 766.29
6023 | TIN-INTERP | Interpolated Ground | 38565.4 | 4.6 | 735.94 | 0 | 30.49 | 0 | OK | Ground clear controls. | 86 | 40.27 | 766.43
6024 | TIN-INTERP | Interpolated Ground | 38565.41 | -6.6 | 735.36 | 0 | 25.76 | 0 | OK | Ground clear controls. | 86 | 40.27 | 761.12
6025 | TIN-INTERP | Interpolated Ground | 38565.44 | 6.6 | 736.1 | 0 | 25.23 | 0 | OK | Ground clear controls. | 86 | 40.27 | 761.33
6026 | TIN-INTERP | Interpolated Ground | 38565.45 | -5.1 | 735.39 | 0 | 20.44 | 0 | OK | Ground clear controls. | 86 | 40.27 | 755.83
6027 | TIN-INTERP | Interpolated Ground | 38565.49 | 5.1 | 735.98 | 0 | 19.91 | 0 | OK | Ground clear controls. | 86 | 40.27 | 755.89
6028 | TIN-INTERP | Interpolated Ground | 38605.37 | -4.6 | 735.87 | 0 | 35.34 | 0 | OK | Ground clear controls. | 86 | 40.27 | 771.21
6029 | TIN-INTERP | Interpolated Ground | 38605.4 | 4.6 | 736.5 | 0 | 34.91 | 0 | OK | Ground clear controls. | 86 | 40.27 | 771.41
6030 | TIN-INTERP | Interpolated Ground | 38605.41 | -6.6 | 735.84 | 0 | 30.2 | 0 | OK | Ground clear controls. | 86 | 40.27 | 766.04
6031 | TIN-INTERP | Interpolated Ground | 38605.44 | 6.6 | 736.63 | 0 | 29.55 | 0 | OK | Ground clear controls. | 86 | 40.27 | 766.18
6032 | TIN-INTERP | Interpolated Ground | 38605.45 | -5.1 | 735.86 | 0 | 24.82 | 0 | OK | Ground clear controls. | 86 | 40.27 | 760.68
6033 | TIN-INTERP | Interpolated Ground | 38605.49 | 5.1 | 736.57 | 0 | 24.16 | 0 | OK | Ground clear controls. | 86 | 40.27 | 760.73
6034 | TIN-INTERP | Interpolated Ground | 38645.37 | -4.6 | 736.95 | 0 | 40.14 | 0 | OK | Ground clear controls. | 86 | 40.27 | 777.09
6035 | TIN-INTERP | Interpolated Ground | 38645.4 | 4.6 | 737.08 | 0 | 40.27 | 0 | OK | Ground clear controls. | 86 | 40.27 | 777.35
6036 | TIN-INTERP | Interpolated Ground | 38645.41 | -6.6 | 737.01 | 0 | 34.89 | 0 | OK | Ground clear controls. | 86 | 34.98 | 771.9
6037 | TIN-INTERP | Interpolated Ground | 38645.44 | 6.6 | 736.98 | 0 | 34.98 | 0 | OK | Ground clear controls. | 86 | 34.98 | 771.96
6038 | TIN-INTERP | Interpolated Ground | 38645.45 | -5.1 | 736.96 | 0 | 29.5 | 0 | OK | Ground clear controls. | 86 | 29.5 | 766.46
6039 | TIN-INTERP | Interpolated Ground | 38645.49 | 5.1 | 737.07 | 0 | 29.41 | 0 | OK | Ground clear controls. | 86 | 29.41 | 766.48
6040 | TIN-INTERP | Interpolated Ground | 38664.68 | 5.1 | 736.97 | 0 | 32.6 | 0 | OK | Ground clear controls. | 87 | 43.7 | 769.57
6041 | TIN-INTERP | Interpolated Ground | 38664.68 | 6.6 | 737.01 | 0 | 38.06 | 0 | OK | Ground clear controls. | 87 | 43.7 | 775.07
6042 | TIN-INTERP | Interpolated Ground | 38664.71 | -5.1 | 736.96 | 0 | 32.61 | 0 | OK | Ground clear controls. | 87 | 43.7 | 769.57
6043 | TIN-INTERP | Interpolated Ground | 38664.73 | -6.6 | 737.04 | 0 | 38.03 | 0 | OK | Ground clear controls. | 87 | 43.7 | 775.07
6044 | TIN-INTERP | Interpolated Ground | 38664.73 | -4.6 | 736.9 | 0 | 43.38 | 0 | OK | Ground clear controls. | 87 | 43.7 | 780.28
6045 | TIN-INTERP | Interpolated Ground | 38664.75 | 4.6 | 736.94 | 0 | 43.63 | 0 | OK | Ground clear controls. | 87 | 43.7 | 780.57
6046 | TIN-INTERP | Interpolated Ground | 38704.68 | 5.1 | 736.96 | 0 | 27.64 | 0 | OK | Ground clear controls. | 87 | 43.7 | 764.6
6047 | TIN-INTERP | Interpolated Ground | 38704.68 | 6.6 | 736.96 | 0 | 33.12 | 0 | OK | Ground clear controls. | 87 | 43.7 | 770.08
6048 | TIN-INTERP | Interpolated Ground | 38704.71 | -5.1 | 737.03 | 0 | 27.58 | 0 | OK | Ground clear controls. | 87 | 43.7 | 764.61
6049 | TIN-INTERP | Interpolated Ground | 38704.73 | -6.6 | 737.06 | 0 | 32.97 | 0 | OK | Ground clear controls. | 87 | 43.7 | 770.03
6050 | TIN-INTERP | Interpolated Ground | 38704.73 | -4.6 | 737 | 0 | 38.23 | 0 | OK | Ground clear controls. | 87 | 43.7 | 775.23
6051 | TIN-INTERP | Interpolated Ground | 38704.75 | 4.6 | 736.95 | 0 | 38.51 | 0 | OK | Ground clear controls. | 87 | 43.7 | 775.46
6052 | TIN-INTERP | Interpolated Ground | 38744.68 | 5.09 | 737.52 | 0 | 23.03 | 0 | OK | Ground clear controls. | 87 | 43.7 | 760.55
6053 | TIN-INTERP | Interpolated Ground | 38744.68 | 6.59 | 737.6 | 0 | 28.42 | 0 | OK | Ground clear controls. | 87 | 43.7 | 766.02
6054 | TIN-INTERP | Interpolated Ground | 38744.71 | -5.11 | 737.35 | 0 | 23.21 | 0 | OK | Ground clear controls. | 87 | 43.7 | 760.56
6055 | TIN-INTERP | Interpolated Ground | 38744.73 | -6.61 | 737.35 | 0 | 28.56 | 0 | OK | Ground clear controls. | 87 | 43.7 | 765.91
6056 | TIN-INTERP | Interpolated Ground | 38744.73 | -4.61 | 737.35 | 0 | 33.76 | 0 | OK | Ground clear controls. | 87 | 43.7 | 771.11
6057 | TIN-INTERP | Interpolated Ground | 38744.75 | 4.59 | 737.51 | 0 | 33.78 | 0 | OK | Ground clear controls. | 87 | 43.7 | 771.29
6058 | TIN-INTERP | Interpolated Ground | 38784.68 | 5.09 | 737.83 | 0 | 19.59 | 0 | OK | Ground clear controls. | 87 | 43.7 | 757.42
6059 | TIN-INTERP | Interpolated Ground | 38784.68 | 6.59 | 737.83 | 0 | 25.04 | 0 | OK | Ground clear controls. | 87 | 43.7 | 762.87
6060 | TIN-INTERP | Interpolated Ground | 38784.71 | -5.11 | 737.78 | 0 | 19.65 | 0 | OK | Ground clear controls. | 87 | 43.7 | 757.43
6061 | TIN-INTERP | Interpolated Ground | 38784.73 | -6.61 | 737.77 | 0 | 24.97 | 0 | OK | Ground clear controls. | 87 | 43.7 | 762.74
6062 | TIN-INTERP | Interpolated Ground | 38784.73 | -4.61 | 737.79 | 0 | 30.14 | 0 | OK | Ground clear controls. | 87 | 43.7 | 767.93
6063 | TIN-INTERP | Interpolated Ground | 38784.75 | 4.59 | 737.83 | 0 | 30.24 | 0 | OK | Ground clear controls. | 87 | 43.7 | 768.07
6064 | TIN-INTERP | Interpolated Ground | 38824.68 | 5.09 | 738.51 | 0 | 16.7 | 0 | OK | Ground clear controls. | 87 | 43.7 | 755.21
6065 | TIN-INTERP | Interpolated Ground | 38824.68 | 6.59 | 738.47 | 0 | 22.19 | 0 | OK | Ground clear controls. | 87 | 43.7 | 760.66
6066 | TIN-INTERP | Interpolated Ground | 38824.71 | -5.11 | 738.57 | 0 | 16.65 | 0 | OK | Ground clear controls. | 87 | 43.7 | 755.22
6067 | TIN-INTERP | Interpolated Ground | 38824.73 | -6.61 | 738.51 | 0 | 21.98 | 0 | OK | Ground clear controls. | 87 | 43.7 | 760.49
6068 | TIN-INTERP | Interpolated Ground | 38824.73 | -4.61 | 738.61 | 0 | 27.08 | 0 | OK | Ground clear controls. | 87 | 43.7 | 765.69
6069 | TIN-INTERP | Interpolated Ground | 38824.75 | 4.59 | 738.5 | 0 | 27.29 | 0 | OK | Ground clear controls. | 87 | 43.7 | 765.79
6070 | TIN-INTERP | Interpolated Ground | 38864.68 | 5.09 | 739.73 | 0 | 14.2 | 0 | OK | Ground clear controls. | 87 | 43.7 | 753.93
6071 | TIN-INTERP | Interpolated Ground | 38864.68 | 6.59 | 739.73 | 0 | 19.63 | 0 | OK | Ground clear controls. | 87 | 43.7 | 759.36
6072 | TIN-INTERP | Interpolated Ground | 38864.71 | -5.11 | 739.64 | 0 | 14.3 | 0 | OK | Ground clear controls. | 87 | 43.7 | 753.94
6073 | TIN-INTERP | Interpolated Ground | 38864.73 | -6.61 | 739.56 | 0 | 19.63 | 0 | OK | Ground clear controls. | 87 | 43.7 | 759.19
6074 | TIN-INTERP | Interpolated Ground | 38864.73 | -4.61 | 739.67 | 0 | 24.72 | 0 | OK | Ground clear controls. | 87 | 43.7 | 764.39
6075 | TIN-INTERP | Interpolated Ground | 38864.75 | 4.59 | 739.73 | 0 | 24.73 | 0 | OK | Ground clear controls. | 87 | 43.7 | 764.46
6076 | TIN-INTERP | Interpolated Ground | 38904.68 | 5.08 | 740.4 | 0 | 13.15 | 0 | OK | Ground clear controls. | 87 | 43.7 | 753.55
6077 | TIN-INTERP | Interpolated Ground | 38904.68 | 6.58 | 740.35 | 0 | 18.63 | 0 | OK | Ground clear controls. | 87 | 43.7 | 758.98
6078 | TIN-INTERP | Interpolated Ground | 38904.71 | -5.12 | 740.45 | 0 | 13.11 | 0 | OK | Ground clear controls. | 87 | 43.7 | 753.56
6079 | TIN-INTERP | Interpolated Ground | 38904.73 | -6.62 | 740.53 | 0 | 18.27 | 0 | OK | Ground clear controls. | 87 | 43.7 | 758.8
6080 | TIN-INTERP | Interpolated Ground | 38904.73 | -4.62 | 740.52 | 0 | 23.5 | 0 | OK | Ground clear controls. | 87 | 43.7 | 764.02
6081 | TIN-INTERP | Interpolated Ground | 38904.75 | 4.58 | 740.4 | 0 | 23.66 | 0 | OK | Ground clear controls. | 87 | 43.7 | 764.06
6082 | TIN-INTERP | Interpolated Ground | 38944.68 | 5.08 | 741.37 | 0 | 12.73 | 0 | OK | Ground clear controls. | 87 | 43.7 | 754.1
6083 | TIN-INTERP | Interpolated Ground | 38944.68 | 6.58 | 741.4 | 0 | 18.14 | 0 | OK | Ground clear controls. | 87 | 43.7 | 759.54
6084 | TIN-INTERP | Interpolated Ground | 38944.71 | -5.12 | 741.45 | 0 | 12.67 | 0 | OK | Ground clear controls. | 87 | 43.7 | 754.12
6085 | TIN-INTERP | Interpolated Ground | 38944.73 | -6.62 | 741.42 | 0 | 17.93 | 0 | OK | Ground clear controls. | 87 | 43.7 | 759.35
6086 | TIN-INTERP | Interpolated Ground | 38944.73 | -4.62 | 741.45 | 0 | 23.14 | 0 | OK | Ground clear controls. | 87 | 43.7 | 764.59
6087 | TIN-INTERP | Interpolated Ground | 38944.75 | 4.58 | 741.32 | 0 | 23.28 | 0 | OK | Ground clear controls. | 87 | 43.7 | 764.6
6088 | TIN-INTERP | Interpolated Ground | 38984.68 | 5.08 | 741.95 | 0 | 13.61 | 0 | OK | Ground clear controls. | 87 | 43.7 | 755.56
6089 | TIN-INTERP | Interpolated Ground | 38984.68 | 6.58 | 741.95 | 0 | 19.05 | 0 | OK | Ground clear controls. | 87 | 43.7 | 761
6090 | TIN-INTERP | Interpolated Ground | 38984.71 | -5.12 | 742.06 | 0 | 13.53 | 0 | OK | Ground clear controls. | 87 | 43.7 | 755.59
6091 | TIN-INTERP | Interpolated Ground | 38984.73 | -6.62 | 742.03 | 0 | 18.8 | 0 | OK | Ground clear controls. | 87 | 43.7 | 760.83
6092 | TIN-INTERP | Interpolated Ground | 38984.73 | -4.62 | 742.09 | 0 | 24 | 0 | OK | Ground clear controls. | 87 | 43.7 | 766.09
6093 | TIN-INTERP | Interpolated Ground | 38984.75 | 4.58 | 741.96 | 0 | 24.13 | 0 | OK | Ground clear controls. | 87 | 43.7 | 766.09
6094 | TIN-INTERP | Interpolated Ground | 39024.68 | 5.07 | 742.41 | 0 | 15.54 | 0 | OK | Ground clear controls. | 87 | 43.7 | 757.95
6095 | TIN-INTERP | Interpolated Ground | 39024.68 | 6.57 | 742.43 | 0 | 20.96 | 0 | OK | Ground clear controls. | 87 | 43.7 | 763.39
6096 | TIN-INTERP | Interpolated Ground | 39024.71 | -5.13 | 742.3 | 0 | 15.67 | 0 | OK | Ground clear controls. | 87 | 43.7 | 757.97
6097 | TIN-INTERP | Interpolated Ground | 39024.73 | -6.63 | 742.31 | 0 | 20.93 | 0 | OK | Ground clear controls. | 87 | 43.7 | 763.24
6098 | TIN-INTERP | Interpolated Ground | 39024.73 | -4.63 | 742.3 | 0 | 26.24 | 0 | OK | Ground clear controls. | 87 | 43.7 | 768.54
6099 | TIN-INTERP | Interpolated Ground | 39024.75 | 4.57 | 742.4 | 0 | 26.13 | 0 | OK | Ground clear controls. | 87 | 43.7 | 768.53
6100 | TIN-INTERP | Interpolated Ground | 39064.68 | 5.07 | 742.88 | 0 | 18.37 | 0 | OK | Ground clear controls. | 87 | 43.7 | 761.25
6101 | TIN-INTERP | Interpolated Ground | 39064.68 | 6.57 | 742.88 | 0 | 23.82 | 0 | OK | Ground clear controls. | 87 | 43.7 | 766.7
6102 | TIN-INTERP | Interpolated Ground | 39064.71 | -5.13 | 742.99 | 0 | 18.28 | 0 | OK | Ground clear controls. | 87 | 43.7 | 761.27
6103 | TIN-INTERP | Interpolated Ground | 39064.73 | -6.63 | 743 | 0 | 23.58 | 0 | OK | Ground clear controls. | 87 | 43.7 | 766.58
6104 | TIN-INTERP | Interpolated Ground | 39064.73 | -4.63 | 742.99 | 0 | 28.93 | 0 | OK | Ground clear controls. | 87 | 43.7 | 771.92
6105 | TIN-INTERP | Interpolated Ground | 39064.75 | 4.57 | 742.88 | 0 | 29.02 | 0 | OK | Ground clear controls. | 87 | 43.7 | 771.9
6106 | TIN-INTERP | Interpolated Ground | 39104.68 | 5.07 | 742.93 | 0 | 22.55 | 0 | OK | Ground clear controls. | 87 | 43.7 | 765.48
6107 | TIN-INTERP | Interpolated Ground | 39104.68 | 6.57 | 742.91 | 0 | 28.03 | 0 | OK | Ground clear controls. | 87 | 43.7 | 770.94
6108 | TIN-INTERP | Interpolated Ground | 39104.71 | -5.13 | 742.84 | 0 | 22.66 | 0 | OK | Ground clear controls. | 87 | 43.7 | 765.5
6109 | TIN-INTERP | Interpolated Ground | 39104.73 | -6.63 | 742.9 | 0 | 27.96 | 0 | OK | Ground clear controls. | 87 | 43.7 | 770.86
6110 | TIN-INTERP | Interpolated Ground | 39104.73 | -4.63 | 742.88 | 0 | 33.36 | 0 | OK | Ground clear controls. | 87 | 43.7 | 776.24
6111 | TIN-INTERP | Interpolated Ground | 39104.75 | 4.57 | 742.95 | 0 | 33.27 | 0 | OK | Ground clear controls. | 87 | 43.7 | 776.22
6112 | TIN-INTERP | Interpolated Ground | 39144.68 | 5.06 | 743.93 | 0 | 26.69 | 0 | OK | Ground clear controls. | 87 | 43.7 | 770.62
6113 | TIN-INTERP | Interpolated Ground | 39144.68 | 6.56 | 743.93 | 0 | 32.17 | 0 | OK | Ground clear controls. | 87 | 43.7 | 776.1
6114 | TIN-INTERP | Interpolated Ground | 39144.71 | -5.14 | 743.94 | 0 | 26.71 | 0 | OK | Ground clear controls. | 87 | 43.7 | 770.65
6115 | TIN-INTERP | Interpolated Ground | 39144.73 | -6.64 | 744 | 0 | 32.08 | 0 | OK | Ground clear controls. | 87 | 43.7 | 776.08
6116 | TIN-INTERP | Interpolated Ground | 39144.73 | -4.64 | 743.92 | 0 | 37.59 | 0 | OK | Ground clear controls. | 87 | 43.7 | 781.51
6117 | TIN-INTERP | Interpolated Ground | 39144.75 | 4.56 | 743.94 | 0 | 37.55 | 0 | OK | Ground clear controls. | 87 | 43.7 | 781.49
6118 | TIN-INTERP | Interpolated Ground | 39184.68 | 5.06 | 744.05 | 0 | 32.65 | 0 | OK | Ground clear controls. | 87 | 43.7 | 776.7
6119 | TIN-INTERP | Interpolated Ground | 39184.68 | 6.56 | 744.14 | 0 | 38.06 | 0 | OK | Ground clear controls. | 87 | 43.7 | 782.2
6120 | TIN-INTERP | Interpolated Ground | 39184.71 | -5.14 | 744.09 | 0 | 32.63 | 0 | OK | Ground clear controls. | 87 | 43.7 | 776.72
6121 | TIN-INTERP | Interpolated Ground | 39184.73 | -6.64 | 744.12 | 0 | 38.11 | 0 | OK | Ground clear controls. | 87 | 43.7 | 782.23
6122 | TIN-INTERP | Interpolated Ground | 39184.73 | -4.64 | 744.04 | 0 | 43.68 | 0 | OK | Ground clear controls. | 87 | 43.7 | 787.72
6123 | TIN-INTERP | Interpolated Ground | 39184.75 | 4.56 | 744.01 | 0 | 43.7 | 0 | OK | Ground clear controls. | 87 | 43.7 | 787.71
6124 | TIN-INTERP | Interpolated Ground | 39185.71 | -6.64 | 744.12 | 0 | 38.27 | 0 | OK | Ground clear controls. | 88 | 43.84 | 782.39
6125 | TIN-INTERP | Interpolated Ground | 39185.76 | -5.14 | 744.08 | 0 | 32.81 | 0 | OK | Ground clear controls. | 88 | 43.84 | 776.89
6126 | TIN-INTERP | Interpolated Ground | 39185.77 | -4.64 | 744.05 | 0 | 43.84 | 0 | OK | Ground clear controls. | 88 | 43.84 | 787.89
6127 | TIN-INTERP | Interpolated Ground | 39185.84 | 5.06 | 744.08 | 0 | 32.81 | 0 | OK | Ground clear controls. | 88 | 43.84 | 776.89
6128 | TIN-INTERP | Interpolated Ground | 39185.86 | 6.56 | 744.14 | 0 | 38.25 | 0 | OK | Ground clear controls. | 88 | 43.84 | 782.39
6129 | TIN-INTERP | Interpolated Ground | 39185.86 | 4.56 | 744.05 | 0 | 43.84 | 0 | OK | Ground clear controls. | 88 | 43.84 | 787.89
6130 | TIN-INTERP | Interpolated Ground | 39225.71 | -6.64 | 744.59 | 0 | 32.11 | 0 | OK | Ground clear controls. | 88 | 42.65 | 776.7
6131 | TIN-INTERP | Interpolated Ground | 39225.76 | -5.14 | 744.55 | 0 | 26.75 | 0 | OK | Ground clear controls. | 88 | 42.65 | 771.3
6132 | TIN-INTERP | Interpolated Ground | 39225.77 | -4.64 | 744.54 | 0 | 37.65 | 0 | OK | Ground clear controls. | 88 | 42.65 | 782.19
6133 | TIN-INTERP | Interpolated Ground | 39225.84 | 5.06 | 744.53 | 0 | 26.77 | 0 | OK | Ground clear controls. | 88 | 42.65 | 771.3
6134 | TIN-INTERP | Interpolated Ground | 39225.86 | 6.56 | 744.52 | 0 | 32.26 | 0 | OK | Ground clear controls. | 88 | 42.65 | 776.78
6135 | TIN-INTERP | Interpolated Ground | 39225.86 | 4.56 | 744.55 | 0 | 37.62 | 0 | OK | Ground clear controls. | 88 | 42.65 | 782.17
6136 | TIN-INTERP | Interpolated Ground | 39265.71 | -6.63 | 744.41 | 0 | 27.51 | 0 | OK | Ground clear controls. | 88 | 42.65 | 771.92
6137 | TIN-INTERP | Interpolated Ground | 39265.76 | -5.13 | 744.38 | 0 | 22.25 | 0 | OK | Ground clear controls. | 88 | 42.65 | 766.63
6138 | TIN-INTERP | Interpolated Ground | 39265.77 | -4.63 | 744.36 | 0 | 33.05 | 0 | OK | Ground clear controls. | 88 | 42.65 | 777.41
6139 | TIN-INTERP | Interpolated Ground | 39265.84 | 5.07 | 744.39 | 0 | 22.22 | 0 | OK | Ground clear controls. | 88 | 42.65 | 766.61
6140 | TIN-INTERP | Interpolated Ground | 39265.86 | 6.57 | 744.37 | 0 | 27.71 | 0 | OK | Ground clear controls. | 88 | 42.65 | 772.08
6141 | TIN-INTERP | Interpolated Ground | 39265.86 | 4.57 | 744.38 | 0 | 32.99 | 0 | OK | Ground clear controls. | 88 | 42.65 | 777.37
6142 | TIN-INTERP | Interpolated Ground | 39305.71 | -6.63 | 744.41 | 0 | 23.69 | 0 | OK | Ground clear controls. | 88 | 42.65 | 768.1
6143 | TIN-INTERP | Interpolated Ground | 39305.76 | -5.13 | 744.4 | 0 | 18.48 | 0 | OK | Ground clear controls. | 88 | 42.65 | 762.88
6144 | TIN-INTERP | Interpolated Ground | 39305.77 | -4.63 | 744.39 | 0 | 29.2 | 0 | OK | Ground clear controls. | 88 | 42.65 | 773.59
6145 | TIN-INTERP | Interpolated Ground | 39305.84 | 5.07 | 744.42 | 0 | 18.44 | 0 | OK | Ground clear controls. | 88 | 42.65 | 762.86
6146 | TIN-INTERP | Interpolated Ground | 39305.86 | 6.57 | 744.36 | 0 | 23.96 | 0 | OK | Ground clear controls. | 88 | 42.65 | 768.32
6147 | TIN-INTERP | Interpolated Ground | 39305.86 | 4.57 | 744.41 | 0 | 29.12 | 0 | OK | Ground clear controls. | 88 | 42.65 | 773.53
6148 | TIN-INTERP | Interpolated Ground | 39345.71 | -6.63 | 743.98 | 0 | 21.22 | 0 | OK | Ground clear controls. | 88 | 42.65 | 765.2
6149 | TIN-INTERP | Interpolated Ground | 39345.76 | -5.13 | 743.95 | 0 | 16.08 | 0 | OK | Ground clear controls. | 88 | 42.65 | 760.03
6150 | TIN-INTERP | Interpolated Ground | 39345.77 | -4.63 | 743.94 | 0 | 26.75 | 0 | OK | Ground clear controls. | 88 | 42.65 | 770.69
6151 | TIN-INTERP | Interpolated Ground | 39345.84 | 5.07 | 743.88 | 0 | 16.13 | 0 | OK | Ground clear controls. | 88 | 42.65 | 760.01
6152 | TIN-INTERP | Interpolated Ground | 39345.86 | 6.57 | 743.87 | 0 | 21.59 | 0 | OK | Ground clear controls. | 88 | 42.65 | 765.46
6153 | TIN-INTERP | Interpolated Ground | 39345.86 | 4.57 | 743.87 | 0 | 26.74 | 0 | OK | Ground clear controls. | 88 | 42.65 | 770.61
6154 | TIN-INTERP | Interpolated Ground | 39385.71 | -6.62 | 743.74 | 0 | 19.5 | 0 | OK | Ground clear controls. | 88 | 42.65 | 763.24
6155 | TIN-INTERP | Interpolated Ground | 39385.76 | -5.12 | 743.74 | 0 | 14.36 | 0 | OK | Ground clear controls. | 88 | 42.65 | 758.1
6156 | TIN-INTERP | Interpolated Ground | 39385.77 | -4.62 | 743.75 | 0 | 24.98 | 0 | OK | Ground clear controls. | 88 | 42.65 | 768.73
6157 | TIN-INTERP | Interpolated Ground | 39385.84 | 5.07 | 743.57 | 0 | 14.52 | 0 | OK | Ground clear controls. | 88 | 42.65 | 758.09
6158 | TIN-INTERP | Interpolated Ground | 39385.86 | 6.57 | 743.5 | 0 | 20.03 | 0 | OK | Ground clear controls. | 88 | 42.65 | 763.53
6159 | TIN-INTERP | Interpolated Ground | 39385.86 | 4.57 | 743.58 | 0 | 25.07 | 0 | OK | Ground clear controls. | 88 | 42.65 | 768.65
6160 | TIN-INTERP | Interpolated Ground | 39425.71 | -6.62 | 743.83 | 0 | 18.38 | 0 | OK | Ground clear controls. | 88 | 42.65 | 762.21
6161 | TIN-INTERP | Interpolated Ground | 39425.76 | -5.12 | 743.83 | 0 | 13.26 | 0 | OK | Ground clear controls. | 88 | 42.65 | 757.09
6162 | TIN-INTERP | Interpolated Ground | 39425.77 | -4.62 | 743.82 | 0 | 23.87 | 0 | OK | Ground clear controls. | 88 | 42.65 | 767.69
6163 | TIN-INTERP | Interpolated Ground | 39425.84 | 5.08 | 743.82 | 0 | 13.25 | 0 | OK | Ground clear controls. | 88 | 42.65 | 757.07
6164 | TIN-INTERP | Interpolated Ground | 39425.86 | 6.58 | 743.74 | 0 | 18.78 | 0 | OK | Ground clear controls. | 88 | 42.65 | 762.52
6165 | TIN-INTERP | Interpolated Ground | 39425.86 | 4.58 | 743.83 | 0 | 23.79 | 0 | OK | Ground clear controls. | 88 | 42.65 | 767.62
6166 | TIN-INTERP | Interpolated Ground | 39465.71 | -6.62 | 743.58 | 0 | 18.53 | 0 | OK | Ground clear controls. | 88 | 42.65 | 762.11
6167 | TIN-INTERP | Interpolated Ground | 39465.76 | -5.12 | 743.61 | 0 | 13.38 | 0 | OK | Ground clear controls. | 88 | 42.65 | 756.99
6168 | TIN-INTERP | Interpolated Ground | 39465.77 | -4.62 | 743.63 | 0 | 23.96 | 0 | OK | Ground clear controls. | 88 | 42.65 | 767.59
6169 | TIN-INTERP | Interpolated Ground | 39465.84 | 5.08 | 743.66 | 0 | 13.31 | 0 | OK | Ground clear controls. | 88 | 42.65 | 756.97
6170 | TIN-INTERP | Interpolated Ground | 39465.86 | 6.58 | 743.66 | 0 | 18.76 | 0 | OK | Ground clear controls. | 88 | 42.65 | 762.42
6171 | TIN-INTERP | Interpolated Ground | 39465.86 | 4.58 | 743.68 | 0 | 23.83 | 0 | OK | Ground clear controls. | 88 | 42.65 | 767.51
6172 | TIN-INTERP | Interpolated Ground | 39505.71 | -6.62 | 743.48 | 0 | 19.46 | 0 | OK | Ground clear controls. | 88 | 42.65 | 762.94
6173 | TIN-INTERP | Interpolated Ground | 39505.76 | -5.12 | 743.44 | 0 | 14.37 | 0 | OK | Ground clear controls. | 88 | 42.65 | 757.81
6174 | TIN-INTERP | Interpolated Ground | 39505.77 | -4.62 | 743.42 | 0 | 25 | 0 | OK | Ground clear controls. | 88 | 42.65 | 768.42
6175 | TIN-INTERP | Interpolated Ground | 39505.84 | 5.08 | 743.57 | 0 | 14.22 | 0 | OK | Ground clear controls. | 88 | 42.65 | 757.79
6176 | TIN-INTERP | Interpolated Ground | 39505.86 | 6.58 | 743.63 | 0 | 19.61 | 0 | OK | Ground clear controls. | 88 | 42.65 | 763.24
6177 | TIN-INTERP | Interpolated Ground | 39505.86 | 4.58 | 743.57 | 0 | 24.78 | 0 | OK | Ground clear controls. | 88 | 42.65 | 768.35
6178 | TIN-INTERP | Interpolated Ground | 39545.71 | -6.61 | 743.74 | 0 | 20.95 | 0 | OK | Ground clear controls. | 88 | 42.65 | 764.69
6179 | TIN-INTERP | Interpolated Ground | 39545.76 | -5.11 | 743.72 | 0 | 15.81 | 0 | OK | Ground clear controls. | 88 | 42.65 | 759.53
6180 | TIN-INTERP | Interpolated Ground | 39545.77 | -4.61 | 743.71 | 0 | 26.46 | 0 | OK | Ground clear controls. | 88 | 42.65 | 770.17
6181 | TIN-INTERP | Interpolated Ground | 39545.84 | 5.09 | 743.68 | 0 | 15.84 | 0 | OK | Ground clear controls. | 88 | 42.65 | 759.52
6182 | TIN-INTERP | Interpolated Ground | 39545.86 | 6.59 | 743.6 | 0 | 21.37 | 0 | OK | Ground clear controls. | 88 | 42.65 | 764.97
6183 | TIN-INTERP | Interpolated Ground | 39545.86 | 4.59 | 743.67 | 0 | 26.44 | 0 | OK | Ground clear controls. | 88 | 42.65 | 770.11
6184 | TIN-INTERP | Interpolated Ground | 39585.71 | -6.61 | 743.8 | 0 | 23.58 | 0 | OK | Ground clear controls. | 88 | 42.65 | 767.38
6185 | TIN-INTERP | Interpolated Ground | 39585.76 | -5.11 | 743.76 | 0 | 18.41 | 0 | OK | Ground clear controls. | 88 | 42.65 | 762.17
6186 | TIN-INTERP | Interpolated Ground | 39585.77 | -4.61 | 743.76 | 0 | 29.1 | 0 | OK | Ground clear controls. | 88 | 42.65 | 772.86
6187 | TIN-INTERP | Interpolated Ground | 39585.84 | 5.09 | 743.69 | 0 | 18.47 | 0 | OK | Ground clear controls. | 88 | 42.65 | 762.16
6188 | TIN-INTERP | Interpolated Ground | 39585.86 | 6.59 | 743.64 | 0 | 23.99 | 0 | OK | Ground clear controls. | 88 | 42.65 | 767.63
6189 | TIN-INTERP | Interpolated Ground | 39585.86 | 4.59 | 743.7 | 0 | 29.12 | 0 | OK | Ground clear controls. | 88 | 42.65 | 772.82
6190 | TIN-INTERP | Interpolated Ground | 39625.71 | -6.61 | 744.32 | 0 | 26.68 | 0 | OK | Ground clear controls. | 88 | 42.65 | 771
6191 | TIN-INTERP | Interpolated Ground | 39625.76 | -5.11 | 744.33 | 0 | 21.38 | 0 | OK | Ground clear controls. | 88 | 42.65 | 765.71
6192 | TIN-INTERP | Interpolated Ground | 39625.77 | -4.61 | 744.34 | 0 | 32.15 | 0 | OK | Ground clear controls. | 88 | 42.65 | 776.49
6193 | TIN-INTERP | Interpolated Ground | 39625.84 | 5.09 | 744.2 | 0 | 21.53 | 0 | OK | Ground clear controls. | 88 | 42.65 | 765.73
6194 | TIN-INTERP | Interpolated Ground | 39625.86 | 6.59 | 744.13 | 0 | 27.07 | 0 | OK | Ground clear controls. | 88 | 42.65 | 771.2
6195 | TIN-INTERP | Interpolated Ground | 39625.86 | 4.59 | 744.22 | 0 | 32.24 | 0 | OK | Ground clear controls. | 88 | 42.65 | 776.46
6196 | TIN-INTERP | Interpolated Ground | 39665.71 | -6.6 | 743.98 | 0 | 31.58 | 0 | OK | Ground clear controls. | 88 | 42.65 | 775.56
6197 | TIN-INTERP | Interpolated Ground | 39665.76 | -5.1 | 744.04 | 0 | 26.15 | 0 | OK | Ground clear controls. | 88 | 42.65 | 770.19
6198 | TIN-INTERP | Interpolated Ground | 39665.77 | -4.6 | 744.05 | 0 | 37.01 | 0 | OK | Ground clear controls. | 88 | 42.65 | 781.06
6199 | TIN-INTERP | Interpolated Ground | 39665.84 | 5.1 | 744.02 | 0 | 26.19 | 0 | OK | Ground clear controls. | 88 | 42.65 | 770.21
6200 | TIN-INTERP | Interpolated Ground | 39665.86 | 6.6 | 743.97 | 0 | 31.74 | 0 | OK | Ground clear controls. | 88 | 42.65 | 775.71
6201 | TIN-INTERP | Interpolated Ground | 39665.86 | 4.6 | 744.03 | 0 | 37.02 | 0 | OK | Ground clear controls. | 88 | 42.65 | 781.05
6202 | TIN-INTERP | Interpolated Ground | 39705.71 | -6.6 | 743.93 | 0 | 37.12 | 0 | OK | Ground clear controls. | 88 | 42.65 | 781.05
6203 | TIN-INTERP | Interpolated Ground | 39705.76 | -5.1 | 743.9 | 0 | 31.69 | 0 | OK | Ground clear controls. | 88 | 42.65 | 775.59
6204 | TIN-INTERP | Interpolated Ground | 39705.77 | -4.6 | 743.9 | 0 | 42.65 | 0 | OK | Ground clear controls. | 88 | 42.65 | 786.55
6205 | TIN-INTERP | Interpolated Ground | 39705.84 | 5.1 | 744.04 | 0 | 31.57 | 0 | OK | Ground clear controls. | 88 | 42.58 | 775.61
6206 | TIN-INTERP | Interpolated Ground | 39705.86 | 6.6 | 744.04 | 0 | 37.08 | 0 | OK | Ground clear controls. | 88 | 42.58 | 781.12
6207 | TIN-INTERP | Interpolated Ground | 39705.86 | 4.6 | 743.99 | 0 | 42.58 | 0 | OK | Ground clear controls. | 88 | 42.58 | 786.57
6208 | TIN-INTERP | Interpolated Ground | 39714.9 | 6.6 | 744.25 | 0 | 38.23 | 0 | OK | Ground clear controls. | 89 | 43.87 | 782.48
6209 | TIN-INTERP | Interpolated Ground | 39714.96 | 5.1 | 744.21 | 0 | 32.76 | 0 | OK | Ground clear controls. | 89 | 43.87 | 776.97
6210 | TIN-INTERP | Interpolated Ground | 39715.04 | 4.6 | 744.13 | 0 | 43.84 | 0 | OK | Ground clear controls. | 89 | 43.87 | 787.97
6211 | TIN-INTERP | Interpolated Ground | 39715.05 | -6.6 | 744.12 | 0 | 38.35 | 0 | OK | Ground clear controls. | 89 | 43.87 | 782.47
6212 | TIN-INTERP | Interpolated Ground | 39715.08 | -4.6 | 744.1 | 0 | 43.87 | 0 | OK | Ground clear controls. | 89 | 43.87 | 787.97
6213 | TIN-INTERP | Interpolated Ground | 39715.09 | -5.1 | 744.11 | 0 | 32.86 | 0 | OK | Ground clear controls. | 89 | 38.4 | 776.97
6214 | TIN-INTERP | Interpolated Ground | 39754.9 | 6.59 | 744.33 | 0 | 32.92 | 0 | OK | Ground clear controls. | 89 | 38.4 | 777.25
6215 | TIN-INTERP | Interpolated Ground | 39754.96 | 5.09 | 744.31 | 0 | 27.48 | 0 | OK | Ground clear controls. | 89 | 38.4 | 771.79
6216 | TIN-INTERP | Interpolated Ground | 39755.04 | 4.59 | 744.33 | 0 | 38.4 | 0 | OK | Ground clear controls. | 89 | 38.4 | 782.73
6217 | TIN-INTERP | Interpolated Ground | 39755.05 | -6.61 | 744.47 | 0 | 32.73 | 0 | OK | Ground clear controls. | 89 | 38.28 | 777.2
6218 | TIN-INTERP | Interpolated Ground | 39755.08 | -4.61 | 744.45 | 0 | 38.28 | 0 | OK | Ground clear controls. | 89 | 38.28 | 782.73
6219 | TIN-INTERP | Interpolated Ground | 39755.09 | -5.11 | 744.44 | 0 | 27.38 | 0 | OK | Ground clear controls. | 89 | 33.61 | 771.82
6220 | TIN-INTERP | Interpolated Ground | 39794.9 | 6.59 | 744.9 | 0 | 28.06 | 0 | OK | Ground clear controls. | 89 | 33.61 | 772.96
6221 | TIN-INTERP | Interpolated Ground | 39794.96 | 5.09 | 744.95 | 0 | 22.59 | 0 | OK | Ground clear controls. | 89 | 33.61 | 767.54
6222 | TIN-INTERP | Interpolated Ground | 39795.04 | 4.59 | 744.97 | 0 | 33.45 | 0 | OK | Ground clear controls. | 89 | 33.61 | 778.42
6223 | TIN-INTERP | Interpolated Ground | 39795.05 | -6.61 | 745 | 0 | 27.88 | 0 | OK | Ground clear controls. | 89 | 33.61 | 772.88
6224 | TIN-INTERP | Interpolated Ground | 39795.08 | -4.61 | 745.01 | 0 | 33.4 | 0 | OK | Ground clear controls. | 89 | 33.61 | 778.41
6225 | TIN-INTERP | Interpolated Ground | 39795.09 | -5.11 | 745.01 | 0 | 22.59 | 0 | OK | Ground clear controls. | 89 | 33.61 | 767.6
6226 | TIN-INTERP | Interpolated Ground | 39834.9 | 6.58 | 745.62 | 0 | 23.98 | 0 | OK | Ground clear controls. | 89 | 33.61 | 769.6
6227 | TIN-INTERP | Interpolated Ground | 39834.96 | 5.08 | 745.66 | 0 | 18.55 | 0 | OK | Ground clear controls. | 89 | 33.61 | 764.21
6228 | TIN-INTERP | Interpolated Ground | 39835.04 | 4.58 | 745.73 | 0 | 29.31 | 0 | OK | Ground clear controls. | 89 | 33.61 | 775.04
6229 | TIN-INTERP | Interpolated Ground | 39835.05 | -6.62 | 745.89 | 0 | 23.61 | 0 | OK | Ground clear controls. | 89 | 33.61 | 769.5
6230 | TIN-INTERP | Interpolated Ground | 39835.08 | -4.62 | 745.86 | 0 | 29.18 | 0 | OK | Ground clear controls. | 89 | 33.61 | 775.04
6231 | TIN-INTERP | Interpolated Ground | 39835.09 | -5.12 | 745.88 | 0 | 18.42 | 0 | OK | Ground clear controls. | 89 | 33.61 | 764.3
6232 | TIN-INTERP | Interpolated Ground | 39874.9 | 6.58 | 747.48 | 0 | 19.71 | 0 | OK | Ground clear controls. | 89 | 33.61 | 767.19
6233 | TIN-INTERP | Interpolated Ground | 39874.96 | 5.08 | 747.46 | 0 | 14.35 | 0 | OK | Ground clear controls. | 89 | 33.61 | 761.81
6234 | TIN-INTERP | Interpolated Ground | 39875.04 | 4.58 | 747.47 | 0 | 25.15 | 0 | OK | Ground clear controls. | 89 | 33.61 | 772.62
6235 | TIN-INTERP | Interpolated Ground | 39875.05 | -6.62 | 747.35 | 0 | 19.71 | 0 | OK | Ground clear controls. | 89 | 33.61 | 767.06
6236 | TIN-INTERP | Interpolated Ground | 39875.08 | -4.62 | 747.33 | 0 | 25.28 | 0 | OK | Ground clear controls. | 89 | 33.61 | 772.61
6237 | TIN-INTERP | Interpolated Ground | 39875.09 | -5.12 | 747.3 | 0 | 14.61 | 0 | OK | Ground clear controls. | 89 | 33.61 | 761.91
6238 | TIN-INTERP | Interpolated Ground | 39914.9 | 6.57 | 747.69 | 0 | 18.01 | 0 | OK | Ground clear controls. | 89 | 33.61 | 765.7
6239 | TIN-INTERP | Interpolated Ground | 39914.96 | 5.07 | 747.73 | 0 | 12.61 | 0 | OK | Ground clear controls. | 89 | 33.61 | 760.34
6240 | TIN-INTERP | Interpolated Ground | 39915.04 | 4.57 | 747.73 | 0 | 23.39 | 0 | OK | Ground clear controls. | 89 | 33.61 | 771.12
6241 | TIN-INTERP | Interpolated Ground | 39915.05 | -6.63 | 747.73 | 0 | 17.82 | 0 | OK | Ground clear controls. | 89 | 33.61 | 765.55
6242 | TIN-INTERP | Interpolated Ground | 39915.08 | -4.63 | 747.77 | 0 | 23.35 | 0 | OK | Ground clear controls. | 89 | 33.61 | 771.12
6243 | TIN-INTERP | Interpolated Ground | 39915.09 | -5.13 | 747.76 | 0 | 12.68 | 0 | OK | Ground clear controls. | 89 | 33.61 | 760.44
6244 | TIN-INTERP | Interpolated Ground | 39954.9 | 6.57 | 747.92 | 0 | 17.22 | 0 | OK | Ground clear controls. | 89 | 33.61 | 765.14
6245 | TIN-INTERP | Interpolated Ground | 39954.96 | 5.07 | 747.93 | 0 | 11.85 | 0 | OK | Ground clear controls. | 89 | 33.61 | 759.78
6246 | TIN-INTERP | Interpolated Ground | 39955.04 | 4.57 | 747.94 | 0 | 22.62 | 0 | OK | Ground clear controls. | 89 | 33.61 | 770.56
6247 | TIN-INTERP | Interpolated Ground | 39955.05 | -6.63 | 748.01 | 0 | 16.99 | 0 | OK | Ground clear controls. | 89 | 33.61 | 765
6248 | TIN-INTERP | Interpolated Ground | 39955.08 | -4.63 | 747.94 | 0 | 22.62 | 0 | OK | Ground clear controls. | 89 | 33.61 | 770.56
6249 | TIN-INTERP | Interpolated Ground | 39955.09 | -5.13 | 747.93 | 0 | 11.96 | 0 | OK | Ground clear controls. | 89 | 33.61 | 759.89
6250 | TIN-INTERP | Interpolated Ground | 39994.9 | 6.56 | 748.25 | 0 | 17.25 | 0 | OK | Ground clear controls. | 89 | 33.61 | 765.5
6251 | TIN-INTERP | Interpolated Ground | 39994.96 | 5.06 | 748.28 | 0 | 11.86 | 0 | OK | Ground clear controls. | 89 | 33.61 | 760.14
6252 | TIN-INTERP | Interpolated Ground | 39995.04 | 4.56 | 748.27 | 0 | 22.67 | 0 | OK | Ground clear controls. | 89 | 33.61 | 770.94
6253 | TIN-INTERP | Interpolated Ground | 39995.05 | -6.64 | 748.15 | 0 | 17.22 | 0 | OK | Ground clear controls. | 89 | 33.61 | 765.37
6254 | TIN-INTERP | Interpolated Ground | 39995.08 | -4.64 | 748.16 | 0 | 22.78 | 0 | OK | Ground clear controls. | 89 | 33.61 | 770.94
6255 | TIN-INTERP | Interpolated Ground | 39995.09 | -5.14 | 748.14 | 0 | 12.12 | 0 | OK | Ground clear controls. | 89 | 33.61 | 760.26
6256 | TIN-INTERP | Interpolated Ground | 40034.9 | 6.56 | 748.33 | 0 | 18.47 | 0 | OK | Ground clear controls. | 89 | 33.61 | 766.8
6257 | TIN-INTERP | Interpolated Ground | 40034.96 | 5.06 | 748.32 | 0 | 13.11 | 0 | OK | Ground clear controls. | 89 | 33.61 | 761.43
6258 | TIN-INTERP | Interpolated Ground | 40035.04 | 4.56 | 748.33 | 0 | 23.92 | 0 | OK | Ground clear controls. | 89 | 33.61 | 772.25
6259 | TIN-INTERP | Interpolated Ground | 40035.05 | -6.64 | 748.26 | 0 | 18.43 | 0 | OK | Ground clear controls. | 89 | 33.61 | 766.69
6260 | TIN-INTERP | Interpolated Ground | 40035.08 | -4.64 | 748.3 | 0 | 23.95 | 0 | OK | Ground clear controls. | 89 | 33.61 | 772.25
6261 | TIN-INTERP | Interpolated Ground | 40035.09 | -5.14 | 748.29 | 0 | 13.25 | 0 | OK | Ground clear controls. | 89 | 33.61 | 761.54
6262 | TIN-INTERP | Interpolated Ground | 40074.9 | 6.55 | 748.42 | 0 | 20.61 | 0 | OK | Ground clear controls. | 89 | 33.61 | 769.03
6263 | TIN-INTERP | Interpolated Ground | 40074.96 | 5.05 | 748.4 | 0 | 15.24 | 0 | OK | Ground clear controls. | 89 | 33.61 | 763.64
6264 | TIN-INTERP | Interpolated Ground | 40075.04 | 4.55 | 748.39 | 0 | 26.1 | 0 | OK | Ground clear controls. | 89 | 33.61 | 774.49
6265 | TIN-INTERP | Interpolated Ground | 40075.05 | -6.65 | 748.38 | 0 | 20.57 | 0 | OK | Ground clear controls. | 89 | 33.61 | 768.95
6266 | TIN-INTERP | Interpolated Ground | 40075.08 | -4.65 | 748.41 | 0 | 26.09 | 0 | OK | Ground clear controls. | 89 | 33.61 | 774.5
6267 | TIN-INTERP | Interpolated Ground | 40075.09 | -5.15 | 748.43 | 0 | 15.3 | 0 | OK | Ground clear controls. | 89 | 33.61 | 763.73
6268 | TIN-INTERP | Interpolated Ground | 40114.9 | 6.55 | 748.27 | 0 | 23.93 | 0 | OK | Ground clear controls. | 89 | 33.61 | 772.2
6269 | TIN-INTERP | Interpolated Ground | 40114.96 | 5.05 | 748.28 | 0 | 18.48 | 0 | OK | Ground clear controls. | 89 | 33.61 | 766.76
6270 | TIN-INTERP | Interpolated Ground | 40115.04 | 4.55 | 748.28 | 0 | 29.39 | 0 | OK | Ground clear controls. | 89 | 33.61 | 777.67
6271 | TIN-INTERP | Interpolated Ground | 40115.05 | -6.65 | 748.29 | 0 | 23.86 | 0 | OK | Ground clear controls. | 89 | 33.61 | 772.15
6272 | TIN-INTERP | Interpolated Ground | 40115.08 | -4.65 | 748.34 | 0 | 29.34 | 0 | OK | Ground clear controls. | 89 | 33.61 | 777.68
6273 | TIN-INTERP | Interpolated Ground | 40115.09 | -5.15 | 748.31 | 0 | 18.53 | 0 | OK | Ground clear controls. | 89 | 33.61 | 766.84
6274 | TIN-INTERP | Interpolated Ground | 40154.9 | 6.54 | 748.2 | 0 | 28.09 | 0 | OK | Ground clear controls. | 89 | 33.61 | 776.29
6275 | TIN-INTERP | Interpolated Ground | 40154.96 | 5.04 | 748.23 | 0 | 22.6 | 0 | OK | Ground clear controls. | 89 | 33.61 | 770.83
6276 | TIN-INTERP | Interpolated Ground | 40155.04 | 4.54 | 748.23 | 0 | 33.57 | 0 | OK | Ground clear controls. | 89 | 33.61 | 781.8
6277 | TIN-INTERP | Interpolated Ground | 40155.05 | -6.66 | 748.14 | 0 | 28.16 | 0 | OK | Ground clear controls. | 89 | 33.61 | 776.3
6278 | TIN-INTERP | Interpolated Ground | 40155.08 | -4.66 | 748.2 | 0 | 33.61 | 0 | OK | Ground clear controls. | 89 | 33.61 | 781.81
6279 | TIN-INTERP | Interpolated Ground | 40155.09 | -5.16 | 748.17 | 0 | 22.7 | 0 | OK | Ground clear controls. | 89 | 22.7 | 770.87
6280 | TIN-INTERP | Interpolated Ground | 40176.5 | -5.16 | 748.15 | 0 | 25.26 | 0 | OK | Ground clear controls. | 90 | 36.29 | 773.41
6281 | TIN-INTERP | Interpolated Ground | 40176.5 | -6.66 | 748.17 | 0 | 30.74 | 0 | OK | Ground clear controls. | 90 | 36.29 | 778.91
6282 | TIN-INTERP | Interpolated Ground | 40176.52 | -4.66 | 748.12 | 0 | 36.29 | 0 | OK | Ground clear controls. | 90 | 36.29 | 784.41
6283 | TIN-INTERP | Interpolated Ground | 40176.6 | 5.04 | 748.22 | 0 | 25.19 | 0 | OK | Ground clear controls. | 90 | 36.21 | 773.41
6284 | TIN-INTERP | Interpolated Ground | 40176.62 | 4.54 | 748.2 | 0 | 36.21 | 0 | OK | Ground clear controls. | 90 | 36.21 | 784.41
6285 | TIN-INTERP | Interpolated Ground | 40176.62 | 6.54 | 748.23 | 0 | 30.68 | 0 | OK | Ground clear controls. | 90 | 31.72 | 778.91
6286 | TIN-INTERP | Interpolated Ground | 40216.5 | -5.18 | 748.06 | 0 | 20.74 | 0 | OK | Ground clear controls. | 90 | 31.72 | 768.8
6287 | TIN-INTERP | Interpolated Ground | 40216.5 | -6.68 | 748.05 | 0 | 26.16 | 0 | OK | Ground clear controls. | 90 | 31.72 | 774.21
6288 | TIN-INTERP | Interpolated Ground | 40216.52 | -4.67 | 748.04 | 0 | 31.68 | 0 | OK | Ground clear controls. | 90 | 31.72 | 779.72
6289 | TIN-INTERP | Interpolated Ground | 40216.6 | 5.04 | 748.04 | 0 | 20.74 | 0 | OK | Ground clear controls. | 90 | 31.72 | 768.78
6290 | TIN-INTERP | Interpolated Ground | 40216.62 | 4.54 | 748.01 | 0 | 31.72 | 0 | OK | Ground clear controls. | 90 | 31.72 | 779.73
6291 | TIN-INTERP | Interpolated Ground | 40216.62 | 6.54 | 748.07 | 0 | 26.18 | 0 | OK | Ground clear controls. | 90 | 28.42 | 774.25
6292 | TIN-INTERP | Interpolated Ground | 40256.5 | -5.19 | 747.9 | 0 | 17.22 | 0 | OK | Ground clear controls. | 90 | 28.42 | 765.12
6293 | TIN-INTERP | Interpolated Ground | 40256.5 | -6.69 | 747.89 | 0 | 22.55 | 0 | OK | Ground clear controls. | 90 | 28.42 | 770.44
6294 | TIN-INTERP | Interpolated Ground | 40256.52 | -4.69 | 747.91 | 0 | 28.07 | 0 | OK | Ground clear controls. | 90 | 28.42 | 775.98
6295 | TIN-INTERP | Interpolated Ground | 40256.6 | 5.03 | 747.94 | 0 | 17.14 | 0 | OK | Ground clear controls. | 90 | 28.42 | 765.08
6296 | TIN-INTERP | Interpolated Ground | 40256.62 | 4.53 | 747.95 | 0 | 28.05 | 0 | OK | Ground clear controls. | 90 | 28.42 | 776
6297 | TIN-INTERP | Interpolated Ground | 40256.62 | 6.53 | 747.96 | 0 | 22.56 | 0 | OK | Ground clear controls. | 90 | 28.42 | 770.52
6298 | TIN-INTERP | Interpolated Ground | 40296.5 | -5.2 | 747.91 | 0 | 14.44 | 0 | OK | Ground clear controls. | 90 | 28.42 | 762.35
6299 | TIN-INTERP | Interpolated Ground | 40296.5 | -6.7 | 747.88 | 0 | 19.75 | 0 | OK | Ground clear controls. | 90 | 28.42 | 767.63
6300 | TIN-INTERP | Interpolated Ground | 40296.52 | -4.7 | 747.93 | 0 | 25.25 | 0 | OK | Ground clear controls. | 90 | 28.42 | 773.18
6301 | TIN-INTERP | Interpolated Ground | 40296.6 | 5.03 | 747.6 | 0 | 14.7 | 0 | OK | Ground clear controls. | 90 | 28.42 | 762.3
6302 | TIN-INTERP | Interpolated Ground | 40296.62 | 4.53 | 747.69 | 0 | 25.51 | 0 | OK | Ground clear controls. | 90 | 28.42 | 773.2
6303 | TIN-INTERP | Interpolated Ground | 40296.62 | 6.53 | 747.48 | 0 | 20.25 | 0 | OK | Ground clear controls. | 90 | 28.42 | 767.73
6304 | TIN-INTERP | Interpolated Ground | 40336.5 | -5.21 | 747.76 | 0 | 12.75 | 0 | OK | Ground clear controls. | 90 | 28.42 | 760.51
6305 | TIN-INTERP | Interpolated Ground | 40336.5 | -6.71 | 747.68 | 0 | 18.09 | 0 | OK | Ground clear controls. | 90 | 28.42 | 765.77
6306 | TIN-INTERP | Interpolated Ground | 40336.52 | -4.71 | 747.75 | 0 | 23.56 | 0 | OK | Ground clear controls. | 90 | 28.42 | 771.31
6307 | TIN-INTERP | Interpolated Ground | 40336.6 | 5.03 | 747.72 | 0 | 12.74 | 0 | OK | Ground clear controls. | 90 | 28.42 | 760.46
6308 | TIN-INTERP | Interpolated Ground | 40336.62 | 4.52 | 747.72 | 0 | 23.62 | 0 | OK | Ground clear controls. | 90 | 28.42 | 771.34
6309 | TIN-INTERP | Interpolated Ground | 40336.62 | 6.53 | 747.69 | 0 | 18.19 | 0 | OK | Ground clear controls. | 90 | 28.42 | 765.88
6310 | TIN-INTERP | Interpolated Ground | 40376.5 | -5.22 | 747.63 | 0 | 11.97 | 0 | OK | Ground clear controls. | 90 | 28.42 | 759.6
6311 | TIN-INTERP | Interpolated Ground | 40376.5 | -6.72 | 747.59 | 0 | 17.25 | 0 | OK | Ground clear controls. | 90 | 28.42 | 764.84
6312 | TIN-INTERP | Interpolated Ground | 40376.52 | -4.72 | 747.66 | 0 | 22.73 | 0 | OK | Ground clear controls. | 90 | 28.42 | 770.39
6313 | TIN-INTERP | Interpolated Ground | 40376.6 | 5.02 | 747.37 | 0 | 12.17 | 0 | OK | Ground clear controls. | 90 | 28.42 | 759.54
6314 | TIN-INTERP | Interpolated Ground | 40376.62 | 4.52 | 747.49 | 0 | 22.93 | 0 | OK | Ground clear controls. | 90 | 28.42 | 770.42
6315 | TIN-INTERP | Interpolated Ground | 40376.62 | 6.52 | 747.42 | 0 | 17.53 | 0 | OK | Ground clear controls. | 90 | 28.42 | 764.95
6316 | TIN-INTERP | Interpolated Ground | 40416.5 | -5.24 | 747.51 | 0 | 12.09 | 0 | OK | Ground clear controls. | 90 | 28.42 | 759.6
6317 | TIN-INTERP | Interpolated Ground | 40416.5 | -6.74 | 747.39 | 0 | 17.47 | 0 | OK | Ground clear controls. | 90 | 28.42 | 764.86
6318 | TIN-INTERP | Interpolated Ground | 40416.52 | -4.73 | 747.53 | 0 | 22.88 | 0 | OK | Ground clear controls. | 90 | 28.42 | 770.41
6319 | TIN-INTERP | Interpolated Ground | 40416.6 | 5.02 | 747.14 | 0 | 12.4 | 0 | OK | Ground clear controls. | 90 | 28.42 | 759.54
6320 | TIN-INTERP | Interpolated Ground | 40416.62 | 4.52 | 747.18 | 0 | 23.25 | 0 | OK | Ground clear controls. | 90 | 28.42 | 770.43
6321 | TIN-INTERP | Interpolated Ground | 40416.62 | 6.52 | 747.16 | 0 | 17.8 | 0 | OK | Ground clear controls. | 90 | 28.42 | 764.96
6322 | TIN-INTERP | Interpolated Ground | 40456.5 | -5.25 | 747.13 | 0 | 13.4 | 0 | OK | Ground clear controls. | 90 | 28.42 | 760.53
6323 | TIN-INTERP | Interpolated Ground | 40456.5 | -6.75 | 747.23 | 0 | 18.6 | 0 | OK | Ground clear controls. | 90 | 28.42 | 765.83
6324 | TIN-INTERP | Interpolated Ground | 40456.52 | -4.74 | 747.15 | 0 | 24.22 | 0 | OK | Ground clear controls. | 90 | 28.42 | 771.37
6325 | TIN-INTERP | Interpolated Ground | 40456.6 | 5.02 | 747.73 | 0 | 12.75 | 0 | OK | Ground clear controls. | 90 | 28.42 | 760.48
6326 | TIN-INTERP | Interpolated Ground | 40456.62 | 4.51 | 747.69 | 0 | 23.69 | 0 | OK | Ground clear controls. | 90 | 28.42 | 771.38
6327 | TIN-INTERP | Interpolated Ground | 40456.62 | 6.52 | 747.82 | 0 | 18.09 | 0 | OK | Ground clear controls. | 90 | 28.42 | 765.91
6328 | TIN-INTERP | Interpolated Ground | 40496.5 | -5.26 | 747.89 | 0 | 14.48 | 0 | OK | Ground clear controls. | 90 | 28.42 | 762.37
6329 | TIN-INTERP | Interpolated Ground | 40496.5 | -6.76 | 747.88 | 0 | 19.86 | 0 | OK | Ground clear controls. | 90 | 28.42 | 767.74
6330 | TIN-INTERP | Interpolated Ground | 40496.52 | -4.75 | 747.88 | 0 | 25.38 | 0 | OK | Ground clear controls. | 90 | 28.42 | 773.26
6331 | TIN-INTERP | Interpolated Ground | 40496.6 | 5.02 | 747.92 | 0 | 14.42 | 0 | OK | Ground clear controls. | 90 | 28.42 | 762.34
6332 | TIN-INTERP | Interpolated Ground | 40496.62 | 4.51 | 747.9 | 0 | 25.37 | 0 | OK | Ground clear controls. | 90 | 28.42 | 773.27
6333 | TIN-INTERP | Interpolated Ground | 40496.62 | 6.52 | 747.95 | 0 | 19.84 | 0 | OK | Ground clear controls. | 90 | 28.42 | 767.79
6334 | TIN-INTERP | Interpolated Ground | 40536.5 | -5.27 | 747.76 | 0 | 17.38 | 0 | OK | Ground clear controls. | 90 | 28.42 | 765.14
6335 | TIN-INTERP | Interpolated Ground | 40536.5 | -6.77 | 747.74 | 0 | 22.84 | 0 | OK | Ground clear controls. | 90 | 28.42 | 770.58
6336 | TIN-INTERP | Interpolated Ground | 40536.52 | -4.77 | 747.74 | 0 | 28.36 | 0 | OK | Ground clear controls. | 90 | 28.42 | 776.1
6337 | TIN-INTERP | Interpolated Ground | 40536.6 | 5.01 | 747.69 | 0 | 17.43 | 0 | OK | Ground clear controls. | 90 | 28.42 | 765.12
6338 | TIN-INTERP | Interpolated Ground | 40536.62 | 4.51 | 747.68 | 0 | 28.42 | 0 | OK | Ground clear controls. | 90 | 28.42 | 776.1
6339 | TIN-INTERP | Interpolated Ground | 40536.62 | 6.51 | 747.7 | 0 | 22.91 | 0 | OK | Ground clear controls. | 90 | 22.91 | 770.61
6340 | TIN-INTERP | Interpolated Ground | 40556.63 | -5.28 | 747.8 | 0 | 19.08 | 0 | OK | Ground clear controls. | 91 | 35.64 | 766.88
6341 | TIN-INTERP | Interpolated Ground | 40556.67 | -6.78 | 747.75 | 0 | 24.63 | 0 | OK | Ground clear controls. | 91 | 35.64 | 772.38
6342 | TIN-INTERP | Interpolated Ground | 40556.72 | -4.77 | 747.8 | 0 | 30.09 | 0 | OK | Ground clear controls. | 91 | 35.64 | 777.89
6343 | TIN-INTERP | Interpolated Ground | 40556.81 | 4.51 | 747.8 | 0 | 30.08 | 0 | OK | Ground clear controls. | 91 | 35.64 | 777.88
6344 | TIN-INTERP | Interpolated Ground | 40556.84 | 5.01 | 747.77 | 0 | 19.11 | 0 | OK | Ground clear controls. | 91 | 35.64 | 766.88
6345 | TIN-INTERP | Interpolated Ground | 40556.84 | 6.51 | 747.67 | 0 | 24.71 | 0 | OK | Ground clear controls. | 91 | 35.64 | 772.38
6346 | TIN-INTERP | Interpolated Ground | 40596.63 | -5.56 | 747.16 | 0 | 16.96 | 0 | OK | Ground clear controls. | 91 | 35.64 | 764.12
6347 | TIN-INTERP | Interpolated Ground | 40596.67 | -7.07 | 747.17 | 0 | 22.4 | 0 | OK | Ground clear controls. | 91 | 35.64 | 769.57
6348 | TIN-INTERP | Interpolated Ground | 40596.72 | -5.04 | 747.15 | 0 | 28.02 | 0 | OK | Ground clear controls. | 91 | 35.64 | 775.17
6349 | TIN-INTERP | Interpolated Ground | 40596.81 | 4.46 | 747.39 | 0 | 27.77 | 0 | OK | Ground clear controls. | 91 | 35.64 | 775.16
6350 | TIN-INTERP | Interpolated Ground | 40596.84 | 4.99 | 747.44 | 0 | 16.67 | 0 | OK | Ground clear controls. | 91 | 35.64 | 764.11
6351 | TIN-INTERP | Interpolated Ground | 40596.84 | 6.49 | 747.49 | 0 | 22.11 | 0 | OK | Ground clear controls. | 91 | 35.64 | 769.6
6352 | TIN-INTERP | Interpolated Ground | 40636.63 | -5.84 | 747.28 | 0 | 15 | 0 | OK | Ground clear controls. | 91 | 35.64 | 762.28
6353 | TIN-INTERP | Interpolated Ground | 40636.67 | -7.35 | 747.28 | 0 | 20.42 | 0 | OK | Ground clear controls. | 91 | 35.64 | 767.7
6354 | TIN-INTERP | Interpolated Ground | 40636.72 | -5.3 | 747.27 | 0 | 26.12 | 0 | OK | Ground clear controls. | 91 | 35.64 | 773.39
6355 | TIN-INTERP | Interpolated Ground | 40636.81 | 4.42 | 747.32 | 0 | 26.06 | 0 | OK | Ground clear controls. | 91 | 35.64 | 773.38
6356 | TIN-INTERP | Interpolated Ground | 40636.84 | 4.96 | 747.33 | 0 | 14.94 | 0 | OK | Ground clear controls. | 91 | 35.64 | 762.27
6357 | TIN-INTERP | Interpolated Ground | 40636.84 | 6.46 | 747.3 | 0 | 20.45 | 0 | OK | Ground clear controls. | 91 | 35.64 | 767.75
6358 | TIN-INTERP | Interpolated Ground | 40676.62 | -6.12 | 747.27 | 0 | 14.09 | 0 | OK | Ground clear controls. | 91 | 35.64 | 761.36
6359 | TIN-INTERP | Interpolated Ground | 40676.67 | -7.64 | 747.26 | 0 | 19.5 | 0 | OK | Ground clear controls. | 91 | 35.64 | 766.76
6360 | TIN-INTERP | Interpolated Ground | 40676.71 | -5.56 | 747.28 | 0 | 25.27 | 0 | OK | Ground clear controls. | 91 | 35.64 | 772.55
6361 | TIN-INTERP | Interpolated Ground | 40676.81 | 4.38 | 747.42 | 0 | 25.1 | 0 | OK | Ground clear controls. | 91 | 35.64 | 772.52
6362 | TIN-INTERP | Interpolated Ground | 40676.84 | 4.93 | 747.43 | 0 | 13.91 | 0 | OK | Ground clear controls. | 91 | 35.64 | 761.34
6363 | TIN-INTERP | Interpolated Ground | 40676.84 | 6.44 | 747.44 | 0 | 19.38 | 0 | OK | Ground clear controls. | 91 | 35.64 | 766.82
6364 | TIN-INTERP | Interpolated Ground | 40716.62 | -6.4 | 747.9 | 0 | 13.47 | 0 | OK | Ground clear controls. | 91 | 35.64 | 761.37
6365 | TIN-INTERP | Interpolated Ground | 40716.67 | -7.93 | 747.84 | 0 | 18.92 | 0 | OK | Ground clear controls. | 91 | 35.64 | 766.76
6366 | TIN-INTERP | Interpolated Ground | 40716.71 | -5.83 | 747.91 | 0 | 24.73 | 0 | OK | Ground clear controls. | 91 | 35.64 | 772.64
6367 | TIN-INTERP | Interpolated Ground | 40716.81 | 4.34 | 748.2 | 0 | 24.4 | 0 | OK | Ground clear controls. | 91 | 35.64 | 772.6
6368 | TIN-INTERP | Interpolated Ground | 40716.84 | 4.91 | 748.22 | 0 | 13.11 | 0 | OK | Ground clear controls. | 91 | 35.64 | 761.33
6369 | TIN-INTERP | Interpolated Ground | 40716.84 | 6.41 | 748.26 | 0 | 18.57 | 0 | OK | Ground clear controls. | 91 | 35.64 | 766.83
6370 | TIN-INTERP | Interpolated Ground | 40756.62 | -6.68 | 747.76 | 0 | 14.54 | 0 | OK | Ground clear controls. | 91 | 35.64 | 762.3
6371 | TIN-INTERP | Interpolated Ground | 40756.67 | -8.22 | 747.76 | 0 | 19.96 | 0 | OK | Ground clear controls. | 91 | 35.64 | 767.72
6372 | TIN-INTERP | Interpolated Ground | 40756.71 | -6.09 | 747.76 | 0 | 25.91 | 0 | OK | Ground clear controls. | 91 | 35.64 | 773.67
6373 | TIN-INTERP | Interpolated Ground | 40756.81 | 4.3 | 748 | 0 | 25.62 | 0 | OK | Ground clear controls. | 91 | 35.64 | 773.62
6374 | TIN-INTERP | Interpolated Ground | 40756.84 | 4.88 | 748.05 | 0 | 14.19 | 0 | OK | Ground clear controls. | 91 | 35.64 | 762.24
6375 | TIN-INTERP | Interpolated Ground | 40756.84 | 6.39 | 748.09 | 0 | 19.68 | 0 | OK | Ground clear controls. | 91 | 35.64 | 767.77
6376 | TIN-INTERP | Interpolated Ground | 40796.62 | -6.96 | 748.32 | 0 | 15.83 | 0 | OK | Ground clear controls. | 91 | 35.64 | 764.15
6377 | TIN-INTERP | Interpolated Ground | 40796.67 | -8.5 | 748.29 | 0 | 21.31 | 0 | OK | Ground clear controls. | 91 | 35.64 | 769.6
6378 | TIN-INTERP | Interpolated Ground | 40796.71 | -6.36 | 748.32 | 0 | 27.31 | 0 | OK | Ground clear controls. | 91 | 35.64 | 775.63
6379 | TIN-INTERP | Interpolated Ground | 40796.81 | 4.26 | 748.3 | 0 | 27.26 | 0 | OK | Ground clear controls. | 91 | 35.64 | 775.56
6380 | TIN-INTERP | Interpolated Ground | 40796.84 | 4.86 | 748.29 | 0 | 15.78 | 0 | OK | Ground clear controls. | 91 | 35.64 | 764.07
6381 | TIN-INTERP | Interpolated Ground | 40796.84 | 6.36 | 748.27 | 0 | 21.36 | 0 | OK | Ground clear controls. | 91 | 35.64 | 769.63
6382 | TIN-INTERP | Interpolated Ground | 40836.62 | -7.24 | 749.43 | 0 | 17.5 | 0 | OK | Ground clear controls. | 91 | 35.64 | 766.93
6383 | TIN-INTERP | Interpolated Ground | 40836.67 | -8.79 | 749.41 | 0 | 23.03 | 0 | OK | Ground clear controls. | 91 | 35.64 | 772.44
6384 | TIN-INTERP | Interpolated Ground | 40836.71 | -6.62 | 749.43 | 0 | 29.11 | 0 | OK | Ground clear controls. | 91 | 35.64 | 778.54
6385 | TIN-INTERP | Interpolated Ground | 40836.81 | 4.22 | 749.49 | 0 | 28.95 | 0 | OK | Ground clear controls. | 91 | 35.64 | 778.44
6386 | TIN-INTERP | Interpolated Ground | 40836.84 | 4.83 | 749.5 | 0 | 17.34 | 0 | OK | Ground clear controls. | 91 | 35.64 | 766.84
6387 | TIN-INTERP | Interpolated Ground | 40836.84 | 6.33 | 749.5 | 0 | 22.93 | 0 | OK | Ground clear controls. | 91 | 35.64 | 772.43
6388 | TIN-INTERP | Interpolated Ground | 40876.62 | -7.52 | 750.74 | 0 | 19.89 | 0 | OK | Ground clear controls. | 91 | 35.64 | 770.63
6389 | TIN-INTERP | Interpolated Ground | 40876.66 | -9.08 | 750.7 | 0 | 25.52 | 0 | OK | Ground clear controls. | 91 | 35.64 | 776.22
6390 | TIN-INTERP | Interpolated Ground | 40876.71 | -6.88 | 750.74 | 0 | 31.64 | 0 | OK | Ground clear controls. | 91 | 35.64 | 782.38
6391 | TIN-INTERP | Interpolated Ground | 40876.81 | 4.18 | 751.02 | 0 | 31.25 | 0 | OK | Ground clear controls. | 91 | 35.64 | 782.27
6392 | TIN-INTERP | Interpolated Ground | 40876.84 | 4.81 | 751.06 | 0 | 19.46 | 0 | OK | Ground clear controls. | 91 | 35.64 | 770.52
6393 | TIN-INTERP | Interpolated Ground | 40876.84 | 6.31 | 751.17 | 0 | 24.99 | 0 | OK | Ground clear controls. | 91 | 35.64 | 776.16
6394 | TIN-INTERP | Interpolated Ground | 40916.62 | -7.8 | 754.67 | 0 | 20.59 | 0 | OK | Ground clear controls. | 91 | 35.64 | 775.26
6395 | TIN-INTERP | Interpolated Ground | 40916.66 | -9.37 | 754.54 | 0 | 26.41 | 0 | OK | Ground clear controls. | 91 | 35.64 | 780.95
6396 | TIN-INTERP | Interpolated Ground | 40916.71 | -7.15 | 754.73 | 0 | 32.44 | 0 | OK | Ground clear controls. | 91 | 35.64 | 787.17
6397 | TIN-INTERP | Interpolated Ground | 40916.81 | 4.14 | 754.8 | 0 | 32.23 | 0 | OK | Ground clear controls. | 91 | 35.64 | 787.03
6398 | TIN-INTERP | Interpolated Ground | 40916.84 | 4.78 | 754.79 | 0 | 20.35 | 0 | OK | Ground clear controls. | 91 | 35.64 | 775.14
6399 | TIN-INTERP | Interpolated Ground | 40916.84 | 6.28 | 754.68 | 0 | 26.15 | 0 | OK | Ground clear controls. | 91 | 35.64 | 780.83
6400 | TIN-INTERP | Interpolated Ground | 40956.62 | -8.08 | 757.34 | 0 | 23.49 | 0 | OK | Ground clear controls. | 91 | 35.64 | 780.83
6401 | TIN-INTERP | Interpolated Ground | 40956.66 | -9.65 | 757.28 | 0 | 29.35 | 0 | OK | Ground clear controls. | 91 | 35.64 | 786.63
6402 | TIN-INTERP | Interpolated Ground | 40956.71 | -7.41 | 757.37 | 0 | 35.52 | 0 | OK | Ground clear controls. | 91 | 35.64 | 792.89
6403 | TIN-INTERP | Interpolated Ground | 40956.81 | 4.1 | 757.09 | 0 | 35.64 | 0 | OK | Ground clear controls. | 91 | 35.64 | 792.73
6404 | TIN-INTERP | Interpolated Ground | 40956.84 | 4.75 | 757.12 | 0 | 23.55 | 0 | OK | Ground clear controls. | 91 | 29.26 | 780.67
6405 | TIN-INTERP | Interpolated Ground | 40956.84 | 6.26 | 757.16 | 0 | 29.26 | 0 | OK | Ground clear controls. | 91 | 29.26 | 786.42
6406 | TIN-INTERP | Interpolated Ground | 40959.97 | -8.1 | 757.36 | 0 | 23.97 | 0 | OK | Ground clear controls. | 92 | 36.29 | 781.33
6407 | TIN-INTERP | Interpolated Ground | 40960.94 | 4.12 | 757.31 | 0 | 36.14 | 0 | OK | Ground clear controls. | 92 | 36.29 | 793.45
6408 | TIN-INTERP | Interpolated Ground | 40960.94 | 4.78 | 757.3 | 0 | 24.08 | 0 | OK | Ground clear controls. | 92 | 36.29 | 781.38
6409 | TIN-INTERP | Interpolated Ground | 40960.94 | 6.3 | 757.2 | 0 | 29.96 | 0 | OK | Ground clear controls. | 92 | 36.29 | 787.16
6410 | TIN-INTERP | Interpolated Ground | 40961.85 | -7.43 | 757.39 | 0 | 36.02 | 0 | OK | Ground clear controls. | 92 | 36.29 | 793.41
6411 | TIN-INTERP | Interpolated Ground | 40962.15 | -9.66 | 757.33 | 0 | 29.79 | 0 | OK | Ground clear controls. | 92 | 36.29 | 787.12
6412 | TIN-INTERP | Interpolated Ground | 41000.18 | 6.28 | 754.56 | 0 | 27.29 | 0 | OK | Ground clear controls. | 92 | 36.29 | 781.85
6413 | TIN-INTERP | Interpolated Ground | 41000.37 | 4.78 | 754.56 | 0 | 21.58 | 0 | OK | Ground clear controls. | 92 | 36.29 | 776.14
6414 | TIN-INTERP | Interpolated Ground | 41000.44 | 4.13 | 754.55 | 0 | 33.5 | 0 | OK | Ground clear controls. | 92 | 36.29 | 788.05
6415 | TIN-INTERP | Interpolated Ground | 41001.85 | -7.21 | 754.61 | 0 | 33.44 | 0 | OK | Ground clear controls. | 92 | 36.29 | 788.05
6416 | TIN-INTERP | Interpolated Ground | 41001.91 | -7.87 | 754.65 | 0 | 21.46 | 0 | OK | Ground clear controls. | 92 | 36.29 | 776.11
6417 | TIN-INTERP | Interpolated Ground | 41002.15 | -9.43 | 754.68 | 0 | 27.12 | 0 | OK | Ground clear controls. | 92 | 36.29 | 781.8
6418 | TIN-INTERP | Interpolated Ground | 41040.18 | 6.31 | 751.26 | 0 | 26.21 | 0 | OK | Ground clear controls. | 92 | 36.29 | 777.47
6419 | TIN-INTERP | Interpolated Ground | 41040.37 | 4.8 | 751.23 | 0 | 20.6 | 0 | OK | Ground clear controls. | 92 | 36.29 | 771.83
6420 | TIN-INTERP | Interpolated Ground | 41040.44 | 4.17 | 751.18 | 0 | 32.42 | 0 | OK | Ground clear controls. | 92 | 36.29 | 783.6
6421 | TIN-INTERP | Interpolated Ground | 41041.85 | -6.99 | 751.14 | 0 | 32.48 | 0 | OK | Ground clear controls. | 92 | 36.29 | 783.62
6422 | TIN-INTERP | Interpolated Ground | 41041.9 | -7.64 | 751.17 | 0 | 20.65 | 0 | OK | Ground clear controls. | 92 | 36.29 | 771.82
6423 | TIN-INTERP | Interpolated Ground | 41042.14 | -9.19 | 751.22 | 0 | 26.22 | 0 | OK | Ground clear controls. | 92 | 36.29 | 777.44
6424 | TIN-INTERP | Interpolated Ground | 41080.18 | 6.33 | 750.44 | 0 | 23.59 | 0 | OK | Ground clear controls. | 92 | 36.29 | 774.03
6425 | TIN-INTERP | Interpolated Ground | 41080.37 | 4.83 | 750.43 | 0 | 18.02 | 0 | OK | Ground clear controls. | 92 | 36.29 | 768.45
6426 | TIN-INTERP | Interpolated Ground | 41080.44 | 4.21 | 750.42 | 0 | 29.66 | 0 | OK | Ground clear controls. | 92 | 36.29 | 780.08
6427 | TIN-INTERP | Interpolated Ground | 41081.85 | -6.78 | 750.05 | 0 | 30.08 | 0 | OK | Ground clear controls. | 92 | 36.29 | 780.13
6428 | TIN-INTERP | Interpolated Ground | 41081.9 | -7.41 | 749.99 | 0 | 18.46 | 0 | OK | Ground clear controls. | 92 | 36.29 | 768.45
6429 | TIN-INTERP | Interpolated Ground | 41082.14 | -8.96 | 749.81 | 0 | 24.19 | 0 | OK | Ground clear controls. | 92 | 36.29 | 774
6430 | TIN-INTERP | Interpolated Ground | 41120.18 | 6.36 | 748.6 | 0 | 22.91 | 0 | OK | Ground clear controls. | 92 | 36.29 | 771.51
6431 | TIN-INTERP | Interpolated Ground | 41120.37 | 4.86 | 748.6 | 0 | 17.39 | 0 | OK | Ground clear controls. | 92 | 36.29 | 765.99
6432 | TIN-INTERP | Interpolated Ground | 41120.44 | 4.25 | 748.59 | 0 | 28.92 | 0 | OK | Ground clear controls. | 92 | 36.29 | 777.51
6433 | TIN-INTERP | Interpolated Ground | 41121.85 | -6.56 | 748.53 | 0 | 29.05 | 0 | OK | Ground clear controls. | 92 | 36.29 | 777.58
6434 | TIN-INTERP | Interpolated Ground | 41121.9 | -7.18 | 748.47 | 0 | 17.54 | 0 | OK | Ground clear controls. | 92 | 36.29 | 766.01
6435 | TIN-INTERP | Interpolated Ground | 41122.14 | -8.72 | 748.32 | 0 | 23.19 | 0 | OK | Ground clear controls. | 92 | 36.29 | 771.51
6436 | TIN-INTERP | Interpolated Ground | 41160.18 | 6.39 | 748.06 | 0 | 21.88 | 0 | OK | Ground clear controls. | 92 | 36.29 | 769.94
6437 | TIN-INTERP | Interpolated Ground | 41160.37 | 4.89 | 747.96 | 0 | 16.49 | 0 | OK | Ground clear controls. | 92 | 36.29 | 764.45
6438 | TIN-INTERP | Interpolated Ground | 41160.44 | 4.29 | 747.92 | 0 | 27.93 | 0 | OK | Ground clear controls. | 92 | 36.29 | 775.85
6439 | TIN-INTERP | Interpolated Ground | 41161.85 | -6.34 | 747.7 | 0 | 28.26 | 0 | OK | Ground clear controls. | 92 | 36.29 | 775.96
6440 | TIN-INTERP | Interpolated Ground | 41161.9 | -6.95 | 747.7 | 0 | 16.8 | 0 | OK | Ground clear controls. | 92 | 36.29 | 764.5
6441 | TIN-INTERP | Interpolated Ground | 41162.14 | -8.48 | 747.65 | 0 | 22.3 | 0 | OK | Ground clear controls. | 92 | 36.29 | 769.95
6442 | TIN-INTERP | Interpolated Ground | 41200.18 | 6.41 | 748.04 | 0 | 21.25 | 0 | OK | Ground clear controls. | 92 | 36.29 | 769.29
6443 | TIN-INTERP | Interpolated Ground | 41200.37 | 4.91 | 747.98 | 0 | 15.86 | 0 | OK | Ground clear controls. | 92 | 36.29 | 763.84
6444 | TIN-INTERP | Interpolated Ground | 41200.44 | 4.33 | 747.96 | 0 | 27.19 | 0 | OK | Ground clear controls. | 92 | 36.29 | 775.15
6445 | TIN-INTERP | Interpolated Ground | 41201.85 | -6.12 | 747.69 | 0 | 27.58 | 0 | OK | Ground clear controls. | 92 | 36.29 | 775.27
6446 | TIN-INTERP | Interpolated Ground | 41201.9 | -6.72 | 747.7 | 0 | 16.2 | 0 | OK | Ground clear controls. | 92 | 36.29 | 763.9
6447 | TIN-INTERP | Interpolated Ground | 41202.14 | -8.25 | 747.73 | 0 | 21.6 | 0 | OK | Ground clear controls. | 92 | 36.29 | 769.33
6448 | TIN-INTERP | Interpolated Ground | 41240.18 | 6.44 | 748.15 | 0 | 21.42 | 0 | OK | Ground clear controls. | 92 | 36.29 | 769.57
6449 | TIN-INTERP | Interpolated Ground | 41240.37 | 4.94 | 748.07 | 0 | 16.07 | 0 | OK | Ground clear controls. | 92 | 36.29 | 764.14
6450 | TIN-INTERP | Interpolated Ground | 41240.44 | 4.36 | 748.05 | 0 | 27.33 | 0 | OK | Ground clear controls. | 92 | 36.29 | 775.38
6451 | TIN-INTERP | Interpolated Ground | 41241.85 | -5.9 | 747.83 | 0 | 27.69 | 0 | OK | Ground clear controls. | 92 | 36.29 | 775.52
6452 | TIN-INTERP | Interpolated Ground | 41241.9 | -6.48 | 747.83 | 0 | 16.4 | 0 | OK | Ground clear controls. | 92 | 36.29 | 764.23
6453 | TIN-INTERP | Interpolated Ground | 41242.14 | -8.01 | 747.78 | 0 | 21.86 | 0 | OK | Ground clear controls. | 92 | 36.29 | 769.64
6454 | TIN-INTERP | Interpolated Ground | 41280.18 | 6.47 | 748.77 | 0 | 22.02 | 0 | OK | Ground clear controls. | 92 | 36.29 | 770.79
6455 | TIN-INTERP | Interpolated Ground | 41280.37 | 4.97 | 748.74 | 0 | 16.63 | 0 | OK | Ground clear controls. | 92 | 36.29 | 765.37
6456 | TIN-INTERP | Interpolated Ground | 41280.44 | 4.4 | 748.72 | 0 | 27.82 | 0 | OK | Ground clear controls. | 92 | 36.29 | 776.54
6457 | TIN-INTERP | Interpolated Ground | 41281.85 | -5.69 | 748.37 | 0 | 28.32 | 0 | OK | Ground clear controls. | 92 | 36.29 | 776.69
6458 | TIN-INTERP | Interpolated Ground | 41281.9 | -6.25 | 748.36 | 0 | 17.12 | 0 | OK | Ground clear controls. | 92 | 36.29 | 765.48
6459 | TIN-INTERP | Interpolated Ground | 41282.14 | -7.77 | 748.28 | 0 | 22.6 | 0 | OK | Ground clear controls. | 92 | 36.29 | 770.88
6460 | TIN-INTERP | Interpolated Ground | 41320.18 | 6.49 | 751.15 | 0 | 21.78 | 0 | OK | Ground clear controls. | 92 | 36.29 | 772.93
6461 | TIN-INTERP | Interpolated Ground | 41320.37 | 4.99 | 751.07 | 0 | 16.46 | 0 | OK | Ground clear controls. | 92 | 36.29 | 767.53
6462 | TIN-INTERP | Interpolated Ground | 41320.44 | 4.44 | 751.03 | 0 | 27.61 | 0 | OK | Ground clear controls. | 92 | 36.29 | 778.64
6463 | TIN-INTERP | Interpolated Ground | 41321.84 | -5.47 | 750.29 | 0 | 28.52 | 0 | OK | Ground clear controls. | 92 | 36.29 | 778.81
6464 | TIN-INTERP | Interpolated Ground | 41321.9 | -6.02 | 750.24 | 0 | 17.42 | 0 | OK | Ground clear controls. | 92 | 36.29 | 767.66
6465 | TIN-INTERP | Interpolated Ground | 41322.14 | -7.54 | 750.11 | 0 | 22.95 | 0 | OK | Ground clear controls. | 92 | 36.29 | 773.06
6466 | TIN-INTERP | Interpolated Ground | 41360.18 | 6.52 | 752.7 | 0 | 23.31 | 0 | OK | Ground clear controls. | 92 | 36.29 | 776.01
6467 | TIN-INTERP | Interpolated Ground | 41360.37 | 5.02 | 752.59 | 0 | 18 | 0 | OK | Ground clear controls. | 92 | 36.29 | 770.59
6468 | TIN-INTERP | Interpolated Ground | 41360.44 | 4.48 | 752.55 | 0 | 29.11 | 0 | OK | Ground clear controls. | 92 | 36.29 | 781.66
6469 | TIN-INTERP | Interpolated Ground | 41361.84 | -5.25 | 751.64 | 0 | 30.22 | 0 | OK | Ground clear controls. | 92 | 36.29 | 781.86
6470 | TIN-INTERP | Interpolated Ground | 41361.9 | -5.79 | 751.59 | 0 | 19.17 | 0 | OK | Ground clear controls. | 92 | 36.29 | 770.76
6471 | TIN-INTERP | Interpolated Ground | 41362.14 | -7.3 | 751.46 | 0 | 24.72 | 0 | OK | Ground clear controls. | 92 | 36.29 | 776.18
6472 | TIN-INTERP | Interpolated Ground | 41400.18 | 6.55 | 753.17 | 0 | 26.86 | 0 | OK | Ground clear controls. | 92 | 36.29 | 780.03
6473 | TIN-INTERP | Interpolated Ground | 41400.37 | 5.05 | 752.94 | 0 | 21.67 | 0 | OK | Ground clear controls. | 92 | 36.29 | 774.61
6474 | TIN-INTERP | Interpolated Ground | 41400.44 | 4.52 | 752.84 | 0 | 32.8 | 0 | OK | Ground clear controls. | 92 | 36.29 | 785.64
6475 | TIN-INTERP | Interpolated Ground | 41401.84 | -5.03 | 751.64 | 0 | 34.2 | 0 | OK | Ground clear controls. | 92 | 36.29 | 785.84
6476 | TIN-INTERP | Interpolated Ground | 41401.9 | -5.56 | 751.59 | 0 | 23.2 | 0 | OK | Ground clear controls. | 92 | 36.29 | 774.79
6477 | TIN-INTERP | Interpolated Ground | 41402.14 | -7.07 | 751.45 | 0 | 28.79 | 0 | OK | Ground clear controls. | 92 | 36.29 | 780.24
6478 | TIN-INTERP | Interpolated Ground | 41440.18 | 6.57 | 755.08 | 0 | 29.89 | 0 | OK | Ground clear controls. | 92 | 36.29 | 784.97
6479 | TIN-INTERP | Interpolated Ground | 41440.37 | 5.07 | 755.01 | 0 | 24.52 | 0 | OK | Ground clear controls. | 92 | 36.29 | 779.53
6480 | TIN-INTERP | Interpolated Ground | 41440.44 | 4.56 | 754.97 | 0 | 35.58 | 0 | OK | Ground clear controls. | 92 | 36.29 | 790.55
6481 | TIN-INTERP | Interpolated Ground | 41441.84 | -4.81 | 754.48 | 0 | 36.29 | 0 | OK | Ground clear controls. | 92 | 36.29 | 790.77
6482 | TIN-INTERP | Interpolated Ground | 41441.9 | -5.33 | 754.44 | 0 | 25.31 | 0 | OK | Ground clear controls. | 92 | 30.93 | 779.75
6483 | TIN-INTERP | Interpolated Ground | 41442.14 | -6.83 | 754.32 | 0 | 30.93 | 0 | OK | Ground clear controls. | 92 | 30.93 | 785.25
6484 | TIN-INTERP | Interpolated Ground | 41473.49 | -4.64 | 755.45 | 0 | 39.87 | 0 | OK | Ground clear controls. | 93 | 42.06 | 795.32
6485 | TIN-INTERP | Interpolated Ground | 41473.5 | -6.64 | 755.38 | 0 | 34.44 | 0 | OK | Ground clear controls. | 93 | 42.06 | 789.82
6486 | TIN-INTERP | Interpolated Ground | 41473.53 | 4.59 | 755.99 | 0 | 39.33 | 0 | OK | Ground clear controls. | 93 | 42.06 | 795.32
6487 | TIN-INTERP | Interpolated Ground | 41473.55 | -5.14 | 755.46 | 0 | 28.86 | 0 | OK | Ground clear controls. | 93 | 42.06 | 784.32
6488 | TIN-INTERP | Interpolated Ground | 41473.56 | 5.1 | 756.02 | 0 | 28.3 | 0 | OK | Ground clear controls. | 93 | 42.06 | 784.32
6489 | TIN-INTERP | Interpolated Ground | 41473.56 | 6.6 | 756.08 | 0 | 33.74 | 0 | OK | Ground clear controls. | 93 | 42.06 | 789.82
6490 | TIN-INTERP | Interpolated Ground | 41513.49 | -4.64 | 753.35 | 0 | 35.7 | 0 | OK | Ground clear controls. | 93 | 42.06 | 789.05
6491 | TIN-INTERP | Interpolated Ground | 41513.5 | -6.64 | 753.35 | 0 | 30.2 | 0 | OK | Ground clear controls. | 93 | 42.06 | 783.55
6492 | TIN-INTERP | Interpolated Ground | 41513.53 | 4.59 | 753.28 | 0 | 35.77 | 0 | OK | Ground clear controls. | 93 | 42.06 | 789.05
6493 | TIN-INTERP | Interpolated Ground | 41513.55 | -5.14 | 753.35 | 0 | 24.81 | 0 | OK | Ground clear controls. | 93 | 42.06 | 778.16
6494 | TIN-INTERP | Interpolated Ground | 41513.56 | 5.1 | 753.33 | 0 | 24.82 | 0 | OK | Ground clear controls. | 93 | 42.06 | 778.15
6495 | TIN-INTERP | Interpolated Ground | 41513.56 | 6.6 | 753.4 | 0 | 30.18 | 0 | OK | Ground clear controls. | 93 | 42.06 | 783.58
6496 | TIN-INTERP | Interpolated Ground | 41553.49 | -4.64 | 750.28 | 0 | 33.45 | 0 | OK | Ground clear controls. | 93 | 42.06 | 783.73
6497 | TIN-INTERP | Interpolated Ground | 41553.5 | -6.64 | 750.16 | 0 | 28.06 | 0 | OK | Ground clear controls. | 93 | 42.06 | 778.22
6498 | TIN-INTERP | Interpolated Ground | 41553.53 | 4.59 | 750.63 | 0 | 33.09 | 0 | OK | Ground clear controls. | 93 | 42.06 | 783.72
6499 | TIN-INTERP | Interpolated Ground | 41553.55 | -5.14 | 750.26 | 0 | 22.66 | 0 | OK | Ground clear controls. | 93 | 42.06 | 772.92
6500 | TIN-INTERP | Interpolated Ground | 41553.56 | 5.1 | 750.7 | 0 | 22.19 | 0 | OK | Ground clear controls. | 93 | 42.06 | 772.89
6501 | TIN-INTERP | Interpolated Ground | 41553.56 | 6.6 | 750.89 | 0 | 27.39 | 0 | OK | Ground clear controls. | 93 | 42.06 | 778.28
6502 | TIN-INTERP | Interpolated Ground | 41593.49 | -4.63 | 748.49 | 0 | 30.86 | 0 | OK | Ground clear controls. | 93 | 42.06 | 779.35
6503 | TIN-INTERP | Interpolated Ground | 41593.5 | -6.64 | 748.39 | 0 | 25.44 | 0 | OK | Ground clear controls. | 93 | 42.06 | 773.83
6504 | TIN-INTERP | Interpolated Ground | 41593.53 | 4.59 | 749.04 | 0 | 30.29 | 0 | OK | Ground clear controls. | 93 | 42.06 | 779.33
6505 | TIN-INTERP | Interpolated Ground | 41593.55 | -5.13 | 748.44 | 0 | 20.16 | 0 | OK | Ground clear controls. | 93 | 42.06 | 768.6
6506 | TIN-INTERP | Interpolated Ground | 41593.56 | 5.1 | 749.09 | 0 | 19.48 | 0 | OK | Ground clear controls. | 93 | 42.06 | 768.57
6507 | TIN-INTERP | Interpolated Ground | 41593.56 | 6.6 | 749.01 | 0 | 24.92 | 0 | OK | Ground clear controls. | 93 | 42.06 | 773.93
6508 | TIN-INTERP | Interpolated Ground | 41633.49 | -4.63 | 747.35 | 0 | 28.55 | 0 | OK | Ground clear controls. | 93 | 42.06 | 775.9
6509 | TIN-INTERP | Interpolated Ground | 41633.5 | -6.63 | 747.25 | 0 | 23.13 | 0 | OK | Ground clear controls. | 93 | 42.06 | 770.38
6510 | TIN-INTERP | Interpolated Ground | 41633.53 | 4.6 | 747.35 | 0 | 28.54 | 0 | OK | Ground clear controls. | 93 | 42.06 | 775.89
6511 | TIN-INTERP | Interpolated Ground | 41633.55 | -5.13 | 747.32 | 0 | 17.89 | 0 | OK | Ground clear controls. | 93 | 42.06 | 765.21
6512 | TIN-INTERP | Interpolated Ground | 41633.56 | 5.1 | 747.37 | 0 | 17.81 | 0 | OK | Ground clear controls. | 93 | 42.06 | 765.18
6513 | TIN-INTERP | Interpolated Ground | 41633.56 | 6.6 | 747.45 | 0 | 23.05 | 0 | OK | Ground clear controls. | 93 | 42.06 | 770.5
6514 | TIN-INTERP | Interpolated Ground | 41673.49 | -4.63 | 747.44 | 0 | 25.96 | 0 | OK | Ground clear controls. | 93 | 42.06 | 773.4
6515 | TIN-INTERP | Interpolated Ground | 41673.5 | -6.63 | 747.47 | 0 | 20.41 | 0 | OK | Ground clear controls. | 93 | 42.06 | 767.88
6516 | TIN-INTERP | Interpolated Ground | 41673.53 | 4.6 | 747.76 | 0 | 25.62 | 0 | OK | Ground clear controls. | 93 | 42.06 | 773.38
6517 | TIN-INTERP | Interpolated Ground | 41673.55 | -5.13 | 747.45 | 0 | 15.3 | 0 | OK | Ground clear controls. | 93 | 42.06 | 762.75
6518 | TIN-INTERP | Interpolated Ground | 41673.56 | 5.1 | 747.79 | 0 | 14.91 | 0 | OK | Ground clear controls. | 93 | 42.06 | 762.7
6519 | TIN-INTERP | Interpolated Ground | 41673.56 | 6.6 | 747.91 | 0 | 20.1 | 0 | OK | Ground clear controls. | 93 | 42.06 | 768.01
6520 | TIN-INTERP | Interpolated Ground | 41713.49 | -4.62 | 747.91 | 0 | 23.93 | 0 | OK | Ground clear controls. | 93 | 42.06 | 771.84
6521 | TIN-INTERP | Interpolated Ground | 41713.5 | -6.63 | 747.99 | 0 | 18.33 | 0 | OK | Ground clear controls. | 93 | 42.06 | 766.32
6522 | TIN-INTERP | Interpolated Ground | 41713.53 | 4.6 | 748.19 | 0 | 23.63 | 0 | OK | Ground clear controls. | 93 | 42.06 | 771.82
6523 | TIN-INTERP | Interpolated Ground | 41713.55 | -5.13 | 747.88 | 0 | 13.33 | 0 | OK | Ground clear controls. | 93 | 42.06 | 761.21
6524 | TIN-INTERP | Interpolated Ground | 41713.56 | 5.1 | 748.16 | 0 | 13 | 0 | OK | Ground clear controls. | 93 | 42.06 | 761.16
6525 | TIN-INTERP | Interpolated Ground | 41713.56 | 6.6 | 748.09 | 0 | 18.37 | 0 | OK | Ground clear controls. | 93 | 42.06 | 766.46
6526 | TIN-INTERP | Interpolated Ground | 41753.49 | -4.62 | 747.54 | 0 | 23.67 | 0 | OK | Ground clear controls. | 93 | 42.06 | 771.21
6527 | TIN-INTERP | Interpolated Ground | 41753.5 | -6.62 | 747.47 | 0 | 18.22 | 0 | OK | Ground clear controls. | 93 | 42.06 | 765.69
6528 | TIN-INTERP | Interpolated Ground | 41753.53 | 4.6 | 747.84 | 0 | 23.35 | 0 | OK | Ground clear controls. | 93 | 42.06 | 771.19
6529 | TIN-INTERP | Interpolated Ground | 41753.55 | -5.12 | 747.53 | 0 | 13.05 | 0 | OK | Ground clear controls. | 93 | 42.06 | 760.58
6530 | TIN-INTERP | Interpolated Ground | 41753.56 | 5.1 | 747.86 | 0 | 12.68 | 0 | OK | Ground clear controls. | 93 | 42.06 | 760.54
6531 | TIN-INTERP | Interpolated Ground | 41753.56 | 6.6 | 747.95 | 0 | 17.88 | 0 | OK | Ground clear controls. | 93 | 42.06 | 765.83
6532 | TIN-INTERP | Interpolated Ground | 41793.49 | -4.62 | 746.11 | 0 | 25.42 | 0 | OK | Ground clear controls. | 93 | 42.06 | 771.53
6533 | TIN-INTERP | Interpolated Ground | 41793.5 | -6.62 | 746.08 | 0 | 19.92 | 0 | OK | Ground clear controls. | 93 | 42.06 | 766
6534 | TIN-INTERP | Interpolated Ground | 41793.53 | 4.6 | 746.35 | 0 | 25.16 | 0 | OK | Ground clear controls. | 93 | 42.06 | 771.51
6535 | TIN-INTERP | Interpolated Ground | 41793.55 | -5.12 | 746.06 | 0 | 14.83 | 0 | OK | Ground clear controls. | 93 | 42.06 | 760.89
6536 | TIN-INTERP | Interpolated Ground | 41793.56 | 5.1 | 746.33 | 0 | 14.51 | 0 | OK | Ground clear controls. | 93 | 42.06 | 760.84
6537 | TIN-INTERP | Interpolated Ground | 41793.56 | 6.6 | 746.43 | 0 | 19.71 | 0 | OK | Ground clear controls. | 93 | 42.06 | 766.14
6538 | TIN-INTERP | Interpolated Ground | 41833.49 | -4.62 | 746.49 | 0 | 26.28 | 0 | OK | Ground clear controls. | 93 | 42.06 | 772.77
6539 | TIN-INTERP | Interpolated Ground | 41833.5 | -6.62 | 746.42 | 0 | 20.84 | 0 | OK | Ground clear controls. | 93 | 42.06 | 767.26
6540 | TIN-INTERP | Interpolated Ground | 41833.53 | 4.6 | 747.45 | 0 | 25.31 | 0 | OK | Ground clear controls. | 93 | 42.06 | 772.76
6541 | TIN-INTERP | Interpolated Ground | 41833.55 | -5.12 | 746.46 | 0 | 15.65 | 0 | OK | Ground clear controls. | 93 | 42.06 | 762.11
6542 | TIN-INTERP | Interpolated Ground | 41833.56 | 5.1 | 747.53 | 0 | 14.53 | 0 | OK | Ground clear controls. | 93 | 42.06 | 762.06
6543 | TIN-INTERP | Interpolated Ground | 41833.56 | 6.6 | 747.75 | 0 | 19.63 | 0 | OK | Ground clear controls. | 93 | 42.06 | 767.38
6544 | TIN-INTERP | Interpolated Ground | 41873.49 | -4.61 | 746.15 | 0 | 28.82 | 0 | OK | Ground clear controls. | 93 | 42.06 | 774.97
6545 | TIN-INTERP | Interpolated Ground | 41873.5 | -6.61 | 746 | 0 | 23.45 | 0 | OK | Ground clear controls. | 93 | 42.06 | 769.45
6546 | TIN-INTERP | Interpolated Ground | 41873.53 | 4.6 | 746.95 | 0 | 28 | 0 | OK | Ground clear controls. | 93 | 42.06 | 774.95
6547 | TIN-INTERP | Interpolated Ground | 41873.55 | -5.11 | 746.09 | 0 | 18.16 | 0 | OK | Ground clear controls. | 93 | 42.06 | 764.25
6548 | TIN-INTERP | Interpolated Ground | 41873.56 | 5.1 | 746.96 | 0 | 17.26 | 0 | OK | Ground clear controls. | 93 | 42.06 | 764.22
6549 | TIN-INTERP | Interpolated Ground | 41873.56 | 6.6 | 747.08 | 0 | 22.48 | 0 | OK | Ground clear controls. | 93 | 42.06 | 769.56
6550 | TIN-INTERP | Interpolated Ground | 41913.49 | -4.61 | 745.54 | 0 | 32.55 | 0 | OK | Ground clear controls. | 93 | 42.06 | 778.09
6551 | TIN-INTERP | Interpolated Ground | 41913.5 | -6.61 | 745.45 | 0 | 27.13 | 0 | OK | Ground clear controls. | 93 | 42.06 | 772.58
6552 | TIN-INTERP | Interpolated Ground | 41913.53 | 4.6 | 745.89 | 0 | 32.19 | 0 | OK | Ground clear controls. | 93 | 42.06 | 778.08
6553 | TIN-INTERP | Interpolated Ground | 41913.55 | -5.11 | 745.52 | 0 | 21.8 | 0 | OK | Ground clear controls. | 93 | 42.06 | 767.32
6554 | TIN-INTERP | Interpolated Ground | 41913.56 | 5.1 | 745.88 | 0 | 21.41 | 0 | OK | Ground clear controls. | 93 | 42.06 | 767.29
6555 | TIN-INTERP | Interpolated Ground | 41913.56 | 6.6 | 746.03 | 0 | 26.64 | 0 | OK | Ground clear controls. | 93 | 42.06 | 772.67
6556 | TIN-INTERP | Interpolated Ground | 41953.49 | -4.61 | 745.2 | 0 | 36.96 | 0 | OK | Ground clear controls. | 93 | 42.06 | 782.16
6557 | TIN-INTERP | Interpolated Ground | 41953.5 | -6.61 | 745.2 | 0 | 31.45 | 0 | OK | Ground clear controls. | 93 | 42.06 | 776.65
6558 | TIN-INTERP | Interpolated Ground | 41953.53 | 4.6 | 745.42 | 0 | 36.73 | 0 | OK | Ground clear controls. | 93 | 42.06 | 782.15
6559 | TIN-INTERP | Interpolated Ground | 41953.55 | -5.11 | 745.17 | 0 | 26.13 | 0 | OK | Ground clear controls. | 93 | 42.06 | 771.3
6560 | TIN-INTERP | Interpolated Ground | 41953.56 | 5.1 | 745.39 | 0 | 25.89 | 0 | OK | Ground clear controls. | 93 | 42.06 | 771.28
6561 | TIN-INTERP | Interpolated Ground | 41953.56 | 6.6 | 745.41 | 0 | 31.3 | 0 | OK | Ground clear controls. | 93 | 42.06 | 776.71
6562 | TIN-INTERP | Interpolated Ground | 41993.49 | -4.6 | 745.11 | 0 | 42.06 | 0 | OK | Ground clear controls. | 93 | 42.06 | 787.17
6563 | TIN-INTERP | Interpolated Ground | 41993.5 | -6.6 | 745.16 | 0 | 36.51 | 0 | OK | Ground clear controls. | 93 | 41.93 | 781.67
6564 | TIN-INTERP | Interpolated Ground | 41993.53 | 4.6 | 745.25 | 0 | 41.93 | 0 | OK | Ground clear controls. | 93 | 41.93 | 787.18
6565 | TIN-INTERP | Interpolated Ground | 41993.55 | -5.1 | 745.09 | 0 | 31.12 | 0 | OK | Ground clear controls. | 93 | 36.42 | 776.21
6566 | TIN-INTERP | Interpolated Ground | 41993.56 | 5.1 | 745.24 | 0 | 30.97 | 0 | OK | Ground clear controls. | 93 | 36.42 | 776.21
6567 | TIN-INTERP | Interpolated Ground | 41993.56 | 6.6 | 745.27 | 0 | 36.42 | 0 | OK | Ground clear controls. | 93 | 36.42 | 781.69
6568 | TIN-INTERP | Interpolated Ground | 42006.68 | -4.6 | 745.24 | 0 | 43.79 | 0 | OK | Ground clear controls. | 94 | 43.79 | 789.03
6569 | TIN-INTERP | Interpolated Ground | 42006.7 | 6.6 | 745.43 | 0 | 38.1 | 0 | OK | Ground clear controls. | 94 | 43.7 | 783.53
6570 | TIN-INTERP | Interpolated Ground | 42006.7 | 5.1 | 745.39 | 0 | 32.64 | 0 | OK | Ground clear controls. | 94 | 43.7 | 778.03
6571 | TIN-INTERP | Interpolated Ground | 42006.7 | -5.1 | 745.28 | 0 | 32.75 | 0 | OK | Ground clear controls. | 94 | 43.7 | 778.03
6572 | TIN-INTERP | Interpolated Ground | 42006.72 | -6.6 | 745.28 | 0 | 38.25 | 0 | OK | Ground clear controls. | 94 | 43.7 | 783.53
6573 | TIN-INTERP | Interpolated Ground | 42006.74 | 4.6 | 745.33 | 0 | 43.7 | 0 | OK | Ground clear controls. | 94 | 43.7 | 789.03
6574 | TIN-INTERP | Interpolated Ground | 42046.68 | -4.61 | 745.81 | 0 | 39.15 | 0 | OK | Ground clear controls. | 94 | 39.15 | 784.96
6575 | TIN-INTERP | Interpolated Ground | 42046.7 | 6.59 | 746.08 | 0 | 33.42 | 0 | OK | Ground clear controls. | 94 | 38.93 | 779.5
6576 | TIN-INTERP | Interpolated Ground | 42046.7 | 5.09 | 746.06 | 0 | 27.99 | 0 | OK | Ground clear controls. | 94 | 38.93 | 774.05
6577 | TIN-INTERP | Interpolated Ground | 42046.7 | -5.11 | 745.78 | 0 | 28.29 | 0 | OK | Ground clear controls. | 94 | 38.93 | 774.07
6578 | TIN-INTERP | Interpolated Ground | 42046.72 | -6.61 | 745.68 | 0 | 33.79 | 0 | OK | Ground clear controls. | 94 | 38.93 | 779.47
6579 | TIN-INTERP | Interpolated Ground | 42046.74 | 4.59 | 746.06 | 0 | 38.93 | 0 | OK | Ground clear controls. | 94 | 38.93 | 784.99
6580 | TIN-INTERP | Interpolated Ground | 42086.68 | -4.61 | 747.47 | 0 | 34.37 | 0 | OK | Ground clear controls. | 94 | 38.25 | 781.84
6581 | TIN-INTERP | Interpolated Ground | 42086.7 | 6.59 | 747.13 | 0 | 29.28 | 0 | OK | Ground clear controls. | 94 | 38.25 | 776.41
6582 | TIN-INTERP | Interpolated Ground | 42086.7 | 5.09 | 747.11 | 0 | 23.89 | 0 | OK | Ground clear controls. | 94 | 38.25 | 771
6583 | TIN-INTERP | Interpolated Ground | 42086.7 | -5.11 | 747.47 | 0 | 23.55 | 0 | OK | Ground clear controls. | 94 | 38.25 | 771.02
6584 | TIN-INTERP | Interpolated Ground | 42086.72 | -6.61 | 747.49 | 0 | 28.88 | 0 | OK | Ground clear controls. | 94 | 38.25 | 776.37
6585 | TIN-INTERP | Interpolated Ground | 42086.74 | 4.59 | 747.12 | 0 | 34.76 | 0 | OK | Ground clear controls. | 94 | 38.25 | 781.88
6586 | TIN-INTERP | Interpolated Ground | 42126.68 | -4.62 | 751.02 | 0 | 28.64 | 0 | OK | Ground clear controls. | 94 | 38.25 | 779.66
6587 | TIN-INTERP | Interpolated Ground | 42126.7 | 6.59 | 750.45 | 0 | 23.8 | 0 | OK | Ground clear controls. | 94 | 38.25 | 774.25
6588 | TIN-INTERP | Interpolated Ground | 42126.7 | 5.09 | 750.45 | 0 | 18.42 | 0 | OK | Ground clear controls. | 94 | 38.25 | 768.87
6589 | TIN-INTERP | Interpolated Ground | 42126.7 | -5.12 | 751.02 | 0 | 17.89 | 0 | OK | Ground clear controls. | 94 | 38.25 | 768.91
6590 | TIN-INTERP | Interpolated Ground | 42126.72 | -6.62 | 750.96 | 0 | 23.23 | 0 | OK | Ground clear controls. | 94 | 38.25 | 774.19
6591 | TIN-INTERP | Interpolated Ground | 42126.74 | 4.59 | 750.5 | 0 | 29.22 | 0 | OK | Ground clear controls. | 94 | 38.25 | 779.72
6592 | TIN-INTERP | Interpolated Ground | 42166.68 | -4.62 | 754.95 | 0 | 23.48 | 0 | OK | Ground clear controls. | 94 | 38.25 | 778.43
6593 | TIN-INTERP | Interpolated Ground | 42166.7 | 6.58 | 754.43 | 0 | 18.6 | 0 | OK | Ground clear controls. | 94 | 38.25 | 773.03
6594 | TIN-INTERP | Interpolated Ground | 42166.7 | 5.08 | 754.64 | 0 | 13.04 | 0 | OK | Ground clear controls. | 94 | 38.25 | 767.68
6595 | TIN-INTERP | Interpolated Ground | 42166.7 | -5.12 | 754.92 | 0 | 12.79 | 0 | OK | Ground clear controls. | 94 | 38.25 | 767.71
6596 | TIN-INTERP | Interpolated Ground | 42166.72 | -6.62 | 754.85 | 0 | 18.12 | 0 | OK | Ground clear controls. | 94 | 38.25 | 772.97
6597 | TIN-INTERP | Interpolated Ground | 42166.74 | 4.58 | 754.7 | 0 | 23.8 | 0 | OK | Ground clear controls. | 94 | 38.25 | 778.5
6598 | TIN-INTERP | Interpolated Ground | 42206.68 | -4.62 | 755.83 | 0 | 22.3 | 0 | OK | Ground clear controls. | 94 | 38.25 | 778.13
6599 | TIN-INTERP | Interpolated Ground | 42206.7 | 6.58 | 756.56 | 0 | 16.19 | 0 | OK | Ground clear controls. | 94 | 38.25 | 772.75
6600 | TIN-INTERP | Interpolated Ground | 42206.7 | 5.08 | 756.46 | 0 | 10.95 | 0 | OK | Ground clear controls. | 94 | 38.25 | 767.41
6601 | TIN-INTERP | Interpolated Ground | 42206.7 | -5.12 | 755.77 | 0 | 11.68 | 0 | OK | Ground clear controls. | 94 | 38.25 | 767.45
6602 | TIN-INTERP | Interpolated Ground | 42206.72 | -6.62 | 755.61 | 0 | 17.08 | 0 | OK | Ground clear controls. | 94 | 38.25 | 772.69
6603 | TIN-INTERP | Interpolated Ground | 42206.74 | 4.58 | 756.45 | 0 | 21.76 | 0 | OK | Ground clear controls. | 94 | 38.25 | 778.21
6604 | TIN-INTERP | Interpolated Ground | 42246.68 | -4.63 | 757.05 | 0 | 21.74 | 0 | OK | Ground clear controls. | 94 | 38.25 | 778.79
6605 | TIN-INTERP | Interpolated Ground | 42246.7 | 6.57 | 757.87 | 0 | 15.54 | 0 | OK | Ground clear controls. | 94 | 38.25 | 773.41
6606 | TIN-INTERP | Interpolated Ground | 42246.7 | 5.07 | 757.73 | 0 | 10.34 | 0 | OK | Ground clear controls. | 94 | 38.25 | 768.07
6607 | TIN-INTERP | Interpolated Ground | 42246.7 | -5.13 | 757 | 0 | 11.1 | 0 | OK | Ground clear controls. | 94 | 38.25 | 768.1
6608 | TIN-INTERP | Interpolated Ground | 42246.72 | -6.63 | 756.99 | 0 | 16.34 | 0 | OK | Ground clear controls. | 94 | 38.25 | 773.33
6609 | TIN-INTERP | Interpolated Ground | 42246.74 | 4.57 | 757.68 | 0 | 21.19 | 0 | OK | Ground clear controls. | 94 | 38.25 | 778.87
6610 | TIN-INTERP | Interpolated Ground | 42286.68 | -4.63 | 757.51 | 0 | 22.87 | 0 | OK | Ground clear controls. | 94 | 38.25 | 780.38
6611 | TIN-INTERP | Interpolated Ground | 42286.7 | 6.57 | 758.57 | 0 | 16.43 | 0 | OK | Ground clear controls. | 94 | 38.25 | 775
6612 | TIN-INTERP | Interpolated Ground | 42286.7 | 5.07 | 758.45 | 0 | 11.2 | 0 | OK | Ground clear controls. | 94 | 38.25 | 769.65
6613 | TIN-INTERP | Interpolated Ground | 42286.7 | -5.13 | 757.47 | 0 | 12.22 | 0 | OK | Ground clear controls. | 94 | 38.25 | 769.69
6614 | TIN-INTERP | Interpolated Ground | 42286.72 | -6.63 | 757.37 | 0 | 17.56 | 0 | OK | Ground clear controls. | 94 | 38.25 | 774.93
6615 | TIN-INTERP | Interpolated Ground | 42286.74 | 4.57 | 758.41 | 0 | 22.05 | 0 | OK | Ground clear controls. | 94 | 38.25 | 780.46
6616 | TIN-INTERP | Interpolated Ground | 42326.68 | -4.63 | 757.33 | 0 | 25.59 | 0 | OK | Ground clear controls. | 94 | 38.25 | 782.92
6617 | TIN-INTERP | Interpolated Ground | 42326.7 | 6.57 | 758.2 | 0 | 19.32 | 0 | OK | Ground clear controls. | 94 | 38.25 | 777.52
6618 | TIN-INTERP | Interpolated Ground | 42326.7 | 5.07 | 758.11 | 0 | 14.05 | 0 | OK | Ground clear controls. | 94 | 38.25 | 772.16
6619 | TIN-INTERP | Interpolated Ground | 42326.7 | -5.13 | 757.25 | 0 | 14.94 | 0 | OK | Ground clear controls. | 94 | 38.25 | 772.19
6620 | TIN-INTERP | Interpolated Ground | 42326.72 | -6.63 | 757.19 | 0 | 20.27 | 0 | OK | Ground clear controls. | 94 | 38.25 | 777.46
6621 | TIN-INTERP | Interpolated Ground | 42326.74 | 4.57 | 758.04 | 0 | 24.96 | 0 | OK | Ground clear controls. | 94 | 38.25 | 783
6622 | TIN-INTERP | Interpolated Ground | 42366.68 | -4.64 | 758.37 | 0 | 28.04 | 0 | OK | Ground clear controls. | 94 | 38.25 | 786.41
6623 | TIN-INTERP | Interpolated Ground | 42366.7 | 6.56 | 759.6 | 0 | 21.39 | 0 | OK | Ground clear controls. | 94 | 38.25 | 780.99
6624 | TIN-INTERP | Interpolated Ground | 42366.7 | 5.06 | 759.47 | 0 | 16.13 | 0 | OK | Ground clear controls. | 94 | 38.25 | 775.6
6625 | TIN-INTERP | Interpolated Ground | 42366.7 | -5.14 | 758.31 | 0 | 17.32 | 0 | OK | Ground clear controls. | 94 | 38.25 | 775.63
6626 | TIN-INTERP | Interpolated Ground | 42366.72 | -6.64 | 758.16 | 0 | 22.78 | 0 | OK | Ground clear controls. | 94 | 38.25 | 780.94
6627 | TIN-INTERP | Interpolated Ground | 42366.74 | 4.56 | 759.42 | 0 | 27.05 | 0 | OK | Ground clear controls. | 94 | 38.25 | 786.47
6628 | TIN-INTERP | Interpolated Ground | 42406.68 | -4.64 | 759.39 | 0 | 31.45 | 0 | OK | Ground clear controls. | 94 | 38.25 | 790.84
6629 | TIN-INTERP | Interpolated Ground | 42406.7 | 6.56 | 760.58 | 0 | 24.82 | 0 | OK | Ground clear controls. | 94 | 38.25 | 785.4
6630 | TIN-INTERP | Interpolated Ground | 42406.7 | 5.06 | 760.36 | 0 | 19.61 | 0 | OK | Ground clear controls. | 94 | 38.25 | 779.97
6631 | TIN-INTERP | Interpolated Ground | 42406.7 | -5.14 | 759.32 | 0 | 20.67 | 0 | OK | Ground clear controls. | 94 | 38.25 | 779.99
6632 | TIN-INTERP | Interpolated Ground | 42406.72 | -6.64 | 759.14 | 0 | 26.23 | 0 | OK | Ground clear controls. | 94 | 38.25 | 785.37
6633 | TIN-INTERP | Interpolated Ground | 42406.74 | 4.56 | 760.3 | 0 | 30.58 | 0 | OK | Ground clear controls. | 94 | 38.25 | 790.88
6634 | TIN-INTERP | Interpolated Ground | 42446.68 | -4.65 | 757.98 | 0 | 38.25 | 0 | OK | Ground clear controls. | 94 | 38.25 | 796.23
6635 | TIN-INTERP | Interpolated Ground | 42446.7 | 6.55 | 758.48 | 0 | 32.26 | 0 | OK | Ground clear controls. | 94 | 37.79 | 790.74
6636 | TIN-INTERP | Interpolated Ground | 42446.7 | 5.05 | 758.49 | 0 | 26.78 | 0 | OK | Ground clear controls. | 94 | 37.79 | 785.27
6637 | TIN-INTERP | Interpolated Ground | 42446.7 | -5.15 | 757.94 | 0 | 27.35 | 0 | OK | Ground clear controls. | 94 | 37.79 | 785.29
6638 | TIN-INTERP | Interpolated Ground | 42446.72 | -6.65 | 757.8 | 0 | 32.93 | 0 | OK | Ground clear controls. | 94 | 37.79 | 790.73
6639 | TIN-INTERP | Interpolated Ground | 42446.74 | 4.55 | 758.45 | 0 | 37.79 | 0 | OK | Ground clear controls. | 94 | 37.79 | 796.24
6640 | TIN-INTERP | Interpolated Ground | 42470.2 | -4.65 | 755.86 | 0 | 43.97 | 0 | OK | Ground clear controls. | 95 | 43.97 | 799.83
6641 | TIN-INTERP | Interpolated Ground | 42470.21 | 4.55 | 756.54 | 0 | 43.3 | 0 | OK | Ground clear controls. | 95 | 43.3 | 799.84
6642 | TIN-INTERP | Interpolated Ground | 42470.25 | -5.15 | 755.84 | 0 | 33 | 0 | OK | Ground clear controls. | 95 | 39.24 | 788.84
6643 | TIN-INTERP | Interpolated Ground | 42470.25 | 6.55 | 756.74 | 0 | 37.59 | 0 | OK | Ground clear controls. | 95 | 39.24 | 794.33
6644 | TIN-INTERP | Interpolated Ground | 42470.27 | -6.65 | 755.78 | 0 | 38.55 | 0 | OK | Ground clear controls. | 95 | 39.24 | 794.33
6645 | TIN-INTERP | Interpolated Ground | 42470.28 | 5.05 | 756.61 | 0 | 32.22 | 0 | OK | Ground clear controls. | 95 | 39.24 | 788.83
6646 | TIN-INTERP | Interpolated Ground | 42510.2 | -4.65 | 752.81 | 0 | 39.24 | 0 | OK | Ground clear controls. | 95 | 39.24 | 792.05
6647 | TIN-INTERP | Interpolated Ground | 42510.21 | 4.55 | 753.17 | 0 | 38.92 | 0 | OK | Ground clear controls. | 95 | 38.92 | 792.09
6648 | TIN-INTERP | Interpolated Ground | 42510.25 | -5.15 | 752.78 | 0 | 28.44 | 0 | OK | Ground clear controls. | 95 | 37.85 | 781.22
6649 | TIN-INTERP | Interpolated Ground | 42510.25 | 6.55 | 753.16 | 0 | 33.49 | 0 | OK | Ground clear controls. | 95 | 37.85 | 786.65
6650 | TIN-INTERP | Interpolated Ground | 42510.27 | -6.65 | 752.68 | 0 | 33.95 | 0 | OK | Ground clear controls. | 95 | 37.85 | 786.63
6651 | TIN-INTERP | Interpolated Ground | 42510.28 | 5.05 | 753.17 | 0 | 28.06 | 0 | OK | Ground clear controls. | 95 | 37.85 | 781.23
6652 | TIN-INTERP | Interpolated Ground | 42550.2 | -4.64 | 749.92 | 0 | 35.32 | 0 | OK | Ground clear controls. | 95 | 37.85 | 785.24
6653 | TIN-INTERP | Interpolated Ground | 42550.21 | 4.56 | 750.24 | 0 | 35.08 | 0 | OK | Ground clear controls. | 95 | 37.85 | 785.32
6654 | TIN-INTERP | Interpolated Ground | 42550.25 | -5.14 | 749.89 | 0 | 24.68 | 0 | OK | Ground clear controls. | 95 | 37.85 | 774.57
6655 | TIN-INTERP | Interpolated Ground | 42550.25 | 6.56 | 750.33 | 0 | 29.59 | 0 | OK | Ground clear controls. | 95 | 37.85 | 779.92
6656 | TIN-INTERP | Interpolated Ground | 42550.27 | -6.64 | 749.77 | 0 | 30.13 | 0 | OK | Ground clear controls. | 95 | 37.85 | 779.9
6657 | TIN-INTERP | Interpolated Ground | 42550.28 | 5.06 | 750.24 | 0 | 24.35 | 0 | OK | Ground clear controls. | 95 | 37.85 | 774.59
6658 | TIN-INTERP | Interpolated Ground | 42590.2 | -4.64 | 747.31 | 0 | 32.11 | 0 | OK | Ground clear controls. | 95 | 37.85 | 779.42
6659 | TIN-INTERP | Interpolated Ground | 42590.21 | 4.56 | 747.63 | 0 | 31.89 | 0 | OK | Ground clear controls. | 95 | 37.85 | 779.52
6660 | TIN-INTERP | Interpolated Ground | 42590.25 | -5.14 | 747.34 | 0 | 21.52 | 0 | OK | Ground clear controls. | 95 | 37.85 | 768.86
6661 | TIN-INTERP | Interpolated Ground | 42590.25 | 6.56 | 747.66 | 0 | 26.51 | 0 | OK | Ground clear controls. | 95 | 37.85 | 774.17
6662 | TIN-INTERP | Interpolated Ground | 42590.27 | -6.64 | 747.48 | 0 | 26.65 | 0 | OK | Ground clear controls. | 95 | 37.85 | 774.13
6663 | TIN-INTERP | Interpolated Ground | 42590.28 | 5.06 | 747.65 | 0 | 21.24 | 0 | OK | Ground clear controls. | 95 | 37.85 | 768.89
6664 | TIN-INTERP | Interpolated Ground | 42630.2 | -4.63 | 746.18 | 0 | 28.39 | 0 | OK | Ground clear controls. | 95 | 37.85 | 774.57
6665 | TIN-INTERP | Interpolated Ground | 42630.21 | 4.57 | 745.97 | 0 | 28.72 | 0 | OK | Ground clear controls. | 95 | 37.85 | 774.69
6666 | TIN-INTERP | Interpolated Ground | 42630.25 | -5.13 | 746.17 | 0 | 17.94 | 0 | OK | Ground clear controls. | 95 | 37.85 | 764.11
6667 | TIN-INTERP | Interpolated Ground | 42630.25 | 6.57 | 745.97 | 0 | 23.39 | 0 | OK | Ground clear controls. | 95 | 37.85 | 769.36
6668 | TIN-INTERP | Interpolated Ground | 42630.27 | -6.63 | 746.21 | 0 | 23.11 | 0 | OK | Ground clear controls. | 95 | 37.85 | 769.32
6669 | TIN-INTERP | Interpolated Ground | 42630.28 | 5.07 | 745.97 | 0 | 18.17 | 0 | OK | Ground clear controls. | 95 | 37.85 | 764.14
6670 | TIN-INTERP | Interpolated Ground | 42670.2 | -4.63 | 744.95 | 0 | 25.74 | 0 | OK | Ground clear controls. | 95 | 37.85 | 770.69
6671 | TIN-INTERP | Interpolated Ground | 42670.21 | 4.57 | 744.9 | 0 | 25.93 | 0 | OK | Ground clear controls. | 95 | 37.85 | 770.83
6672 | TIN-INTERP | Interpolated Ground | 42670.25 | -5.13 | 744.91 | 0 | 15.39 | 0 | OK | Ground clear controls. | 95 | 37.85 | 760.3
6673 | TIN-INTERP | Interpolated Ground | 42670.25 | 6.57 | 745.02 | 0 | 20.51 | 0 | OK | Ground clear controls. | 95 | 37.85 | 765.53
6674 | TIN-INTERP | Interpolated Ground | 42670.27 | -6.63 | 744.82 | 0 | 20.65 | 0 | OK | Ground clear controls. | 95 | 37.85 | 765.47
6675 | TIN-INTERP | Interpolated Ground | 42670.28 | 5.07 | 744.96 | 0 | 15.37 | 0 | OK | Ground clear controls. | 95 | 37.85 | 760.33
6676 | TIN-INTERP | Interpolated Ground | 42710.2 | -4.63 | 743.43 | 0 | 24.36 | 0 | OK | Ground clear controls. | 95 | 37.85 | 767.79
6677 | TIN-INTERP | Interpolated Ground | 42710.21 | 4.57 | 743.02 | 0 | 24.92 | 0 | OK | Ground clear controls. | 95 | 37.85 | 767.94
6678 | TIN-INTERP | Interpolated Ground | 42710.25 | -5.13 | 743.44 | 0 | 14 | 0 | OK | Ground clear controls. | 95 | 37.85 | 757.44
6679 | TIN-INTERP | Interpolated Ground | 42710.25 | 6.57 | 742.98 | 0 | 19.67 | 0 | OK | Ground clear controls. | 95 | 37.85 | 762.65
6680 | TIN-INTERP | Interpolated Ground | 42710.27 | -6.63 | 743.47 | 0 | 19.12 | 0 | OK | Ground clear controls. | 95 | 37.85 | 762.59
6681 | TIN-INTERP | Interpolated Ground | 42710.28 | 5.07 | 743 | 0 | 14.47 | 0 | OK | Ground clear controls. | 95 | 37.85 | 757.47
6682 | TIN-INTERP | Interpolated Ground | 42750.2 | -4.62 | 742.84 | 0 | 23.01 | 0 | OK | Ground clear controls. | 95 | 37.85 | 765.85
6683 | TIN-INTERP | Interpolated Ground | 42750.21 | 4.58 | 742.81 | 0 | 23.2 | 0 | OK | Ground clear controls. | 95 | 37.85 | 766.01
6684 | TIN-INTERP | Interpolated Ground | 42750.25 | -5.12 | 742.81 | 0 | 12.7 | 0 | OK | Ground clear controls. | 95 | 37.85 | 755.51
6685 | TIN-INTERP | Interpolated Ground | 42750.25 | 6.58 | 742.79 | 0 | 17.93 | 0 | OK | Ground clear controls. | 95 | 37.85 | 760.72
6686 | TIN-INTERP | Interpolated Ground | 42750.27 | -6.62 | 742.84 | 0 | 17.82 | 0 | OK | Ground clear controls. | 95 | 37.85 | 760.66
6687 | TIN-INTERP | Interpolated Ground | 42750.28 | 5.08 | 742.79 | 0 | 12.77 | 0 | OK | Ground clear controls. | 95 | 37.85 | 755.56
6688 | TIN-INTERP | Interpolated Ground | 42790.2 | -4.62 | 742.4 | 0 | 22.49 | 0 | OK | Ground clear controls. | 95 | 37.85 | 764.89
6689 | TIN-INTERP | Interpolated Ground | 42790.21 | 4.58 | 742.36 | 0 | 22.68 | 0 | OK | Ground clear controls. | 95 | 37.85 | 765.04
6690 | TIN-INTERP | Interpolated Ground | 42790.25 | -5.12 | 742.38 | 0 | 12.17 | 0 | OK | Ground clear controls. | 95 | 37.85 | 754.55
6691 | TIN-INTERP | Interpolated Ground | 42790.25 | 6.58 | 742.33 | 0 | 17.42 | 0 | OK | Ground clear controls. | 95 | 37.85 | 759.75
6692 | TIN-INTERP | Interpolated Ground | 42790.27 | -6.62 | 742.36 | 0 | 17.34 | 0 | OK | Ground clear controls. | 95 | 37.85 | 759.7
6693 | TIN-INTERP | Interpolated Ground | 42790.28 | 5.08 | 742.36 | 0 | 12.22 | 0 | OK | Ground clear controls. | 95 | 37.85 | 754.58
6694 | TIN-INTERP | Interpolated Ground | 42830.2 | -4.62 | 742.26 | 0 | 22.63 | 0 | OK | Ground clear controls. | 95 | 37.85 | 764.89
6695 | TIN-INTERP | Interpolated Ground | 42830.21 | 4.58 | 742.13 | 0 | 22.91 | 0 | OK | Ground clear controls. | 95 | 37.85 | 765.04
6696 | TIN-INTERP | Interpolated Ground | 42830.25 | -5.12 | 742.24 | 0 | 12.28 | 0 | OK | Ground clear controls. | 95 | 37.85 | 754.52
6697 | TIN-INTERP | Interpolated Ground | 42830.25 | 6.58 | 742.2 | 0 | 17.54 | 0 | OK | Ground clear controls. | 95 | 37.85 | 759.74
6698 | TIN-INTERP | Interpolated Ground | 42830.27 | -6.62 | 742.24 | 0 | 17.44 | 0 | OK | Ground clear controls. | 95 | 37.85 | 759.68
6699 | TIN-INTERP | Interpolated Ground | 42830.28 | 5.08 | 742.15 | 0 | 12.41 | 0 | OK | Ground clear controls. | 95 | 37.85 | 754.56
6700 | TIN-INTERP | Interpolated Ground | 42870.2 | -4.61 | 741.88 | 0 | 23.98 | 0 | OK | Ground clear controls. | 95 | 37.85 | 765.86
6701 | TIN-INTERP | Interpolated Ground | 42870.21 | 4.59 | 741.92 | 0 | 24.08 | 0 | OK | Ground clear controls. | 95 | 37.85 | 766
6702 | TIN-INTERP | Interpolated Ground | 42870.25 | -5.11 | 741.86 | 0 | 13.56 | 0 | OK | Ground clear controls. | 95 | 37.85 | 755.42
6703 | TIN-INTERP | Interpolated Ground | 42870.25 | 6.59 | 742.07 | 0 | 18.6 | 0 | OK | Ground clear controls. | 95 | 37.85 | 760.67
6704 | TIN-INTERP | Interpolated Ground | 42870.27 | -6.61 | 741.85 | 0 | 18.78 | 0 | OK | Ground clear controls. | 95 | 37.85 | 760.63
6705 | TIN-INTERP | Interpolated Ground | 42870.28 | 5.09 | 741.96 | 0 | 13.5 | 0 | OK | Ground clear controls. | 95 | 37.85 | 755.46
6706 | TIN-INTERP | Interpolated Ground | 42910.2 | -4.61 | 742.06 | 0 | 25.75 | 0 | OK | Ground clear controls. | 95 | 37.85 | 767.81
6707 | TIN-INTERP | Interpolated Ground | 42910.21 | 4.59 | 742.02 | 0 | 25.9 | 0 | OK | Ground clear controls. | 95 | 37.85 | 767.92
6708 | TIN-INTERP | Interpolated Ground | 42910.25 | -5.11 | 742.06 | 0 | 15.22 | 0 | OK | Ground clear controls. | 95 | 37.85 | 757.28
6709 | TIN-INTERP | Interpolated Ground | 42910.25 | 6.59 | 742.03 | 0 | 20.54 | 0 | OK | Ground clear controls. | 95 | 37.85 | 762.57
6710 | TIN-INTERP | Interpolated Ground | 42910.27 | -6.61 | 742.05 | 0 | 20.49 | 0 | OK | Ground clear controls. | 95 | 37.85 | 762.54
6711 | TIN-INTERP | Interpolated Ground | 42910.28 | 5.09 | 742.02 | 0 | 15.29 | 0 | OK | Ground clear controls. | 95 | 37.85 | 757.31
6712 | TIN-INTERP | Interpolated Ground | 42950.2 | -4.61 | 741.96 | 0 | 28.76 | 0 | OK | Ground clear controls. | 95 | 37.85 | 770.72
6713 | TIN-INTERP | Interpolated Ground | 42950.21 | 4.59 | 741.87 | 0 | 28.94 | 0 | OK | Ground clear controls. | 95 | 37.85 | 770.81
6714 | TIN-INTERP | Interpolated Ground | 42950.25 | -5.11 | 741.96 | 0 | 18.12 | 0 | OK | Ground clear controls. | 95 | 37.85 | 760.08
6715 | TIN-INTERP | Interpolated Ground | 42950.25 | 6.59 | 741.9 | 0 | 23.52 | 0 | OK | Ground clear controls. | 95 | 37.85 | 765.42
6716 | TIN-INTERP | Interpolated Ground | 42950.27 | -6.61 | 741.91 | 0 | 23.48 | 0 | OK | Ground clear controls. | 95 | 37.85 | 765.39
6717 | TIN-INTERP | Interpolated Ground | 42950.28 | 5.09 | 741.85 | 0 | 18.26 | 0 | OK | Ground clear controls. | 95 | 37.85 | 760.11
6718 | TIN-INTERP | Interpolated Ground | 42990.2 | -4.6 | 741.85 | 0 | 32.75 | 0 | OK | Ground clear controls. | 95 | 37.85 | 774.6
6719 | TIN-INTERP | Interpolated Ground | 42990.21 | 4.6 | 741.84 | 0 | 32.82 | 0 | OK | Ground clear controls. | 95 | 37.85 | 774.66
6720 | TIN-INTERP | Interpolated Ground | 42990.25 | -5.1 | 741.86 | 0 | 21.96 | 0 | OK | Ground clear controls. | 95 | 37.85 | 763.82
6721 | TIN-INTERP | Interpolated Ground | 42990.25 | 6.6 | 741.86 | 0 | 27.37 | 0 | OK | Ground clear controls. | 95 | 37.85 | 769.23
6722 | TIN-INTERP | Interpolated Ground | 42990.27 | -6.6 | 741.79 | 0 | 27.41 | 0 | OK | Ground clear controls. | 95 | 37.85 | 769.2
6723 | TIN-INTERP | Interpolated Ground | 42990.28 | 5.1 | 741.83 | 0 | 22.02 | 0 | OK | Ground clear controls. | 95 | 37.85 | 763.85
6724 | TIN-INTERP | Interpolated Ground | 43030.2 | -4.6 | 741.61 | 0 | 37.85 | 0 | OK | Ground clear controls. | 95 | 37.85 | 779.46
6725 | TIN-INTERP | Interpolated Ground | 43030.21 | 4.6 | 741.62 | 0 | 37.85 | 0 | OK | Ground clear controls. | 95 | 37.85 | 779.47
6726 | TIN-INTERP | Interpolated Ground | 43030.25 | -5.1 | 741.6 | 0 | 26.91 | 0 | OK | Ground clear controls. | 95 | 32.32 | 768.51
6727 | TIN-INTERP | Interpolated Ground | 43030.25 | 6.6 | 741.76 | 0 | 32.23 | 0 | OK | Ground clear controls. | 95 | 32.32 | 773.99
6728 | TIN-INTERP | Interpolated Ground | 43030.27 | -6.6 | 741.66 | 0 | 32.32 | 0 | OK | Ground clear controls. | 95 | 32.32 | 773.98
6729 | TIN-INTERP | Interpolated Ground | 43030.28 | 5.1 | 741.65 | 0 | 26.87 | 0 | OK | Ground clear controls. | 95 | 26.87 | 768.52
6730 | TIN-INTERP | Interpolated Ground | 43040.52 | 5.1 | 741.75 | 0 | 28.12 | 0 | OK | Ground clear controls. | 96 | 40.76 | 769.87
6731 | TIN-INTERP | Interpolated Ground | 43040.54 | 4.6 | 741.75 | 0 | 39.12 | 0 | OK | Ground clear controls. | 96 | 40.76 | 780.87
6732 | TIN-INTERP | Interpolated Ground | 43040.54 | -5.1 | 741.74 | 0 | 28.13 | 0 | OK | Ground clear controls. | 96 | 40.76 | 769.87
6733 | TIN-INTERP | Interpolated Ground | 43040.54 | 6.6 | 741.76 | 0 | 33.61 | 0 | OK | Ground clear controls. | 96 | 40.76 | 775.37
6734 | TIN-INTERP | Interpolated Ground | 43040.56 | -4.6 | 741.69 | 0 | 39.18 | 0 | OK | Ground clear controls. | 96 | 40.76 | 780.87
6735 | TIN-INTERP | Interpolated Ground | 43040.56 | -6.6 | 741.76 | 0 | 33.61 | 0 | OK | Ground clear controls. | 96 | 40.76 | 775.37
6736 | TIN-INTERP | Interpolated Ground | 43080.52 | 5.1 | 740.13 | 0 | 24.83 | 0 | OK | Ground clear controls. | 96 | 40.76 | 764.96
6737 | TIN-INTERP | Interpolated Ground | 43080.54 | 4.6 | 740.09 | 0 | 35.76 | 0 | OK | Ground clear controls. | 96 | 40.76 | 775.85
6738 | TIN-INTERP | Interpolated Ground | 43080.54 | -5.1 | 742.06 | 0 | 22.9 | 0 | OK | Ground clear controls. | 96 | 40.76 | 764.96
6739 | TIN-INTERP | Interpolated Ground | 43080.54 | 6.6 | 740.06 | 0 | 30.34 | 0 | OK | Ground clear controls. | 96 | 40.76 | 770.4
6740 | TIN-INTERP | Interpolated Ground | 43080.56 | -4.6 | 741.86 | 0 | 33.96 | 0 | OK | Ground clear controls. | 96 | 40.76 | 775.82
6741 | TIN-INTERP | Interpolated Ground | 43080.56 | -6.6 | 742 | 0 | 28.4 | 0 | OK | Ground clear controls. | 96 | 40.76 | 770.4
6742 | TIN-INTERP | Interpolated Ground | 43120.52 | 5.1 | 741.68 | 0 | 19.32 | 0 | OK | Ground clear controls. | 96 | 40.76 | 761
6743 | TIN-INTERP | Interpolated Ground | 43120.54 | 4.6 | 741.71 | 0 | 30.09 | 0 | OK | Ground clear controls. | 96 | 40.76 | 771.8
6744 | TIN-INTERP | Interpolated Ground | 43120.54 | -5.1 | 741.84 | 0 | 19.17 | 0 | OK | Ground clear controls. | 96 | 40.76 | 761.01
6745 | TIN-INTERP | Interpolated Ground | 43120.54 | 6.6 | 741.59 | 0 | 24.79 | 0 | OK | Ground clear controls. | 96 | 40.76 | 766.38
6746 | TIN-INTERP | Interpolated Ground | 43120.56 | -4.6 | 741.83 | 0 | 29.92 | 0 | OK | Ground clear controls. | 96 | 40.76 | 771.75
6747 | TIN-INTERP | Interpolated Ground | 43120.56 | -6.6 | 741.87 | 0 | 24.51 | 0 | OK | Ground clear controls. | 96 | 40.76 | 766.38
6748 | TIN-INTERP | Interpolated Ground | 43160.52 | 5.1 | 741.76 | 0 | 16.23 | 0 | OK | Ground clear controls. | 96 | 40.76 | 757.99
6749 | TIN-INTERP | Interpolated Ground | 43160.54 | 4.6 | 741.75 | 0 | 26.96 | 0 | OK | Ground clear controls. | 96 | 40.76 | 768.71
6750 | TIN-INTERP | Interpolated Ground | 43160.54 | -5.1 | 741.82 | 0 | 16.18 | 0 | OK | Ground clear controls. | 96 | 40.76 | 758
6751 | TIN-INTERP | Interpolated Ground | 43160.54 | 6.6 | 741.78 | 0 | 21.55 | 0 | OK | Ground clear controls. | 96 | 40.76 | 763.33
6752 | TIN-INTERP | Interpolated Ground | 43160.56 | -4.6 | 741.8 | 0 | 26.84 | 0 | OK | Ground clear controls. | 96 | 40.76 | 768.64
6753 | TIN-INTERP | Interpolated Ground | 43160.56 | -6.6 | 741.82 | 0 | 21.51 | 0 | OK | Ground clear controls. | 96 | 40.76 | 763.33
6754 | TIN-INTERP | Interpolated Ground | 43200.52 | 5.1 | 741.76 | 0 | 14.16 | 0 | OK | Ground clear controls. | 96 | 40.76 | 755.92
6755 | TIN-INTERP | Interpolated Ground | 43200.54 | 4.6 | 741.76 | 0 | 24.82 | 0 | OK | Ground clear controls. | 96 | 40.76 | 766.58
6756 | TIN-INTERP | Interpolated Ground | 43200.54 | -5.1 | 741.78 | 0 | 14.14 | 0 | OK | Ground clear controls. | 96 | 40.76 | 755.92
6757 | TIN-INTERP | Interpolated Ground | 43200.54 | 6.6 | 741.8 | 0 | 19.43 | 0 | OK | Ground clear controls. | 96 | 40.76 | 761.23
6758 | TIN-INTERP | Interpolated Ground | 43200.56 | -4.6 | 741.79 | 0 | 24.72 | 0 | OK | Ground clear controls. | 96 | 40.76 | 766.51
6759 | TIN-INTERP | Interpolated Ground | 43200.56 | -6.6 | 741.76 | 0 | 19.47 | 0 | OK | Ground clear controls. | 96 | 40.76 | 761.23
6760 | TIN-INTERP | Interpolated Ground | 43240.52 | 5.1 | 742.09 | 0 | 12.71 | 0 | OK | Ground clear controls. | 96 | 40.76 | 754.8
6761 | TIN-INTERP | Interpolated Ground | 43240.54 | 4.6 | 742.1 | 0 | 23.33 | 0 | OK | Ground clear controls. | 96 | 40.76 | 765.43
6762 | TIN-INTERP | Interpolated Ground | 43240.54 | -5.1 | 742.05 | 0 | 12.76 | 0 | OK | Ground clear controls. | 96 | 40.76 | 754.81
6763 | TIN-INTERP | Interpolated Ground | 43240.54 | 6.6 | 742.12 | 0 | 17.98 | 0 | OK | Ground clear controls. | 96 | 40.76 | 760.1
6764 | TIN-INTERP | Interpolated Ground | 43240.56 | -4.6 | 742.06 | 0 | 23.29 | 0 | OK | Ground clear controls. | 96 | 40.76 | 765.35
6765 | TIN-INTERP | Interpolated Ground | 43240.56 | -6.6 | 742.01 | 0 | 18.08 | 0 | OK | Ground clear controls. | 96 | 40.76 | 760.09
6766 | TIN-INTERP | Interpolated Ground | 43280.52 | 5.1 | 743.08 | 0 | 11.54 | 0 | OK | Ground clear controls. | 96 | 40.76 | 754.62
6767 | TIN-INTERP | Interpolated Ground | 43280.54 | 4.6 | 743.09 | 0 | 22.14 | 0 | OK | Ground clear controls. | 96 | 40.76 | 765.23
6768 | TIN-INTERP | Interpolated Ground | 43280.54 | -5.1 | 743.17 | 0 | 11.46 | 0 | OK | Ground clear controls. | 96 | 40.76 | 754.63
6769 | TIN-INTERP | Interpolated Ground | 43280.54 | 6.6 | 743.05 | 0 | 16.86 | 0 | OK | Ground clear controls. | 96 | 40.76 | 759.91
6770 | TIN-INTERP | Interpolated Ground | 43280.56 | -4.6 | 743.18 | 0 | 21.98 | 0 | OK | Ground clear controls. | 96 | 40.76 | 765.16
6771 | TIN-INTERP | Interpolated Ground | 43280.56 | -6.6 | 743.16 | 0 | 16.75 | 0 | OK | Ground clear controls. | 96 | 40.76 | 759.91
6772 | TIN-INTERP | Interpolated Ground | 43320.52 | 5.1 | 742.84 | 0 | 12.55 | 0 | OK | Ground clear controls. | 96 | 40.76 | 755.39
6773 | TIN-INTERP | Interpolated Ground | 43320.54 | 4.6 | 742.82 | 0 | 23.19 | 0 | OK | Ground clear controls. | 96 | 40.76 | 766.01
6774 | TIN-INTERP | Interpolated Ground | 43320.54 | -5.1 | 742.75 | 0 | 12.65 | 0 | OK | Ground clear controls. | 96 | 40.76 | 755.4
6775 | TIN-INTERP | Interpolated Ground | 43320.54 | 6.6 | 742.85 | 0 | 17.84 | 0 | OK | Ground clear controls. | 96 | 40.76 | 760.69
6776 | TIN-INTERP | Interpolated Ground | 43320.56 | -4.6 | 742.79 | 0 | 23.14 | 0 | OK | Ground clear controls. | 96 | 40.76 | 765.93
6777 | TIN-INTERP | Interpolated Ground | 43320.56 | -6.6 | 742.79 | 0 | 17.88 | 0 | OK | Ground clear controls. | 96 | 40.76 | 760.67
6778 | TIN-INTERP | Interpolated Ground | 43360.52 | 5.1 | 742.85 | 0 | 14.25 | 0 | OK | Ground clear controls. | 96 | 40.76 | 757.1
6779 | TIN-INTERP | Interpolated Ground | 43360.54 | 4.6 | 742.82 | 0 | 24.92 | 0 | OK | Ground clear controls. | 96 | 40.76 | 767.74
6780 | TIN-INTERP | Interpolated Ground | 43360.54 | -5.1 | 743.02 | 0 | 14.09 | 0 | OK | Ground clear controls. | 96 | 40.76 | 757.11
6781 | TIN-INTERP | Interpolated Ground | 43360.54 | 6.6 | 742.93 | 0 | 19.48 | 0 | OK | Ground clear controls. | 96 | 40.76 | 762.41
6782 | TIN-INTERP | Interpolated Ground | 43360.56 | -4.6 | 743.04 | 0 | 24.63 | 0 | OK | Ground clear controls. | 96 | 40.76 | 767.67
6783 | TIN-INTERP | Interpolated Ground | 43360.56 | -6.6 | 743.02 | 0 | 19.39 | 0 | OK | Ground clear controls. | 96 | 40.76 | 762.41
6784 | TIN-INTERP | Interpolated Ground | 43400.52 | 5.1 | 743.12 | 0 | 16.64 | 0 | OK | Ground clear controls. | 96 | 40.76 | 759.76
6785 | TIN-INTERP | Interpolated Ground | 43400.54 | 4.6 | 743.09 | 0 | 27.36 | 0 | OK | Ground clear controls. | 96 | 40.76 | 770.45
6786 | TIN-INTERP | Interpolated Ground | 43400.54 | -5.1 | 742.99 | 0 | 16.78 | 0 | OK | Ground clear controls. | 96 | 40.76 | 759.77
6787 | TIN-INTERP | Interpolated Ground | 43400.54 | 6.6 | 743.18 | 0 | 21.92 | 0 | OK | Ground clear controls. | 96 | 40.76 | 765.1
6788 | TIN-INTERP | Interpolated Ground | 43400.56 | -4.6 | 742.98 | 0 | 27.4 | 0 | OK | Ground clear controls. | 96 | 40.76 | 770.38
6789 | TIN-INTERP | Interpolated Ground | 43400.56 | -6.6 | 743.04 | 0 | 22.05 | 0 | OK | Ground clear controls. | 96 | 40.76 | 765.09
6790 | TIN-INTERP | Interpolated Ground | 43440.52 | 5.1 | 743.24 | 0 | 20.13 | 0 | OK | Ground clear controls. | 96 | 40.76 | 763.37
6791 | TIN-INTERP | Interpolated Ground | 43440.54 | 4.6 | 743.25 | 0 | 30.88 | 0 | OK | Ground clear controls. | 96 | 40.76 | 774.13
6792 | TIN-INTERP | Interpolated Ground | 43440.54 | -5.1 | 743.33 | 0 | 20.05 | 0 | OK | Ground clear controls. | 96 | 40.76 | 763.38
6793 | TIN-INTERP | Interpolated Ground | 43440.54 | 6.6 | 743.24 | 0 | 25.49 | 0 | OK | Ground clear controls. | 96 | 40.76 | 768.73
6794 | TIN-INTERP | Interpolated Ground | 43440.56 | -4.6 | 743.32 | 0 | 30.75 | 0 | OK | Ground clear controls. | 96 | 40.76 | 774.07
6795 | TIN-INTERP | Interpolated Ground | 43440.56 | -6.6 | 743.39 | 0 | 25.34 | 0 | OK | Ground clear controls. | 96 | 40.76 | 768.73
6796 | TIN-INTERP | Interpolated Ground | 43480.52 | 5.1 | 743.62 | 0 | 24.3 | 0 | OK | Ground clear controls. | 96 | 40.76 | 767.92
6797 | TIN-INTERP | Interpolated Ground | 43480.54 | 4.6 | 743.62 | 0 | 35.14 | 0 | OK | Ground clear controls. | 96 | 40.76 | 778.76
6798 | TIN-INTERP | Interpolated Ground | 43480.54 | -5.1 | 743.56 | 0 | 24.37 | 0 | OK | Ground clear controls. | 96 | 40.76 | 767.93
6799 | TIN-INTERP | Interpolated Ground | 43480.54 | 6.6 | 743.65 | 0 | 29.69 | 0 | OK | Ground clear controls. | 96 | 40.76 | 773.34
6800 | TIN-INTERP | Interpolated Ground | 43480.56 | -4.6 | 743.58 | 0 | 35.14 | 0 | OK | Ground clear controls. | 96 | 40.76 | 778.72
6801 | TIN-INTERP | Interpolated Ground | 43480.56 | -6.6 | 743.5 | 0 | 29.84 | 0 | OK | Ground clear controls. | 96 | 40.76 | 773.34
6802 | TIN-INTERP | Interpolated Ground | 43520.52 | 5.1 | 743.68 | 0 | 29.75 | 0 | OK | Ground clear controls. | 96 | 40.76 | 773.43
6803 | TIN-INTERP | Interpolated Ground | 43520.54 | 4.6 | 743.7 | 0 | 40.68 | 0 | OK | Ground clear controls. | 96 | 40.76 | 784.38
6804 | TIN-INTERP | Interpolated Ground | 43520.54 | -5.1 | 743.59 | 0 | 29.85 | 0 | OK | Ground clear controls. | 96 | 40.76 | 773.44
6805 | TIN-INTERP | Interpolated Ground | 43520.54 | 6.6 | 743.65 | 0 | 35.25 | 0 | OK | Ground clear controls. | 96 | 40.76 | 778.9
6806 | TIN-INTERP | Interpolated Ground | 43520.56 | -4.6 | 743.6 | 0 | 40.76 | 0 | OK | Ground clear controls. | 96 | 40.76 | 784.36
6807 | TIN-INTERP | Interpolated Ground | 43520.56 | -6.6 | 743.55 | 0 | 35.35 | 0 | OK | Ground clear controls. | 96 | 35.35 | 778.9
6808 | TIN-INTERP | Interpolated Ground | 43538.27 | -5.1 | 743.63 | 0 | 32.55 | 0 | OK | Ground clear controls. | 97 | 43.64 | 776.18
6809 | TIN-INTERP | Interpolated Ground | 43538.29 | 5.1 | 743.55 | 0 | 32.63 | 0 | OK | Ground clear controls. | 97 | 43.64 | 776.18
6810 | TIN-INTERP | Interpolated Ground | 43538.29 | -6.6 | 743.78 | 0 | 37.9 | 0 | OK | Ground clear controls. | 97 | 43.64 | 781.68
6811 | TIN-INTERP | Interpolated Ground | 43538.3 | 4.6 | 743.54 | 0 | 43.64 | 0 | OK | Ground clear controls. | 97 | 43.64 | 787.18
6812 | TIN-INTERP | Interpolated Ground | 43538.3 | 6.6 | 743.56 | 0 | 38.12 | 0 | OK | Ground clear controls. | 97 | 43.58 | 781.68
6813 | TIN-INTERP | Interpolated Ground | 43538.37 | -4.6 | 743.6 | 0 | 43.58 | 0 | OK | Ground clear controls. | 97 | 43.58 | 787.18
6814 | TIN-INTERP | Interpolated Ground | 43578.27 | -5.11 | 743.84 | 0 | 26.81 | 0 | OK | Ground clear controls. | 97 | 42.44 | 770.65
6815 | TIN-INTERP | Interpolated Ground | 43578.29 | 5.09 | 743.79 | 0 | 26.87 | 0 | OK | Ground clear controls. | 97 | 42.44 | 770.66
6816 | TIN-INTERP | Interpolated Ground | 43578.29 | -6.61 | 743.84 | 0 | 32.26 | 0 | OK | Ground clear controls. | 97 | 42.44 | 776.1
6817 | TIN-INTERP | Interpolated Ground | 43578.3 | 4.59 | 743.8 | 0 | 37.76 | 0 | OK | Ground clear controls. | 97 | 42.44 | 781.56
6818 | TIN-INTERP | Interpolated Ground | 43578.3 | 6.59 | 743.8 | 0 | 32.32 | 0 | OK | Ground clear controls. | 97 | 42.44 | 776.12
6819 | TIN-INTERP | Interpolated Ground | 43578.37 | -4.61 | 743.82 | 0 | 37.76 | 0 | OK | Ground clear controls. | 97 | 42.44 | 781.58
6820 | TIN-INTERP | Interpolated Ground | 43618.27 | -5.11 | 744.1 | 0 | 21.97 | 0 | OK | Ground clear controls. | 97 | 42.44 | 766.07
6821 | TIN-INTERP | Interpolated Ground | 43618.29 | 5.09 | 743.96 | 0 | 22.13 | 0 | OK | Ground clear controls. | 97 | 42.44 | 766.09
6822 | TIN-INTERP | Interpolated Ground | 43618.29 | -6.61 | 744.19 | 0 | 27.28 | 0 | OK | Ground clear controls. | 97 | 42.44 | 771.47
6823 | TIN-INTERP | Interpolated Ground | 43618.3 | 4.59 | 743.95 | 0 | 32.93 | 0 | OK | Ground clear controls. | 97 | 42.44 | 776.88
6824 | TIN-INTERP | Interpolated Ground | 43618.3 | 6.59 | 743.99 | 0 | 27.49 | 0 | OK | Ground clear controls. | 97 | 42.44 | 771.48
6825 | TIN-INTERP | Interpolated Ground | 43618.37 | -4.61 | 744.1 | 0 | 32.83 | 0 | OK | Ground clear controls. | 97 | 42.44 | 776.93
6826 | TIN-INTERP | Interpolated Ground | 43658.27 | -5.11 | 744.12 | 0 | 18.32 | 0 | OK | Ground clear controls. | 97 | 42.44 | 762.44
6827 | TIN-INTERP | Interpolated Ground | 43658.29 | 5.09 | 744.04 | 0 | 18.42 | 0 | OK | Ground clear controls. | 97 | 42.44 | 762.46
6828 | TIN-INTERP | Interpolated Ground | 43658.29 | -6.61 | 744.13 | 0 | 23.67 | 0 | OK | Ground clear controls. | 97 | 42.44 | 767.8
6829 | TIN-INTERP | Interpolated Ground | 43658.3 | 4.59 | 744.03 | 0 | 29.15 | 0 | OK | Ground clear controls. | 97 | 42.44 | 773.18
6830 | TIN-INTERP | Interpolated Ground | 43658.3 | 6.59 | 744.06 | 0 | 23.77 | 0 | OK | Ground clear controls. | 97 | 42.44 | 767.83
6831 | TIN-INTERP | Interpolated Ground | 43658.37 | -4.61 | 744.12 | 0 | 29.12 | 0 | OK | Ground clear controls. | 97 | 42.44 | 773.24
6832 | TIN-INTERP | Interpolated Ground | 43698.27 | -5.12 | 744.28 | 0 | 15.45 | 0 | OK | Ground clear controls. | 97 | 42.44 | 759.73
6833 | TIN-INTERP | Interpolated Ground | 43698.29 | 5.08 | 744.23 | 0 | 15.54 | 0 | OK | Ground clear controls. | 97 | 42.44 | 759.77
6834 | TIN-INTERP | Interpolated Ground | 43698.29 | -6.62 | 744.27 | 0 | 20.81 | 0 | OK | Ground clear controls. | 97 | 42.44 | 765.08
6835 | TIN-INTERP | Interpolated Ground | 43698.3 | 4.58 | 744.22 | 0 | 26.21 | 0 | OK | Ground clear controls. | 97 | 42.44 | 770.43
6836 | TIN-INTERP | Interpolated Ground | 43698.3 | 6.58 | 744.27 | 0 | 20.84 | 0 | OK | Ground clear controls. | 97 | 42.44 | 765.11
6837 | TIN-INTERP | Interpolated Ground | 43698.37 | -4.62 | 744.29 | 0 | 26.22 | 0 | OK | Ground clear controls. | 97 | 42.44 | 770.51
6838 | TIN-INTERP | Interpolated Ground | 43738.27 | -5.12 | 744.6 | 0 | 13.38 | 0 | OK | Ground clear controls. | 97 | 42.44 | 757.98
6839 | TIN-INTERP | Interpolated Ground | 43738.29 | 5.08 | 744.57 | 0 | 13.46 | 0 | OK | Ground clear controls. | 97 | 42.44 | 758.03
6840 | TIN-INTERP | Interpolated Ground | 43738.29 | -6.62 | 744.63 | 0 | 18.68 | 0 | OK | Ground clear controls. | 97 | 42.44 | 763.31
6841 | TIN-INTERP | Interpolated Ground | 43738.3 | 4.58 | 744.57 | 0 | 24.08 | 0 | OK | Ground clear controls. | 97 | 42.44 | 768.65
6842 | TIN-INTERP | Interpolated Ground | 43738.3 | 6.58 | 744.59 | 0 | 18.75 | 0 | OK | Ground clear controls. | 97 | 42.44 | 763.34
6843 | TIN-INTERP | Interpolated Ground | 43738.37 | -4.62 | 744.62 | 0 | 24.11 | 0 | OK | Ground clear controls. | 97 | 42.44 | 768.73
6844 | TIN-INTERP | Interpolated Ground | 43778.27 | -5.12 | 744.88 | 0 | 12.29 | 0 | OK | Ground clear controls. | 97 | 42.44 | 757.17
6845 | TIN-INTERP | Interpolated Ground | 43778.29 | 5.08 | 744.96 | 0 | 12.26 | 0 | OK | Ground clear controls. | 97 | 42.44 | 757.22
6846 | TIN-INTERP | Interpolated Ground | 43778.29 | -6.62 | 744.87 | 0 | 17.62 | 0 | OK | Ground clear controls. | 97 | 42.44 | 762.49
6847 | TIN-INTERP | Interpolated Ground | 43778.3 | 4.58 | 744.95 | 0 | 22.87 | 0 | OK | Ground clear controls. | 97 | 42.44 | 767.82
6848 | TIN-INTERP | Interpolated Ground | 43778.3 | 6.58 | 744.93 | 0 | 17.6 | 0 | OK | Ground clear controls. | 97 | 42.44 | 762.53
6849 | TIN-INTERP | Interpolated Ground | 43778.37 | -4.62 | 744.92 | 0 | 22.99 | 0 | OK | Ground clear controls. | 97 | 42.44 | 767.91
6850 | TIN-INTERP | Interpolated Ground | 43818.27 | -5.13 | 744.85 | 0 | 12.45 | 0 | OK | Ground clear controls. | 97 | 42.44 | 757.3
6851 | TIN-INTERP | Interpolated Ground | 43818.29 | 5.07 | 744.86 | 0 | 12.49 | 0 | OK | Ground clear controls. | 97 | 42.44 | 757.35
6852 | TIN-INTERP | Interpolated Ground | 43818.29 | -6.63 | 744.89 | 0 | 17.73 | 0 | OK | Ground clear controls. | 97 | 42.44 | 762.62
6853 | TIN-INTERP | Interpolated Ground | 43818.3 | 4.57 | 744.87 | 0 | 23.08 | 0 | OK | Ground clear controls. | 97 | 42.44 | 767.95
6854 | TIN-INTERP | Interpolated Ground | 43818.3 | 6.57 | 744.89 | 0 | 17.76 | 0 | OK | Ground clear controls. | 97 | 42.44 | 762.65
6855 | TIN-INTERP | Interpolated Ground | 43818.37 | -4.63 | 744.85 | 0 | 23.19 | 0 | OK | Ground clear controls. | 97 | 42.44 | 768.04
6856 | TIN-INTERP | Interpolated Ground | 43858.27 | -5.13 | 744.98 | 0 | 13.4 | 0 | OK | Ground clear controls. | 97 | 42.44 | 758.38
6857 | TIN-INTERP | Interpolated Ground | 43858.29 | 5.07 | 744.9 | 0 | 13.52 | 0 | OK | Ground clear controls. | 97 | 42.44 | 758.42
6858 | TIN-INTERP | Interpolated Ground | 43858.29 | -6.63 | 744.94 | 0 | 18.76 | 0 | OK | Ground clear controls. | 97 | 42.44 | 763.7
6859 | TIN-INTERP | Interpolated Ground | 43858.3 | 4.57 | 744.89 | 0 | 24.15 | 0 | OK | Ground clear controls. | 97 | 42.44 | 769.04
6860 | TIN-INTERP | Interpolated Ground | 43858.3 | 6.57 | 744.94 | 0 | 18.79 | 0 | OK | Ground clear controls. | 97 | 42.44 | 763.73
6861 | TIN-INTERP | Interpolated Ground | 43858.37 | -4.63 | 744.99 | 0 | 24.13 | 0 | OK | Ground clear controls. | 97 | 42.44 | 769.12
6862 | TIN-INTERP | Interpolated Ground | 43898.27 | -5.13 | 745 | 0 | 15.39 | 0 | OK | Ground clear controls. | 97 | 42.44 | 760.39
6863 | TIN-INTERP | Interpolated Ground | 43898.29 | 5.07 | 745.1 | 0 | 15.33 | 0 | OK | Ground clear controls. | 97 | 42.44 | 760.43
6864 | TIN-INTERP | Interpolated Ground | 43898.29 | -6.63 | 744.99 | 0 | 20.74 | 0 | OK | Ground clear controls. | 97 | 42.44 | 765.73
6865 | TIN-INTERP | Interpolated Ground | 43898.3 | 4.57 | 745.09 | 0 | 25.99 | 0 | OK | Ground clear controls. | 97 | 42.44 | 771.08
6866 | TIN-INTERP | Interpolated Ground | 43898.3 | 6.57 | 745.13 | 0 | 20.63 | 0 | OK | Ground clear controls. | 97 | 42.44 | 765.76
6867 | TIN-INTERP | Interpolated Ground | 43898.37 | -4.63 | 744.99 | 0 | 26.17 | 0 | OK | Ground clear controls. | 97 | 42.44 | 771.16
6868 | TIN-INTERP | Interpolated Ground | 43938.27 | -5.14 | 745.36 | 0 | 17.99 | 0 | OK | Ground clear controls. | 97 | 42.44 | 763.35
6869 | TIN-INTERP | Interpolated Ground | 43938.29 | 5.06 | 745.33 | 0 | 18.05 | 0 | OK | Ground clear controls. | 97 | 42.44 | 763.38
6870 | TIN-INTERP | Interpolated Ground | 43938.29 | -6.64 | 745.37 | 0 | 23.34 | 0 | OK | Ground clear controls. | 97 | 42.44 | 768.71
6871 | TIN-INTERP | Interpolated Ground | 43938.3 | 4.56 | 745.33 | 0 | 28.76 | 0 | OK | Ground clear controls. | 97 | 42.44 | 774.09
6872 | TIN-INTERP | Interpolated Ground | 43938.3 | 6.56 | 745.37 | 0 | 23.37 | 0 | OK | Ground clear controls. | 97 | 42.44 | 768.74
6873 | TIN-INTERP | Interpolated Ground | 43938.37 | -4.64 | 745.36 | 0 | 28.8 | 0 | OK | Ground clear controls. | 97 | 42.44 | 774.16
6874 | TIN-INTERP | Interpolated Ground | 43978.27 | -5.14 | 745.66 | 0 | 21.58 | 0 | OK | Ground clear controls. | 97 | 42.44 | 767.24
6875 | TIN-INTERP | Interpolated Ground | 43978.29 | 5.06 | 745.51 | 0 | 21.76 | 0 | OK | Ground clear controls. | 97 | 42.44 | 767.27
6876 | TIN-INTERP | Interpolated Ground | 43978.29 | -6.64 | 745.65 | 0 | 27 | 0 | OK | Ground clear controls. | 97 | 42.44 | 772.65
6877 | TIN-INTERP | Interpolated Ground | 43978.3 | 4.56 | 745.49 | 0 | 32.55 | 0 | OK | Ground clear controls. | 97 | 42.44 | 778.04
6878 | TIN-INTERP | Interpolated Ground | 43978.3 | 6.56 | 745.52 | 0 | 27.15 | 0 | OK | Ground clear controls. | 97 | 42.44 | 772.67
6879 | TIN-INTERP | Interpolated Ground | 43978.37 | -4.64 | 745.66 | 0 | 32.44 | 0 | OK | Ground clear controls. | 97 | 42.44 | 778.1
6880 | TIN-INTERP | Interpolated Ground | 44018.27 | -5.14 | 746.22 | 0 | 25.88 | 0 | OK | Ground clear controls. | 97 | 42.44 | 772.1
6881 | TIN-INTERP | Interpolated Ground | 44018.29 | 5.06 | 746.05 | 0 | 26.07 | 0 | OK | Ground clear controls. | 97 | 42.44 | 772.12
6882 | TIN-INTERP | Interpolated Ground | 44018.29 | -6.64 | 746.27 | 0 | 31.27 | 0 | OK | Ground clear controls. | 97 | 42.44 | 777.54
6883 | TIN-INTERP | Interpolated Ground | 44018.3 | 4.56 | 746.04 | 0 | 36.94 | 0 | OK | Ground clear controls. | 97 | 42.44 | 782.98
6884 | TIN-INTERP | Interpolated Ground | 44018.3 | 6.56 | 746.04 | 0 | 31.52 | 0 | OK | Ground clear controls. | 97 | 42.44 | 777.56
6885 | TIN-INTERP | Interpolated Ground | 44018.37 | -4.64 | 746.22 | 0 | 36.8 | 0 | OK | Ground clear controls. | 97 | 42.44 | 783.02
6886 | TIN-INTERP | Interpolated Ground | 44058.27 | -5.15 | 746.44 | 0 | 31.45 | 0 | OK | Ground clear controls. | 97 | 42.44 | 777.89
6887 | TIN-INTERP | Interpolated Ground | 44058.29 | 5.05 | 746.51 | 0 | 31.39 | 0 | OK | Ground clear controls. | 97 | 42.44 | 777.9
6888 | TIN-INTERP | Interpolated Ground | 44058.29 | -6.65 | 746.44 | 0 | 36.94 | 0 | OK | Ground clear controls. | 97 | 42.44 | 783.38
6889 | TIN-INTERP | Interpolated Ground | 44058.3 | 4.55 | 746.51 | 0 | 42.36 | 0 | OK | Ground clear controls. | 97 | 42.44 | 788.87
6890 | TIN-INTERP | Interpolated Ground | 44058.3 | 6.55 | 746.49 | 0 | 36.9 | 0 | OK | Ground clear controls. | 97 | 42.44 | 783.39
6891 | TIN-INTERP | Interpolated Ground | 44058.37 | -4.65 | 746.44 | 0 | 42.44 | 0 | OK | Ground clear controls. | 97 | 42.44 | 788.88
6892 | TIN-INTERP | Interpolated Ground | 44067.34 | 6.55 | 746.64 | 0 | 38.2 | 0 | OK | Ground clear controls. | 98 | 43.88 | 784.84
6893 | TIN-INTERP | Interpolated Ground | 44067.36 | 5.05 | 746.64 | 0 | 32.7 | 0 | OK | Ground clear controls. | 98 | 43.88 | 779.34
6894 | TIN-INTERP | Interpolated Ground | 44067.36 | -6.65 | 746.74 | 0 | 38.1 | 0 | OK | Ground clear controls. | 98 | 43.88 | 784.84
6895 | TIN-INTERP | Interpolated Ground | 44067.36 | 4.55 | 746.62 | 0 | 43.72 | 0 | OK | Ground clear controls. | 98 | 43.88 | 790.34
6896 | TIN-INTERP | Interpolated Ground | 44067.37 | -5.15 | 746.64 | 0 | 32.7 | 0 | OK | Ground clear controls. | 98 | 43.88 | 779.34
6897 | TIN-INTERP | Interpolated Ground | 44067.38 | -4.65 | 746.46 | 0 | 43.88 | 0 | OK | Ground clear controls. | 98 | 43.88 | 790.34
6898 | TIN-INTERP | Interpolated Ground | 44107.34 | 6.56 | 748.02 | 0 | 31.32 | 0 | OK | Ground clear controls. | 98 | 36.86 | 779.34
6899 | TIN-INTERP | Interpolated Ground | 44107.36 | 5.06 | 748.06 | 0 | 25.84 | 0 | OK | Ground clear controls. | 98 | 36.86 | 773.9
6900 | TIN-INTERP | Interpolated Ground | 44107.36 | -6.64 | 747.66 | 0 | 31.69 | 0 | OK | Ground clear controls. | 98 | 36.86 | 779.35
6901 | TIN-INTERP | Interpolated Ground | 44107.36 | 4.56 | 748.09 | 0 | 36.71 | 0 | OK | Ground clear controls. | 98 | 36.86 | 784.8
6902 | TIN-INTERP | Interpolated Ground | 44107.37 | -5.14 | 747.9 | 0 | 25.99 | 0 | OK | Ground clear controls. | 98 | 36.86 | 773.89
6903 | TIN-INTERP | Interpolated Ground | 44107.38 | -4.64 | 747.98 | 0 | 36.86 | 0 | OK | Ground clear controls. | 98 | 36.86 | 784.84
6904 | TIN-INTERP | Interpolated Ground | 44147.34 | 6.56 | 748.52 | 0 | 26.27 | 0 | OK | Ground clear controls. | 98 | 32.63 | 774.79
6905 | TIN-INTERP | Interpolated Ground | 44147.36 | 5.06 | 748.55 | 0 | 20.85 | 0 | OK | Ground clear controls. | 98 | 32.63 | 769.4
6906 | TIN-INTERP | Interpolated Ground | 44147.36 | -6.64 | 748.6 | 0 | 26.2 | 0 | OK | Ground clear controls. | 98 | 32.63 | 774.8
6907 | TIN-INTERP | Interpolated Ground | 44147.36 | 4.56 | 748.55 | 0 | 31.69 | 0 | OK | Ground clear controls. | 98 | 32.63 | 780.24
6908 | TIN-INTERP | Interpolated Ground | 44147.37 | -5.14 | 748.61 | 0 | 20.78 | 0 | OK | Ground clear controls. | 98 | 32.63 | 769.39
6909 | TIN-INTERP | Interpolated Ground | 44147.38 | -4.64 | 748.6 | 0 | 31.68 | 0 | OK | Ground clear controls. | 98 | 32.63 | 780.28
6910 | TIN-INTERP | Interpolated Ground | 44187.34 | 6.56 | 748.5 | 0 | 22.7 | 0 | OK | Ground clear controls. | 98 | 32.63 | 771.2
6911 | TIN-INTERP | Interpolated Ground | 44187.36 | 5.06 | 748.48 | 0 | 17.35 | 0 | OK | Ground clear controls. | 98 | 32.63 | 765.83
6912 | TIN-INTERP | Interpolated Ground | 44187.36 | -6.64 | 748.29 | 0 | 22.91 | 0 | OK | Ground clear controls. | 98 | 32.63 | 771.2
6913 | TIN-INTERP | Interpolated Ground | 44187.36 | 4.56 | 748.45 | 0 | 28.17 | 0 | OK | Ground clear controls. | 98 | 32.63 | 776.62
6914 | TIN-INTERP | Interpolated Ground | 44187.37 | -5.14 | 748.32 | 0 | 17.51 | 0 | OK | Ground clear controls. | 98 | 32.63 | 765.83
6915 | TIN-INTERP | Interpolated Ground | 44187.38 | -4.64 | 748.32 | 0 | 28.36 | 0 | OK | Ground clear controls. | 98 | 32.63 | 776.68
6916 | TIN-INTERP | Interpolated Ground | 44227.34 | 6.56 | 748.65 | 0 | 19.91 | 0 | OK | Ground clear controls. | 98 | 32.63 | 768.56
6917 | TIN-INTERP | Interpolated Ground | 44227.36 | 5.06 | 748.61 | 0 | 14.61 | 0 | OK | Ground clear controls. | 98 | 32.63 | 763.22
6918 | TIN-INTERP | Interpolated Ground | 44227.36 | -6.64 | 748.67 | 0 | 19.91 | 0 | OK | Ground clear controls. | 98 | 32.63 | 768.58
6919 | TIN-INTERP | Interpolated Ground | 44227.36 | 4.56 | 748.59 | 0 | 25.38 | 0 | OK | Ground clear controls. | 98 | 32.63 | 773.97
6920 | TIN-INTERP | Interpolated Ground | 44227.37 | -5.14 | 748.68 | 0 | 14.53 | 0 | OK | Ground clear controls. | 98 | 32.63 | 763.21
6921 | TIN-INTERP | Interpolated Ground | 44227.38 | -4.64 | 748.69 | 0 | 25.36 | 0 | OK | Ground clear controls. | 98 | 32.63 | 774.05
6922 | TIN-INTERP | Interpolated Ground | 44267.34 | 6.56 | 748.69 | 0 | 18.18 | 0 | OK | Ground clear controls. | 98 | 32.63 | 766.87
6923 | TIN-INTERP | Interpolated Ground | 44267.36 | 5.06 | 748.83 | 0 | 12.72 | 0 | OK | Ground clear controls. | 98 | 32.63 | 761.55
6924 | TIN-INTERP | Interpolated Ground | 44267.36 | -6.64 | 748.85 | 0 | 18.04 | 0 | OK | Ground clear controls. | 98 | 32.63 | 766.89
6925 | TIN-INTERP | Interpolated Ground | 44267.36 | 4.56 | 748.84 | 0 | 23.43 | 0 | OK | Ground clear controls. | 98 | 32.63 | 772.27
6926 | TIN-INTERP | Interpolated Ground | 44267.37 | -5.14 | 748.96 | 0 | 12.57 | 0 | OK | Ground clear controls. | 98 | 32.63 | 761.53
6927 | TIN-INTERP | Interpolated Ground | 44267.38 | -4.64 | 749 | 0 | 23.36 | 0 | OK | Ground clear controls. | 98 | 32.63 | 772.36
6928 | TIN-INTERP | Interpolated Ground | 44307.34 | 6.57 | 749.33 | 0 | 16.8 | 0 | OK | Ground clear controls. | 98 | 32.63 | 766.13
6929 | TIN-INTERP | Interpolated Ground | 44307.36 | 5.07 | 749.28 | 0 | 11.53 | 0 | OK | Ground clear controls. | 98 | 32.63 | 760.81
6930 | TIN-INTERP | Interpolated Ground | 44307.36 | -6.63 | 748.56 | 0 | 17.59 | 0 | OK | Ground clear controls. | 98 | 32.63 | 766.15
6931 | TIN-INTERP | Interpolated Ground | 44307.36 | 4.57 | 749.3 | 0 | 22.24 | 0 | OK | Ground clear controls. | 98 | 32.63 | 771.54
6932 | TIN-INTERP | Interpolated Ground | 44307.37 | -5.13 | 748.12 | 0 | 12.67 | 0 | OK | Ground clear controls. | 98 | 32.63 | 760.79
6933 | TIN-INTERP | Interpolated Ground | 44307.38 | -4.63 | 748 | 0 | 23.62 | 0 | OK | Ground clear controls. | 98 | 32.63 | 771.62
6934 | TIN-INTERP | Interpolated Ground | 44347.34 | 6.57 | 749.67 | 0 | 16.68 | 0 | OK | Ground clear controls. | 98 | 32.63 | 766.35
6935 | TIN-INTERP | Interpolated Ground | 44347.36 | 5.07 | 749.67 | 0 | 11.33 | 0 | OK | Ground clear controls. | 98 | 32.63 | 761
6936 | TIN-INTERP | Interpolated Ground | 44347.36 | -6.63 | 749.45 | 0 | 16.9 | 0 | OK | Ground clear controls. | 98 | 32.63 | 766.35
6937 | TIN-INTERP | Interpolated Ground | 44347.36 | 4.57 | 749.67 | 0 | 22.09 | 0 | OK | Ground clear controls. | 98 | 32.63 | 771.76
6938 | TIN-INTERP | Interpolated Ground | 44347.37 | -5.13 | 749.57 | 0 | 11.43 | 0 | OK | Ground clear controls. | 98 | 32.63 | 761
6939 | TIN-INTERP | Interpolated Ground | 44347.38 | -4.63 | 749.6 | 0 | 22.23 | 0 | OK | Ground clear controls. | 98 | 32.63 | 771.83
6940 | TIN-INTERP | Interpolated Ground | 44387.34 | 6.57 | 750.83 | 0 | 16.68 | 0 | OK | Ground clear controls. | 98 | 32.63 | 767.51
6941 | TIN-INTERP | Interpolated Ground | 44387.36 | 5.07 | 750.77 | 0 | 11.38 | 0 | OK | Ground clear controls. | 98 | 32.63 | 762.15
6942 | TIN-INTERP | Interpolated Ground | 44387.36 | -6.63 | 750.1 | 0 | 17.42 | 0 | OK | Ground clear controls. | 98 | 32.63 | 767.52
6943 | TIN-INTERP | Interpolated Ground | 44387.36 | 4.57 | 750.75 | 0 | 22.17 | 0 | OK | Ground clear controls. | 98 | 32.63 | 772.92
6944 | TIN-INTERP | Interpolated Ground | 44387.37 | -5.13 | 750.22 | 0 | 11.92 | 0 | OK | Ground clear controls. | 98 | 32.63 | 762.14
6945 | TIN-INTERP | Interpolated Ground | 44387.38 | -4.63 | 750.26 | 0 | 22.74 | 0 | OK | Ground clear controls. | 98 | 32.63 | 773
6946 | TIN-INTERP | Interpolated Ground | 44427.34 | 6.57 | 750.71 | 0 | 18.91 | 0 | OK | Ground clear controls. | 98 | 32.63 | 769.62
6947 | TIN-INTERP | Interpolated Ground | 44427.36 | 5.07 | 750.65 | 0 | 13.57 | 0 | OK | Ground clear controls. | 98 | 32.63 | 764.22
6948 | TIN-INTERP | Interpolated Ground | 44427.36 | -6.63 | 750.45 | 0 | 19.17 | 0 | OK | Ground clear controls. | 98 | 32.63 | 769.62
6949 | TIN-INTERP | Interpolated Ground | 44427.36 | 4.57 | 750.62 | 0 | 24.44 | 0 | OK | Ground clear controls. | 98 | 32.63 | 775.06
6950 | TIN-INTERP | Interpolated Ground | 44427.37 | -5.13 | 750.48 | 0 | 13.74 | 0 | OK | Ground clear controls. | 98 | 32.63 | 764.22
6951 | TIN-INTERP | Interpolated Ground | 44427.38 | -4.63 | 750.5 | 0 | 24.61 | 0 | OK | Ground clear controls. | 98 | 32.63 | 775.11
6952 | TIN-INTERP | Interpolated Ground | 44467.34 | 6.58 | 750.65 | 0 | 22.02 | 0 | OK | Ground clear controls. | 98 | 32.63 | 772.67
6953 | TIN-INTERP | Interpolated Ground | 44467.36 | 5.08 | 750.58 | 0 | 16.66 | 0 | OK | Ground clear controls. | 98 | 32.63 | 767.24
6954 | TIN-INTERP | Interpolated Ground | 44467.36 | -6.62 | 750.11 | 0 | 22.57 | 0 | OK | Ground clear controls. | 98 | 32.63 | 772.68
6955 | TIN-INTERP | Interpolated Ground | 44467.36 | 4.58 | 750.56 | 0 | 27.59 | 0 | OK | Ground clear controls. | 98 | 32.63 | 778.15
6956 | TIN-INTERP | Interpolated Ground | 44467.37 | -5.12 | 750.15 | 0 | 17.09 | 0 | OK | Ground clear controls. | 98 | 32.63 | 767.24
6957 | TIN-INTERP | Interpolated Ground | 44467.38 | -4.62 | 750.15 | 0 | 28.02 | 0 | OK | Ground clear controls. | 98 | 32.63 | 778.17
6958 | TIN-INTERP | Interpolated Ground | 44507.34 | 6.58 | 749.66 | 0 | 27.03 | 0 | OK | Ground clear controls. | 98 | 32.63 | 776.69
6959 | TIN-INTERP | Interpolated Ground | 44507.36 | 5.08 | 749.6 | 0 | 21.61 | 0 | OK | Ground clear controls. | 98 | 32.63 | 771.21
6960 | TIN-INTERP | Interpolated Ground | 44507.36 | -6.62 | 749.7 | 0 | 26.99 | 0 | OK | Ground clear controls. | 98 | 32.63 | 776.69
6961 | TIN-INTERP | Interpolated Ground | 44507.36 | 4.58 | 749.57 | 0 | 32.63 | 0 | OK | Ground clear controls. | 98 | 32.63 | 782.2
6962 | TIN-INTERP | Interpolated Ground | 44507.37 | -5.12 | 749.62 | 0 | 21.59 | 0 | OK | Ground clear controls. | 98 | 32.61 | 771.21
6963 | TIN-INTERP | Interpolated Ground | 44507.38 | -4.62 | 749.59 | 0 | 32.61 | 0 | OK | Ground clear controls. | 98 | 32.61 | 782.2
6964 | TIN-INTERP | Interpolated Ground | 44511.69 | 5.08 | 749.66 | 0 | 22.03 | 0 | OK | Ground clear controls. | 99 | 34.83 | 771.69
6965 | TIN-INTERP | Interpolated Ground | 44511.7 | 4.58 | 749.66 | 0 | 33.03 | 0 | OK | Ground clear controls. | 99 | 34.83 | 782.69
6966 | TIN-INTERP | Interpolated Ground | 44511.71 | -5.12 | 749.6 | 0 | 22.09 | 0 | OK | Ground clear controls. | 99 | 34.83 | 771.69
6967 | TIN-INTERP | Interpolated Ground | 44511.71 | 6.58 | 749.63 | 0 | 27.56 | 0 | OK | Ground clear controls. | 99 | 34.83 | 777.19
6968 | TIN-INTERP | Interpolated Ground | 44511.74 | -6.62 | 749.6 | 0 | 27.59 | 0 | OK | Ground clear controls. | 99 | 34.83 | 777.19
6969 | TIN-INTERP | Interpolated Ground | 44511.77 | -4.62 | 749.56 | 0 | 33.13 | 0 | OK | Ground clear controls. | 99 | 34.83 | 782.69
6970 | TIN-INTERP | Interpolated Ground | 44551.69 | 5.08 | 749.17 | 0 | 18.53 | 0 | OK | Ground clear controls. | 99 | 34.83 | 767.7
6971 | TIN-INTERP | Interpolated Ground | 44551.7 | 4.58 | 749.17 | 0 | 29.45 | 0 | OK | Ground clear controls. | 99 | 34.83 | 778.62
6972 | TIN-INTERP | Interpolated Ground | 44551.71 | -5.12 | 749.18 | 0 | 18.52 | 0 | OK | Ground clear controls. | 99 | 34.83 | 767.7
6973 | TIN-INTERP | Interpolated Ground | 44551.71 | 6.58 | 749.16 | 0 | 24 | 0 | OK | Ground clear controls. | 99 | 34.83 | 773.16
6974 | TIN-INTERP | Interpolated Ground | 44551.74 | -6.62 | 749.22 | 0 | 23.95 | 0 | OK | Ground clear controls. | 99 | 34.83 | 773.17
6975 | TIN-INTERP | Interpolated Ground | 44551.77 | -4.62 | 749.18 | 0 | 29.5 | 0 | OK | Ground clear controls. | 99 | 34.83 | 778.68
6976 | TIN-INTERP | Interpolated Ground | 44591.69 | 5.08 | 747.67 | 0 | 16.98 | 0 | OK | Ground clear controls. | 99 | 34.83 | 764.65
6977 | TIN-INTERP | Interpolated Ground | 44591.7 | 4.58 | 747.68 | 0 | 27.82 | 0 | OK | Ground clear controls. | 99 | 34.83 | 775.5
6978 | TIN-INTERP | Interpolated Ground | 44591.71 | -5.12 | 748.81 | 0 | 15.84 | 0 | OK | Ground clear controls. | 99 | 34.83 | 764.65
6979 | TIN-INTERP | Interpolated Ground | 44591.71 | 6.58 | 747.97 | 0 | 22.1 | 0 | OK | Ground clear controls. | 99 | 34.83 | 770.07
6980 | TIN-INTERP | Interpolated Ground | 44591.74 | -6.62 | 748.97 | 0 | 21.12 | 0 | OK | Ground clear controls. | 99 | 34.83 | 770.09
6981 | TIN-INTERP | Interpolated Ground | 44591.77 | -4.62 | 748.78 | 0 | 26.83 | 0 | OK | Ground clear controls. | 99 | 34.83 | 775.61
6982 | TIN-INTERP | Interpolated Ground | 44631.69 | 5.08 | 748.01 | 0 | 14.53 | 0 | OK | Ground clear controls. | 99 | 34.83 | 762.54
6983 | TIN-INTERP | Interpolated Ground | 44631.7 | 4.58 | 747.9 | 0 | 25.44 | 0 | OK | Ground clear controls. | 99 | 34.83 | 773.34
6984 | TIN-INTERP | Interpolated Ground | 44631.71 | -5.12 | 749.66 | 0 | 12.89 | 0 | OK | Ground clear controls. | 99 | 34.83 | 762.55
6985 | TIN-INTERP | Interpolated Ground | 44631.71 | 6.58 | 748.32 | 0 | 19.61 | 0 | OK | Ground clear controls. | 99 | 34.83 | 767.93
6986 | TIN-INTERP | Interpolated Ground | 44631.74 | -6.62 | 749.63 | 0 | 18.34 | 0 | OK | Ground clear controls. | 99 | 34.83 | 767.97
6987 | TIN-INTERP | Interpolated Ground | 44631.77 | -4.62 | 749.68 | 0 | 23.8 | 0 | OK | Ground clear controls. | 99 | 34.83 | 773.48
6988 | TIN-INTERP | Interpolated Ground | 44671.69 | 5.08 | 748.32 | 0 | 13.04 | 0 | OK | Ground clear controls. | 99 | 34.83 | 761.36
6989 | TIN-INTERP | Interpolated Ground | 44671.7 | 4.58 | 748.19 | 0 | 23.95 | 0 | OK | Ground clear controls. | 99 | 34.83 | 772.14
6990 | TIN-INTERP | Interpolated Ground | 44671.71 | -5.12 | 750.19 | 0 | 11.18 | 0 | OK | Ground clear controls. | 99 | 34.83 | 761.37
6991 | TIN-INTERP | Interpolated Ground | 44671.71 | 6.58 | 748.71 | 0 | 18.03 | 0 | OK | Ground clear controls. | 99 | 34.83 | 766.74
6992 | TIN-INTERP | Interpolated Ground | 44671.74 | -6.62 | 750.16 | 0 | 16.62 | 0 | OK | Ground clear controls. | 99 | 34.83 | 766.78
6993 | TIN-INTERP | Interpolated Ground | 44671.77 | -4.62 | 750.17 | 0 | 22.12 | 0 | OK | Ground clear controls. | 99 | 34.83 | 772.29
6994 | TIN-INTERP | Interpolated Ground | 44711.69 | 5.08 | 749.69 | 0 | 11.43 | 0 | OK | Ground clear controls. | 99 | 34.83 | 761.12
6995 | TIN-INTERP | Interpolated Ground | 44711.7 | 4.58 | 749.7 | 0 | 22.19 | 0 | OK | Ground clear controls. | 99 | 34.83 | 771.89
6996 | TIN-INTERP | Interpolated Ground | 44711.71 | -5.12 | 749.7 | 0 | 11.44 | 0 | OK | Ground clear controls. | 99 | 34.83 | 761.14
6997 | TIN-INTERP | Interpolated Ground | 44711.71 | 6.58 | 749.72 | 0 | 16.78 | 0 | OK | Ground clear controls. | 99 | 34.83 | 766.5
6998 | TIN-INTERP | Interpolated Ground | 44711.74 | -6.62 | 749.61 | 0 | 16.93 | 0 | OK | Ground clear controls. | 99 | 34.83 | 766.54
6999 | TIN-INTERP | Interpolated Ground | 44711.77 | -4.62 | 749.69 | 0 | 22.37 | 0 | OK | Ground clear controls. | 99 | 34.83 | 772.06
7000 | TIN-INTERP | Interpolated Ground | 44751.69 | 5.08 | 749.7 | 0 | 12.13 | 0 | OK | Ground clear controls. | 99 | 34.83 | 761.83
7001 | TIN-INTERP | Interpolated Ground | 44751.7 | 4.58 | 749.71 | 0 | 22.88 | 0 | OK | Ground clear controls. | 99 | 34.83 | 772.59
7002 | TIN-INTERP | Interpolated Ground | 44751.71 | -5.12 | 749.7 | 0 | 12.14 | 0 | OK | Ground clear controls. | 99 | 34.83 | 761.84
7003 | TIN-INTERP | Interpolated Ground | 44751.71 | 6.58 | 749.71 | 0 | 17.5 | 0 | OK | Ground clear controls. | 99 | 34.83 | 767.21
7004 | TIN-INTERP | Interpolated Ground | 44751.74 | -6.62 | 749.71 | 0 | 17.53 | 0 | OK | Ground clear controls. | 99 | 34.83 | 767.24
7005 | TIN-INTERP | Interpolated Ground | 44751.77 | -4.62 | 749.72 | 0 | 23.04 | 0 | OK | Ground clear controls. | 99 | 34.83 | 772.76
7006 | TIN-INTERP | Interpolated Ground | 44791.69 | 5.08 | 749.89 | 0 | 13.57 | 0 | OK | Ground clear controls. | 99 | 34.83 | 763.46
7007 | TIN-INTERP | Interpolated Ground | 44791.7 | 4.58 | 749.89 | 0 | 24.36 | 0 | OK | Ground clear controls. | 99 | 34.83 | 774.25
7008 | TIN-INTERP | Interpolated Ground | 44791.71 | -5.12 | 749.97 | 0 | 13.5 | 0 | OK | Ground clear controls. | 99 | 34.83 | 763.47
7009 | TIN-INTERP | Interpolated Ground | 44791.71 | 6.58 | 749.87 | 0 | 18.98 | 0 | OK | Ground clear controls. | 99 | 34.83 | 768.85
7010 | TIN-INTERP | Interpolated Ground | 44791.74 | -6.62 | 749.96 | 0 | 18.92 | 0 | OK | Ground clear controls. | 99 | 34.83 | 768.88
7011 | TIN-INTERP | Interpolated Ground | 44791.77 | -4.62 | 749.97 | 0 | 24.43 | 0 | OK | Ground clear controls. | 99 | 34.83 | 774.4
7012 | TIN-INTERP | Interpolated Ground | 44831.69 | 5.08 | 750.02 | 0 | 16.02 | 0 | OK | Ground clear controls. | 99 | 34.83 | 766.04
7013 | TIN-INTERP | Interpolated Ground | 44831.7 | 4.58 | 750.02 | 0 | 26.85 | 0 | OK | Ground clear controls. | 99 | 34.83 | 776.87
7014 | TIN-INTERP | Interpolated Ground | 44831.71 | -5.12 | 750.05 | 0 | 16 | 0 | OK | Ground clear controls. | 99 | 34.83 | 766.05
7015 | TIN-INTERP | Interpolated Ground | 44831.71 | 6.58 | 750.01 | 0 | 21.44 | 0 | OK | Ground clear controls. | 99 | 34.83 | 771.45
7016 | TIN-INTERP | Interpolated Ground | 44831.74 | -6.62 | 750.03 | 0 | 21.44 | 0 | OK | Ground clear controls. | 99 | 34.83 | 771.47
7017 | TIN-INTERP | Interpolated Ground | 44831.77 | -4.62 | 750.05 | 0 | 26.94 | 0 | OK | Ground clear controls. | 99 | 34.83 | 776.99
7018 | TIN-INTERP | Interpolated Ground | 44871.69 | 5.08 | 750.11 | 0 | 19.44 | 0 | OK | Ground clear controls. | 99 | 34.83 | 769.55
7019 | TIN-INTERP | Interpolated Ground | 44871.7 | 4.58 | 750.11 | 0 | 30.33 | 0 | OK | Ground clear controls. | 99 | 34.83 | 780.44
7020 | TIN-INTERP | Interpolated Ground | 44871.71 | -5.12 | 750.15 | 0 | 19.41 | 0 | OK | Ground clear controls. | 99 | 34.83 | 769.56
7021 | TIN-INTERP | Interpolated Ground | 44871.71 | 6.58 | 750.11 | 0 | 24.88 | 0 | OK | Ground clear controls. | 99 | 34.83 | 774.99
7022 | TIN-INTERP | Interpolated Ground | 44871.74 | -6.62 | 750.15 | 0 | 24.86 | 0 | OK | Ground clear controls. | 99 | 34.83 | 775.01
7023 | TIN-INTERP | Interpolated Ground | 44871.77 | -4.62 | 750.16 | 0 | 30.37 | 0 | OK | Ground clear controls. | 99 | 34.83 | 780.53
7024 | TIN-INTERP | Interpolated Ground | 44911.69 | 5.08 | 750.3 | 0 | 23.72 | 0 | OK | Ground clear controls. | 99 | 34.83 | 774.02
7025 | TIN-INTERP | Interpolated Ground | 44911.7 | 4.58 | 750.28 | 0 | 34.69 | 0 | OK | Ground clear controls. | 99 | 34.83 | 784.97
7026 | TIN-INTERP | Interpolated Ground | 44911.71 | -5.12 | 750.17 | 0 | 23.85 | 0 | OK | Ground clear controls. | 99 | 34.83 | 774.02
7027 | TIN-INTERP | Interpolated Ground | 44911.71 | 6.58 | 750.32 | 0 | 29.17 | 0 | OK | Ground clear controls. | 99 | 34.83 | 779.49
7028 | TIN-INTERP | Interpolated Ground | 44911.74 | -6.62 | 750.15 | 0 | 29.34 | 0 | OK | Ground clear controls. | 99 | 34.83 | 779.49
7029 | TIN-INTERP | Interpolated Ground | 44911.77 | -4.62 | 750.18 | 0 | 34.83 | 0 | OK | Ground clear controls. | 99 | 34.83 | 785.01
7030 | TIN-INTERP | Interpolated Ground | 44935.53 | 4.58 | 750.42 | 0 | 37.7 | 0 | OK | Ground clear controls. | 100 | 37.87 | 788.12
7031 | TIN-INTERP | Interpolated Ground | 44935.56 | 6.58 | 750.35 | 0 | 32.27 | 0 | OK | Ground clear controls. | 100 | 37.87 | 782.62
7032 | TIN-INTERP | Interpolated Ground | 44935.56 | -4.62 | 750.25 | 0 | 37.87 | 0 | OK | Ground clear controls. | 100 | 37.87 | 788.12
7033 | TIN-INTERP | Interpolated Ground | 44935.56 | 5.08 | 750.42 | 0 | 26.7 | 0 | OK | Ground clear controls. | 100 | 34.42 | 777.12
7034 | TIN-INTERP | Interpolated Ground | 44935.57 | -6.62 | 750.29 | 0 | 32.33 | 0 | OK | Ground clear controls. | 100 | 34.42 | 782.62
7035 | TIN-INTERP | Interpolated Ground | 44935.58 | -5.12 | 750.26 | 0 | 26.86 | 0 | OK | Ground clear controls. | 100 | 34.42 | 777.12
7036 | TIN-INTERP | Interpolated Ground | 44975.53 | 4.57 | 750.29 | 0 | 32.83 | 0 | OK | Ground clear controls. | 100 | 34.42 | 783.12
7037 | TIN-INTERP | Interpolated Ground | 44975.56 | 6.57 | 750.3 | 0 | 27.38 | 0 | OK | Ground clear controls. | 100 | 34.42 | 777.68
7038 | TIN-INTERP | Interpolated Ground | 44975.56 | -4.64 | 750.15 | 0 | 33.04 | 0 | OK | Ground clear controls. | 100 | 34.42 | 783.19
7039 | TIN-INTERP | Interpolated Ground | 44975.56 | 5.07 | 750.29 | 0 | 21.93 | 0 | OK | Ground clear controls. | 100 | 34.42 | 772.22
7040 | TIN-INTERP | Interpolated Ground | 44975.57 | -6.64 | 750.11 | 0 | 27.59 | 0 | OK | Ground clear controls. | 100 | 34.42 | 777.7
7041 | TIN-INTERP | Interpolated Ground | 44975.58 | -5.14 | 750.1 | 0 | 22.14 | 0 | OK | Ground clear controls. | 100 | 34.42 | 772.24
7042 | TIN-INTERP | Interpolated Ground | 45015.53 | 4.56 | 750.06 | 0 | 29.01 | 0 | OK | Ground clear controls. | 100 | 34.42 | 779.07
7043 | TIN-INTERP | Interpolated Ground | 45015.56 | 6.56 | 749.97 | 0 | 23.71 | 0 | OK | Ground clear controls. | 100 | 34.42 | 773.68
7044 | TIN-INTERP | Interpolated Ground | 45015.56 | -4.66 | 750.36 | 0 | 28.86 | 0 | OK | Ground clear controls. | 100 | 34.42 | 779.22
7045 | TIN-INTERP | Interpolated Ground | 45015.56 | 5.06 | 750.02 | 0 | 18.25 | 0 | OK | Ground clear controls. | 100 | 34.42 | 768.27
7046 | TIN-INTERP | Interpolated Ground | 45015.57 | -6.66 | 750.25 | 0 | 23.46 | 0 | OK | Ground clear controls. | 100 | 34.42 | 773.71
7047 | TIN-INTERP | Interpolated Ground | 45015.58 | -5.16 | 750.33 | 0 | 17.96 | 0 | OK | Ground clear controls. | 100 | 34.42 | 768.29
7048 | TIN-INTERP | Interpolated Ground | 45055.53 | 4.55 | 750.17 | 0 | 25.81 | 0 | OK | Ground clear controls. | 100 | 34.42 | 775.98
7049 | TIN-INTERP | Interpolated Ground | 45055.56 | 6.55 | 750.16 | 0 | 20.46 | 0 | OK | Ground clear controls. | 100 | 34.42 | 770.62
7050 | TIN-INTERP | Interpolated Ground | 45055.56 | -4.67 | 750.19 | 0 | 25.99 | 0 | OK | Ground clear controls. | 100 | 34.42 | 776.18
7051 | TIN-INTERP | Interpolated Ground | 45055.56 | 5.05 | 750.16 | 0 | 15.09 | 0 | OK | Ground clear controls. | 100 | 34.42 | 765.25
7052 | TIN-INTERP | Interpolated Ground | 45055.57 | -6.67 | 750.24 | 0 | 20.44 | 0 | OK | Ground clear controls. | 100 | 34.42 | 770.68
7053 | TIN-INTERP | Interpolated Ground | 45055.58 | -5.17 | 750.19 | 0 | 15.09 | 0 | OK | Ground clear controls. | 100 | 34.42 | 765.28
7054 | TIN-INTERP | Interpolated Ground | 45095.53 | 4.54 | 750.13 | 0 | 23.72 | 0 | OK | Ground clear controls. | 100 | 34.42 | 773.85
7055 | TIN-INTERP | Interpolated Ground | 45095.56 | 6.54 | 750.14 | 0 | 18.38 | 0 | OK | Ground clear controls. | 100 | 34.42 | 768.52
7056 | TIN-INTERP | Interpolated Ground | 45095.56 | -4.69 | 750.21 | 0 | 23.86 | 0 | OK | Ground clear controls. | 100 | 34.42 | 774.07
7057 | TIN-INTERP | Interpolated Ground | 45095.56 | 5.04 | 750.15 | 0 | 13.02 | 0 | OK | Ground clear controls. | 100 | 34.42 | 763.17
7058 | TIN-INTERP | Interpolated Ground | 45095.57 | -6.69 | 750.19 | 0 | 18.39 | 0 | OK | Ground clear controls. | 100 | 34.42 | 768.58
7059 | TIN-INTERP | Interpolated Ground | 45095.58 | -5.19 | 750.21 | 0 | 13 | 0 | OK | Ground clear controls. | 100 | 34.42 | 763.21
7060 | TIN-INTERP | Interpolated Ground | 45135.53 | 4.53 | 750.39 | 0 | 22.29 | 0 | OK | Ground clear controls. | 100 | 34.42 | 772.68
7061 | TIN-INTERP | Interpolated Ground | 45135.56 | 6.53 | 750.28 | 0 | 17.08 | 0 | OK | Ground clear controls. | 100 | 34.42 | 767.36
7062 | TIN-INTERP | Interpolated Ground | 45135.56 | -4.7 | 750.34 | 0 | 22.58 | 0 | OK | Ground clear controls. | 100 | 34.42 | 772.92
7063 | TIN-INTERP | Interpolated Ground | 45135.56 | 5.03 | 750.37 | 0 | 11.65 | 0 | OK | Ground clear controls. | 100 | 34.42 | 762.02
7064 | TIN-INTERP | Interpolated Ground | 45135.57 | -6.71 | 750.31 | 0 | 17.11 | 0 | OK | Ground clear controls. | 100 | 34.42 | 767.42
7065 | TIN-INTERP | Interpolated Ground | 45135.58 | -5.21 | 750.33 | 0 | 11.73 | 0 | OK | Ground clear controls. | 100 | 34.42 | 762.06
7066 | TIN-INTERP | Interpolated Ground | 45175.53 | 4.52 | 750.47 | 0 | 21.99 | 0 | OK | Ground clear controls. | 100 | 34.42 | 772.46
7067 | TIN-INTERP | Interpolated Ground | 45175.56 | 6.53 | 750.28 | 0 | 16.86 | 0 | OK | Ground clear controls. | 100 | 34.42 | 767.14
7068 | TIN-INTERP | Interpolated Ground | 45175.56 | -4.72 | 750.64 | 0 | 22.06 | 0 | OK | Ground clear controls. | 100 | 34.42 | 772.7
7069 | TIN-INTERP | Interpolated Ground | 45175.56 | 5.03 | 750.42 | 0 | 11.39 | 0 | OK | Ground clear controls. | 100 | 34.42 | 761.81
7070 | TIN-INTERP | Interpolated Ground | 45175.57 | -6.72 | 750.61 | 0 | 16.59 | 0 | OK | Ground clear controls. | 100 | 34.42 | 767.2
7071 | TIN-INTERP | Interpolated Ground | 45175.58 | -5.22 | 750.65 | 0 | 11.21 | 0 | OK | Ground clear controls. | 100 | 34.42 | 761.86
7072 | TIN-INTERP | Interpolated Ground | 45215.53 | 4.51 | 750.51 | 0 | 22.68 | 0 | OK | Ground clear controls. | 100 | 34.42 | 773.19
7073 | TIN-INTERP | Interpolated Ground | 45215.56 | 6.52 | 750.53 | 0 | 17.34 | 0 | OK | Ground clear controls. | 100 | 34.42 | 767.87
7074 | TIN-INTERP | Interpolated Ground | 45215.56 | -4.74 | 750.45 | 0 | 22.97 | 0 | OK | Ground clear controls. | 100 | 34.42 | 773.42
7075 | TIN-INTERP | Interpolated Ground | 45215.56 | 5.02 | 750.52 | 0 | 12.01 | 0 | OK | Ground clear controls. | 100 | 34.42 | 762.53
7076 | TIN-INTERP | Interpolated Ground | 45215.57 | -6.74 | 750.45 | 0 | 17.48 | 0 | OK | Ground clear controls. | 100 | 34.42 | 767.93
7077 | TIN-INTERP | Interpolated Ground | 45215.58 | -5.24 | 750.46 | 0 | 12.11 | 0 | OK | Ground clear controls. | 100 | 34.42 | 762.57
7078 | TIN-INTERP | Interpolated Ground | 45255.53 | 4.5 | 750.55 | 0 | 24.32 | 0 | OK | Ground clear controls. | 100 | 34.42 | 774.87
7079 | TIN-INTERP | Interpolated Ground | 45255.56 | 6.51 | 750.55 | 0 | 18.99 | 0 | OK | Ground clear controls. | 100 | 34.42 | 769.54
7080 | TIN-INTERP | Interpolated Ground | 45255.56 | -4.75 | 750.44 | 0 | 24.65 | 0 | OK | Ground clear controls. | 100 | 34.42 | 775.09
7081 | TIN-INTERP | Interpolated Ground | 45255.56 | 5.01 | 750.53 | 0 | 13.67 | 0 | OK | Ground clear controls. | 100 | 34.42 | 764.2
7082 | TIN-INTERP | Interpolated Ground | 45255.57 | -6.76 | 750.53 | 0 | 19.07 | 0 | OK | Ground clear controls. | 100 | 34.42 | 769.6
7083 | TIN-INTERP | Interpolated Ground | 45255.58 | -5.25 | 750.47 | 0 | 13.75 | 0 | OK | Ground clear controls. | 100 | 34.42 | 764.22
7084 | TIN-INTERP | Interpolated Ground | 45295.53 | 4.5 | 750.71 | 0 | 26.81 | 0 | OK | Ground clear controls. | 100 | 34.42 | 777.52
7085 | TIN-INTERP | Interpolated Ground | 45295.56 | 6.5 | 750.73 | 0 | 21.43 | 0 | OK | Ground clear controls. | 100 | 34.42 | 772.16
7086 | TIN-INTERP | Interpolated Ground | 45295.56 | -4.77 | 750.77 | 0 | 26.93 | 0 | OK | Ground clear controls. | 100 | 34.42 | 777.7
7087 | TIN-INTERP | Interpolated Ground | 45295.56 | 5 | 750.72 | 0 | 16.07 | 0 | OK | Ground clear controls. | 100 | 34.42 | 766.79
7088 | TIN-INTERP | Interpolated Ground | 45295.57 | -6.77 | 750.76 | 0 | 21.44 | 0 | OK | Ground clear controls. | 100 | 34.42 | 772.2
7089 | TIN-INTERP | Interpolated Ground | 45295.58 | -5.27 | 750.77 | 0 | 16.04 | 0 | OK | Ground clear controls. | 100 | 34.42 | 766.81
7090 | TIN-INTERP | Interpolated Ground | 45335.53 | 4.49 | 750.87 | 0 | 30.25 | 0 | OK | Ground clear controls. | 100 | 34.42 | 781.12
7091 | TIN-INTERP | Interpolated Ground | 45335.56 | 6.49 | 750.85 | 0 | 24.88 | 0 | OK | Ground clear controls. | 100 | 34.42 | 775.73
7092 | TIN-INTERP | Interpolated Ground | 45335.56 | -4.78 | 750.86 | 0 | 30.39 | 0 | OK | Ground clear controls. | 100 | 34.42 | 781.25
7093 | TIN-INTERP | Interpolated Ground | 45335.56 | 4.99 | 750.87 | 0 | 19.46 | 0 | OK | Ground clear controls. | 100 | 34.42 | 770.33
7094 | TIN-INTERP | Interpolated Ground | 45335.57 | -6.79 | 750.86 | 0 | 24.89 | 0 | OK | Ground clear controls. | 100 | 34.42 | 775.75
7095 | TIN-INTERP | Interpolated Ground | 45335.58 | -5.29 | 750.86 | 0 | 19.47 | 0 | OK | Ground clear controls. | 100 | 34.42 | 770.33
7096 | TIN-INTERP | Interpolated Ground | 45375.53 | 4.48 | 751.34 | 0 | 34.35 | 0 | OK | Ground clear controls. | 100 | 34.42 | 785.69
7097 | TIN-INTERP | Interpolated Ground | 45375.56 | 6.48 | 751.33 | 0 | 28.91 | 0 | OK | Ground clear controls. | 100 | 34.42 | 780.24
7098 | TIN-INTERP | Interpolated Ground | 45375.56 | -4.8 | 751.32 | 0 | 34.42 | 0 | OK | Ground clear controls. | 100 | 34.42 | 785.74
7099 | TIN-INTERP | Interpolated Ground | 45375.56 | 4.98 | 751.34 | 0 | 23.46 | 0 | OK | Ground clear controls. | 100 | 28.91 | 774.8
7100 | TIN-INTERP | Interpolated Ground | 45375.57 | -6.8 | 751.33 | 0 | 28.91 | 0 | OK | Ground clear controls. | 100 | 28.91 | 780.24
7101 | TIN-INTERP | Interpolated Ground | 45375.58 | -5.3 | 751.32 | 0 | 23.47 | 0 | OK | Ground clear controls. | 100 | 23.47 | 774.79
7102 | TIN-INTERP | Interpolated Ground | 45408.01 | 4.98 | 752.34 | 0 | 26.77 | 0 | OK | Ground clear controls. | 101 | 42.66 | 779.11
7103 | TIN-INTERP | Interpolated Ground | 45408.09 | 6.48 | 752.28 | 0 | 32.33 | 0 | OK | Ground clear controls. | 101 | 42.66 | 784.61
7104 | TIN-INTERP | Interpolated Ground | 45408.11 | 4.47 | 752.37 | 0 | 37.74 | 0 | OK | Ground clear controls. | 101 | 42.66 | 790.11
7105 | TIN-INTERP | Interpolated Ground | 45408.22 | -5.32 | 752.36 | 0 | 26.75 | 0 | OK | Ground clear controls. | 101 | 42.66 | 779.11
7106 | TIN-INTERP | Interpolated Ground | 45408.23 | -4.81 | 752.36 | 0 | 37.76 | 0 | OK | Ground clear controls. | 101 | 42.66 | 790.12
7107 | TIN-INTERP | Interpolated Ground | 45408.27 | -6.82 | 752.32 | 0 | 32.3 | 0 | OK | Ground clear controls. | 101 | 42.66 | 784.62
7108 | TIN-INTERP | Interpolated Ground | 45448.01 | 4.94 | 752.33 | 0 | 25.57 | 0 | OK | Ground clear controls. | 101 | 42.66 | 777.9
7109 | TIN-INTERP | Interpolated Ground | 45448.08 | 6.44 | 752.35 | 0 | 31.07 | 0 | OK | Ground clear controls. | 101 | 42.66 | 783.42
7110 | TIN-INTERP | Interpolated Ground | 45448.11 | 4.42 | 752.34 | 0 | 36.65 | 0 | OK | Ground clear controls. | 101 | 42.66 | 788.99
7111 | TIN-INTERP | Interpolated Ground | 45448.21 | -5.62 | 752.23 | 0 | 25.78 | 0 | OK | Ground clear controls. | 101 | 42.66 | 778.01
7112 | TIN-INTERP | Interpolated Ground | 45448.23 | -5.11 | 752.23 | 0 | 36.88 | 0 | OK | Ground clear controls. | 101 | 42.66 | 789.11
7113 | TIN-INTERP | Interpolated Ground | 45448.27 | -7.13 | 752.19 | 0 | 31.35 | 0 | OK | Ground clear controls. | 101 | 42.66 | 783.54
7114 | TIN-INTERP | Interpolated Ground | 45488.01 | 4.91 | 752.42 | 0 | 25.22 | 0 | OK | Ground clear controls. | 101 | 42.66 | 777.64
7115 | TIN-INTERP | Interpolated Ground | 45488.08 | 6.41 | 752.37 | 0 | 30.81 | 0 | OK | Ground clear controls. | 101 | 42.66 | 783.18
7116 | TIN-INTERP | Interpolated Ground | 45488.11 | 4.37 | 752.44 | 0 | 36.39 | 0 | OK | Ground clear controls. | 101 | 42.66 | 788.83
7117 | TIN-INTERP | Interpolated Ground | 45488.21 | -5.93 | 752.43 | 0 | 25.4 | 0 | OK | Ground clear controls. | 101 | 42.66 | 777.83
7118 | TIN-INTERP | Interpolated Ground | 45488.23 | -5.4 | 752.44 | 0 | 36.61 | 0 | OK | Ground clear controls. | 101 | 42.66 | 789.05
7119 | TIN-INTERP | Interpolated Ground | 45488.27 | -7.43 | 752.43 | 0 | 30.96 | 0 | OK | Ground clear controls. | 101 | 42.66 | 783.39
7120 | TIN-INTERP | Interpolated Ground | 45528.01 | 4.88 | 752.76 | 0 | 25.56 | 0 | OK | Ground clear controls. | 101 | 42.66 | 778.32
7121 | TIN-INTERP | Interpolated Ground | 45528.08 | 6.38 | 752.73 | 0 | 31.16 | 0 | OK | Ground clear controls. | 101 | 42.66 | 783.89
7122 | TIN-INTERP | Interpolated Ground | 45528.11 | 4.32 | 752.75 | 0 | 36.87 | 0 | OK | Ground clear controls. | 101 | 42.66 | 789.62
7123 | TIN-INTERP | Interpolated Ground | 45528.21 | -6.23 | 753.24 | 0 | 25.35 | 0 | OK | Ground clear controls. | 101 | 42.66 | 778.59
7124 | TIN-INTERP | Interpolated Ground | 45528.23 | -5.69 | 753.24 | 0 | 36.68 | 0 | OK | Ground clear controls. | 101 | 42.66 | 789.92
7125 | TIN-INTERP | Interpolated Ground | 45528.27 | -7.74 | 753.24 | 0 | 30.94 | 0 | OK | Ground clear controls. | 101 | 42.66 | 784.18
7126 | TIN-INTERP | Interpolated Ground | 45568.01 | 4.84 | 754.11 | 0 | 25.84 | 0 | OK | Ground clear controls. | 101 | 42.66 | 779.95
7127 | TIN-INTERP | Interpolated Ground | 45568.08 | 6.35 | 754.09 | 0 | 31.46 | 0 | OK | Ground clear controls. | 101 | 42.66 | 785.55
7128 | TIN-INTERP | Interpolated Ground | 45568.11 | 4.27 | 754.1 | 0 | 37.28 | 0 | OK | Ground clear controls. | 101 | 42.66 | 791.38
7129 | TIN-INTERP | Interpolated Ground | 45568.21 | -6.53 | 754.08 | 0 | 26.18 | 0 | OK | Ground clear controls. | 101 | 42.66 | 780.26
7130 | TIN-INTERP | Interpolated Ground | 45568.23 | -5.98 | 754.07 | 0 | 37.65 | 0 | OK | Ground clear controls. | 101 | 42.66 | 791.72
7131 | TIN-INTERP | Interpolated Ground | 45568.27 | -8.05 | 754.14 | 0 | 31.75 | 0 | OK | Ground clear controls. | 101 | 42.66 | 785.89
7132 | TIN-INTERP | Interpolated Ground | 45608.01 | 4.81 | 753.87 | 0 | 28.65 | 0 | OK | Ground clear controls. | 101 | 42.66 | 782.52
7133 | TIN-INTERP | Interpolated Ground | 45608.08 | 6.31 | 753.88 | 0 | 34.28 | 0 | OK | Ground clear controls. | 101 | 42.66 | 788.16
7134 | TIN-INTERP | Interpolated Ground | 45608.11 | 4.22 | 753.84 | 0 | 40.25 | 0 | OK | Ground clear controls. | 101 | 42.66 | 794.09
7135 | TIN-INTERP | Interpolated Ground | 45608.21 | -6.84 | 753.89 | 0 | 28.98 | 0 | OK | Ground clear controls. | 101 | 42.66 | 782.87
7136 | TIN-INTERP | Interpolated Ground | 45608.23 | -6.27 | 753.89 | 0 | 40.58 | 0 | OK | Ground clear controls. | 101 | 42.66 | 794.47
7137 | TIN-INTERP | Interpolated Ground | 45608.27 | -8.36 | 753.91 | 0 | 34.64 | 0 | OK | Ground clear controls. | 101 | 42.66 | 788.55
7138 | TIN-INTERP | Interpolated Ground | 45648.01 | 4.78 | 755.11 | 0 | 30.94 | 0 | OK | Ground clear controls. | 101 | 42.66 | 786.05
7139 | TIN-INTERP | Interpolated Ground | 45648.08 | 6.28 | 755.06 | 0 | 36.66 | 0 | OK | Ground clear controls. | 101 | 42.66 | 791.72
7140 | TIN-INTERP | Interpolated Ground | 45648.11 | 4.17 | 755.11 | 0 | 42.66 | 0 | OK | Ground clear controls. | 101 | 42.66 | 797.77
7141 | TIN-INTERP | Interpolated Ground | 45648.21 | -7.14 | 755.53 | 0 | 30.89 | 0 | OK | Ground clear controls. | 101 | 42.65 | 786.42
7142 | TIN-INTERP | Interpolated Ground | 45648.23 | -6.57 | 755.51 | 0 | 42.65 | 0 | OK | Ground clear controls. | 101 | 42.65 | 798.16
7143 | TIN-INTERP | Interpolated Ground | 45648.27 | -8.67 | 755.56 | 0 | 36.58 | 0 | OK | Ground clear controls. | 101 | 38.57 | 792.14
7144 | TIN-INTERP | Interpolated Ground | 45688.01 | 4.74 | 763.92 | 0 | 26.59 | 0 | OK | Ground clear controls. | 101 | 38.57 | 790.51
7145 | TIN-INTERP | Interpolated Ground | 45688.08 | 6.25 | 763.83 | 0 | 32.41 | 0 | OK | Ground clear controls. | 101 | 38.57 | 796.24
7146 | TIN-INTERP | Interpolated Ground | 45688.11 | 4.12 | 763.99 | 0 | 38.42 | 0 | OK | Ground clear controls. | 101 | 38.57 | 802.41
7147 | TIN-INTERP | Interpolated Ground | 45688.21 | -7.45 | 764.25 | 0 | 26.65 | 0 | OK | Ground clear controls. | 101 | 38.57 | 790.9
7148 | TIN-INTERP | Interpolated Ground | 45688.22 | -6.86 | 764.22 | 0 | 38.57 | 0 | OK | Ground clear controls. | 101 | 38.57 | 802.79
7149 | TIN-INTERP | Interpolated Ground | 45688.27 | -8.97 | 764.3 | 0 | 32.37 | 0 | OK | Ground clear controls. | 101 | 32.95 | 796.67
7150 | TIN-INTERP | Interpolated Ground | 45728.01 | 4.71 | 775.15 | 0 | 20.8 | 0 | OK | Ground clear controls. | 101 | 32.95 | 795.95
7151 | TIN-INTERP | Interpolated Ground | 45728.08 | 6.21 | 775.05 | 0 | 26.66 | 0 | OK | Ground clear controls. | 101 | 32.95 | 801.71
7152 | TIN-INTERP | Interpolated Ground | 45728.11 | 4.06 | 775.24 | 0 | 32.78 | 0 | OK | Ground clear controls. | 101 | 32.95 | 808.02
7153 | TIN-INTERP | Interpolated Ground | 45728.21 | -7.75 | 775.33 | 0 | 20.98 | 0 | OK | Ground clear controls. | 101 | 32.95 | 796.31
7154 | TIN-INTERP | Interpolated Ground | 45728.22 | -7.15 | 775.4 | 0 | 32.95 | 0 | OK | Ground clear controls. | 101 | 32.95 | 808.35
7155 | TIN-INTERP | Interpolated Ground | 45728.26 | -9.28 | 775.17 | 0 | 26.96 | 0 | OK | Ground clear controls. | 101 | 26.96 | 802.13
7156 | TIN-INTERP | Interpolated Ground | 45733.48 | -9.32 | 775.22 | 0 | 27.69 | 0 | OK | Ground clear controls. | 102 | 39.61 | 802.91
7157 | TIN-INTERP | Interpolated Ground | 45733.68 | -7.79 | 775.47 | 0 | 21.65 | 0 | OK | Ground clear controls. | 102 | 39.61 | 797.12
7158 | TIN-INTERP | Interpolated Ground | 45733.81 | -7.19 | 775.56 | 0 | 33.64 | 0 | OK | Ground clear controls. | 102 | 39.61 | 809.2
7159 | TIN-INTERP | Interpolated Ground | 45734.86 | 4.07 | 775.75 | 0 | 33.36 | 0 | OK | Ground clear controls. | 102 | 39.61 | 809.11
7160 | TIN-INTERP | Interpolated Ground | 45734.86 | 4.73 | 775.69 | 0 | 21.35 | 0 | OK | Ground clear controls. | 102 | 39.61 | 797.04
7161 | TIN-INTERP | Interpolated Ground | 45734.86 | 6.24 | 775.36 | 0 | 27.47 | 0 | OK | Ground clear controls. | 102 | 39.61 | 802.83
7162 | TIN-INTERP | Interpolated Ground | 45773.81 | 6.19 | 773.69 | 0 | 23.14 | 0 | OK | Ground clear controls. | 102 | 39.61 | 796.83
7163 | TIN-INTERP | Interpolated Ground | 45774.06 | 4.7 | 773.21 | 0 | 17.9 | 0 | OK | Ground clear controls. | 102 | 39.61 | 791.11
7164 | TIN-INTERP | Interpolated Ground | 45774.09 | 4.05 | 773.05 | 0 | 29.92 | 0 | OK | Ground clear controls. | 102 | 39.61 | 802.97
7165 | TIN-INTERP | Interpolated Ground | 45775.77 | -6.96 | 770.2 | 0 | 33.02 | 0 | OK | Ground clear controls. | 102 | 39.61 | 803.22
7166 | TIN-INTERP | Interpolated Ground | 45775.81 | -7.56 | 769.99 | 0 | 21.24 | 0 | OK | Ground clear controls. | 102 | 39.61 | 791.23
7167 | TIN-INTERP | Interpolated Ground | 45776.02 | -9.09 | 769.47 | 0 | 27.51 | 0 | OK | Ground clear controls. | 102 | 39.61 | 796.98
7168 | TIN-INTERP | Interpolated Ground | 45813.81 | 6.23 | 761.42 | 0 | 30.38 | 0 | OK | Ground clear controls. | 102 | 39.61 | 791.8
7169 | TIN-INTERP | Interpolated Ground | 45814.06 | 4.73 | 760.97 | 0 | 25.17 | 0 | OK | Ground clear controls. | 102 | 39.61 | 786.14
7170 | TIN-INTERP | Interpolated Ground | 45814.09 | 4.1 | 760.82 | 0 | 37 | 0 | OK | Ground clear controls. | 102 | 39.61 | 797.82
7171 | TIN-INTERP | Interpolated Ground | 45815.77 | -6.7 | 758.56 | 0 | 39.61 | 0 | OK | Ground clear controls. | 102 | 39.61 | 798.17
7172 | TIN-INTERP | Interpolated Ground | 45815.81 | -7.3 | 758.48 | 0 | 27.83 | 0 | OK | Ground clear controls. | 102 | 38.42 | 786.31
7173 | TIN-INTERP | Interpolated Ground | 45816.02 | -8.82 | 758.2 | 0 | 33.8 | 0 | OK | Ground clear controls. | 102 | 38.42 | 792
7174 | TIN-INTERP | Interpolated Ground | 45853.81 | 6.26 | 755.54 | 0 | 32.19 | 0 | OK | Ground clear controls. | 102 | 38.42 | 787.73
7175 | TIN-INTERP | Interpolated Ground | 45854.06 | 4.77 | 755.58 | 0 | 26.54 | 0 | OK | Ground clear controls. | 102 | 38.42 | 782.12
7176 | TIN-INTERP | Interpolated Ground | 45854.09 | 4.16 | 755.58 | 0 | 38.06 | 0 | OK | Ground clear controls. | 102 | 38.42 | 793.64
7177 | TIN-INTERP | Interpolated Ground | 45855.77 | -6.45 | 755.66 | 0 | 38.42 | 0 | OK | Ground clear controls. | 102 | 38.42 | 794.08
7178 | TIN-INTERP | Interpolated Ground | 45855.81 | -7.03 | 755.66 | 0 | 26.66 | 0 | OK | Ground clear controls. | 102 | 35.53 | 782.32
7179 | TIN-INTERP | Interpolated Ground | 45856.02 | -8.55 | 755.67 | 0 | 32.3 | 0 | OK | Ground clear controls. | 102 | 35.53 | 787.97
7180 | TIN-INTERP | Interpolated Ground | 45893.81 | 6.3 | 754.73 | 0 | 29.89 | 0 | OK | Ground clear controls. | 102 | 35.53 | 784.62
7181 | TIN-INTERP | Interpolated Ground | 45894.06 | 4.81 | 754.85 | 0 | 24.22 | 0 | OK | Ground clear controls. | 102 | 35.53 | 779.07
7182 | TIN-INTERP | Interpolated Ground | 45894.09 | 4.21 | 754.9 | 0 | 35.53 | 0 | OK | Ground clear controls. | 102 | 35.53 | 790.43
7183 | TIN-INTERP | Interpolated Ground | 45895.77 | -6.2 | 755.55 | 0 | 35.38 | 0 | OK | Ground clear controls. | 102 | 35.38 | 790.93
7184 | TIN-INTERP | Interpolated Ground | 45895.8 | -6.77 | 755.56 | 0 | 23.72 | 0 | OK | Ground clear controls. | 102 | 34.52 | 779.28
7185 | TIN-INTERP | Interpolated Ground | 45896.01 | -8.28 | 755.65 | 0 | 29.24 | 0 | OK | Ground clear controls. | 102 | 34.52 | 784.89
7186 | TIN-INTERP | Interpolated Ground | 45933.81 | 6.34 | 757.33 | 0 | 25.14 | 0 | OK | Ground clear controls. | 102 | 34.52 | 782.47
7187 | TIN-INTERP | Interpolated Ground | 45934.06 | 4.84 | 757.51 | 0 | 19.44 | 0 | OK | Ground clear controls. | 102 | 34.52 | 776.95
7188 | TIN-INTERP | Interpolated Ground | 45934.09 | 4.26 | 757.5 | 0 | 30.7 | 0 | OK | Ground clear controls. | 102 | 34.52 | 788.2
7189 | TIN-INTERP | Interpolated Ground | 45935.77 | -5.95 | 758.1 | 0 | 30.61 | 0 | OK | Ground clear controls. | 102 | 34.52 | 788.71
7190 | TIN-INTERP | Interpolated Ground | 45935.8 | -6.5 | 758.16 | 0 | 19.01 | 0 | OK | Ground clear controls. | 102 | 34.52 | 777.17
7191 | TIN-INTERP | Interpolated Ground | 45936.01 | -8.02 | 758.28 | 0 | 24.47 | 0 | OK | Ground clear controls. | 102 | 34.52 | 782.75
7192 | TIN-INTERP | Interpolated Ground | 45973.81 | 6.38 | 760.91 | 0 | 20.37 | 0 | OK | Ground clear controls. | 102 | 34.52 | 781.28
7193 | TIN-INTERP | Interpolated Ground | 45974.06 | 4.88 | 761.12 | 0 | 14.67 | 0 | OK | Ground clear controls. | 102 | 34.52 | 775.79
7194 | TIN-INTERP | Interpolated Ground | 45974.09 | 4.32 | 761.24 | 0 | 25.71 | 0 | OK | Ground clear controls. | 102 | 34.52 | 786.95
7195 | TIN-INTERP | Interpolated Ground | 45975.77 | -5.69 | 762.95 | 0 | 24.48 | 0 | OK | Ground clear controls. | 102 | 34.52 | 787.43
7196 | TIN-INTERP | Interpolated Ground | 45975.8 | -6.24 | 763 | 0 | 13 | 0 | OK | Ground clear controls. | 102 | 34.52 | 776
7197 | TIN-INTERP | Interpolated Ground | 45976.01 | -7.75 | 763.24 | 0 | 18.32 | 0 | OK | Ground clear controls. | 102 | 34.52 | 781.56
7198 | TIN-INTERP | Interpolated Ground | 46013.81 | 6.42 | 762.84 | 0 | 18.21 | 0 | OK | Ground clear controls. | 102 | 34.52 | 781.05
7199 | TIN-INTERP | Interpolated Ground | 46014.06 | 4.92 | 763 | 0 | 12.58 | 0 | OK | Ground clear controls. | 102 | 34.52 | 775.58
7200 | TIN-INTERP | Interpolated Ground | 46014.09 | 4.37 | 763.09 | 0 | 23.57 | 0 | OK | Ground clear controls. | 102 | 34.52 | 786.66
7201 | TIN-INTERP | Interpolated Ground | 46015.77 | -5.44 | 764.31 | 0 | 22.78 | 0 | OK | Ground clear controls. | 102 | 34.52 | 787.09
7202 | TIN-INTERP | Interpolated Ground | 46015.8 | -5.97 | 764.37 | 0 | 11.4 | 0 | OK | Ground clear controls. | 102 | 34.52 | 775.77
7203 | TIN-INTERP | Interpolated Ground | 46016.01 | -7.48 | 764.54 | 0 | 16.77 | 0 | OK | Ground clear controls. | 102 | 34.52 | 781.31
7204 | TIN-INTERP | Interpolated Ground | 46053.81 | 6.45 | 757.44 | 0 | 24.34 | 0 | OK | Ground clear controls. | 102 | 34.52 | 781.78
7205 | TIN-INTERP | Interpolated Ground | 46054.06 | 4.96 | 757.5 | 0 | 18.81 | 0 | OK | Ground clear controls. | 102 | 34.52 | 776.31
7206 | TIN-INTERP | Interpolated Ground | 46054.09 | 4.42 | 757.55 | 0 | 29.79 | 0 | OK | Ground clear controls. | 102 | 34.52 | 787.34
7207 | TIN-INTERP | Interpolated Ground | 46055.77 | -5.19 | 759.02 | 0 | 28.66 | 0 | OK | Ground clear controls. | 102 | 34.52 | 787.68
7208 | TIN-INTERP | Interpolated Ground | 46055.8 | -5.71 | 759.13 | 0 | 17.36 | 0 | OK | Ground clear controls. | 102 | 34.52 | 776.49
7209 | TIN-INTERP | Interpolated Ground | 46056.01 | -7.21 | 759.39 | 0 | 22.63 | 0 | OK | Ground clear controls. | 102 | 34.52 | 782.02
7210 | TIN-INTERP | Interpolated Ground | 46093.81 | 6.49 | 754.18 | 0 | 29.29 | 0 | OK | Ground clear controls. | 102 | 34.52 | 783.47
7211 | TIN-INTERP | Interpolated Ground | 46094.06 | 4.99 | 754.39 | 0 | 23.6 | 0 | OK | Ground clear controls. | 102 | 34.52 | 777.99
7212 | TIN-INTERP | Interpolated Ground | 46094.09 | 4.48 | 754.48 | 0 | 34.52 | 0 | OK | Ground clear controls. | 102 | 34.52 | 789
7213 | TIN-INTERP | Interpolated Ground | 46095.77 | -4.94 | 756.08 | 0 | 33.14 | 0 | OK | Ground clear controls. | 102 | 33.14 | 789.22
7214 | TIN-INTERP | Interpolated Ground | 46095.8 | -5.44 | 756.16 | 0 | 21.98 | 0 | OK | Ground clear controls. | 102 | 27.25 | 778.14
7215 | TIN-INTERP | Interpolated Ground | 46096.01 | -6.94 | 756.41 | 0 | 27.25 | 0 | OK | Ground clear controls. | 102 | 27.25 | 783.66
7216 | TIN-INTERP | Interpolated Ground | 46122.13 | -6.77 | 753.02 | 0 | 32.22 | 0 | OK | Ground clear controls. | 103 | 37.82 | 785.24
7217 | TIN-INTERP | Interpolated Ground | 46122.16 | -4.77 | 752.96 | 0 | 37.78 | 0 | OK | Ground clear controls. | 103 | 37.82 | 790.74
7218 | TIN-INTERP | Interpolated Ground | 46122.16 | 6.52 | 752.94 | 0 | 32.31 | 0 | OK | Ground clear controls. | 103 | 37.82 | 785.25
7219 | TIN-INTERP | Interpolated Ground | 46122.17 | -5.27 | 753.01 | 0 | 26.73 | 0 | OK | Ground clear controls. | 103 | 37.82 | 779.74
7220 | TIN-INTERP | Interpolated Ground | 46122.17 | 5.02 | 752.93 | 0 | 26.81 | 0 | OK | Ground clear controls. | 103 | 37.82 | 779.74
7221 | TIN-INTERP | Interpolated Ground | 46122.19 | 4.52 | 752.92 | 0 | 37.82 | 0 | OK | Ground clear controls. | 103 | 37.82 | 790.74
7222 | TIN-INTERP | Interpolated Ground | 46162.13 | -6.78 | 753.02 | 0 | 27.5 | 0 | OK | Ground clear controls. | 103 | 33.06 | 780.52
7223 | TIN-INTERP | Interpolated Ground | 46162.16 | -4.79 | 753.03 | 0 | 33.06 | 0 | OK | Ground clear controls. | 103 | 33.06 | 786.09
7224 | TIN-INTERP | Interpolated Ground | 46162.16 | 6.55 | 752.94 | 0 | 27.51 | 0 | OK | Ground clear controls. | 103 | 32.99 | 780.45
7225 | TIN-INTERP | Interpolated Ground | 46162.17 | -5.28 | 753.03 | 0 | 22.02 | 0 | OK | Ground clear controls. | 103 | 32.99 | 775.05
7226 | TIN-INTERP | Interpolated Ground | 46162.17 | 5.05 | 752.95 | 0 | 22.06 | 0 | OK | Ground clear controls. | 103 | 32.99 | 775.01
7227 | TIN-INTERP | Interpolated Ground | 46162.19 | 4.56 | 752.95 | 0 | 32.99 | 0 | OK | Ground clear controls. | 103 | 32.99 | 785.94
7228 | TIN-INTERP | Interpolated Ground | 46202.13 | -6.79 | 753.09 | 0 | 23.65 | 0 | OK | Ground clear controls. | 103 | 29.79 | 776.74
7229 | TIN-INTERP | Interpolated Ground | 46202.16 | -4.81 | 753.11 | 0 | 29.27 | 0 | OK | Ground clear controls. | 103 | 29.79 | 782.38
7230 | TIN-INTERP | Interpolated Ground | 46202.16 | 6.59 | 753.02 | 0 | 23.62 | 0 | OK | Ground clear controls. | 103 | 29.79 | 776.64
7231 | TIN-INTERP | Interpolated Ground | 46202.17 | -5.29 | 753.12 | 0 | 18.2 | 0 | OK | Ground clear controls. | 103 | 29.79 | 771.32
7232 | TIN-INTERP | Interpolated Ground | 46202.17 | 5.09 | 752.99 | 0 | 18.24 | 0 | OK | Ground clear controls. | 103 | 29.79 | 771.23
7233 | TIN-INTERP | Interpolated Ground | 46202.19 | 4.6 | 753 | 0 | 29.11 | 0 | OK | Ground clear controls. | 103 | 29.79 | 782.11
7234 | TIN-INTERP | Interpolated Ground | 46242.13 | -6.8 | 753.28 | 0 | 20.65 | 0 | OK | Ground clear controls. | 103 | 29.79 | 773.93
7235 | TIN-INTERP | Interpolated Ground | 46242.16 | -4.83 | 753.29 | 0 | 26.33 | 0 | OK | Ground clear controls. | 103 | 29.79 | 779.62
7236 | TIN-INTERP | Interpolated Ground | 46242.16 | 6.62 | 753.33 | 0 | 20.47 | 0 | OK | Ground clear controls. | 103 | 29.79 | 773.8
7237 | TIN-INTERP | Interpolated Ground | 46242.17 | -5.3 | 753.3 | 0 | 15.23 | 0 | OK | Ground clear controls. | 103 | 29.79 | 768.53
7238 | TIN-INTERP | Interpolated Ground | 46242.17 | 5.12 | 753.31 | 0 | 15.11 | 0 | OK | Ground clear controls. | 103 | 29.79 | 768.42
7239 | TIN-INTERP | Interpolated Ground | 46242.19 | 4.65 | 753.3 | 0 | 25.95 | 0 | OK | Ground clear controls. | 103 | 29.79 | 779.25
7240 | TIN-INTERP | Interpolated Ground | 46282.13 | -6.81 | 753.51 | 0 | 18.57 | 0 | OK | Ground clear controls. | 103 | 29.79 | 772.08
7241 | TIN-INTERP | Interpolated Ground | 46282.16 | -4.85 | 753.49 | 0 | 24.33 | 0 | OK | Ground clear controls. | 103 | 29.79 | 777.82
7242 | TIN-INTERP | Interpolated Ground | 46282.16 | 6.65 | 753.44 | 0 | 18.48 | 0 | OK | Ground clear controls. | 103 | 29.79 | 771.92
7243 | TIN-INTERP | Interpolated Ground | 46282.17 | -5.31 | 753.51 | 0 | 13.18 | 0 | OK | Ground clear controls. | 103 | 29.79 | 766.69
7244 | TIN-INTERP | Interpolated Ground | 46282.17 | 5.15 | 753.46 | 0 | 13.1 | 0 | OK | Ground clear controls. | 103 | 29.79 | 766.56
7245 | TIN-INTERP | Interpolated Ground | 46282.19 | 4.69 | 753.46 | 0 | 23.93 | 0 | OK | Ground clear controls. | 103 | 29.79 | 777.39
7246 | TIN-INTERP | Interpolated Ground | 46322.13 | -6.82 | 753.48 | 0 | 17.7 | 0 | OK | Ground clear controls. | 103 | 29.79 | 771.18
7247 | TIN-INTERP | Interpolated Ground | 46322.16 | -4.87 | 753.48 | 0 | 23.48 | 0 | OK | Ground clear controls. | 103 | 29.79 | 776.96
7248 | TIN-INTERP | Interpolated Ground | 46322.16 | 6.69 | 753.37 | 0 | 17.64 | 0 | OK | Ground clear controls. | 103 | 29.79 | 771.01
7249 | TIN-INTERP | Interpolated Ground | 46322.17 | -5.32 | 753.5 | 0 | 12.3 | 0 | OK | Ground clear controls. | 103 | 29.79 | 765.8
7250 | TIN-INTERP | Interpolated Ground | 46322.17 | 5.19 | 753.37 | 0 | 12.3 | 0 | OK | Ground clear controls. | 103 | 29.79 | 765.67
7251 | TIN-INTERP | Interpolated Ground | 46322.19 | 4.73 | 753.36 | 0 | 23.15 | 0 | OK | Ground clear controls. | 103 | 29.79 | 776.51
7252 | TIN-INTERP | Interpolated Ground | 46362.13 | -6.84 | 753.86 | 0 | 17.38 | 0 | OK | Ground clear controls. | 103 | 29.79 | 771.24
7253 | TIN-INTERP | Interpolated Ground | 46362.16 | -4.89 | 753.94 | 0 | 23.11 | 0 | OK | Ground clear controls. | 103 | 29.79 | 777.05
7254 | TIN-INTERP | Interpolated Ground | 46362.16 | 6.72 | 754.17 | 0 | 16.91 | 0 | OK | Ground clear controls. | 103 | 29.79 | 771.08
7255 | TIN-INTERP | Interpolated Ground | 46362.17 | -5.34 | 753.91 | 0 | 11.95 | 0 | OK | Ground clear controls. | 103 | 29.79 | 765.86
7256 | TIN-INTERP | Interpolated Ground | 46362.17 | 5.22 | 754.23 | 0 | 11.49 | 0 | OK | Ground clear controls. | 103 | 29.79 | 765.72
7257 | TIN-INTERP | Interpolated Ground | 46362.19 | 4.78 | 754.26 | 0 | 22.34 | 0 | OK | Ground clear controls. | 103 | 29.79 | 776.6
7258 | TIN-INTERP | Interpolated Ground | 46402.13 | -6.85 | 753.97 | 0 | 18.29 | 0 | OK | Ground clear controls. | 103 | 29.79 | 772.26
7259 | TIN-INTERP | Interpolated Ground | 46402.16 | -4.91 | 753.99 | 0 | 24.09 | 0 | OK | Ground clear controls. | 103 | 29.79 | 778.08
7260 | TIN-INTERP | Interpolated Ground | 46402.16 | 6.76 | 753.94 | 0 | 18.16 | 0 | OK | Ground clear controls. | 103 | 29.79 | 772.1
7261 | TIN-INTERP | Interpolated Ground | 46402.17 | -5.35 | 753.99 | 0 | 12.87 | 0 | OK | Ground clear controls. | 103 | 29.79 | 766.86
7262 | TIN-INTERP | Interpolated Ground | 46402.17 | 5.26 | 753.97 | 0 | 12.77 | 0 | OK | Ground clear controls. | 103 | 29.79 | 766.74
7263 | TIN-INTERP | Interpolated Ground | 46402.19 | 4.82 | 753.97 | 0 | 23.7 | 0 | OK | Ground clear controls. | 103 | 29.79 | 777.67
7264 | TIN-INTERP | Interpolated Ground | 46442.13 | -6.86 | 754.53 | 0 | 19.7 | 0 | OK | Ground clear controls. | 103 | 29.79 | 774.23
7265 | TIN-INTERP | Interpolated Ground | 46442.16 | -4.93 | 754.54 | 0 | 25.52 | 0 | OK | Ground clear controls. | 103 | 29.79 | 780.06
7266 | TIN-INTERP | Interpolated Ground | 46442.16 | 6.79 | 754.49 | 0 | 19.61 | 0 | OK | Ground clear controls. | 103 | 29.79 | 774.1
7267 | TIN-INTERP | Interpolated Ground | 46442.17 | -5.36 | 754.55 | 0 | 14.27 | 0 | OK | Ground clear controls. | 103 | 29.79 | 768.82
7268 | TIN-INTERP | Interpolated Ground | 46442.17 | 5.29 | 754.48 | 0 | 14.23 | 0 | OK | Ground clear controls. | 103 | 29.79 | 768.71
7269 | TIN-INTERP | Interpolated Ground | 46442.19 | 4.86 | 754.47 | 0 | 25.26 | 0 | OK | Ground clear controls. | 103 | 29.79 | 779.73
7270 | TIN-INTERP | Interpolated Ground | 46482.13 | -6.87 | 755.72 | 0 | 21.44 | 0 | OK | Ground clear controls. | 103 | 29.79 | 777.16
7271 | TIN-INTERP | Interpolated Ground | 46482.16 | -4.95 | 755.88 | 0 | 27.11 | 0 | OK | Ground clear controls. | 103 | 29.79 | 782.99
7272 | TIN-INTERP | Interpolated Ground | 46482.16 | 6.83 | 755.47 | 0 | 21.6 | 0 | OK | Ground clear controls. | 103 | 29.79 | 777.07
7273 | TIN-INTERP | Interpolated Ground | 46482.17 | -5.37 | 755.89 | 0 | 15.83 | 0 | OK | Ground clear controls. | 103 | 29.79 | 771.72
7274 | TIN-INTERP | Interpolated Ground | 46482.17 | 5.32 | 755.4 | 0 | 16.24 | 0 | OK | Ground clear controls. | 103 | 29.79 | 771.64
7275 | TIN-INTERP | Interpolated Ground | 46482.19 | 4.91 | 755.39 | 0 | 27.37 | 0 | OK | Ground clear controls. | 103 | 29.79 | 782.76
7276 | TIN-INTERP | Interpolated Ground | 46522.13 | -6.88 | 757.45 | 0 | 23.6 | 0 | OK | Ground clear controls. | 103 | 29.79 | 781.05
7277 | TIN-INTERP | Interpolated Ground | 46522.16 | -4.97 | 757.4 | 0 | 29.48 | 0 | OK | Ground clear controls. | 103 | 29.79 | 786.88
7278 | TIN-INTERP | Interpolated Ground | 46522.16 | 6.86 | 756.9 | 0 | 24.12 | 0 | OK | Ground clear controls. | 103 | 29.79 | 781.02
7279 | TIN-INTERP | Interpolated Ground | 46522.17 | -5.38 | 757.4 | 0 | 18.18 | 0 | OK | Ground clear controls. | 103 | 29.79 | 775.58
7280 | TIN-INTERP | Interpolated Ground | 46522.17 | 5.36 | 756.97 | 0 | 18.57 | 0 | OK | Ground clear controls. | 103 | 29.79 | 775.54
7281 | TIN-INTERP | Interpolated Ground | 46522.19 | 4.95 | 756.98 | 0 | 29.79 | 0 | OK | Ground clear controls. | 103 | 29.79 | 786.77
7282 | TIN-INTERP | Interpolated Ground | 46545.15 | -4.98 | 757.56 | 0 | 31.97 | 0 | OK | Ground clear controls. | 104 | 40.56 | 789.53
7283 | TIN-INTERP | Interpolated Ground | 46545.22 | 4.97 | 757.81 | 0 | 31.72 | 0 | OK | Ground clear controls. | 104 | 40.56 | 789.53
7284 | TIN-INTERP | Interpolated Ground | 46545.22 | -6.89 | 757.65 | 0 | 26.08 | 0 | OK | Ground clear controls. | 104 | 40.56 | 783.73
7285 | TIN-INTERP | Interpolated Ground | 46545.23 | -5.39 | 757.61 | 0 | 20.62 | 0 | OK | Ground clear controls. | 104 | 40.56 | 778.23
7286 | TIN-INTERP | Interpolated Ground | 46545.24 | 6.88 | 757.75 | 0 | 25.98 | 0 | OK | Ground clear controls. | 104 | 40.56 | 783.73
7287 | TIN-INTERP | Interpolated Ground | 46545.31 | 5.38 | 757.81 | 0 | 20.43 | 0 | OK | Ground clear controls. | 104 | 40.56 | 778.24
7288 | TIN-INTERP | Interpolated Ground | 46585.15 | -4.95 | 761.46 | 0 | 26.98 | 0 | OK | Ground clear controls. | 104 | 40.56 | 788.44
7289 | TIN-INTERP | Interpolated Ground | 46585.22 | 4.94 | 760.74 | 0 | 27.56 | 0 | OK | Ground clear controls. | 104 | 40.56 | 788.3
7290 | TIN-INTERP | Interpolated Ground | 46585.22 | -6.86 | 761.6 | 0 | 21.05 | 0 | OK | Ground clear controls. | 104 | 40.56 | 782.65
7291 | TIN-INTERP | Interpolated Ground | 46585.23 | -5.36 | 761.5 | 0 | 15.69 | 0 | OK | Ground clear controls. | 104 | 40.56 | 777.19
7292 | TIN-INTERP | Interpolated Ground | 46585.24 | 6.85 | 760.62 | 0 | 21.97 | 0 | OK | Ground clear controls. | 104 | 40.56 | 782.59
7293 | TIN-INTERP | Interpolated Ground | 46585.31 | 5.35 | 760.72 | 0 | 16.45 | 0 | OK | Ground clear controls. | 104 | 40.56 | 777.17
7294 | TIN-INTERP | Interpolated Ground | 46625.15 | -4.92 | 760.56 | 0 | 27.74 | 0 | OK | Ground clear controls. | 104 | 40.56 | 788.3
7295 | TIN-INTERP | Interpolated Ground | 46625.22 | 4.9 | 759.46 | 0 | 28.58 | 0 | OK | Ground clear controls. | 104 | 40.56 | 788.04
7296 | TIN-INTERP | Interpolated Ground | 46625.22 | -6.84 | 760.78 | 0 | 21.73 | 0 | OK | Ground clear controls. | 104 | 40.56 | 782.51
7297 | TIN-INTERP | Interpolated Ground | 46625.23 | -5.34 | 760.63 | 0 | 16.45 | 0 | OK | Ground clear controls. | 104 | 40.56 | 777.08
7298 | TIN-INTERP | Interpolated Ground | 46625.24 | 6.83 | 759.21 | 0 | 23.2 | 0 | OK | Ground clear controls. | 104 | 40.56 | 782.41
7299 | TIN-INTERP | Interpolated Ground | 46625.31 | 5.33 | 759.4 | 0 | 17.65 | 0 | OK | Ground clear controls. | 104 | 40.56 | 777.05
7300 | TIN-INTERP | Interpolated Ground | 46665.15 | -4.89 | 764.71 | 0 | 24.4 | 0 | OK | Ground clear controls. | 104 | 40.56 | 789.11
7301 | TIN-INTERP | Interpolated Ground | 46665.22 | 4.87 | 764.16 | 0 | 24.6 | 0 | OK | Ground clear controls. | 104 | 40.56 | 788.76
7302 | TIN-INTERP | Interpolated Ground | 46665.22 | -6.82 | 764.75 | 0 | 18.58 | 0 | OK | Ground clear controls. | 104 | 40.56 | 783.33
7303 | TIN-INTERP | Interpolated Ground | 46665.23 | -5.32 | 764.74 | 0 | 13.19 | 0 | OK | Ground clear controls. | 104 | 40.56 | 777.93
7304 | TIN-INTERP | Interpolated Ground | 46665.24 | 6.8 | 764.02 | 0 | 19.17 | 0 | OK | Ground clear controls. | 104 | 40.56 | 783.19
7305 | TIN-INTERP | Interpolated Ground | 46665.31 | 5.3 | 764.13 | 0 | 13.76 | 0 | OK | Ground clear controls. | 104 | 40.56 | 777.89
7306 | TIN-INTERP | Interpolated Ground | 46705.15 | -4.86 | 756.45 | 0 | 34.41 | 0 | OK | Ground clear controls. | 104 | 40.56 | 790.86
7307 | TIN-INTERP | Interpolated Ground | 46705.22 | 4.84 | 753.34 | 0 | 37.11 | 0 | OK | Ground clear controls. | 104 | 40.56 | 790.45
7308 | TIN-INTERP | Interpolated Ground | 46705.22 | -6.79 | 756.61 | 0 | 28.49 | 0 | OK | Ground clear controls. | 104 | 40.56 | 785.1
7309 | TIN-INTERP | Interpolated Ground | 46705.23 | -5.29 | 756.44 | 0 | 23.29 | 0 | OK | Ground clear controls. | 104 | 40.56 | 779.73
7310 | TIN-INTERP | Interpolated Ground | 46705.24 | 6.77 | 752.24 | 0 | 32.7 | 0 | OK | Ground clear controls. | 104 | 40.56 | 784.94
7311 | TIN-INTERP | Interpolated Ground | 46705.31 | 5.27 | 753.08 | 0 | 26.59 | 0 | OK | Ground clear controls. | 104 | 40.56 | 779.67
7312 | TIN-INTERP | Interpolated Ground | 46745.15 | -4.82 | 758.52 | 0 | 35.05 | 0 | OK | Ground clear controls. | 104 | 40.56 | 793.57
7313 | TIN-INTERP | Interpolated Ground | 46745.22 | 4.8 | 758.33 | 0 | 34.8 | 0 | OK | Ground clear controls. | 104 | 40.56 | 793.13
7314 | TIN-INTERP | Interpolated Ground | 46745.22 | -6.77 | 758.53 | 0 | 29.29 | 0 | OK | Ground clear controls. | 104 | 40.56 | 787.82
7315 | TIN-INTERP | Interpolated Ground | 46745.23 | -5.27 | 758.53 | 0 | 23.93 | 0 | OK | Ground clear controls. | 104 | 40.56 | 782.46
7316 | TIN-INTERP | Interpolated Ground | 46745.24 | 6.75 | 758.28 | 0 | 29.37 | 0 | OK | Ground clear controls. | 104 | 40.56 | 787.65
7317 | TIN-INTERP | Interpolated Ground | 46745.31 | 5.25 | 758.32 | 0 | 24.09 | 0 | OK | Ground clear controls. | 104 | 40.56 | 782.41
7318 | TIN-INTERP | Interpolated Ground | 46785.15 | -4.79 | 761.21 | 0 | 36.01 | 0 | OK | Ground clear controls. | 104 | 40.56 | 797.22
7319 | TIN-INTERP | Interpolated Ground | 46785.22 | 4.77 | 761.02 | 0 | 35.76 | 0 | OK | Ground clear controls. | 104 | 40.56 | 796.78
7320 | TIN-INTERP | Interpolated Ground | 46785.22 | -6.75 | 761.22 | 0 | 30.28 | 0 | OK | Ground clear controls. | 104 | 40.56 | 791.5
7321 | TIN-INTERP | Interpolated Ground | 46785.23 | -5.25 | 761.26 | 0 | 24.88 | 0 | OK | Ground clear controls. | 104 | 40.56 | 786.14
7322 | TIN-INTERP | Interpolated Ground | 46785.24 | 6.72 | 760.72 | 0 | 30.61 | 0 | OK | Ground clear controls. | 104 | 40.56 | 791.33
7323 | TIN-INTERP | Interpolated Ground | 46785.31 | 5.22 | 761.03 | 0 | 25.05 | 0 | OK | Ground clear controls. | 104 | 40.56 | 786.08
7324 | TIN-INTERP | Interpolated Ground | 46825.15 | -4.76 | 773.83 | 0 | 28 | 0 | OK | Ground clear controls. | 104 | 40.56 | 801.83
7325 | TIN-INTERP | Interpolated Ground | 46825.22 | 4.73 | 772.05 | 0 | 29.36 | 0 | OK | Ground clear controls. | 104 | 40.56 | 801.41
7326 | TIN-INTERP | Interpolated Ground | 46825.22 | -6.73 | 773.97 | 0 | 22.18 | 0 | OK | Ground clear controls. | 104 | 40.56 | 796.15
7327 | TIN-INTERP | Interpolated Ground | 46825.23 | -5.23 | 773.87 | 0 | 16.91 | 0 | OK | Ground clear controls. | 104 | 40.56 | 790.78
7328 | TIN-INTERP | Interpolated Ground | 46825.24 | 6.7 | 771.43 | 0 | 24.55 | 0 | OK | Ground clear controls. | 104 | 40.56 | 795.98
7329 | TIN-INTERP | Interpolated Ground | 46825.31 | 5.2 | 771.9 | 0 | 18.83 | 0 | OK | Ground clear controls. | 104 | 40.56 | 790.73
7330 | TIN-INTERP | Interpolated Ground | 46865.15 | -4.73 | 778.9 | 0 | 28.49 | 0 | OK | Ground clear controls. | 104 | 40.56 | 807.39
7331 | TIN-INTERP | Interpolated Ground | 46865.22 | 4.7 | 775.46 | 0 | 31.57 | 0 | OK | Ground clear controls. | 104 | 40.56 | 807.03
7332 | TIN-INTERP | Interpolated Ground | 46865.22 | -6.7 | 779.41 | 0 | 22.35 | 0 | OK | Ground clear controls. | 104 | 40.56 | 801.76
7333 | TIN-INTERP | Interpolated Ground | 46865.23 | -5.2 | 779.06 | 0 | 17.31 | 0 | OK | Ground clear controls. | 104 | 40.56 | 796.37
7334 | TIN-INTERP | Interpolated Ground | 46865.24 | 6.67 | 774.63 | 0 | 26.98 | 0 | OK | Ground clear controls. | 104 | 40.56 | 801.61
7335 | TIN-INTERP | Interpolated Ground | 46865.31 | 5.17 | 775.24 | 0 | 21.09 | 0 | OK | Ground clear controls. | 104 | 40.56 | 796.33
7336 | TIN-INTERP | Interpolated Ground | 46905.15 | -4.7 | 784.63 | 0 | 29.28 | 0 | OK | Ground clear controls. | 104 | 40.56 | 813.91
7337 | TIN-INTERP | Interpolated Ground | 46905.22 | 4.66 | 783.5 | 0 | 30.14 | 0 | OK | Ground clear controls. | 104 | 40.56 | 813.64
7338 | TIN-INTERP | Interpolated Ground | 46905.22 | -6.68 | 784.78 | 0 | 23.54 | 0 | OK | Ground clear controls. | 104 | 40.56 | 808.32
7339 | TIN-INTERP | Interpolated Ground | 46905.23 | -5.18 | 784.7 | 0 | 18.21 | 0 | OK | Ground clear controls. | 104 | 40.56 | 802.91
7340 | TIN-INTERP | Interpolated Ground | 46905.24 | 6.64 | 782.99 | 0 | 25.22 | 0 | OK | Ground clear controls. | 104 | 40.56 | 808.21
7341 | TIN-INTERP | Interpolated Ground | 46905.31 | 5.14 | 783.39 | 0 | 19.5 | 0 | OK | Ground clear controls. | 104 | 40.56 | 802.89
7342 | TIN-INTERP | Interpolated Ground | 46945.15 | -4.67 | 788.59 | 0 | 32.81 | 0 | OK | Ground clear controls. | 104 | 40.56 | 821.4
7343 | TIN-INTERP | Interpolated Ground | 46945.22 | 4.63 | 788.06 | 0 | 33.17 | 0 | OK | Ground clear controls. | 104 | 40.56 | 821.23
7344 | TIN-INTERP | Interpolated Ground | 46945.22 | -6.66 | 788.58 | 0 | 27.28 | 0 | OK | Ground clear controls. | 104 | 40.56 | 815.86
7345 | TIN-INTERP | Interpolated Ground | 46945.23 | -5.16 | 788.6 | 0 | 21.82 | 0 | OK | Ground clear controls. | 104 | 40.56 | 810.42
7346 | TIN-INTERP | Interpolated Ground | 46945.24 | 6.62 | 787.68 | 0 | 28.11 | 0 | OK | Ground clear controls. | 104 | 40.56 | 815.79
7347 | TIN-INTERP | Interpolated Ground | 46945.31 | 5.12 | 788 | 0 | 22.4 | 0 | OK | Ground clear controls. | 104 | 40.56 | 810.4
7348 | TIN-INTERP | Interpolated Ground | 46985.15 | -4.64 | 789.3 | 0 | 40.56 | 0 | OK | Ground clear controls. | 104 | 40.56 | 829.86
7349 | TIN-INTERP | Interpolated Ground | 46985.22 | 4.6 | 790.09 | 0 | 39.73 | 0 | OK | Ground clear controls. | 104 | 39.73 | 829.82
7350 | TIN-INTERP | Interpolated Ground | 46985.22 | -6.63 | 788.89 | 0 | 35.48 | 0 | OK | Ground clear controls. | 104 | 35.48 | 824.37
7351 | TIN-INTERP | Interpolated Ground | 46985.23 | -5.13 | 789.21 | 0 | 29.67 | 0 | OK | Ground clear controls. | 104 | 34.25 | 818.88
7352 | TIN-INTERP | Interpolated Ground | 46985.24 | 6.59 | 790.1 | 0 | 34.25 | 0 | OK | Ground clear controls. | 104 | 34.25 | 824.35
7353 | TIN-INTERP | Interpolated Ground | 46985.31 | 5.09 | 790.1 | 0 | 28.79 | 0 | OK | Ground clear controls. | 104 | 28.79 | 818.89
7354 | TIN-INTERP | Interpolated Ground | 46999.45 | 6.58 | 790.63 | 0 | 37 | 0 | OK | Ground clear controls. | 105 | 44.85 | 827.63
7355 | TIN-INTERP | Interpolated Ground | 46999.46 | -6.63 | 789.01 | 0 | 38.62 | 0 | OK | Ground clear controls. | 105 | 44.85 | 827.63
7356 | TIN-INTERP | Interpolated Ground | 46999.48 | -5.13 | 789.14 | 0 | 32.99 | 0 | OK | Ground clear controls. | 105 | 44.85 | 822.13
7357 | TIN-INTERP | Interpolated Ground | 46999.51 | 5.08 | 790.5 | 0 | 31.63 | 0 | OK | Ground clear controls. | 105 | 44.85 | 822.13
7358 | TIN-INTERP | Interpolated Ground | 46999.52 | 4.58 | 790.45 | 0 | 42.68 | 0 | OK | Ground clear controls. | 105 | 44.85 | 833.13
7359 | TIN-INTERP | Interpolated Ground | 46999.54 | -4.63 | 789.17 | 0 | 43.96 | 0 | OK | Ground clear controls. | 105 | 44.85 | 833.13
7360 | TIN-INTERP | Interpolated Ground | 47039.45 | 6.58 | 786.73 | 0 | 35.7 | 0 | OK | Ground clear controls. | 105 | 44.85 | 822.43
7361 | TIN-INTERP | Interpolated Ground | 47039.46 | -6.62 | 784.11 | 0 | 38.41 | 0 | OK | Ground clear controls. | 105 | 44.85 | 822.52
7362 | TIN-INTERP | Interpolated Ground | 47039.48 | -5.12 | 784.35 | 0 | 32.75 | 0 | OK | Ground clear controls. | 105 | 44.85 | 817.1
7363 | TIN-INTERP | Interpolated Ground | 47039.51 | 5.08 | 786.57 | 0 | 30.53 | 0 | OK | Ground clear controls. | 105 | 44.85 | 817.1
7364 | TIN-INTERP | Interpolated Ground | 47039.52 | 4.58 | 786.49 | 0 | 41.43 | 0 | OK | Ground clear controls. | 105 | 44.85 | 827.92
7365 | TIN-INTERP | Interpolated Ground | 47039.54 | -4.63 | 784.39 | 0 | 43.74 | 0 | OK | Ground clear controls. | 105 | 44.85 | 828.13
7366 | TIN-INTERP | Interpolated Ground | 47079.45 | 6.58 | 789 | 0 | 29.2 | 0 | OK | Ground clear controls. | 105 | 44.85 | 818.2
7367 | TIN-INTERP | Interpolated Ground | 47079.46 | -6.62 | 786.25 | 0 | 32.1 | 0 | OK | Ground clear controls. | 105 | 44.85 | 818.35
7368 | TIN-INTERP | Interpolated Ground | 47079.48 | -5.12 | 786.54 | 0 | 26.47 | 0 | OK | Ground clear controls. | 105 | 44.85 | 813.01
7369 | TIN-INTERP | Interpolated Ground | 47079.51 | 5.08 | 788.72 | 0 | 24.29 | 0 | OK | Ground clear controls. | 105 | 44.85 | 813.01
7370 | TIN-INTERP | Interpolated Ground | 47079.52 | 4.59 | 788.63 | 0 | 35.04 | 0 | OK | Ground clear controls. | 105 | 44.85 | 823.67
7371 | TIN-INTERP | Interpolated Ground | 47079.54 | -4.62 | 786.65 | 0 | 37.42 | 0 | OK | Ground clear controls. | 105 | 44.85 | 824.07
7372 | TIN-INTERP | Interpolated Ground | 47119.45 | 6.59 | 788.03 | 0 | 26.91 | 0 | OK | Ground clear controls. | 105 | 44.85 | 814.94
7373 | TIN-INTERP | Interpolated Ground | 47119.46 | -6.62 | 785.32 | 0 | 29.82 | 0 | OK | Ground clear controls. | 105 | 44.85 | 815.14
7374 | TIN-INTERP | Interpolated Ground | 47119.48 | -5.12 | 785.69 | 0 | 24.17 | 0 | OK | Ground clear controls. | 105 | 44.85 | 809.86
7375 | TIN-INTERP | Interpolated Ground | 47119.51 | 5.09 | 787.7 | 0 | 22.17 | 0 | OK | Ground clear controls. | 105 | 44.85 | 809.87
7376 | TIN-INTERP | Interpolated Ground | 47119.52 | 4.59 | 787.58 | 0 | 32.82 | 0 | OK | Ground clear controls. | 105 | 44.85 | 820.4
7377 | TIN-INTERP | Interpolated Ground | 47119.54 | -4.62 | 785.81 | 0 | 35.12 | 0 | OK | Ground clear controls. | 105 | 44.85 | 820.93
7378 | TIN-INTERP | Interpolated Ground | 47159.45 | 6.59 | 788.47 | 0 | 24.16 | 0 | OK | Ground clear controls. | 105 | 44.85 | 812.63
7379 | TIN-INTERP | Interpolated Ground | 47159.46 | -6.62 | 785.84 | 0 | 27.04 | 0 | OK | Ground clear controls. | 105 | 44.85 | 812.88
7380 | TIN-INTERP | Interpolated Ground | 47159.48 | -5.12 | 786.2 | 0 | 21.45 | 0 | OK | Ground clear controls. | 105 | 44.85 | 807.65
7381 | TIN-INTERP | Interpolated Ground | 47159.51 | 5.09 | 788.14 | 0 | 19.52 | 0 | OK | Ground clear controls. | 105 | 44.85 | 807.66
7382 | TIN-INTERP | Interpolated Ground | 47159.52 | 4.59 | 788 | 0 | 30.08 | 0 | OK | Ground clear controls. | 105 | 44.85 | 818.08
7383 | TIN-INTERP | Interpolated Ground | 47159.54 | -4.62 | 786.34 | 0 | 32.4 | 0 | OK | Ground clear controls. | 105 | 44.85 | 818.74
7384 | TIN-INTERP | Interpolated Ground | 47199.45 | 6.59 | 781.08 | 0 | 30.21 | 0 | OK | Ground clear controls. | 105 | 44.85 | 811.29
7385 | TIN-INTERP | Interpolated Ground | 47199.46 | -6.62 | 777.36 | 0 | 34.22 | 0 | OK | Ground clear controls. | 105 | 44.85 | 811.58
7386 | TIN-INTERP | Interpolated Ground | 47199.48 | -5.12 | 777.61 | 0 | 28.76 | 0 | OK | Ground clear controls. | 105 | 44.85 | 806.37
7387 | TIN-INTERP | Interpolated Ground | 47199.51 | 5.09 | 780.71 | 0 | 25.68 | 0 | OK | Ground clear controls. | 105 | 44.85 | 806.39
7388 | TIN-INTERP | Interpolated Ground | 47199.52 | 4.59 | 780.51 | 0 | 36.23 | 0 | OK | Ground clear controls. | 105 | 44.85 | 816.74
7389 | TIN-INTERP | Interpolated Ground | 47199.54 | -4.62 | 777.83 | 0 | 39.65 | 0 | OK | Ground clear controls. | 105 | 44.85 | 817.48
7390 | TIN-INTERP | Interpolated Ground | 47239.45 | 6.59 | 785.69 | 0 | 25.21 | 0 | OK | Ground clear controls. | 105 | 44.85 | 810.9
7391 | TIN-INTERP | Interpolated Ground | 47239.46 | -6.61 | 781.05 | 0 | 30.17 | 0 | OK | Ground clear controls. | 105 | 44.85 | 811.22
7392 | TIN-INTERP | Interpolated Ground | 47239.48 | -5.11 | 781.53 | 0 | 24.51 | 0 | OK | Ground clear controls. | 105 | 44.85 | 806.04
7393 | TIN-INTERP | Interpolated Ground | 47239.51 | 5.09 | 784.92 | 0 | 21.14 | 0 | OK | Ground clear controls. | 105 | 44.85 | 806.06
7394 | TIN-INTERP | Interpolated Ground | 47239.52 | 4.59 | 784.69 | 0 | 31.65 | 0 | OK | Ground clear controls. | 105 | 44.85 | 816.34
7395 | TIN-INTERP | Interpolated Ground | 47239.54 | -4.62 | 781.7 | 0 | 35.45 | 0 | OK | Ground clear controls. | 105 | 44.85 | 817.15
7396 | TIN-INTERP | Interpolated Ground | 47279.45 | 6.59 | 785.45 | 0 | 26.03 | 0 | OK | Ground clear controls. | 105 | 44.85 | 811.48
7397 | TIN-INTERP | Interpolated Ground | 47279.46 | -6.61 | 783.78 | 0 | 28.03 | 0 | OK | Ground clear controls. | 105 | 44.85 | 811.81
7398 | TIN-INTERP | Interpolated Ground | 47279.48 | -5.11 | 784.06 | 0 | 22.58 | 0 | OK | Ground clear controls. | 105 | 44.85 | 806.64
7399 | TIN-INTERP | Interpolated Ground | 47279.51 | 5.09 | 785.54 | 0 | 21.12 | 0 | OK | Ground clear controls. | 105 | 44.85 | 806.66
7400 | TIN-INTERP | Interpolated Ground | 47279.52 | 4.59 | 785.57 | 0 | 31.36 | 0 | OK | Ground clear controls. | 105 | 44.85 | 816.93
7401 | TIN-INTERP | Interpolated Ground | 47279.54 | -4.61 | 784.15 | 0 | 33.61 | 0 | OK | Ground clear controls. | 105 | 44.85 | 817.76
7402 | TIN-INTERP | Interpolated Ground | 47319.45 | 6.59 | 791.52 | 0 | 21.5 | 0 | OK | Ground clear controls. | 105 | 44.85 | 813.02
7403 | TIN-INTERP | Interpolated Ground | 47319.46 | -6.61 | 787.82 | 0 | 25.54 | 0 | OK | Ground clear controls. | 105 | 44.85 | 813.36
7404 | TIN-INTERP | Interpolated Ground | 47319.48 | -5.11 | 788.5 | 0 | 19.69 | 0 | OK | Ground clear controls. | 105 | 44.85 | 808.19
7405 | TIN-INTERP | Interpolated Ground | 47319.51 | 5.09 | 790.92 | 0 | 17.29 | 0 | OK | Ground clear controls. | 105 | 44.85 | 808.21
7406 | TIN-INTERP | Interpolated Ground | 47319.52 | 4.59 | 790.74 | 0 | 27.73 | 0 | OK | Ground clear controls. | 105 | 44.85 | 818.47
7407 | TIN-INTERP | Interpolated Ground | 47319.54 | -4.61 | 788.74 | 0 | 30.57 | 0 | OK | Ground clear controls. | 105 | 44.85 | 819.31
7408 | TIN-INTERP | Interpolated Ground | 47359.45 | 6.59 | 792.97 | 0 | 22.56 | 0 | OK | Ground clear controls. | 105 | 44.85 | 815.53
7409 | TIN-INTERP | Interpolated Ground | 47359.46 | -6.61 | 789.31 | 0 | 26.54 | 0 | OK | Ground clear controls. | 105 | 44.85 | 815.85
7410 | TIN-INTERP | Interpolated Ground | 47359.48 | -5.11 | 789.73 | 0 | 20.95 | 0 | OK | Ground clear controls. | 105 | 44.85 | 810.68
7411 | TIN-INTERP | Interpolated Ground | 47359.51 | 5.09 | 792.58 | 0 | 18.11 | 0 | OK | Ground clear controls. | 105 | 44.85 | 810.69
7412 | TIN-INTERP | Interpolated Ground | 47359.52 | 4.6 | 792.54 | 0 | 28.44 | 0 | OK | Ground clear controls. | 105 | 44.85 | 820.98
7413 | TIN-INTERP | Interpolated Ground | 47359.54 | -4.61 | 789.86 | 0 | 31.93 | 0 | OK | Ground clear controls. | 105 | 44.85 | 821.79
7414 | TIN-INTERP | Interpolated Ground | 47399.45 | 6.6 | 787.84 | 0 | 31.16 | 0 | OK | Ground clear controls. | 105 | 44.85 | 819
7415 | TIN-INTERP | Interpolated Ground | 47399.46 | -6.61 | 783.1 | 0 | 36.2 | 0 | OK | Ground clear controls. | 105 | 44.85 | 819.3
7416 | TIN-INTERP | Interpolated Ground | 47399.48 | -5.11 | 783.43 | 0 | 30.67 | 0 | OK | Ground clear controls. | 105 | 44.85 | 814.1
7417 | TIN-INTERP | Interpolated Ground | 47399.51 | 5.1 | 787.15 | 0 | 26.96 | 0 | OK | Ground clear controls. | 105 | 44.85 | 814.11
7418 | TIN-INTERP | Interpolated Ground | 47399.52 | 4.6 | 786.98 | 0 | 37.47 | 0 | OK | Ground clear controls. | 105 | 44.85 | 824.45
7419 | TIN-INTERP | Interpolated Ground | 47399.54 | -4.61 | 783.72 | 0 | 41.48 | 0 | OK | Ground clear controls. | 105 | 44.85 | 825.2
7420 | TIN-INTERP | Interpolated Ground | 47439.45 | 6.6 | 783.56 | 0 | 39.87 | 0 | OK | Ground clear controls. | 105 | 44.85 | 823.43
7421 | TIN-INTERP | Interpolated Ground | 47439.46 | -6.6 | 786.77 | 0 | 36.93 | 0 | OK | Ground clear controls. | 105 | 44.85 | 823.7
7422 | TIN-INTERP | Interpolated Ground | 47439.48 | -5.1 | 786.53 | 0 | 31.94 | 0 | OK | Ground clear controls. | 105 | 44.85 | 818.47
7423 | TIN-INTERP | Interpolated Ground | 47439.51 | 5.1 | 783.92 | 0 | 34.55 | 0 | OK | Ground clear controls. | 105 | 44.85 | 818.47
7424 | TIN-INTERP | Interpolated Ground | 47439.52 | 4.6 | 784.03 | 0 | 44.85 | 0 | OK | Ground clear controls. | 105 | 44.85 | 828.88
7425 | TIN-INTERP | Interpolated Ground | 47439.54 | -4.61 | 786.42 | 0 | 43.14 | 0 | OK | Ground clear controls. | 105 | 43.14 | 829.56
7426 | TIN-INTERP | Interpolated Ground | 47479.45 | 6.6 | 793.46 | 0 | 35.37 | 0 | OK | Ground clear controls. | 105 | 42.14 | 828.83
7427 | TIN-INTERP | Interpolated Ground | 47479.46 | -6.6 | 795.59 | 0 | 33.46 | 0 | OK | Ground clear controls. | 105 | 42.14 | 829.05
7428 | TIN-INTERP | Interpolated Ground | 47479.48 | -5.1 | 795.48 | 0 | 28.3 | 0 | OK | Ground clear controls. | 105 | 42.14 | 823.78
7429 | TIN-INTERP | Interpolated Ground | 47479.51 | 5.1 | 793.9 | 0 | 29.88 | 0 | OK | Ground clear controls. | 105 | 42.14 | 823.78
7430 | TIN-INTERP | Interpolated Ground | 47479.52 | 4.6 | 793.99 | 0 | 40.29 | 0 | OK | Ground clear controls. | 105 | 42.14 | 834.28
7431 | TIN-INTERP | Interpolated Ground | 47479.54 | -4.6 | 795.48 | 0 | 39.37 | 0 | OK | Ground clear controls. | 105 | 42.14 | 834.85
7432 | TIN-INTERP | Interpolated Ground | 47519.45 | 6.6 | 804.76 | 0 | 30.44 | 0 | OK | Ground clear controls. | 105 | 42.14 | 835.2
7433 | TIN-INTERP | Interpolated Ground | 47519.46 | -6.6 | 806.63 | 0 | 28.74 | 0 | OK | Ground clear controls. | 105 | 42.14 | 835.37
7434 | TIN-INTERP | Interpolated Ground | 47519.48 | -5.1 | 806.61 | 0 | 23.43 | 0 | OK | Ground clear controls. | 105 | 42.14 | 830.04
7435 | TIN-INTERP | Interpolated Ground | 47519.51 | 5.1 | 805.09 | 0 | 24.94 | 0 | OK | Ground clear controls. | 105 | 42.14 | 830.03
7436 | TIN-INTERP | Interpolated Ground | 47519.52 | 4.6 | 805.23 | 0 | 35.44 | 0 | OK | Ground clear controls. | 105 | 42.14 | 840.67
7437 | TIN-INTERP | Interpolated Ground | 47519.54 | -4.6 | 806.59 | 0 | 34.5 | 0 | OK | Ground clear controls. | 105 | 42.14 | 841.09
7438 | TIN-INTERP | Interpolated Ground | 47559.45 | 6.6 | 811.46 | 0 | 31.09 | 0 | OK | Ground clear controls. | 105 | 42.14 | 842.55
7439 | TIN-INTERP | Interpolated Ground | 47559.46 | -6.6 | 809.72 | 0 | 32.94 | 0 | OK | Ground clear controls. | 105 | 42.14 | 842.66
7440 | TIN-INTERP | Interpolated Ground | 47559.48 | -5.1 | 810.11 | 0 | 27.15 | 0 | OK | Ground clear controls. | 105 | 42.14 | 837.26
7441 | TIN-INTERP | Interpolated Ground | 47559.51 | 5.1 | 811.37 | 0 | 25.87 | 0 | OK | Ground clear controls. | 105 | 42.14 | 837.24
7442 | TIN-INTERP | Interpolated Ground | 47559.52 | 4.6 | 811.35 | 0 | 36.68 | 0 | OK | Ground clear controls. | 105 | 42.14 | 848.03
7443 | TIN-INTERP | Interpolated Ground | 47559.54 | -4.6 | 810.22 | 0 | 38.07 | 0 | OK | Ground clear controls. | 105 | 42.14 | 848.29
7444 | TIN-INTERP | Interpolated Ground | 47599.45 | 6.6 | 816.13 | 0 | 34.75 | 0 | OK | Ground clear controls. | 105 | 42.14 | 850.88
7445 | TIN-INTERP | Interpolated Ground | 47599.46 | -6.6 | 813.55 | 0 | 37.36 | 0 | OK | Ground clear controls. | 105 | 42.14 | 850.91
7446 | TIN-INTERP | Interpolated Ground | 47599.48 | -5.1 | 814.12 | 0 | 31.31 | 0 | OK | Ground clear controls. | 105 | 42.14 | 845.43
7447 | TIN-INTERP | Interpolated Ground | 47599.51 | 5.1 | 815.88 | 0 | 29.53 | 0 | OK | Ground clear controls. | 105 | 42.14 | 845.41
7448 | TIN-INTERP | Interpolated Ground | 47599.52 | 4.6 | 815.79 | 0 | 40.59 | 0 | OK | Ground clear controls. | 105 | 42.14 | 856.38
7449 | TIN-INTERP | Interpolated Ground | 47599.54 | -4.6 | 814.29 | 0 | 42.14 | 0 | OK | Ground clear controls. | 105 | 42.14 | 856.43
7450 | TIN-INTERP | Interpolated Ground | 47612.27 | -6.6 | 815.24 | 0 | 38.51 | 0 | OK | Ground clear controls. | 106 | 43.49 | 853.75
7451 | TIN-INTERP | Interpolated Ground | 47612.27 | 6.6 | 817.02 | 0 | 36.73 | 0 | OK | Ground clear controls. | 106 | 43.49 | 853.75
7452 | TIN-INTERP | Interpolated Ground | 47612.33 | -5.1 | 815.67 | 0 | 32.58 | 0 | OK | Ground clear controls. | 106 | 43.49 | 848.25
7453 | TIN-INTERP | Interpolated Ground | 47612.35 | 4.6 | 816.83 | 0 | 42.42 | 0 | OK | Ground clear controls. | 106 | 43.49 | 859.25
7454 | TIN-INTERP | Interpolated Ground | 47612.5 | -4.6 | 815.77 | 0 | 43.49 | 0 | OK | Ground clear controls. | 106 | 43.49 | 859.26
7455 | TIN-INTERP | Interpolated Ground | 47612.51 | 5.1 | 816.91 | 0 | 31.35 | 0 | OK | Ground clear controls. | 106 | 38.92 | 848.26
7456 | TIN-INTERP | Interpolated Ground | 47652.26 | -6.6 | 817.32 | 0 | 34.15 | 0 | OK | Ground clear controls. | 106 | 38.92 | 851.47
7457 | TIN-INTERP | Interpolated Ground | 47652.27 | 6.6 | 820.91 | 0 | 30.49 | 0 | OK | Ground clear controls. | 106 | 38.92 | 851.4
7458 | TIN-INTERP | Interpolated Ground | 47652.33 | -5.1 | 817.97 | 0 | 28.07 | 0 | OK | Ground clear controls. | 106 | 38.92 | 846.04
7459 | TIN-INTERP | Interpolated Ground | 47652.35 | 4.6 | 820.61 | 0 | 36.32 | 0 | OK | Ground clear controls. | 106 | 38.92 | 856.93
7460 | TIN-INTERP | Interpolated Ground | 47652.5 | -4.6 | 818.2 | 0 | 38.92 | 0 | OK | Ground clear controls. | 106 | 38.92 | 857.12
7461 | TIN-INTERP | Interpolated Ground | 47652.51 | 5.1 | 820.7 | 0 | 25.37 | 0 | OK | Ground clear controls. | 106 | 36.51 | 846.07
7462 | TIN-INTERP | Interpolated Ground | 47692.26 | -6.6 | 819.5 | 0 | 30.64 | 0 | OK | Ground clear controls. | 106 | 36.51 | 850.14
7463 | TIN-INTERP | Interpolated Ground | 47692.27 | 6.6 | 820.41 | 0 | 29.6 | 0 | OK | Ground clear controls. | 106 | 36.51 | 850.01
7464 | TIN-INTERP | Interpolated Ground | 47692.33 | -5.1 | 819.41 | 0 | 25.32 | 0 | OK | Ground clear controls. | 106 | 36.51 | 844.73
7465 | TIN-INTERP | Interpolated Ground | 47692.35 | 4.6 | 820.03 | 0 | 35.53 | 0 | OK | Ground clear controls. | 106 | 36.51 | 855.56
7466 | TIN-INTERP | Interpolated Ground | 47692.5 | -4.6 | 819.37 | 0 | 36.51 | 0 | OK | Ground clear controls. | 106 | 36.51 | 855.88
7467 | TIN-INTERP | Interpolated Ground | 47692.51 | 5.1 | 820.11 | 0 | 24.7 | 0 | OK | Ground clear controls. | 106 | 27.56 | 844.81
7468 | TIN-INTERP | Interpolated Ground | 47732.26 | -6.6 | 828.68 | 0 | 21.07 | 0 | OK | Ground clear controls. | 106 | 27.56 | 849.75
7469 | TIN-INTERP | Interpolated Ground | 47732.27 | 6.6 | 827.31 | 0 | 22.29 | 0 | OK | Ground clear controls. | 106 | 27.56 | 849.6
7470 | TIN-INTERP | Interpolated Ground | 47732.33 | -5.1 | 828.46 | 0 | 15.92 | 0 | OK | Ground clear controls. | 106 | 27.56 | 844.38
7471 | TIN-INTERP | Interpolated Ground | 47732.35 | 4.61 | 827.6 | 0 | 27.56 | 0 | OK | Ground clear controls. | 106 | 27.56 | 855.16
7472 | TIN-INTERP | Interpolated Ground | 47732.5 | -4.6 | 828.43 | 0 | 27.11 | 0 | OK | Ground clear controls. | 106 | 27.11 | 855.54
7473 | TIN-INTERP | Interpolated Ground | 47732.51 | 5.1 | 827.52 | 0 | 16.95 | 0 | OK | Ground clear controls. | 106 | 26.46 | 844.47
7474 | TIN-INTERP | Interpolated Ground | 47772.26 | -6.6 | 833.99 | 0 | 16.31 | 0 | OK | Ground clear controls. | 106 | 26.46 | 850.3
7475 | TIN-INTERP | Interpolated Ground | 47772.27 | 6.6 | 834.83 | 0 | 15.31 | 0 | OK | Ground clear controls. | 106 | 26.46 | 850.14
7476 | TIN-INTERP | Interpolated Ground | 47772.33 | -5.1 | 834.23 | 0 | 10.7 | 0 | OK | Ground clear controls. | 106 | 26.46 | 844.93
7477 | TIN-INTERP | Interpolated Ground | 47772.35 | 4.61 | 834.77 | 0 | 20.93 | 0 | OK | Ground clear controls. | 106 | 26.46 | 855.7
7478 | TIN-INTERP | Interpolated Ground | 47772.5 | -4.61 | 834.33 | 0 | 21.79 | 0 | OK | Ground clear controls. | 106 | 26.46 | 856.12
7479 | TIN-INTERP | Interpolated Ground | 47772.51 | 5.1 | 834.82 | 0 | 10.21 | 0 | OK | Ground clear controls. | 106 | 26.46 | 845.03
7480 | TIN-INTERP | Interpolated Ground | 47812.26 | -6.61 | 833.33 | 0 | 18.48 | 0 | OK | Ground clear controls. | 106 | 26.46 | 851.81
7481 | TIN-INTERP | Interpolated Ground | 47812.27 | 6.6 | 835.98 | 0 | 15.68 | 0 | OK | Ground clear controls. | 106 | 26.46 | 851.66
7482 | TIN-INTERP | Interpolated Ground | 47812.33 | -5.11 | 833.46 | 0 | 12.96 | 0 | OK | Ground clear controls. | 106 | 26.46 | 846.42
7483 | TIN-INTERP | Interpolated Ground | 47812.35 | 4.61 | 835.58 | 0 | 21.64 | 0 | OK | Ground clear controls. | 106 | 26.46 | 857.22
7484 | TIN-INTERP | Interpolated Ground | 47812.5 | -4.61 | 833.49 | 0 | 24.11 | 0 | OK | Ground clear controls. | 106 | 26.46 | 857.6
7485 | TIN-INTERP | Interpolated Ground | 47812.51 | 5.1 | 835.66 | 0 | 10.87 | 0 | OK | Ground clear controls. | 106 | 26.46 | 846.53
7486 | TIN-INTERP | Interpolated Ground | 47852.26 | -6.61 | 835.36 | 0 | 18.89 | 0 | OK | Ground clear controls. | 106 | 26.46 | 854.25
7487 | TIN-INTERP | Interpolated Ground | 47852.27 | 6.6 | 836.87 | 0 | 17.27 | 0 | OK | Ground clear controls. | 106 | 26.46 | 854.14
7488 | TIN-INTERP | Interpolated Ground | 47852.33 | -5.11 | 835.5 | 0 | 13.34 | 0 | OK | Ground clear controls. | 106 | 26.46 | 848.84
7489 | TIN-INTERP | Interpolated Ground | 47852.35 | 4.61 | 836.65 | 0 | 23.03 | 0 | OK | Ground clear controls. | 106 | 26.46 | 859.68
7490 | TIN-INTERP | Interpolated Ground | 47852.5 | -4.61 | 835.54 | 0 | 24.44 | 0 | OK | Ground clear controls. | 106 | 26.46 | 859.98
7491 | TIN-INTERP | Interpolated Ground | 47852.51 | 5.11 | 836.67 | 0 | 12.26 | 0 | OK | Ground clear controls. | 106 | 26.46 | 848.93
7492 | TIN-INTERP | Interpolated Ground | 47892.26 | -6.61 | 836.76 | 0 | 20.88 | 0 | OK | Ground clear controls. | 106 | 26.46 | 857.64
7493 | TIN-INTERP | Interpolated Ground | 47892.27 | 6.61 | 836.78 | 0 | 20.83 | 0 | OK | Ground clear controls. | 106 | 26.46 | 857.61
7494 | TIN-INTERP | Interpolated Ground | 47892.33 | -5.11 | 836.8 | 0 | 15.4 | 0 | OK | Ground clear controls. | 106 | 26.46 | 852.2
7495 | TIN-INTERP | Interpolated Ground | 47892.35 | 4.61 | 836.7 | 0 | 26.42 | 0 | OK | Ground clear controls. | 106 | 26.46 | 863.12
7496 | TIN-INTERP | Interpolated Ground | 47892.5 | -4.61 | 836.82 | 0 | 26.46 | 0 | OK | Ground clear controls. | 106 | 26.46 | 863.28
7497 | TIN-INTERP | Interpolated Ground | 47892.51 | 5.11 | 836.74 | 0 | 15.52 | 0 | OK | Ground clear controls. | 106 | 15.52 | 852.26
7498 | TIN-INTERP | Interpolated Ground | 47926.78 | 6.61 | 841.01 | 0 | 20.36 | 0 | OK | Ground clear controls. | 107 | 40.47 | 861.37
7499 | TIN-INTERP | Interpolated Ground | 47926.92 | 4.61 | 840.48 | 0 | 26.38 | 0 | OK | Ground clear controls. | 107 | 40.47 | 866.86
7500 | TIN-INTERP | Interpolated Ground | 47926.95 | 5.11 | 840.57 | 0 | 15.29 | 0 | OK | Ground clear controls. | 107 | 40.47 | 855.86
7501 | TIN-INTERP | Interpolated Ground | 47927.03 | -6.61 | 838.7 | 0 | 22.67 | 0 | OK | Ground clear controls. | 107 | 40.47 | 861.37
7502 | TIN-INTERP | Interpolated Ground | 47927.14 | -5.11 | 839.13 | 0 | 16.73 | 0 | OK | Ground clear controls. | 107 | 40.47 | 855.86
7503 | TIN-INTERP | Interpolated Ground | 47927.17 | -4.62 | 839.28 | 0 | 27.59 | 0 | OK | Ground clear controls. | 107 | 40.47 | 866.87
7504 | TIN-INTERP | Interpolated Ground | 47966.78 | 6.63 | 835.52 | 0 | 24.43 | 0 | OK | Ground clear controls. | 107 | 40.47 | 859.95
7505 | TIN-INTERP | Interpolated Ground | 47966.92 | 4.64 | 835.87 | 0 | 29.69 | 0 | OK | Ground clear controls. | 107 | 40.47 | 865.56
7506 | TIN-INTERP | Interpolated Ground | 47966.95 | 5.13 | 835.79 | 0 | 18.95 | 0 | OK | Ground clear controls. | 107 | 40.47 | 854.74
7507 | TIN-INTERP | Interpolated Ground | 47967.03 | -6.63 | 836.89 | 0 | 23.24 | 0 | OK | Ground clear controls. | 107 | 40.47 | 860.13
7508 | TIN-INTERP | Interpolated Ground | 47967.14 | -5.14 | 836.82 | 0 | 17.93 | 0 | OK | Ground clear controls. | 107 | 40.47 | 854.75
7509 | TIN-INTERP | Interpolated Ground | 47967.17 | -4.65 | 836.76 | 0 | 29.13 | 0 | OK | Ground clear controls. | 107 | 40.47 | 865.89
7510 | TIN-INTERP | Interpolated Ground | 48006.78 | 6.65 | 839.77 | 0 | 19.73 | 0 | OK | Ground clear controls. | 107 | 40.47 | 859.5
7511 | TIN-INTERP | Interpolated Ground | 48006.92 | 4.67 | 840.12 | 0 | 25.09 | 0 | OK | Ground clear controls. | 107 | 40.47 | 865.21
7512 | TIN-INTERP | Interpolated Ground | 48006.95 | 5.15 | 840.04 | 0 | 14.49 | 0 | OK | Ground clear controls. | 107 | 40.47 | 854.53
7513 | TIN-INTERP | Interpolated Ground | 48007.03 | -6.66 | 839.51 | 0 | 20.33 | 0 | OK | Ground clear controls. | 107 | 40.47 | 859.84
7514 | TIN-INTERP | Interpolated Ground | 48007.14 | -5.16 | 839.71 | 0 | 14.84 | 0 | OK | Ground clear controls. | 107 | 40.47 | 854.55
7515 | TIN-INTERP | Interpolated Ground | 48007.17 | -4.68 | 839.77 | 0 | 26.04 | 0 | OK | Ground clear controls. | 107 | 40.47 | 865.81
7516 | TIN-INTERP | Interpolated Ground | 48046.78 | 6.67 | 840.51 | 0 | 19.53 | 0 | OK | Ground clear controls. | 107 | 40.47 | 860.04
7517 | TIN-INTERP | Interpolated Ground | 48046.92 | 4.7 | 840.34 | 0 | 25.49 | 0 | OK | Ground clear controls. | 107 | 40.47 | 865.83
7518 | TIN-INTERP | Interpolated Ground | 48046.95 | 5.17 | 840.37 | 0 | 14.88 | 0 | OK | Ground clear controls. | 107 | 40.47 | 855.25
7519 | TIN-INTERP | Interpolated Ground | 48047.03 | -6.68 | 838.96 | 0 | 21.53 | 0 | OK | Ground clear controls. | 107 | 40.47 | 860.49
7520 | TIN-INTERP | Interpolated Ground | 48047.14 | -5.18 | 839.04 | 0 | 16.22 | 0 | OK | Ground clear controls. | 107 | 40.47 | 855.26
7521 | TIN-INTERP | Interpolated Ground | 48047.17 | -4.71 | 839.17 | 0 | 27.46 | 0 | OK | Ground clear controls. | 107 | 40.47 | 866.63
7522 | TIN-INTERP | Interpolated Ground | 48086.78 | 6.69 | 829.97 | 0 | 31.57 | 0 | OK | Ground clear controls. | 107 | 40.47 | 861.54
7523 | TIN-INTERP | Interpolated Ground | 48086.92 | 4.73 | 828.66 | 0 | 38.74 | 0 | OK | Ground clear controls. | 107 | 40.47 | 867.4
7524 | TIN-INTERP | Interpolated Ground | 48086.95 | 5.19 | 828.81 | 0 | 28.07 | 0 | OK | Ground clear controls. | 107 | 40.47 | 856.88
7525 | TIN-INTERP | Interpolated Ground | 48087.03 | -6.7 | 828.05 | 0 | 34.03 | 0 | OK | Ground clear controls. | 107 | 40.47 | 862.08
7526 | TIN-INTERP | Interpolated Ground | 48087.14 | -5.21 | 827.9 | 0 | 29 | 0 | OK | Ground clear controls. | 107 | 40.47 | 856.9
7527 | TIN-INTERP | Interpolated Ground | 48087.17 | -4.74 | 827.86 | 0 | 40.47 | 0 | OK | Ground clear controls. | 107 | 40.47 | 868.33
7528 | TIN-INTERP | Interpolated Ground | 48126.78 | 6.72 | 838.45 | 0 | 25.59 | 0 | OK | Ground clear controls. | 107 | 38.18 | 864.04
7529 | TIN-INTERP | Interpolated Ground | 48126.92 | 4.76 | 838.05 | 0 | 31.89 | 0 | OK | Ground clear controls. | 107 | 38.18 | 869.94
7530 | TIN-INTERP | Interpolated Ground | 48126.95 | 5.21 | 838.15 | 0 | 21.29 | 0 | OK | Ground clear controls. | 107 | 38.18 | 859.44
7531 | TIN-INTERP | Interpolated Ground | 48127.03 | -6.73 | 831.9 | 0 | 32.71 | 0 | OK | Ground clear controls. | 107 | 38.18 | 864.61
7532 | TIN-INTERP | Interpolated Ground | 48127.14 | -5.23 | 832.45 | 0 | 27 | 0 | OK | Ground clear controls. | 107 | 38.18 | 859.45
7533 | TIN-INTERP | Interpolated Ground | 48127.17 | -4.77 | 832.75 | 0 | 38.18 | 0 | OK | Ground clear controls. | 107 | 38.18 | 870.93
7534 | TIN-INTERP | Interpolated Ground | 48166.78 | 6.74 | 836.87 | 0 | 30.64 | 0 | OK | Ground clear controls. | 107 | 36.21 | 867.51
7535 | TIN-INTERP | Interpolated Ground | 48166.92 | 4.79 | 837.23 | 0 | 36.21 | 0 | OK | Ground clear controls. | 107 | 36.21 | 873.44
7536 | TIN-INTERP | Interpolated Ground | 48166.95 | 5.23 | 837.21 | 0 | 25.69 | 0 | OK | Ground clear controls. | 107 | 33.96 | 862.9
7537 | TIN-INTERP | Interpolated Ground | 48167.03 | -6.75 | 840.63 | 0 | 27.45 | 0 | OK | Ground clear controls. | 107 | 33.96 | 868.08
7538 | TIN-INTERP | Interpolated Ground | 48167.14 | -5.25 | 840.49 | 0 | 22.42 | 0 | OK | Ground clear controls. | 107 | 33.96 | 862.91
7539 | TIN-INTERP | Interpolated Ground | 48167.17 | -4.8 | 840.47 | 0 | 33.96 | 0 | OK | Ground clear controls. | 107 | 33.96 | 874.43
7540 | TIN-INTERP | Interpolated Ground | 48206.78 | 6.76 | 849.13 | 0 | 22.84 | 0 | OK | Ground clear controls. | 107 | 30.35 | 871.97
7541 | TIN-INTERP | Interpolated Ground | 48206.92 | 4.82 | 849.28 | 0 | 28.63 | 0 | OK | Ground clear controls. | 107 | 30.35 | 877.91
7542 | TIN-INTERP | Interpolated Ground | 48206.95 | 5.26 | 849.29 | 0 | 18 | 0 | OK | Ground clear controls. | 107 | 30.35 | 867.29
7543 | TIN-INTERP | Interpolated Ground | 48207.03 | -6.77 | 848.2 | 0 | 24.29 | 0 | OK | Ground clear controls. | 107 | 30.35 | 872.49
7544 | TIN-INTERP | Interpolated Ground | 48207.14 | -5.28 | 848.41 | 0 | 18.9 | 0 | OK | Ground clear controls. | 107 | 30.35 | 867.31
7545 | TIN-INTERP | Interpolated Ground | 48207.17 | -4.83 | 848.48 | 0 | 30.35 | 0 | OK | Ground clear controls. | 107 | 30.35 | 878.83
7546 | TIN-INTERP | Interpolated Ground | 48246.78 | 6.78 | 858.04 | 0 | 19.37 | 0 | OK | Ground clear controls. | 107 | 27.45 | 877.41
7547 | TIN-INTERP | Interpolated Ground | 48246.92 | 4.85 | 858.15 | 0 | 25.2 | 0 | OK | Ground clear controls. | 107 | 27.45 | 883.35
7548 | TIN-INTERP | Interpolated Ground | 48246.95 | 5.28 | 858.17 | 0 | 14.43 | 0 | OK | Ground clear controls. | 107 | 27.45 | 872.6
7549 | TIN-INTERP | Interpolated Ground | 48247.03 | -6.8 | 856.39 | 0 | 21.47 | 0 | OK | Ground clear controls. | 107 | 27.45 | 877.86
7550 | TIN-INTERP | Interpolated Ground | 48247.14 | -5.3 | 856.6 | 0 | 16.03 | 0 | OK | Ground clear controls. | 107 | 27.45 | 872.63
7551 | TIN-INTERP | Interpolated Ground | 48247.17 | -4.86 | 856.66 | 0 | 27.45 | 0 | OK | Ground clear controls. | 107 | 27.45 | 884.11
7552 | TIN-INTERP | Interpolated Ground | 48286.78 | 6.8 | 867.77 | 0 | 16.07 | 0 | OK | Ground clear controls. | 107 | 23.15 | 883.84
7553 | TIN-INTERP | Interpolated Ground | 48286.92 | 4.88 | 867.81 | 0 | 21.94 | 0 | OK | Ground clear controls. | 107 | 23.15 | 889.75
7554 | TIN-INTERP | Interpolated Ground | 48286.95 | 5.3 | 867.85 | 0 | 11 | 0 | OK | Ground clear controls. | 107 | 23.15 | 878.85
7555 | TIN-INTERP | Interpolated Ground | 48287.03 | -6.82 | 867.37 | 0 | 16.81 | 0 | OK | Ground clear controls. | 107 | 23.15 | 884.18
7556 | TIN-INTERP | Interpolated Ground | 48287.14 | -5.32 | 867.44 | 0 | 11.44 | 0 | OK | Ground clear controls. | 107 | 23.15 | 878.88
7557 | TIN-INTERP | Interpolated Ground | 48287.17 | -4.9 | 867.46 | 0 | 22.86 | 0 | OK | Ground clear controls. | 107 | 23.15 | 890.32
7558 | TIN-INTERP | Interpolated Ground | 48326.78 | 6.83 | 875.18 | 0 | 16.09 | 0 | OK | Ground clear controls. | 107 | 23.15 | 891.27
7559 | TIN-INTERP | Interpolated Ground | 48326.92 | 4.91 | 875.21 | 0 | 21.93 | 0 | OK | Ground clear controls. | 107 | 23.15 | 897.14
7560 | TIN-INTERP | Interpolated Ground | 48326.95 | 5.32 | 875.2 | 0 | 10.81 | 0 | OK | Ground clear controls. | 107 | 23.15 | 886.01
7561 | TIN-INTERP | Interpolated Ground | 48327.03 | -6.84 | 873.91 | 0 | 17.53 | 0 | OK | Ground clear controls. | 107 | 23.15 | 891.44
7562 | TIN-INTERP | Interpolated Ground | 48327.14 | -5.35 | 874.2 | 0 | 11.85 | 0 | OK | Ground clear controls. | 107 | 23.15 | 886.05
7563 | TIN-INTERP | Interpolated Ground | 48327.17 | -4.93 | 874.28 | 0 | 23.15 | 0 | OK | Ground clear controls. | 107 | 23.15 | 897.43
7564 | TIN-INTERP | Interpolated Ground | 48356.21 | 6.84 | 878.2 | 0 | 19.17 | 0 | OK | Ground clear controls. | 108 | 27.62 | 897.37
7565 | TIN-INTERP | Interpolated Ground | 48356.24 | 4.93 | 877.91 | 0 | 25.26 | 0 | OK | Ground clear controls. | 108 | 27.62 | 903.17
7566 | TIN-INTERP | Interpolated Ground | 48356.29 | -4.95 | 876.15 | 0 | 27.02 | 0 | OK | Ground clear controls. | 108 | 27.62 | 903.17
7567 | TIN-INTERP | Interpolated Ground | 48356.31 | 5.33 | 877.97 | 0 | 13.9 | 0 | OK | Ground clear controls. | 108 | 27.62 | 891.87
7568 | TIN-INTERP | Interpolated Ground | 48356.37 | -5.36 | 876.07 | 0 | 15.81 | 0 | OK | Ground clear controls. | 108 | 27.62 | 891.88
7569 | TIN-INTERP | Interpolated Ground | 48356.37 | -6.86 | 875.7 | 0 | 21.67 | 0 | OK | Ground clear controls. | 108 | 27.62 | 897.37
7570 | TIN-INTERP | Interpolated Ground | 48396.21 | 6.72 | 882.21 | 0 | 18.23 | 0 | OK | Ground clear controls. | 108 | 27.62 | 900.44
7571 | TIN-INTERP | Interpolated Ground | 48396.24 | 4.81 | 881.8 | 0 | 24.47 | 0 | OK | Ground clear controls. | 108 | 27.62 | 906.27
7572 | TIN-INTERP | Interpolated Ground | 48396.29 | -4.88 | 879.98 | 0 | 26.51 | 0 | OK | Ground clear controls. | 108 | 27.62 | 906.49
7573 | TIN-INTERP | Interpolated Ground | 48396.31 | 5.21 | 881.9 | 0 | 13.3 | 0 | OK | Ground clear controls. | 108 | 27.62 | 895.2
7574 | TIN-INTERP | Interpolated Ground | 48396.37 | -5.31 | 879.88 | 0 | 15.28 | 0 | OK | Ground clear controls. | 108 | 27.62 | 895.16
7575 | TIN-INTERP | Interpolated Ground | 48396.37 | -6.8 | 879.52 | 0 | 21.04 | 0 | OK | Ground clear controls. | 108 | 27.62 | 900.56
7576 | TIN-INTERP | Interpolated Ground | 48436.21 | 6.6 | 888.23 | 0 | 16.26 | 0 | OK | Ground clear controls. | 108 | 27.62 | 904.49
7577 | TIN-INTERP | Interpolated Ground | 48436.24 | 4.68 | 887.58 | 0 | 22.74 | 0 | OK | Ground clear controls. | 108 | 27.62 | 910.32
7578 | TIN-INTERP | Interpolated Ground | 48436.29 | -4.81 | 885.14 | 0 | 25.55 | 0 | OK | Ground clear controls. | 108 | 27.62 | 910.69
7579 | TIN-INTERP | Interpolated Ground | 48436.31 | 5.09 | 887.7 | 0 | 11.74 | 0 | OK | Ground clear controls. | 108 | 27.62 | 899.44
7580 | TIN-INTERP | Interpolated Ground | 48436.37 | -5.26 | 884.9 | 0 | 14.44 | 0 | OK | Ground clear controls. | 108 | 27.62 | 899.34
7581 | TIN-INTERP | Interpolated Ground | 48436.37 | -6.74 | 883.95 | 0 | 20.71 | 0 | OK | Ground clear controls. | 108 | 27.62 | 904.66
7582 | TIN-INTERP | Interpolated Ground | 48476.21 | 6.48 | 891.45 | 0 | 18.07 | 0 | OK | Ground clear controls. | 108 | 27.62 | 909.52
7583 | TIN-INTERP | Interpolated Ground | 48476.24 | 4.55 | 891.04 | 0 | 24.28 | 0 | OK | Ground clear controls. | 108 | 27.62 | 915.32
7584 | TIN-INTERP | Interpolated Ground | 48476.29 | -4.74 | 888.17 | 0 | 27.62 | 0 | OK | Ground clear controls. | 108 | 27.62 | 915.79
7585 | TIN-INTERP | Interpolated Ground | 48476.31 | 4.97 | 891.16 | 0 | 13.43 | 0 | OK | Ground clear controls. | 108 | 27.15 | 904.59
7586 | TIN-INTERP | Interpolated Ground | 48476.37 | -5.21 | 888.02 | 0 | 16.41 | 0 | OK | Ground clear controls. | 108 | 27.15 | 904.43
7587 | TIN-INTERP | Interpolated Ground | 48476.37 | -6.68 | 887.72 | 0 | 21.98 | 0 | OK | Ground clear controls. | 108 | 27.15 | 909.7
7588 | TIN-INTERP | Interpolated Ground | 48516.21 | 6.35 | 899.24 | 0 | 16.28 | 0 | OK | Ground clear controls. | 108 | 27.15 | 915.52
7589 | TIN-INTERP | Interpolated Ground | 48516.24 | 4.43 | 899.22 | 0 | 22.08 | 0 | OK | Ground clear controls. | 108 | 27.15 | 921.3
7590 | TIN-INTERP | Interpolated Ground | 48516.29 | -4.67 | 897.86 | 0 | 23.91 | 0 | OK | Ground clear controls. | 108 | 27.15 | 921.77
7591 | TIN-INTERP | Interpolated Ground | 48516.31 | 4.85 | 899.28 | 0 | 11.38 | 0 | OK | Ground clear controls. | 108 | 27.15 | 910.66
7592 | TIN-INTERP | Interpolated Ground | 48516.37 | -5.15 | 897.9 | 0 | 12.54 | 0 | OK | Ground clear controls. | 108 | 27.15 | 910.44
7593 | TIN-INTERP | Interpolated Ground | 48516.37 | -6.62 | 897.85 | 0 | 17.82 | 0 | OK | Ground clear controls. | 108 | 27.15 | 915.67
7594 | TIN-INTERP | Interpolated Ground | 48556.21 | 6.23 | 906.2 | 0 | 16.31 | 0 | OK | Ground clear controls. | 108 | 27.15 | 922.51
7595 | TIN-INTERP | Interpolated Ground | 48556.24 | 4.3 | 906.51 | 0 | 21.72 | 0 | OK | Ground clear controls. | 108 | 27.15 | 928.23
7596 | TIN-INTERP | Interpolated Ground | 48556.29 | -4.59 | 905.73 | 0 | 22.92 | 0 | OK | Ground clear controls. | 108 | 27.15 | 928.65
7597 | TIN-INTERP | Interpolated Ground | 48556.3 | 4.73 | 906.43 | 0 | 11.21 | 0 | OK | Ground clear controls. | 108 | 27.15 | 917.64
7598 | TIN-INTERP | Interpolated Ground | 48556.37 | -5.1 | 905.57 | 0 | 11.79 | 0 | OK | Ground clear controls. | 108 | 27.15 | 917.36
7599 | TIN-INTERP | Interpolated Ground | 48556.37 | -6.57 | 905.27 | 0 | 17.31 | 0 | OK | Ground clear controls. | 108 | 27.15 | 922.58
7600 | TIN-INTERP | Interpolated Ground | 48596.21 | 6.11 | 913.72 | 0 | 16.77 | 0 | OK | Ground clear controls. | 108 | 27.15 | 930.49
7601 | TIN-INTERP | Interpolated Ground | 48596.24 | 4.17 | 912.47 | 0 | 23.67 | 0 | OK | Ground clear controls. | 108 | 27.15 | 936.14
7602 | TIN-INTERP | Interpolated Ground | 48596.29 | -4.52 | 909.28 | 0 | 27.15 | 0 | OK | Ground clear controls. | 108 | 27.15 | 936.43
7603 | TIN-INTERP | Interpolated Ground | 48596.3 | 4.61 | 912.75 | 0 | 12.8 | 0 | OK | Ground clear controls. | 108 | 27.14 | 925.55
7604 | TIN-INTERP | Interpolated Ground | 48596.37 | -5.05 | 908.94 | 0 | 16.25 | 0 | OK | Ground clear controls. | 108 | 27.14 | 925.19
7605 | TIN-INTERP | Interpolated Ground | 48596.37 | -6.51 | 907.83 | 0 | 22.59 | 0 | OK | Ground clear controls. | 108 | 27.14 | 930.42
7606 | TIN-INTERP | Interpolated Ground | 48636.21 | 5.99 | 920.98 | 0 | 18.49 | 0 | OK | Ground clear controls. | 108 | 27.14 | 939.47
7607 | TIN-INTERP | Interpolated Ground | 48636.24 | 4.04 | 920.45 | 0 | 24.56 | 0 | OK | Ground clear controls. | 108 | 27.14 | 945.01
7608 | TIN-INTERP | Interpolated Ground | 48636.29 | -4.45 | 919.85 | 0 | 25.26 | 0 | OK | Ground clear controls. | 108 | 27.14 | 945.11
7609 | TIN-INTERP | Interpolated Ground | 48636.3 | 4.49 | 920.51 | 0 | 13.87 | 0 | OK | Ground clear controls. | 108 | 27.14 | 934.38
7610 | TIN-INTERP | Interpolated Ground | 48636.37 | -5 | 919.67 | 0 | 14.29 | 0 | OK | Ground clear controls. | 108 | 27.14 | 933.96
7611 | TIN-INTERP | Interpolated Ground | 48636.37 | -6.45 | 919.35 | 0 | 19.87 | 0 | OK | Ground clear controls. | 108 | 27.14 | 939.22
7612 | TIN-INTERP | Interpolated Ground | 48676.21 | 5.87 | 929.49 | 0 | 19.94 | 0 | OK | Ground clear controls. | 108 | 27.14 | 949.43
7613 | TIN-INTERP | Interpolated Ground | 48676.24 | 3.92 | 928.84 | 0 | 26.03 | 0 | OK | Ground clear controls. | 108 | 27.14 | 954.87
7614 | TIN-INTERP | Interpolated Ground | 48676.29 | -4.38 | 927.57 | 0 | 27.14 | 0 | OK | Ground clear controls. | 108 | 27.14 | 954.71
7615 | TIN-INTERP | Interpolated Ground | 48676.3 | 4.37 | 929.1 | 0 | 15.05 | 0 | OK | Ground clear controls. | 108 | 21.48 | 944.15
7616 | TIN-INTERP | Interpolated Ground | 48676.37 | -4.94 | 927.58 | 0 | 16.07 | 0 | OK | Ground clear controls. | 108 | 21.48 | 943.65
7617 | TIN-INTERP | Interpolated Ground | 48676.37 | -6.39 | 927.48 | 0 | 21.48 | 0 | OK | Ground clear controls. | 108 | 21.48 | 948.96
7618 | TIN-INTERP | Interpolated Ground | 48714.67 | -6.35 | 932.99 | 0 | 25.39 | 0 | OK | Ground clear controls. | 109 | 44.29 | 958.38
7619 | TIN-INTERP | Interpolated Ground | 48714.83 | -4.28 | 932.78 | 0 | 31.09 | 0 | OK | Ground clear controls. | 109 | 44.29 | 963.87
7620 | TIN-INTERP | Interpolated Ground | 48715.04 | -4.89 | 932.83 | 0 | 20.04 | 0 | OK | Ground clear controls. | 109 | 44.29 | 952.87
7621 | TIN-INTERP | Interpolated Ground | 48716.72 | 3.82 | 933.34 | 0 | 30.54 | 0 | OK | Ground clear controls. | 109 | 44.29 | 963.88
7622 | TIN-INTERP | Interpolated Ground | 48717.2 | 4.27 | 933.39 | 0 | 19.48 | 0 | OK | Ground clear controls. | 109 | 44.29 | 952.87
7623 | TIN-INTERP | Interpolated Ground | 48717.52 | 5.73 | 933.46 | 0 | 24.92 | 0 | OK | Ground clear controls. | 109 | 44.29 | 958.38
7624 | TIN-INTERP | Interpolated Ground | 48754.67 | -6.38 | 921.39 | 0 | 34.29 | 0 | OK | Ground clear controls. | 109 | 44.29 | 955.68
7625 | TIN-INTERP | Interpolated Ground | 48754.83 | -4.32 | 921.83 | 0 | 39.33 | 0 | OK | Ground clear controls. | 109 | 44.29 | 961.16
7626 | TIN-INTERP | Interpolated Ground | 48755.04 | -4.92 | 921.59 | 0 | 28.57 | 0 | OK | Ground clear controls. | 109 | 44.29 | 950.16
7627 | TIN-INTERP | Interpolated Ground | 48756.72 | 3.95 | 922.75 | 0 | 38.42 | 0 | OK | Ground clear controls. | 109 | 44.29 | 961.17
7628 | TIN-INTERP | Interpolated Ground | 48757.2 | 4.41 | 922.7 | 0 | 27.47 | 0 | OK | Ground clear controls. | 109 | 44.29 | 950.17
7629 | TIN-INTERP | Interpolated Ground | 48757.52 | 5.88 | 923.14 | 0 | 32.58 | 0 | OK | Ground clear controls. | 109 | 44.29 | 955.72
7630 | TIN-INTERP | Interpolated Ground | 48794.67 | -6.42 | 914.35 | 0 | 39.54 | 0 | OK | Ground clear controls. | 109 | 44.29 | 953.89
7631 | TIN-INTERP | Interpolated Ground | 48794.83 | -4.37 | 915.06 | 0 | 44.29 | 0 | OK | Ground clear controls. | 109 | 44.29 | 959.35
7632 | TIN-INTERP | Interpolated Ground | 48795.04 | -4.95 | 914.79 | 0 | 33.57 | 0 | OK | Ground clear controls. | 109 | 39.77 | 948.36
7633 | TIN-INTERP | Interpolated Ground | 48796.72 | 4.09 | 919.61 | 0 | 39.77 | 0 | OK | Ground clear controls. | 109 | 39.77 | 959.38
7634 | TIN-INTERP | Interpolated Ground | 48797.2 | 4.55 | 919.46 | 0 | 28.91 | 0 | OK | Ground clear controls. | 109 | 37.75 | 948.37
7635 | TIN-INTERP | Interpolated Ground | 48797.52 | 6.03 | 919.76 | 0 | 34.2 | 0 | OK | Ground clear controls. | 109 | 37.75 | 953.96
7636 | TIN-INTERP | Interpolated Ground | 48834.67 | -6.45 | 925.06 | 0 | 27.92 | 0 | OK | Ground clear controls. | 109 | 37.75 | 952.98
7637 | TIN-INTERP | Interpolated Ground | 48834.83 | -4.42 | 925.46 | 0 | 32.99 | 0 | OK | Ground clear controls. | 109 | 37.75 | 958.45
7638 | TIN-INTERP | Interpolated Ground | 48835.04 | -4.98 | 925.4 | 0 | 22.06 | 0 | OK | Ground clear controls. | 109 | 37.75 | 947.46
7639 | TIN-INTERP | Interpolated Ground | 48836.72 | 4.23 | 927.87 | 0 | 30.62 | 0 | OK | Ground clear controls. | 109 | 37.75 | 958.49
7640 | TIN-INTERP | Interpolated Ground | 48837.2 | 4.7 | 928.07 | 0 | 19.42 | 0 | OK | Ground clear controls. | 109 | 37.75 | 947.49
7641 | TIN-INTERP | Interpolated Ground | 48837.52 | 6.18 | 928.58 | 0 | 24.5 | 0 | OK | Ground clear controls. | 109 | 37.75 | 953.08
7642 | TIN-INTERP | Interpolated Ground | 48874.67 | -6.49 | 918.71 | 0 | 34.27 | 0 | OK | Ground clear controls. | 109 | 37.75 | 952.98
7643 | TIN-INTERP | Interpolated Ground | 48874.83 | -4.46 | 920.7 | 0 | 37.75 | 0 | OK | Ground clear controls. | 109 | 37.75 | 958.45
7644 | TIN-INTERP | Interpolated Ground | 48875.04 | -5 | 920.01 | 0 | 27.46 | 0 | OK | Ground clear controls. | 109 | 34.34 | 947.47
7645 | TIN-INTERP | Interpolated Ground | 48876.72 | 4.36 | 924.17 | 0 | 34.34 | 0 | OK | Ground clear controls. | 109 | 34.34 | 958.51
7646 | TIN-INTERP | Interpolated Ground | 48877.2 | 4.84 | 924.32 | 0 | 23.19 | 0 | OK | Ground clear controls. | 109 | 33.08 | 947.51
7647 | TIN-INTERP | Interpolated Ground | 48877.51 | 6.33 | 924.89 | 0 | 28.21 | 0 | OK | Ground clear controls. | 109 | 33.08 | 953.1
7648 | TIN-INTERP | Interpolated Ground | 48914.67 | -6.52 | 925.06 | 0 | 28.8 | 0 | OK | Ground clear controls. | 109 | 33.08 | 953.86
7649 | TIN-INTERP | Interpolated Ground | 48914.83 | -4.51 | 926.26 | 0 | 33.08 | 0 | OK | Ground clear controls. | 109 | 33.08 | 959.34
7650 | TIN-INTERP | Interpolated Ground | 48915.04 | -5.03 | 926 | 0 | 22.36 | 0 | OK | Ground clear controls. | 109 | 28.52 | 948.36
7651 | TIN-INTERP | Interpolated Ground | 48916.72 | 4.5 | 930.9 | 0 | 28.52 | 0 | OK | Ground clear controls. | 109 | 28.52 | 959.42
7652 | TIN-INTERP | Interpolated Ground | 48917.19 | 4.99 | 931.15 | 0 | 17.29 | 0 | OK | Ground clear controls. | 109 | 21.98 | 948.44
7653 | TIN-INTERP | Interpolated Ground | 48917.51 | 6.48 | 932.02 | 0 | 21.98 | 0 | OK | Ground clear controls. | 109 | 21.98 | 954
7654 | TIN-INTERP | Interpolated Ground | 48949.29 | -6.55 | 930.06 | 0 | 25.3 | 0 | OK | Ground clear controls. | 110 | 75.67 | 955.36
7655 | TIN-INTERP | Interpolated Ground | 48949.33 | -4.55 | 930.69 | 0 | 30.16 | 0 | OK | Ground clear controls. | 110 | 75.67 | 960.85
7656 | TIN-INTERP | Interpolated Ground | 48949.34 | -5.05 | 930.59 | 0 | 19.26 | 0 | OK | Ground clear controls. | 110 | 75.67 | 949.85
7657 | TIN-INTERP | Interpolated Ground | 48949.43 | 5.1 | 934.55 | 0 | 15.31 | 0 | OK | Ground clear controls. | 110 | 75.67 | 949.86
7658 | TIN-INTERP | Interpolated Ground | 48949.43 | 4.61 | 934.39 | 0 | 26.47 | 0 | OK | Ground clear controls. | 110 | 75.67 | 960.86
7659 | TIN-INTERP | Interpolated Ground | 48949.5 | 6.6 | 934.58 | 0 | 20.77 | 0 | OK | Ground clear controls. | 110 | 75.67 | 955.35
7660 | TIN-INTERP | Interpolated Ground | 48989.27 | -6.57 | 915.67 | 0 | 35.36 | 0 | OK | Ground clear controls. | 110 | 75.67 | 951.03
7661 | TIN-INTERP | Interpolated Ground | 48989.32 | -4.58 | 916.51 | 0 | 40.02 | 0 | OK | Ground clear controls. | 110 | 75.67 | 956.53
7662 | TIN-INTERP | Interpolated Ground | 48989.32 | -5.07 | 916.46 | 0 | 29.06 | 0 | OK | Ground clear controls. | 110 | 75.67 | 945.52
7663 | TIN-INTERP | Interpolated Ground | 48989.44 | 5.14 | 919.7 | 0 | 25.77 | 0 | OK | Ground clear controls. | 110 | 75.67 | 945.47
7664 | TIN-INTERP | Interpolated Ground | 48989.45 | 4.66 | 919.46 | 0 | 37.06 | 0 | OK | Ground clear controls. | 110 | 75.67 | 956.52
7665 | TIN-INTERP | Interpolated Ground | 48989.5 | 6.64 | 920.98 | 0 | 30.11 | 0 | OK | Ground clear controls. | 110 | 75.67 | 951.09
7666 | TIN-INTERP | Interpolated Ground | 49029.27 | -6.58 | 905.08 | 0 | 42.55 | 0 | OK | Ground clear controls. | 110 | 75.67 | 947.63
7667 | TIN-INTERP | Interpolated Ground | 49029.32 | -4.6 | 906.34 | 0 | 46.77 | 0 | OK | Ground clear controls. | 110 | 75.67 | 953.11
7668 | TIN-INTERP | Interpolated Ground | 49029.32 | -5.09 | 906.03 | 0 | 36.06 | 0 | OK | Ground clear controls. | 110 | 75.67 | 942.09
7669 | TIN-INTERP | Interpolated Ground | 49029.44 | 5.18 | 908.66 | 0 | 33.34 | 0 | OK | Ground clear controls. | 110 | 75.67 | 942
7670 | TIN-INTERP | Interpolated Ground | 49029.45 | 4.71 | 908.31 | 0 | 44.8 | 0 | OK | Ground clear controls. | 110 | 75.67 | 953.11
7671 | TIN-INTERP | Interpolated Ground | 49029.5 | 6.68 | 909.54 | 0 | 38.16 | 0 | OK | Ground clear controls. | 110 | 75.67 | 947.7
7672 | TIN-INTERP | Interpolated Ground | 49069.27 | -6.6 | 875.24 | 0 | 69.87 | 0 | OK | Ground clear controls. | 110 | 75.67 | 945.11
7673 | TIN-INTERP | Interpolated Ground | 49069.32 | -4.63 | 875.51 | 0 | 75.1 | 0 | OK | Ground clear controls. | 110 | 75.67 | 950.61
7674 | TIN-INTERP | Interpolated Ground | 49069.32 | -5.1 | 875.45 | 0 | 64.12 | 0 | OK | Ground clear controls. | 110 | 75.67 | 939.57
7675 | TIN-INTERP | Interpolated Ground | 49069.44 | 5.22 | 875.01 | 0 | 64.44 | 0 | OK | Ground clear controls. | 110 | 75.67 | 939.45
7676 | TIN-INTERP | Interpolated Ground | 49069.45 | 4.76 | 874.93 | 0 | 75.67 | 0 | OK | Ground clear controls. | 110 | 75.67 | 950.6
7677 | TIN-INTERP | Interpolated Ground | 49069.5 | 6.72 | 875.2 | 0 | 70.03 | 0 | OK | Ground clear controls. | 110 | 70.03 | 945.23
7678 | TIN-INTERP | Interpolated Ground | 49109.27 | -6.62 | 885.54 | 0 | 57.96 | 0 | OK | Ground clear controls. | 110 | 63.02 | 943.5
7679 | TIN-INTERP | Interpolated Ground | 49109.32 | -4.65 | 886 | 0 | 63.02 | 0 | OK | Ground clear controls. | 110 | 63.02 | 949.02
7680 | TIN-INTERP | Interpolated Ground | 49109.32 | -5.12 | 885.97 | 0 | 51.99 | 0 | OK | Ground clear controls. | 110 | 59.17 | 937.96
7681 | TIN-INTERP | Interpolated Ground | 49109.44 | 5.26 | 889.94 | 0 | 47.88 | 0 | OK | Ground clear controls. | 110 | 59.17 | 937.82
7682 | TIN-INTERP | Interpolated Ground | 49109.45 | 4.8 | 889.84 | 0 | 59.17 | 0 | OK | Ground clear controls. | 110 | 59.17 | 949.01
7683 | TIN-INTERP | Interpolated Ground | 49109.5 | 6.76 | 890.32 | 0 | 53.33 | 0 | OK | Ground clear controls. | 110 | 58.73 | 943.65
7684 | TIN-INTERP | Interpolated Ground | 49149.27 | -6.63 | 898.4 | 0 | 44.41 | 0 | OK | Ground clear controls. | 110 | 58.73 | 942.81
7685 | TIN-INTERP | Interpolated Ground | 49149.32 | -4.68 | 899.3 | 0 | 49.03 | 0 | OK | Ground clear controls. | 110 | 58.73 | 948.33
7686 | TIN-INTERP | Interpolated Ground | 49149.32 | -5.14 | 899.06 | 0 | 38.19 | 0 | OK | Ground clear controls. | 110 | 58.73 | 937.25
7687 | TIN-INTERP | Interpolated Ground | 49149.44 | 5.3 | 904.42 | 0 | 32.69 | 0 | OK | Ground clear controls. | 110 | 58.73 | 937.11
7688 | TIN-INTERP | Interpolated Ground | 49149.45 | 4.85 | 904.11 | 0 | 44.21 | 0 | OK | Ground clear controls. | 110 | 58.73 | 948.32
7689 | TIN-INTERP | Interpolated Ground | 49149.5 | 6.8 | 905.07 | 0 | 37.88 | 0 | OK | Ground clear controls. | 110 | 58.73 | 942.95
7690 | TIN-INTERP | Interpolated Ground | 49189.27 | -6.65 | 889.26 | 0 | 53.74 | 0 | OK | Ground clear controls. | 110 | 58.73 | 943
7691 | TIN-INTERP | Interpolated Ground | 49189.32 | -4.7 | 889.82 | 0 | 58.73 | 0 | OK | Ground clear controls. | 110 | 58.73 | 948.55
7692 | TIN-INTERP | Interpolated Ground | 49189.32 | -5.15 | 889.7 | 0 | 47.75 | 0 | OK | Ground clear controls. | 110 | 58.22 | 937.45
7693 | TIN-INTERP | Interpolated Ground | 49189.44 | 5.34 | 890.41 | 0 | 46.91 | 0 | OK | Ground clear controls. | 110 | 58.22 | 937.32
7694 | TIN-INTERP | Interpolated Ground | 49189.45 | 4.9 | 890.34 | 0 | 58.22 | 0 | OK | Ground clear controls. | 110 | 58.22 | 948.56
7695 | TIN-INTERP | Interpolated Ground | 49189.5 | 6.84 | 890.92 | 0 | 52.24 | 0 | OK | Ground clear controls. | 110 | 52.24 | 943.16
7696 | TIN-INTERP | Interpolated Ground | 49229.27 | -6.67 | 909.92 | 0 | 34.18 | 0 | OK | Ground clear controls. | 110 | 39.16 | 944.1
7697 | TIN-INTERP | Interpolated Ground | 49229.32 | -4.73 | 910.54 | 0 | 39.16 | 0 | OK | Ground clear controls. | 110 | 39.16 | 949.7
7698 | TIN-INTERP | Interpolated Ground | 49229.32 | -5.17 | 910.4 | 0 | 28.16 | 0 | OK | Ground clear controls. | 110 | 36.74 | 938.56
7699 | TIN-INTERP | Interpolated Ground | 49229.44 | 5.39 | 913.05 | 0 | 25.39 | 0 | OK | Ground clear controls. | 110 | 36.74 | 938.44
7700 | TIN-INTERP | Interpolated Ground | 49229.45 | 4.95 | 912.95 | 0 | 36.74 | 0 | OK | Ground clear controls. | 110 | 36.74 | 949.69
7701 | TIN-INTERP | Interpolated Ground | 49229.5 | 6.89 | 913.47 | 0 | 30.78 | 0 | OK | Ground clear controls. | 110 | 32.77 | 944.25
7702 | TIN-INTERP | Interpolated Ground | 49269.27 | -6.68 | 919.07 | 0 | 27.03 | 0 | OK | Ground clear controls. | 110 | 32.77 | 946.1
7703 | TIN-INTERP | Interpolated Ground | 49269.32 | -4.75 | 918.97 | 0 | 32.77 | 0 | OK | Ground clear controls. | 110 | 32.77 | 951.74
7704 | TIN-INTERP | Interpolated Ground | 49269.32 | -5.18 | 919 | 0 | 21.58 | 0 | OK | Ground clear controls. | 110 | 31.89 | 940.58
7705 | TIN-INTERP | Interpolated Ground | 49269.44 | 5.43 | 920.52 | 0 | 19.95 | 0 | OK | Ground clear controls. | 110 | 31.89 | 940.47
7706 | TIN-INTERP | Interpolated Ground | 49269.45 | 5 | 920.51 | 0 | 31.24 | 0 | OK | Ground clear controls. | 110 | 31.89 | 951.75
7707 | TIN-INTERP | Interpolated Ground | 49269.5 | 6.93 | 920.22 | 0 | 26.02 | 0 | OK | Ground clear controls. | 110 | 31.89 | 946.24
7708 | TIN-INTERP | Interpolated Ground | 49309.27 | -6.7 | 929.23 | 0 | 19.79 | 0 | OK | Ground clear controls. | 110 | 31.89 | 949.02
7709 | TIN-INTERP | Interpolated Ground | 49309.32 | -4.78 | 929.55 | 0 | 25.15 | 0 | OK | Ground clear controls. | 110 | 31.89 | 954.7
7710 | TIN-INTERP | Interpolated Ground | 49309.32 | -5.2 | 929.45 | 0 | 14.05 | 0 | OK | Ground clear controls. | 110 | 31.89 | 943.5
7711 | TIN-INTERP | Interpolated Ground | 49309.44 | 5.47 | 930.03 | 0 | 13.4 | 0 | OK | Ground clear controls. | 110 | 31.89 | 943.43
7712 | TIN-INTERP | Interpolated Ground | 49309.45 | 5.05 | 930.06 | 0 | 24.65 | 0 | OK | Ground clear controls. | 110 | 31.89 | 954.71
7713 | TIN-INTERP | Interpolated Ground | 49309.5 | 6.97 | 929.99 | 0 | 19.14 | 0 | OK | Ground clear controls. | 110 | 31.89 | 949.13
7714 | TIN-INTERP | Interpolated Ground | 49349.27 | -6.71 | 932.05 | 0 | 20.77 | 0 | OK | Ground clear controls. | 110 | 31.89 | 952.82
7715 | TIN-INTERP | Interpolated Ground | 49349.32 | -4.8 | 931.5 | 0 | 27.07 | 0 | OK | Ground clear controls. | 110 | 31.89 | 958.57
7716 | TIN-INTERP | Interpolated Ground | 49349.32 | -5.22 | 931.58 | 0 | 15.74 | 0 | OK | Ground clear controls. | 110 | 31.89 | 947.32
7717 | TIN-INTERP | Interpolated Ground | 49349.44 | 5.51 | 926.54 | 0 | 20.76 | 0 | OK | Ground clear controls. | 110 | 31.89 | 947.3
7718 | TIN-INTERP | Interpolated Ground | 49349.45 | 5.1 | 926.7 | 0 | 31.89 | 0 | OK | Ground clear controls. | 110 | 31.89 | 958.59
7719 | TIN-INTERP | Interpolated Ground | 49349.5 | 7.01 | 925.92 | 0 | 26.99 | 0 | OK | Ground clear controls. | 110 | 26.99 | 952.91
7720 | TIN-INTERP | Interpolated Ground | 49386.69 | 5.54 | 920.61 | 0 | 31.13 | 0 | OK | Ground clear controls. | 111 | 74.38 | 951.74
7721 | TIN-INTERP | Interpolated Ground | 49386.72 | 7.05 | 920.47 | 0 | 36.77 | 0 | OK | Ground clear controls. | 111 | 74.38 | 957.24
7722 | TIN-INTERP | Interpolated Ground | 49386.76 | -5.23 | 923.25 | 0 | 28.49 | 0 | OK | Ground clear controls. | 111 | 74.38 | 951.74
7723 | TIN-INTERP | Interpolated Ground | 49386.77 | 5.14 | 920.64 | 0 | 42.39 | 0 | OK | Ground clear controls. | 111 | 74.38 | 963.03
7724 | TIN-INTERP | Interpolated Ground | 49386.83 | -4.83 | 923.14 | 0 | 39.89 | 0 | OK | Ground clear controls. | 111 | 74.38 | 963.03
7725 | TIN-INTERP | Interpolated Ground | 49386.85 | -6.73 | 923.65 | 0 | 33.58 | 0 | OK | Ground clear controls. | 111 | 74.38 | 957.23
7726 | TIN-INTERP | Interpolated Ground | 49426.64 | -5.17 | 921.07 | 0 | 14.54 | 0 | OK | Ground clear controls. | 111 | 74.38 | 935.61
7727 | TIN-INTERP | Interpolated Ground | 49426.69 | -6.67 | 920.81 | 0 | 20.38 | 0 | OK | Ground clear controls. | 111 | 74.38 | 941.19
7728 | TIN-INTERP | Interpolated Ground | 49426.72 | -4.75 | 921.05 | 0 | 25.87 | 0 | OK | Ground clear controls. | 111 | 74.38 | 946.92
7729 | TIN-INTERP | Interpolated Ground | 49426.82 | 5.46 | 920.17 | 0 | 15.37 | 0 | OK | Ground clear controls. | 111 | 74.38 | 935.54
7730 | TIN-INTERP | Interpolated Ground | 49426.89 | 6.96 | 919.87 | 0 | 21.32 | 0 | OK | Ground clear controls. | 111 | 74.38 | 941.19
7731 | TIN-INTERP | Interpolated Ground | 49426.89 | 5.04 | 920.25 | 0 | 26.64 | 0 | OK | Ground clear controls. | 111 | 74.38 | 946.89
7732 | TIN-INTERP | Interpolated Ground | 49466.64 | -5.11 | 901.03 | 0 | 19.48 | 0 | OK | Ground clear controls. | 111 | 74.38 | 920.51
7733 | TIN-INTERP | Interpolated Ground | 49466.69 | -6.61 | 900.19 | 0 | 25.97 | 0 | OK | Ground clear controls. | 111 | 74.38 | 926.16
7734 | TIN-INTERP | Interpolated Ground | 49466.72 | -4.68 | 901.14 | 0 | 30.69 | 0 | OK | Ground clear controls. | 111 | 74.38 | 931.83
7735 | TIN-INTERP | Interpolated Ground | 49466.82 | 5.37 | 902.46 | 0 | 17.92 | 0 | OK | Ground clear controls. | 111 | 74.38 | 920.38
7736 | TIN-INTERP | Interpolated Ground | 49466.89 | 6.87 | 902.47 | 0 | 23.67 | 0 | OK | Ground clear controls. | 111 | 74.38 | 926.14
7737 | TIN-INTERP | Interpolated Ground | 49466.89 | 4.94 | 902.41 | 0 | 29.38 | 0 | OK | Ground clear controls. | 111 | 74.38 | 931.79
7738 | TIN-INTERP | Interpolated Ground | 49506.64 | -5.05 | 877.05 | 0 | 29.38 | 0 | OK | Ground clear controls. | 111 | 74.38 | 906.43
7739 | TIN-INTERP | Interpolated Ground | 49506.69 | -6.55 | 876.98 | 0 | 35.16 | 0 | OK | Ground clear controls. | 111 | 74.38 | 912.14
7740 | TIN-INTERP | Interpolated Ground | 49506.72 | -4.6 | 876.99 | 0 | 40.77 | 0 | OK | Ground clear controls. | 111 | 74.38 | 917.76
7741 | TIN-INTERP | Interpolated Ground | 49506.82 | 5.28 | 877.32 | 0 | 28.95 | 0 | OK | Ground clear controls. | 111 | 74.38 | 906.27
7742 | TIN-INTERP | Interpolated Ground | 49506.89 | 6.78 | 877.31 | 0 | 34.8 | 0 | OK | Ground clear controls. | 111 | 74.38 | 912.11
7743 | TIN-INTERP | Interpolated Ground | 49506.89 | 4.83 | 877.27 | 0 | 40.43 | 0 | OK | Ground clear controls. | 111 | 74.38 | 917.7
7744 | TIN-INTERP | Interpolated Ground | 49546.64 | -5 | 847.49 | 0 | 45.89 | 0 | OK | Ground clear controls. | 111 | 74.38 | 893.38
7745 | TIN-INTERP | Interpolated Ground | 49546.69 | -6.5 | 847.06 | 0 | 52.05 | 0 | OK | Ground clear controls. | 111 | 74.38 | 899.11
7746 | TIN-INTERP | Interpolated Ground | 49546.72 | -4.53 | 847.67 | 0 | 57.01 | 0 | OK | Ground clear controls. | 111 | 74.38 | 904.68
7747 | TIN-INTERP | Interpolated Ground | 49546.82 | 5.19 | 852.2 | 0 | 40.99 | 0 | OK | Ground clear controls. | 111 | 74.38 | 893.19
7748 | TIN-INTERP | Interpolated Ground | 49546.89 | 6.69 | 852.97 | 0 | 46.1 | 0 | OK | Ground clear controls. | 111 | 74.38 | 899.07
7749 | TIN-INTERP | Interpolated Ground | 49546.89 | 4.73 | 851.9 | 0 | 52.72 | 0 | OK | Ground clear controls. | 111 | 74.38 | 904.62
7750 | TIN-INTERP | Interpolated Ground | 49586.64 | -4.94 | 821.92 | 0 | 59.41 | 0 | OK | Ground clear controls. | 111 | 74.38 | 881.33
7751 | TIN-INTERP | Interpolated Ground | 49586.69 | -6.44 | 823.25 | 0 | 63.82 | 0 | OK | Ground clear controls. | 111 | 74.38 | 887.07
7752 | TIN-INTERP | Interpolated Ground | 49586.72 | -4.46 | 821.49 | 0 | 71.12 | 0 | OK | Ground clear controls. | 111 | 74.38 | 892.61
7753 | TIN-INTERP | Interpolated Ground | 49586.82 | 5.1 | 822.79 | 0 | 58.35 | 0 | OK | Ground clear controls. | 111 | 74.38 | 881.14
7754 | TIN-INTERP | Interpolated Ground | 49586.89 | 6.6 | 823.51 | 0 | 63.51 | 0 | OK | Ground clear controls. | 111 | 74.38 | 887.02
7755 | TIN-INTERP | Interpolated Ground | 49586.89 | 4.62 | 822.52 | 0 | 70.03 | 0 | OK | Ground clear controls. | 111 | 74.38 | 892.55
7756 | TIN-INTERP | Interpolated Ground | 49626.64 | -4.88 | 814.55 | 0 | 55.73 | 0 | OK | Ground clear controls. | 111 | 74.38 | 870.28
7757 | TIN-INTERP | Interpolated Ground | 49626.69 | -6.38 | 815.85 | 0 | 60.16 | 0 | OK | Ground clear controls. | 111 | 74.38 | 876.01
7758 | TIN-INTERP | Interpolated Ground | 49626.72 | -4.39 | 814.15 | 0 | 67.38 | 0 | OK | Ground clear controls. | 111 | 74.38 | 881.53
7759 | TIN-INTERP | Interpolated Ground | 49626.82 | 5.01 | 806.88 | 0 | 63.23 | 0 | OK | Ground clear controls. | 111 | 74.38 | 870.11
7760 | TIN-INTERP | Interpolated Ground | 49626.89 | 6.51 | 805.91 | 0 | 70.05 | 0 | OK | Ground clear controls. | 111 | 74.38 | 875.96
7761 | TIN-INTERP | Interpolated Ground | 49626.89 | 4.51 | 807.09 | 0 | 74.38 | 0 | OK | Ground clear controls. | 111 | 74.38 | 881.47
7762 | TIN-INTERP | Interpolated Ground | 49666.64 | -4.82 | 807.33 | 0 | 52.91 | 0 | OK | Ground clear controls. | 111 | 64.93 | 860.24
7763 | TIN-INTERP | Interpolated Ground | 49666.69 | -6.33 | 807.42 | 0 | 58.5 | 0 | OK | Ground clear controls. | 111 | 64.93 | 865.92
7764 | TIN-INTERP | Interpolated Ground | 49666.72 | -4.31 | 807.24 | 0 | 64.2 | 0 | OK | Ground clear controls. | 111 | 64.93 | 871.44
7765 | TIN-INTERP | Interpolated Ground | 49666.82 | 4.92 | 806.29 | 0 | 53.8 | 0 | OK | Ground clear controls. | 111 | 64.93 | 860.09
7766 | TIN-INTERP | Interpolated Ground | 49666.89 | 6.42 | 805.45 | 0 | 60.43 | 0 | OK | Ground clear controls. | 111 | 64.93 | 865.88
7767 | TIN-INTERP | Interpolated Ground | 49666.89 | 4.41 | 806.45 | 0 | 64.93 | 0 | OK | Ground clear controls. | 111 | 64.93 | 871.38
7768 | TIN-INTERP | Interpolated Ground | 49706.64 | -4.77 | 810.74 | 0 | 40.45 | 0 | OK | Ground clear controls. | 111 | 58.09 | 851.19
7769 | TIN-INTERP | Interpolated Ground | 49706.69 | -6.27 | 811.77 | 0 | 45.05 | 0 | OK | Ground clear controls. | 111 | 58.09 | 856.82
7770 | TIN-INTERP | Interpolated Ground | 49706.72 | -4.24 | 810.44 | 0 | 51.88 | 0 | OK | Ground clear controls. | 111 | 58.09 | 862.32
7771 | TIN-INTERP | Interpolated Ground | 49706.82 | 4.83 | 803.74 | 0 | 47.34 | 0 | OK | Ground clear controls. | 111 | 58.09 | 851.08
7772 | TIN-INTERP | Interpolated Ground | 49706.89 | 6.33 | 802.95 | 0 | 53.82 | 0 | OK | Ground clear controls. | 111 | 58.09 | 856.77
7773 | TIN-INTERP | Interpolated Ground | 49706.89 | 4.3 | 804.19 | 0 | 58.09 | 0 | OK | Ground clear controls. | 111 | 58.09 | 862.28
7774 | TIN-INTERP | Interpolated Ground | 49746.64 | -4.71 | 821.05 | 0 | 22.07 | 0 | OK | Ground clear controls. | 111 | 36.6 | 843.12
7775 | TIN-INTERP | Interpolated Ground | 49746.69 | -6.21 | 821.24 | 0 | 27.43 | 0 | OK | Ground clear controls. | 111 | 36.6 | 848.67
7776 | TIN-INTERP | Interpolated Ground | 49746.72 | -4.17 | 820.99 | 0 | 33.2 | 0 | OK | Ground clear controls. | 111 | 36.6 | 854.19
7777 | TIN-INTERP | Interpolated Ground | 49746.82 | 4.75 | 817.27 | 0 | 25.8 | 0 | OK | Ground clear controls. | 111 | 36.6 | 843.07
7778 | TIN-INTERP | Interpolated Ground | 49746.89 | 6.24 | 816.6 | 0 | 32.03 | 0 | OK | Ground clear controls. | 111 | 36.6 | 848.63
7779 | TIN-INTERP | Interpolated Ground | 49746.89 | 4.2 | 817.55 | 0 | 36.6 | 0 | OK | Ground clear controls. | 111 | 36.6 | 854.15
7780 | TIN-INTERP | Interpolated Ground | 49766.57 | -4.16 | 820.17 | 0 | 30.44 | 0 | OK | Ground clear controls. | 112 | 56.65 | 850.61
7781 | TIN-INTERP | Interpolated Ground | 49766.59 | 4.14 | 819.8 | 0 | 30.82 | 0 | OK | Ground clear controls. | 112 | 56.65 | 850.62
7782 | TIN-INTERP | Interpolated Ground | 49766.75 | -6.21 | 820.24 | 0 | 24.87 | 0 | OK | Ground clear controls. | 112 | 56.65 | 845.11
7783 | TIN-INTERP | Interpolated Ground | 49766.76 | 6.19 | 819.67 | 0 | 25.46 | 0 | OK | Ground clear controls. | 112 | 56.65 | 845.13
7784 | TIN-INTERP | Interpolated Ground | 49766.8 | 4.69 | 819.75 | 0 | 19.87 | 0 | OK | Ground clear controls. | 112 | 56.65 | 839.62
7785 | TIN-INTERP | Interpolated Ground | 49766.86 | -4.71 | 820.16 | 0 | 19.46 | 0 | OK | Ground clear controls. | 112 | 56.65 | 839.62
7786 | TIN-INTERP | Interpolated Ground | 49806.57 | -4.18 | 803.81 | 0 | 35.77 | 0 | OK | Ground clear controls. | 112 | 56.65 | 839.58
7787 | TIN-INTERP | Interpolated Ground | 49806.59 | 4.16 | 807.34 | 0 | 32.38 | 0 | OK | Ground clear controls. | 112 | 56.65 | 839.72
7788 | TIN-INTERP | Interpolated Ground | 49806.75 | -6.23 | 802.88 | 0 | 31.31 | 0 | OK | Ground clear controls. | 112 | 56.65 | 834.19
7789 | TIN-INTERP | Interpolated Ground | 49806.76 | 6.21 | 807.99 | 0 | 26.36 | 0 | OK | Ground clear controls. | 112 | 56.65 | 834.35
7790 | TIN-INTERP | Interpolated Ground | 49806.8 | 4.71 | 807.46 | 0 | 21.34 | 0 | OK | Ground clear controls. | 112 | 56.65 | 828.8
7791 | TIN-INTERP | Interpolated Ground | 49806.86 | -4.73 | 803.47 | 0 | 25.3 | 0 | OK | Ground clear controls. | 112 | 56.65 | 828.77
7792 | TIN-INTERP | Interpolated Ground | 49846.57 | -4.21 | 790.98 | 0 | 38.63 | 0 | OK | Ground clear controls. | 112 | 56.65 | 829.61
7793 | TIN-INTERP | Interpolated Ground | 49846.59 | 4.18 | 790.71 | 0 | 39.16 | 0 | OK | Ground clear controls. | 112 | 56.65 | 829.87
7794 | TIN-INTERP | Interpolated Ground | 49846.75 | -6.25 | 790.19 | 0 | 34.13 | 0 | OK | Ground clear controls. | 112 | 56.65 | 824.32
7795 | TIN-INTERP | Interpolated Ground | 49846.76 | 6.23 | 790.73 | 0 | 33.87 | 0 | OK | Ground clear controls. | 112 | 56.65 | 824.6
7796 | TIN-INTERP | Interpolated Ground | 49846.8 | 4.73 | 790.64 | 0 | 28.38 | 0 | OK | Ground clear controls. | 112 | 56.65 | 819.02
7797 | TIN-INTERP | Interpolated Ground | 49846.86 | -4.75 | 790.64 | 0 | 28.33 | 0 | OK | Ground clear controls. | 112 | 56.65 | 818.97
7798 | TIN-INTERP | Interpolated Ground | 49886.57 | -4.23 | 766.1 | 0 | 54.57 | 0 | OK | Ground clear controls. | 112 | 56.65 | 820.67
7799 | TIN-INTERP | Interpolated Ground | 49886.59 | 4.2 | 772.37 | 0 | 48.68 | 0 | OK | Ground clear controls. | 112 | 56.65 | 821.05
7800 | TIN-INTERP | Interpolated Ground | 49886.75 | -6.27 | 765 | 0 | 50.47 | 0 | OK | Ground clear controls. | 112 | 56.65 | 815.47
7801 | TIN-INTERP | Interpolated Ground | 49886.76 | 6.24 | 772.78 | 0 | 43.09 | 0 | OK | Ground clear controls. | 112 | 56.65 | 815.87
7802 | TIN-INTERP | Interpolated Ground | 49886.8 | 4.74 | 772.3 | 0 | 37.96 | 0 | OK | Ground clear controls. | 112 | 56.65 | 810.26
7803 | TIN-INTERP | Interpolated Ground | 49886.86 | -4.77 | 765.43 | 0 | 44.75 | 0 | OK | Ground clear controls. | 112 | 56.65 | 810.18
7804 | TIN-INTERP | Interpolated Ground | 49926.57 | -4.25 | 762 | 0 | 50.79 | 0 | OK | Ground clear controls. | 112 | 56.65 | 812.79
7805 | TIN-INTERP | Interpolated Ground | 49926.59 | 4.22 | 763 | 0 | 50.26 | 0 | OK | Ground clear controls. | 112 | 56.65 | 813.26
7806 | TIN-INTERP | Interpolated Ground | 49926.75 | -6.29 | 760.21 | 0 | 47.46 | 0 | OK | Ground clear controls. | 112 | 56.65 | 807.67
7807 | TIN-INTERP | Interpolated Ground | 49926.76 | 6.26 | 763.18 | 0 | 44.99 | 0 | OK | Ground clear controls. | 112 | 56.65 | 808.17
7808 | TIN-INTERP | Interpolated Ground | 49926.8 | 4.76 | 762.95 | 0 | 39.57 | 0 | OK | Ground clear controls. | 112 | 56.65 | 802.52
7809 | TIN-INTERP | Interpolated Ground | 49926.86 | -4.79 | 761.75 | 0 | 40.67 | 0 | OK | Ground clear controls. | 112 | 56.65 | 802.42
7810 | TIN-INTERP | Interpolated Ground | 49966.57 | -4.28 | 757.41 | 0 | 48.54 | 0 | OK | Ground clear controls. | 112 | 56.65 | 805.95
7811 | TIN-INTERP | Interpolated Ground | 49966.59 | 4.24 | 755.02 | 0 | 51.47 | 0 | OK | Ground clear controls. | 112 | 56.65 | 806.49
7812 | TIN-INTERP | Interpolated Ground | 49966.75 | -6.31 | 757.93 | 0 | 42.95 | 0 | OK | Ground clear controls. | 112 | 56.65 | 800.88
7813 | TIN-INTERP | Interpolated Ground | 49966.76 | 6.28 | 754.42 | 0 | 47.05 | 0 | OK | Ground clear controls. | 112 | 56.65 | 801.47
7814 | TIN-INTERP | Interpolated Ground | 49966.8 | 4.78 | 754.84 | 0 | 40.96 | 0 | OK | Ground clear controls. | 112 | 56.65 | 795.8
7815 | TIN-INTERP | Interpolated Ground | 49966.86 | -4.82 | 757.49 | 0 | 38.21 | 0 | OK | Ground clear controls. | 112 | 56.65 | 795.7
7816 | TIN-INTERP | Interpolated Ground | 50006.57 | -4.3 | 749.31 | 0 | 50.82 | 0 | OK | Ground clear controls. | 112 | 56.65 | 800.13
7817 | TIN-INTERP | Interpolated Ground | 50006.59 | 4.26 | 749.96 | 0 | 50.78 | 0 | OK | Ground clear controls. | 112 | 56.65 | 800.74
7818 | TIN-INTERP | Interpolated Ground | 50006.75 | -6.34 | 750.07 | 0 | 45.06 | 0 | OK | Ground clear controls. | 112 | 56.65 | 795.13
7819 | TIN-INTERP | Interpolated Ground | 50006.76 | 6.3 | 750.14 | 0 | 45.64 | 0 | OK | Ground clear controls. | 112 | 56.65 | 795.78
7820 | TIN-INTERP | Interpolated Ground | 50006.8 | 4.79 | 750.07 | 0 | 40.02 | 0 | OK | Ground clear controls. | 112 | 56.65 | 790.09
7821 | TIN-INTERP | Interpolated Ground | 50006.86 | -4.84 | 749.39 | 0 | 40.57 | 0 | OK | Ground clear controls. | 112 | 56.65 | 789.96
7822 | TIN-INTERP | Interpolated Ground | 50046.57 | -4.32 | 746.95 | 0 | 48.39 | 0 | OK | Ground clear controls. | 112 | 56.65 | 795.34
7823 | TIN-INTERP | Interpolated Ground | 50046.59 | 4.28 | 748.68 | 0 | 47.33 | 0 | OK | Ground clear controls. | 112 | 56.65 | 796.01
7824 | TIN-INTERP | Interpolated Ground | 50046.75 | -6.36 | 746.52 | 0 | 43.86 | 0 | OK | Ground clear controls. | 112 | 56.65 | 790.38
7825 | TIN-INTERP | Interpolated Ground | 50046.76 | 6.31 | 749.11 | 0 | 41.98 | 0 | OK | Ground clear controls. | 112 | 56.65 | 791.09
7826 | TIN-INTERP | Interpolated Ground | 50046.8 | 4.81 | 748.79 | 0 | 36.59 | 0 | OK | Ground clear controls. | 112 | 56.65 | 785.38
7827 | TIN-INTERP | Interpolated Ground | 50046.86 | -4.86 | 746.84 | 0 | 38.41 | 0 | OK | Ground clear controls. | 112 | 56.65 | 785.25
7828 | TIN-INTERP | Interpolated Ground | 50086.57 | -4.34 | 743.23 | 0 | 48.37 | 0 | OK | Ground clear controls. | 112 | 56.65 | 791.6
7829 | TIN-INTERP | Interpolated Ground | 50086.59 | 4.3 | 745.72 | 0 | 46.58 | 0 | OK | Ground clear controls. | 112 | 56.65 | 792.3
7830 | TIN-INTERP | Interpolated Ground | 50086.75 | -6.38 | 742.68 | 0 | 43.98 | 0 | OK | Ground clear controls. | 112 | 56.65 | 786.66
7831 | TIN-INTERP | Interpolated Ground | 50086.76 | 6.33 | 746.25 | 0 | 41.17 | 0 | OK | Ground clear controls. | 112 | 56.65 | 787.42
7832 | TIN-INTERP | Interpolated Ground | 50086.8 | 4.83 | 745.86 | 0 | 35.84 | 0 | OK | Ground clear controls. | 112 | 56.65 | 781.7
7833 | TIN-INTERP | Interpolated Ground | 50086.86 | -4.88 | 743.05 | 0 | 38.51 | 0 | OK | Ground clear controls. | 112 | 56.65 | 781.56
7834 | TIN-INTERP | Interpolated Ground | 50126.57 | -4.37 | 737.6 | 0 | 51.28 | 0 | OK | Ground clear controls. | 112 | 56.65 | 788.88
7835 | TIN-INTERP | Interpolated Ground | 50126.59 | 4.32 | 742.23 | 0 | 47.37 | 0 | OK | Ground clear controls. | 112 | 56.65 | 789.6
7836 | TIN-INTERP | Interpolated Ground | 50126.75 | -6.4 | 736.74 | 0 | 47.23 | 0 | OK | Ground clear controls. | 112 | 56.65 | 783.97
7837 | TIN-INTERP | Interpolated Ground | 50126.76 | 6.35 | 742.74 | 0 | 42 | 0 | OK | Ground clear controls. | 112 | 56.65 | 784.74
7838 | TIN-INTERP | Interpolated Ground | 50126.8 | 4.85 | 742.36 | 0 | 36.66 | 0 | OK | Ground clear controls. | 112 | 56.65 | 779.02
7839 | TIN-INTERP | Interpolated Ground | 50126.86 | -4.9 | 737.33 | 0 | 41.55 | 0 | OK | Ground clear controls. | 112 | 56.65 | 778.88
7840 | TIN-INTERP | Interpolated Ground | 50166.57 | -4.39 | 733.28 | 0 | 53.9 | 0 | OK | Ground clear controls. | 112 | 56.65 | 787.18
7841 | TIN-INTERP | Interpolated Ground | 50166.59 | 4.34 | 731.92 | 0 | 55.99 | 0 | OK | Ground clear controls. | 112 | 56.65 | 787.91
7842 | TIN-INTERP | Interpolated Ground | 50166.75 | -6.42 | 734.27 | 0 | 48.01 | 0 | OK | Ground clear controls. | 112 | 56.65 | 782.28
7843 | TIN-INTERP | Interpolated Ground | 50166.76 | 6.36 | 732.05 | 0 | 51.02 | 0 | OK | Ground clear controls. | 112 | 56.65 | 783.07
7844 | TIN-INTERP | Interpolated Ground | 50166.8 | 4.86 | 731.94 | 0 | 45.39 | 0 | OK | Ground clear controls. | 112 | 56.65 | 777.33
7845 | TIN-INTERP | Interpolated Ground | 50166.86 | -4.92 | 733.41 | 0 | 43.78 | 0 | OK | Ground clear controls. | 112 | 56.65 | 777.19
7846 | TIN-INTERP | Interpolated Ground | 50206.57 | -4.41 | 730.36 | 0 | 56.14 | 0 | OK | Ground clear controls. | 112 | 56.65 | 786.5
7847 | TIN-INTERP | Interpolated Ground | 50206.59 | 4.36 | 731.93 | 0 | 55.3 | 0 | OK | Ground clear controls. | 112 | 56.65 | 787.23
7848 | TIN-INTERP | Interpolated Ground | 50206.75 | -6.44 | 731.67 | 0 | 49.93 | 0 | OK | Ground clear controls. | 112 | 56.65 | 781.6
7849 | TIN-INTERP | Interpolated Ground | 50206.76 | 6.38 | 732.41 | 0 | 49.97 | 0 | OK | Ground clear controls. | 112 | 56.65 | 782.38
7850 | TIN-INTERP | Interpolated Ground | 50206.8 | 4.88 | 732.02 | 0 | 44.63 | 0 | OK | Ground clear controls. | 112 | 56.65 | 776.65
7851 | TIN-INTERP | Interpolated Ground | 50206.86 | -4.94 | 730.59 | 0 | 45.92 | 0 | OK | Ground clear controls. | 112 | 56.65 | 776.51
7852 | TIN-INTERP | Interpolated Ground | 50246.57 | -4.44 | 732.6 | 0 | 54.23 | 0 | OK | Ground clear controls. | 112 | 56.65 | 786.83
7853 | TIN-INTERP | Interpolated Ground | 50246.59 | 4.38 | 735.02 | 0 | 52.52 | 0 | OK | Ground clear controls. | 112 | 56.65 | 787.54
7854 | TIN-INTERP | Interpolated Ground | 50246.75 | -6.46 | 731.78 | 0 | 50.14 | 0 | OK | Ground clear controls. | 112 | 56.65 | 781.92
7855 | TIN-INTERP | Interpolated Ground | 50246.76 | 6.4 | 735.88 | 0 | 46.81 | 0 | OK | Ground clear controls. | 112 | 56.65 | 782.69
7856 | TIN-INTERP | Interpolated Ground | 50246.8 | 4.9 | 735.25 | 0 | 41.71 | 0 | OK | Ground clear controls. | 112 | 56.65 | 776.96
7857 | TIN-INTERP | Interpolated Ground | 50246.86 | -4.96 | 732.69 | 0 | 44.14 | 0 | OK | Ground clear controls. | 112 | 56.65 | 776.83
7858 | TIN-INTERP | Interpolated Ground | 50286.57 | -4.46 | 733.09 | 0 | 55.1 | 0 | OK | Ground clear controls. | 112 | 56.65 | 788.19
7859 | TIN-INTERP | Interpolated Ground | 50286.59 | 4.4 | 732.3 | 0 | 56.58 | 0 | OK | Ground clear controls. | 112 | 56.65 | 788.88
7860 | TIN-INTERP | Interpolated Ground | 50286.75 | -6.48 | 733 | 0 | 50.27 | 0 | OK | Ground clear controls. | 112 | 56.65 | 783.27
7861 | TIN-INTERP | Interpolated Ground | 50286.76 | 6.42 | 732.24 | 0 | 51.77 | 0 | OK | Ground clear controls. | 112 | 56.65 | 784.01
7862 | TIN-INTERP | Interpolated Ground | 50286.8 | 4.92 | 732.21 | 0 | 46.08 | 0 | OK | Ground clear controls. | 112 | 56.65 | 778.29
7863 | TIN-INTERP | Interpolated Ground | 50286.86 | -4.98 | 733.05 | 0 | 45.11 | 0 | OK | Ground clear controls. | 112 | 56.65 | 778.16
7864 | TIN-INTERP | Interpolated Ground | 50326.57 | -4.48 | 734.14 | 0 | 56.46 | 0 | OK | Ground clear controls. | 112 | 56.65 | 790.6
7865 | TIN-INTERP | Interpolated Ground | 50326.59 | 4.42 | 734.86 | 0 | 56.37 | 0 | OK | Ground clear controls. | 112 | 56.65 | 791.23
7866 | TIN-INTERP | Interpolated Ground | 50326.75 | -6.5 | 734.02 | 0 | 51.61 | 0 | OK | Ground clear controls. | 112 | 56.65 | 785.63
7867 | TIN-INTERP | Interpolated Ground | 50326.76 | 6.43 | 735.26 | 0 | 51.06 | 0 | OK | Ground clear controls. | 112 | 56.65 | 786.32
7868 | TIN-INTERP | Interpolated Ground | 50326.8 | 4.93 | 734.98 | 0 | 45.64 | 0 | OK | Ground clear controls. | 112 | 56.65 | 780.62
7869 | TIN-INTERP | Interpolated Ground | 50326.86 | -5 | 734.18 | 0 | 46.32 | 0 | OK | Ground clear controls. | 112 | 56.65 | 780.5
7870 | TIN-INTERP | Interpolated Ground | 50366.57 | -4.51 | 737.36 | 0 | 56.65 | 0 | OK | Ground clear controls. | 112 | 56.65 | 794.01
7871 | TIN-INTERP | Interpolated Ground | 50366.59 | 4.44 | 739.17 | 0 | 55.42 | 0 | OK | Ground clear controls. | 112 | 55.42 | 794.59
7872 | TIN-INTERP | Interpolated Ground | 50366.75 | -6.52 | 737.03 | 0 | 51.98 | 0 | OK | Ground clear controls. | 112 | 51.98 | 789.01
7873 | TIN-INTERP | Interpolated Ground | 50366.76 | 6.45 | 739.53 | 0 | 50.11 | 0 | OK | Ground clear controls. | 112 | 50.11 | 789.64
7874 | TIN-INTERP | Interpolated Ground | 50366.8 | 4.95 | 739.31 | 0 | 44.63 | 0 | OK | Ground clear controls. | 112 | 47.8 | 783.94
7875 | TIN-INTERP | Interpolated Ground | 50366.86 | -5.02 | 737.32 | 0 | 46.52 | 0 | OK | Ground clear controls. | 112 | 47.8 | 783.84
7876 | TIN-INTERP | Interpolated Ground | 50406.57 | -4.53 | 751.12 | 0 | 47.33 | 0 | OK | Ground clear controls. | 112 | 47.8 | 798.45
7877 | TIN-INTERP | Interpolated Ground | 50406.59 | 4.46 | 751.15 | 0 | 47.8 | 0 | OK | Ground clear controls. | 112 | 47.8 | 798.95
7878 | TIN-INTERP | Interpolated Ground | 50406.75 | -6.54 | 751.04 | 0 | 42.36 | 0 | OK | Ground clear controls. | 112 | 42.62 | 793.4
7879 | TIN-INTERP | Interpolated Ground | 50406.76 | 6.47 | 751.32 | 0 | 42.62 | 0 | OK | Ground clear controls. | 112 | 42.62 | 793.94
7880 | TIN-INTERP | Interpolated Ground | 50406.8 | 4.97 | 751.23 | 0 | 37.04 | 0 | OK | Ground clear controls. | 112 | 37.75 | 788.27
7881 | TIN-INTERP | Interpolated Ground | 50406.86 | -5.04 | 751.21 | 0 | 36.99 | 0 | OK | Ground clear controls. | 112 | 37.75 | 788.2
7882 | TIN-INTERP | Interpolated Ground | 50446.57 | -4.55 | 766.16 | 0 | 37.75 | 0 | OK | Ground clear controls. | 112 | 37.75 | 803.91
7883 | TIN-INTERP | Interpolated Ground | 50446.59 | 4.48 | 767.6 | 0 | 36.73 | 0 | OK | Ground clear controls. | 112 | 36.73 | 804.33
7884 | TIN-INTERP | Interpolated Ground | 50446.75 | -6.56 | 766.12 | 0 | 32.68 | 0 | OK | Ground clear controls. | 112 | 32.68 | 798.8
7885 | TIN-INTERP | Interpolated Ground | 50446.76 | 6.49 | 767.61 | 0 | 31.65 | 0 | OK | Ground clear controls. | 112 | 31.65 | 799.26
7886 | TIN-INTERP | Interpolated Ground | 50446.8 | 4.99 | 767.66 | 0 | 25.94 | 0 | OK | Ground clear controls. | 112 | 29.32 | 793.6
7887 | TIN-INTERP | Interpolated Ground | 50446.86 | -5.06 | 766.14 | 0 | 27.42 | 0 | OK | Ground clear controls. | 112 | 29.32 | 793.56
7888 | TIN-INTERP | Interpolated Ground | 50486.57 | -4.57 | 781.09 | 0 | 29.32 | 0 | OK | Ground clear controls. | 112 | 29.32 | 810.41
7889 | TIN-INTERP | Interpolated Ground | 50486.59 | 4.5 | 781.94 | 0 | 28.79 | 0 | OK | Ground clear controls. | 112 | 28.79 | 810.73
7890 | TIN-INTERP | Interpolated Ground | 50486.75 | -6.58 | 780.8 | 0 | 24.43 | 0 | OK | Ground clear controls. | 112 | 26.91 | 805.23
7891 | TIN-INTERP | Interpolated Ground | 50486.76 | 6.5 | 782.18 | 0 | 23.39 | 0 | OK | Ground clear controls. | 112 | 26.91 | 805.57
7892 | TIN-INTERP | Interpolated Ground | 50486.8 | 5 | 782.1 | 0 | 17.85 | 0 | OK | Ground clear controls. | 112 | 26.91 | 799.95
7893 | TIN-INTERP | Interpolated Ground | 50486.86 | -5.08 | 781.14 | 0 | 18.78 | 0 | OK | Ground clear controls. | 112 | 26.91 | 799.92
7894 | TIN-INTERP | Interpolated Ground | 50526.57 | -4.6 | 795.27 | 0 | 22.69 | 0 | OK | Ground clear controls. | 112 | 26.91 | 817.96
7895 | TIN-INTERP | Interpolated Ground | 50526.59 | 4.52 | 797.33 | 0 | 20.84 | 0 | OK | Ground clear controls. | 112 | 26.91 | 818.17
7896 | TIN-INTERP | Interpolated Ground | 50526.75 | -6.6 | 795.29 | 0 | 17.41 | 0 | OK | Ground clear controls. | 112 | 26.91 | 812.7
7897 | TIN-INTERP | Interpolated Ground | 50526.76 | 6.52 | 797.77 | 0 | 15.14 | 0 | OK | Ground clear controls. | 112 | 26.91 | 812.91
7898 | TIN-INTERP | Interpolated Ground | 50526.8 | 5.02 | 797.53 | 0 | 9.8 | 0 | OK | Ground clear controls. | 112 | 26.91 | 807.33
7899 | TIN-INTERP | Interpolated Ground | 50526.86 | -5.1 | 795.39 | 0 | 11.94 | 0 | OK | Ground clear controls. | 112 | 26.91 | 807.33
7900 | TIN-INTERP | Interpolated Ground | 50566.57 | -4.62 | 799.63 | 0 | 26.91 | 0 | OK | Ground clear controls. | 112 | 26.91 | 826.54
7901 | TIN-INTERP | Interpolated Ground | 50566.59 | 4.54 | 801.07 | 0 | 25.55 | 0 | OK | Ground clear controls. | 112 | 25.55 | 826.62
7902 | TIN-INTERP | Interpolated Ground | 50566.75 | -6.62 | 799.16 | 0 | 22.03 | 0 | OK | Ground clear controls. | 112 | 22.03 | 821.19
7903 | TIN-INTERP | Interpolated Ground | 50566.76 | 6.54 | 801.43 | 0 | 19.84 | 0 | OK | Ground clear controls. | 112 | 19.84 | 821.27
7904 | TIN-INTERP | Interpolated Ground | 50566.8 | 5.04 | 801.16 | 0 | 14.55 | 0 | OK | Ground clear controls. | 112 | 16.09 | 815.71
7905 | TIN-INTERP | Interpolated Ground | 50566.86 | -5.12 | 799.66 | 0 | 16.09 | 0 | OK | Ground clear controls. | 112 | 16.09 | 815.75
7906 | TIN-INTERP | Interpolated Ground | 50597.68 | -6.64 | 799.76 | 0 | 28.69 | 0 | OK | Ground clear controls. | 113 | 33.9 | 828.45
7907 | TIN-INTERP | Interpolated Ground | 50597.77 | -4.64 | 800.06 | 0 | 33.9 | 0 | OK | Ground clear controls. | 113 | 33.9 | 833.96
7908 | TIN-INTERP | Interpolated Ground | 50597.81 | 6.55 | 804.13 | 0 | 24.32 | 0 | OK | Ground clear controls. | 113 | 32.72 | 828.45
7909 | TIN-INTERP | Interpolated Ground | 50597.89 | -5.14 | 800.02 | 0 | 22.96 | 0 | OK | Ground clear controls. | 113 | 32.72 | 822.98
7910 | TIN-INTERP | Interpolated Ground | 50597.94 | 4.55 | 803.8 | 0 | 30.16 | 0 | OK | Ground clear controls. | 113 | 32.72 | 833.96
7911 | TIN-INTERP | Interpolated Ground | 50598.09 | 5.05 | 803.97 | 0 | 19.01 | 0 | OK | Ground clear controls. | 113 | 32.72 | 822.98
7912 | TIN-INTERP | Interpolated Ground | 50637.68 | -6.63 | 798.93 | 0 | 28.27 | 0 | OK | Ground clear controls. | 113 | 32.72 | 827.2
7913 | TIN-INTERP | Interpolated Ground | 50637.77 | -4.63 | 799.98 | 0 | 32.72 | 0 | OK | Ground clear controls. | 113 | 32.72 | 832.7
7914 | TIN-INTERP | Interpolated Ground | 50637.81 | 6.56 | 804.84 | 0 | 22.37 | 0 | OK | Ground clear controls. | 113 | 32.24 | 827.21
7915 | TIN-INTERP | Interpolated Ground | 50637.89 | -5.13 | 799.71 | 0 | 22.07 | 0 | OK | Ground clear controls. | 113 | 32.24 | 821.78
7916 | TIN-INTERP | Interpolated Ground | 50637.94 | 4.56 | 803.96 | 0 | 28.78 | 0 | OK | Ground clear controls. | 113 | 32.24 | 832.74
7917 | TIN-INTERP | Interpolated Ground | 50638.09 | 5.06 | 804.09 | 0 | 17.7 | 0 | OK | Ground clear controls. | 113 | 32.24 | 821.79
7918 | TIN-INTERP | Interpolated Ground | 50677.68 | -6.62 | 802.61 | 0 | 24.33 | 0 | OK | Ground clear controls. | 113 | 32.24 | 826.94
7919 | TIN-INTERP | Interpolated Ground | 50677.77 | -4.62 | 803.13 | 0 | 29.31 | 0 | OK | Ground clear controls. | 113 | 32.24 | 832.44
7920 | TIN-INTERP | Interpolated Ground | 50677.81 | 6.58 | 806.18 | 0 | 20.77 | 0 | OK | Ground clear controls. | 113 | 32.24 | 826.95
7921 | TIN-INTERP | Interpolated Ground | 50677.89 | -5.12 | 803.05 | 0 | 18.49 | 0 | OK | Ground clear controls. | 113 | 32.24 | 821.54
7922 | TIN-INTERP | Interpolated Ground | 50677.94 | 4.58 | 805.8 | 0 | 26.69 | 0 | OK | Ground clear controls. | 113 | 32.24 | 832.49
7923 | TIN-INTERP | Interpolated Ground | 50678.09 | 5.08 | 805.89 | 0 | 15.67 | 0 | OK | Ground clear controls. | 113 | 32.24 | 821.56
7924 | TIN-INTERP | Interpolated Ground | 50717.68 | -6.61 | 805.84 | 0 | 21.82 | 0 | OK | Ground clear controls. | 113 | 32.24 | 827.66
7925 | TIN-INTERP | Interpolated Ground | 50717.77 | -4.61 | 806.78 | 0 | 26.38 | 0 | OK | Ground clear controls. | 113 | 32.24 | 833.16
7926 | TIN-INTERP | Interpolated Ground | 50717.81 | 6.59 | 812.97 | 0 | 14.71 | 0 | OK | Ground clear controls. | 113 | 32.24 | 827.68
7927 | TIN-INTERP | Interpolated Ground | 50717.89 | -5.11 | 806.54 | 0 | 15.71 | 0 | OK | Ground clear controls. | 113 | 32.24 | 822.25
7928 | TIN-INTERP | Interpolated Ground | 50717.94 | 4.59 | 812.3 | 0 | 20.9 | 0 | OK | Ground clear controls. | 113 | 32.24 | 833.2
7929 | TIN-INTERP | Interpolated Ground | 50718.09 | 5.09 | 812.54 | 0 | 9.74 | 0 | OK | Ground clear controls. | 113 | 32.24 | 822.28
7930 | TIN-INTERP | Interpolated Ground | 50757.68 | -6.6 | 800.76 | 0 | 28.61 | 0 | OK | Ground clear controls. | 113 | 32.24 | 829.37
7931 | TIN-INTERP | Interpolated Ground | 50757.77 | -4.6 | 802.63 | 0 | 32.24 | 0 | OK | Ground clear controls. | 113 | 32.24 | 834.87
7932 | TIN-INTERP | Interpolated Ground | 50757.81 | 6.6 | 805.69 | 0 | 23.68 | 0 | OK | Ground clear controls. | 113 | 29 | 829.37
7933 | TIN-INTERP | Interpolated Ground | 50757.89 | -5.1 | 802.22 | 0 | 21.7 | 0 | OK | Ground clear controls. | 113 | 29 | 823.92
7934 | TIN-INTERP | Interpolated Ground | 50757.94 | 4.6 | 805.9 | 0 | 29 | 0 | OK | Ground clear controls. | 113 | 29 | 834.9
7935 | TIN-INTERP | Interpolated Ground | 50758.09 | 5.1 | 805.87 | 0 | 18.07 | 0 | OK | Ground clear controls. | 113 | 18.07 | 823.94
7936 | TIN-INTERP | Interpolated Ground | 50779.34 | -5.09 | 802.71 | 0 | 22.5 | 0 | OK | Ground clear controls. | 114 | 35.45 | 825.21
7937 | TIN-INTERP | Interpolated Ground | 50779.35 | 5.11 | 805.41 | 0 | 19.8 | 0 | OK | Ground clear controls. | 114 | 35.45 | 825.21
7938 | TIN-INTERP | Interpolated Ground | 50779.49 | -6.59 | 801.92 | 0 | 28.79 | 0 | OK | Ground clear controls. | 114 | 35.45 | 830.71
7939 | TIN-INTERP | Interpolated Ground | 50779.49 | 6.61 | 805.48 | 0 | 25.23 | 0 | OK | Ground clear controls. | 114 | 35.45 | 830.71
7940 | TIN-INTERP | Interpolated Ground | 50779.5 | 4.61 | 805.37 | 0 | 30.84 | 0 | OK | Ground clear controls. | 114 | 35.45 | 836.21
7941 | TIN-INTERP | Interpolated Ground | 50779.52 | -4.59 | 802.88 | 0 | 33.33 | 0 | OK | Ground clear controls. | 114 | 35.45 | 836.21
7942 | TIN-INTERP | Interpolated Ground | 50819.34 | -5.1 | 792.19 | 0 | 24.41 | 0 | OK | Ground clear controls. | 114 | 35.45 | 816.6
7943 | TIN-INTERP | Interpolated Ground | 50819.36 | 5.12 | 794.06 | 0 | 22.56 | 0 | OK | Ground clear controls. | 114 | 35.45 | 816.62
7944 | TIN-INTERP | Interpolated Ground | 50819.48 | -6.6 | 791.83 | 0 | 30.23 | 0 | OK | Ground clear controls. | 114 | 35.45 | 822.06
7945 | TIN-INTERP | Interpolated Ground | 50819.5 | 6.62 | 794.5 | 0 | 27.57 | 0 | OK | Ground clear controls. | 114 | 35.45 | 822.07
7946 | TIN-INTERP | Interpolated Ground | 50819.5 | 4.61 | 794.01 | 0 | 33.59 | 0 | OK | Ground clear controls. | 114 | 35.45 | 827.6
7947 | TIN-INTERP | Interpolated Ground | 50819.52 | -4.6 | 792.11 | 0 | 35.45 | 0 | OK | Ground clear controls. | 114 | 35.45 | 827.56
7948 | TIN-INTERP | Interpolated Ground | 50859.34 | -5.11 | 787.72 | 0 | 21.27 | 0 | OK | Ground clear controls. | 114 | 35.18 | 808.99
7949 | TIN-INTERP | Interpolated Ground | 50859.36 | 5.12 | 791.31 | 0 | 17.71 | 0 | OK | Ground clear controls. | 114 | 35.18 | 809.02
7950 | TIN-INTERP | Interpolated Ground | 50859.48 | -6.61 | 787.34 | 0 | 27.06 | 0 | OK | Ground clear controls. | 114 | 35.18 | 814.4
7951 | TIN-INTERP | Interpolated Ground | 50859.5 | 6.62 | 791.61 | 0 | 22.83 | 0 | OK | Ground clear controls. | 114 | 35.18 | 814.44
7952 | TIN-INTERP | Interpolated Ground | 50859.5 | 4.62 | 791.01 | 0 | 28.98 | 0 | OK | Ground clear controls. | 114 | 35.18 | 819.99
7953 | TIN-INTERP | Interpolated Ground | 50859.52 | -4.61 | 787.86 | 0 | 32.05 | 0 | OK | Ground clear controls. | 114 | 35.18 | 819.91
7954 | TIN-INTERP | Interpolated Ground | 50899.34 | -5.12 | 783.13 | 0 | 19.23 | 0 | OK | Ground clear controls. | 114 | 35.18 | 802.36
7955 | TIN-INTERP | Interpolated Ground | 50899.36 | 5.13 | 786.99 | 0 | 15.42 | 0 | OK | Ground clear controls. | 114 | 35.18 | 802.41
7956 | TIN-INTERP | Interpolated Ground | 50899.48 | -6.62 | 782.35 | 0 | 25.41 | 0 | OK | Ground clear controls. | 114 | 35.18 | 807.76
7957 | TIN-INTERP | Interpolated Ground | 50899.5 | 6.63 | 787.55 | 0 | 20.26 | 0 | OK | Ground clear controls. | 114 | 35.18 | 807.81
7958 | TIN-INTERP | Interpolated Ground | 50899.5 | 4.62 | 786.8 | 0 | 26.56 | 0 | OK | Ground clear controls. | 114 | 35.18 | 813.36
7959 | TIN-INTERP | Interpolated Ground | 50899.52 | -4.62 | 783.36 | 0 | 29.91 | 0 | OK | Ground clear controls. | 114 | 35.18 | 813.27
7960 | TIN-INTERP | Interpolated Ground | 50939.34 | -5.13 | 777.76 | 0 | 18.96 | 0 | OK | Ground clear controls. | 114 | 35.18 | 796.72
7961 | TIN-INTERP | Interpolated Ground | 50939.36 | 5.13 | 777.98 | 0 | 18.8 | 0 | OK | Ground clear controls. | 114 | 35.18 | 796.78
7962 | TIN-INTERP | Interpolated Ground | 50939.48 | -6.63 | 777.36 | 0 | 24.76 | 0 | OK | Ground clear controls. | 114 | 35.18 | 802.12
7963 | TIN-INTERP | Interpolated Ground | 50939.5 | 6.63 | 778.28 | 0 | 23.89 | 0 | OK | Ground clear controls. | 114 | 35.18 | 802.17
7964 | TIN-INTERP | Interpolated Ground | 50939.5 | 4.63 | 777.93 | 0 | 29.79 | 0 | OK | Ground clear controls. | 114 | 35.18 | 807.72
7965 | TIN-INTERP | Interpolated Ground | 50939.52 | -4.62 | 777.9 | 0 | 29.73 | 0 | OK | Ground clear controls. | 114 | 35.18 | 807.63
7966 | TIN-INTERP | Interpolated Ground | 50979.34 | -5.14 | 767.64 | 0 | 24.43 | 0 | OK | Ground clear controls. | 114 | 35.18 | 792.07
7967 | TIN-INTERP | Interpolated Ground | 50979.36 | 5.14 | 771.53 | 0 | 20.6 | 0 | OK | Ground clear controls. | 114 | 35.18 | 792.13
7968 | TIN-INTERP | Interpolated Ground | 50979.48 | -6.64 | 767.46 | 0 | 30.02 | 0 | OK | Ground clear controls. | 114 | 35.18 | 797.48
7969 | TIN-INTERP | Interpolated Ground | 50979.5 | 6.64 | 772.07 | 0 | 25.45 | 0 | OK | Ground clear controls. | 114 | 35.18 | 797.52
7970 | TIN-INTERP | Interpolated Ground | 50979.5 | 4.64 | 771.36 | 0 | 31.72 | 0 | OK | Ground clear controls. | 114 | 35.18 | 803.08
7971 | TIN-INTERP | Interpolated Ground | 50979.52 | -4.63 | 767.81 | 0 | 35.18 | 0 | OK | Ground clear controls. | 114 | 35.18 | 802.99
7972 | TIN-INTERP | Interpolated Ground | 51019.34 | -5.14 | 770.84 | 0 | 17.57 | 0 | OK | Ground clear controls. | 114 | 28.76 | 788.41
7973 | TIN-INTERP | Interpolated Ground | 51019.36 | 5.15 | 771.52 | 0 | 16.92 | 0 | OK | Ground clear controls. | 114 | 28.76 | 788.44
7974 | TIN-INTERP | Interpolated Ground | 51019.48 | -6.65 | 770.63 | 0 | 23.2 | 0 | OK | Ground clear controls. | 114 | 28.76 | 793.83
7975 | TIN-INTERP | Interpolated Ground | 51019.5 | 6.65 | 771.63 | 0 | 22.24 | 0 | OK | Ground clear controls. | 114 | 28.76 | 793.87
7976 | TIN-INTERP | Interpolated Ground | 51019.5 | 4.64 | 771.52 | 0 | 27.89 | 0 | OK | Ground clear controls. | 114 | 28.76 | 799.41
7977 | TIN-INTERP | Interpolated Ground | 51019.52 | -4.64 | 770.9 | 0 | 28.44 | 0 | OK | Ground clear controls. | 114 | 28.76 | 799.34
7978 | TIN-INTERP | Interpolated Ground | 51059.34 | -5.15 | 769.62 | 0 | 16.1 | 0 | OK | Ground clear controls. | 114 | 28.76 | 785.72
7979 | TIN-INTERP | Interpolated Ground | 51059.36 | 5.15 | 767.93 | 0 | 17.81 | 0 | OK | Ground clear controls. | 114 | 28.76 | 785.74
7980 | TIN-INTERP | Interpolated Ground | 51059.48 | -6.65 | 769.74 | 0 | 21.44 | 0 | OK | Ground clear controls. | 114 | 28.76 | 791.18
7981 | TIN-INTERP | Interpolated Ground | 51059.5 | 6.65 | 767.95 | 0 | 23.25 | 0 | OK | Ground clear controls. | 114 | 28.76 | 791.2
7982 | TIN-INTERP | Interpolated Ground | 51059.5 | 4.65 | 767.95 | 0 | 28.76 | 0 | OK | Ground clear controls. | 114 | 28.76 | 796.71
7983 | TIN-INTERP | Interpolated Ground | 51059.52 | -4.65 | 769.61 | 0 | 27.07 | 0 | OK | Ground clear controls. | 114 | 27.07 | 796.68
7984 | TIN-INTERP | Interpolated Ground | 51088.28 | -5.16 | 769.12 | 0 | 15.27 | 0 | OK | Ground clear controls. | 115 | 54.82 | 784.39
7985 | TIN-INTERP | Interpolated Ground | 51088.38 | -6.66 | 769.05 | 0 | 20.82 | 0 | OK | Ground clear controls. | 115 | 54.82 | 789.87
7986 | TIN-INTERP | Interpolated Ground | 51088.39 | -4.65 | 769.11 | 0 | 26.26 | 0 | OK | Ground clear controls. | 115 | 54.82 | 795.37
7987 | TIN-INTERP | Interpolated Ground | 51088.4 | 5.16 | 767.59 | 0 | 16.8 | 0 | OK | Ground clear controls. | 115 | 54.82 | 784.39
7988 | TIN-INTERP | Interpolated Ground | 51088.48 | 6.66 | 767.24 | 0 | 22.64 | 0 | OK | Ground clear controls. | 115 | 54.82 | 789.88
7989 | TIN-INTERP | Interpolated Ground | 51088.52 | 4.65 | 767.71 | 0 | 27.66 | 0 | OK | Ground clear controls. | 115 | 54.82 | 795.37
7990 | TIN-INTERP | Interpolated Ground | 51128.28 | -5.32 | 760.67 | 0 | 16.01 | 0 | OK | Ground clear controls. | 115 | 54.82 | 776.68
7991 | TIN-INTERP | Interpolated Ground | 51128.38 | -6.82 | 760.09 | 0 | 22.12 | 0 | OK | Ground clear controls. | 115 | 54.82 | 782.21
7992 | TIN-INTERP | Interpolated Ground | 51128.39 | -4.79 | 760.79 | 0 | 27.02 | 0 | OK | Ground clear controls. | 115 | 54.82 | 787.81
7993 | TIN-INTERP | Interpolated Ground | 51128.4 | 5.32 | 762.77 | 0 | 13.94 | 0 | OK | Ground clear controls. | 115 | 54.82 | 776.71
7994 | TIN-INTERP | Interpolated Ground | 51128.47 | 6.82 | 762.91 | 0 | 19.31 | 0 | OK | Ground clear controls. | 115 | 54.82 | 782.22
7995 | TIN-INTERP | Interpolated Ground | 51128.51 | 4.79 | 762.69 | 0 | 25.16 | 0 | OK | Ground clear controls. | 115 | 54.82 | 787.85
7996 | TIN-INTERP | Interpolated Ground | 51168.28 | -5.48 | 747.06 | 0 | 22.94 | 0 | OK | Ground clear controls. | 115 | 54.82 | 770
7997 | TIN-INTERP | Interpolated Ground | 51168.38 | -6.98 | 746.42 | 0 | 29.15 | 0 | OK | Ground clear controls. | 115 | 54.82 | 775.57
7998 | TIN-INTERP | Interpolated Ground | 51168.39 | -4.92 | 747.33 | 0 | 33.93 | 0 | OK | Ground clear controls. | 115 | 54.82 | 781.26
7999 | TIN-INTERP | Interpolated Ground | 51168.4 | 5.48 | 750.65 | 0 | 19.41 | 0 | OK | Ground clear controls. | 115 | 54.82 | 770.06
8000 | TIN-INTERP | Interpolated Ground | 51168.47 | 6.99 | 750.72 | 0 | 24.87 | 0 | OK | Ground clear controls. | 115 | 54.82 | 775.59
8001 | TIN-INTERP | Interpolated Ground | 51168.51 | 4.93 | 750.63 | 0 | 30.71 | 0 | OK | Ground clear controls. | 115 | 54.82 | 781.34
8002 | TIN-INTERP | Interpolated Ground | 51208.28 | -5.63 | 732.12 | 0 | 32.2 | 0 | OK | Ground clear controls. | 115 | 54.82 | 764.32
8003 | TIN-INTERP | Interpolated Ground | 51208.38 | -7.13 | 731.62 | 0 | 38.32 | 0 | OK | Ground clear controls. | 115 | 54.82 | 769.94
8004 | TIN-INTERP | Interpolated Ground | 51208.39 | -5.06 | 732.28 | 0 | 43.44 | 0 | OK | Ground clear controls. | 115 | 54.82 | 775.72
8005 | TIN-INTERP | Interpolated Ground | 51208.4 | 5.65 | 737.95 | 0 | 26.44 | 0 | OK | Ground clear controls. | 115 | 54.82 | 764.39
8006 | TIN-INTERP | Interpolated Ground | 51208.47 | 7.15 | 738.65 | 0 | 31.33 | 0 | OK | Ground clear controls. | 115 | 54.82 | 769.98
8007 | TIN-INTERP | Interpolated Ground | 51208.51 | 5.08 | 737.66 | 0 | 38.18 | 0 | OK | Ground clear controls. | 115 | 54.82 | 775.84
8008 | TIN-INTERP | Interpolated Ground | 51248.28 | -5.79 | 731.61 | 0 | 28.06 | 0 | OK | Ground clear controls. | 115 | 54.82 | 759.67
8009 | TIN-INTERP | Interpolated Ground | 51248.38 | -7.29 | 730.97 | 0 | 34.36 | 0 | OK | Ground clear controls. | 115 | 54.82 | 765.33
8010 | TIN-INTERP | Interpolated Ground | 51248.39 | -5.2 | 731.86 | 0 | 39.36 | 0 | OK | Ground clear controls. | 115 | 54.82 | 771.22
8011 | TIN-INTERP | Interpolated Ground | 51248.4 | 5.81 | 735.84 | 0 | 23.9 | 0 | OK | Ground clear controls. | 115 | 54.82 | 759.74
8012 | TIN-INTERP | Interpolated Ground | 51248.47 | 7.32 | 736.12 | 0 | 29.26 | 0 | OK | Ground clear controls. | 115 | 54.82 | 765.38
8013 | TIN-INTERP | Interpolated Ground | 51248.51 | 5.22 | 735.7 | 0 | 35.62 | 0 | OK | Ground clear controls. | 115 | 54.82 | 771.32
8014 | TIN-INTERP | Interpolated Ground | 51288.28 | -5.95 | 729.38 | 0 | 26.64 | 0 | OK | Ground clear controls. | 115 | 54.82 | 756.02
8015 | TIN-INTERP | Interpolated Ground | 51288.38 | -7.45 | 729.07 | 0 | 32.68 | 0 | OK | Ground clear controls. | 115 | 54.82 | 761.75
8016 | TIN-INTERP | Interpolated Ground | 51288.39 | -5.33 | 729.47 | 0 | 38.23 | 0 | OK | Ground clear controls. | 115 | 54.82 | 767.7
8017 | TIN-INTERP | Interpolated Ground | 51288.4 | 5.98 | 728.23 | 0 | 27.85 | 0 | OK | Ground clear controls. | 115 | 54.82 | 756.08
8018 | TIN-INTERP | Interpolated Ground | 51288.47 | 7.48 | 727.78 | 0 | 34 | 0 | OK | Ground clear controls. | 115 | 54.82 | 761.78
8019 | TIN-INTERP | Interpolated Ground | 51288.51 | 5.36 | 728.55 | 0 | 39.25 | 0 | OK | Ground clear controls. | 115 | 54.82 | 767.8
8020 | TIN-INTERP | Interpolated Ground | 51328.28 | -6.11 | 718.3 | 0 | 35.08 | 0 | OK | Ground clear controls. | 115 | 54.82 | 753.38
8021 | TIN-INTERP | Interpolated Ground | 51328.38 | -7.61 | 719.58 | 0 | 39.58 | 0 | OK | Ground clear controls. | 115 | 54.82 | 759.16
8022 | TIN-INTERP | Interpolated Ground | 51328.39 | -5.47 | 717.69 | 0 | 47.53 | 0 | OK | Ground clear controls. | 115 | 54.82 | 765.22
8023 | TIN-INTERP | Interpolated Ground | 51328.4 | 6.14 | 710.16 | 0 | 43.27 | 0 | OK | Ground clear controls. | 115 | 54.82 | 753.43
8024 | TIN-INTERP | Interpolated Ground | 51328.47 | 7.65 | 709.27 | 0 | 49.92 | 0 | OK | Ground clear controls. | 115 | 54.82 | 759.19
8025 | TIN-INTERP | Interpolated Ground | 51328.51 | 5.5 | 710.47 | 0 | 54.82 | 0 | OK | Ground clear controls. | 115 | 54.82 | 765.29
8026 | TIN-INTERP | Interpolated Ground | 51368.28 | -6.27 | 717.3 | 0 | 34.44 | 0 | OK | Ground clear controls. | 115 | 45.89 | 751.74
8027 | TIN-INTERP | Interpolated Ground | 51368.38 | -7.77 | 716.8 | 0 | 40.8 | 0 | OK | Ground clear controls. | 115 | 45.89 | 757.6
8028 | TIN-INTERP | Interpolated Ground | 51368.39 | -5.6 | 717.84 | 0 | 45.89 | 0 | OK | Ground clear controls. | 115 | 45.89 | 763.73
8029 | TIN-INTERP | Interpolated Ground | 51368.4 | 6.31 | 722.04 | 0 | 29.72 | 0 | OK | Ground clear controls. | 115 | 41.77 | 751.76
8030 | TIN-INTERP | Interpolated Ground | 51368.47 | 7.81 | 722.39 | 0 | 35.22 | 0 | OK | Ground clear controls. | 115 | 41.77 | 757.61
8031 | TIN-INTERP | Interpolated Ground | 51368.51 | 5.65 | 721.99 | 0 | 41.77 | 0 | OK | Ground clear controls. | 115 | 41.77 | 763.76
8032 | TIN-INTERP | Interpolated Ground | 51400.03 | -5.71 | 720.49 | 0 | 42.77 | 0 | OK | Ground clear controls. | 116 | 59.75 | 763.26
8033 | TIN-INTERP | Interpolated Ground | 51400.04 | 7.94 | 720.87 | 0 | 36.19 | 0 | OK | Ground clear controls. | 116 | 59.75 | 757.06
8034 | TIN-INTERP | Interpolated Ground | 51400.07 | 5.76 | 720.76 | 0 | 42.5 | 0 | OK | Ground clear controls. | 116 | 59.75 | 763.26
8035 | TIN-INTERP | Interpolated Ground | 51400.07 | -7.89 | 720.58 | 0 | 36.49 | 0 | OK | Ground clear controls. | 116 | 59.75 | 757.07
8036 | TIN-INTERP | Interpolated Ground | 51400.11 | -6.39 | 720.53 | 0 | 30.63 | 0 | OK | Ground clear controls. | 116 | 59.75 | 751.16
8037 | TIN-INTERP | Interpolated Ground | 51400.11 | 6.44 | 720.79 | 0 | 30.37 | 0 | OK | Ground clear controls. | 116 | 59.75 | 751.16
8038 | TIN-INTERP | Interpolated Ground | 51440.03 | -5.62 | 707.27 | 0 | 50.04 | 0 | OK | Ground clear controls. | 116 | 59.75 | 757.31
8039 | TIN-INTERP | Interpolated Ground | 51440.04 | 7.81 | 711.42 | 0 | 39.81 | 0 | OK | Ground clear controls. | 116 | 59.75 | 751.23
8040 | TIN-INTERP | Interpolated Ground | 51440.07 | -7.79 | 706.86 | 0 | 44.28 | 0 | OK | Ground clear controls. | 116 | 59.75 | 751.14
8041 | TIN-INTERP | Interpolated Ground | 51440.07 | 5.64 | 710.65 | 0 | 46.82 | 0 | OK | Ground clear controls. | 116 | 59.75 | 757.47
8042 | TIN-INTERP | Interpolated Ground | 51440.11 | -6.29 | 707.08 | 0 | 38.24 | 0 | OK | Ground clear controls. | 116 | 59.75 | 745.32
8043 | TIN-INTERP | Interpolated Ground | 51440.11 | 6.31 | 710.97 | 0 | 34.48 | 0 | OK | Ground clear controls. | 116 | 59.75 | 745.45
8044 | TIN-INTERP | Interpolated Ground | 51480.03 | -5.53 | 693.28 | 0 | 59.1 | 0 | OK | Ground clear controls. | 116 | 59.75 | 752.38
8045 | TIN-INTERP | Interpolated Ground | 51480.04 | 7.69 | 692.97 | 0 | 53.44 | 0 | OK | Ground clear controls. | 116 | 59.75 | 746.41
8046 | TIN-INTERP | Interpolated Ground | 51480.07 | -7.69 | 693.17 | 0 | 53.09 | 0 | OK | Ground clear controls. | 116 | 59.75 | 746.26
8047 | TIN-INTERP | Interpolated Ground | 51480.07 | 5.53 | 692.95 | 0 | 59.75 | 0 | OK | Ground clear controls. | 116 | 59.75 | 752.7
8048 | TIN-INTERP | Interpolated Ground | 51480.11 | -6.2 | 693.27 | 0 | 47.25 | 0 | OK | Ground clear controls. | 116 | 56.77 | 740.52
8049 | TIN-INTERP | Interpolated Ground | 51480.11 | 6.18 | 692.98 | 0 | 47.77 | 0 | OK | Ground clear controls. | 116 | 56.77 | 740.75
8050 | TIN-INTERP | Interpolated Ground | 51520.03 | -5.44 | 691.99 | 0 | 56.48 | 0 | OK | Ground clear controls. | 116 | 56.77 | 748.47
8051 | TIN-INTERP | Interpolated Ground | 51520.04 | 7.56 | 692.07 | 0 | 50.55 | 0 | OK | Ground clear controls. | 116 | 56.77 | 742.62
8052 | TIN-INTERP | Interpolated Ground | 51520.07 | -7.59 | 692 | 0 | 50.41 | 0 | OK | Ground clear controls. | 116 | 56.77 | 742.41
8053 | TIN-INTERP | Interpolated Ground | 51520.07 | 5.41 | 692.15 | 0 | 56.77 | 0 | OK | Ground clear controls. | 116 | 56.77 | 748.92
8054 | TIN-INTERP | Interpolated Ground | 51520.11 | -6.1 | 691.99 | 0 | 44.73 | 0 | OK | Ground clear controls. | 116 | 56.63 | 736.72
8055 | TIN-INTERP | Interpolated Ground | 51520.11 | 6.05 | 692.11 | 0 | 44.94 | 0 | OK | Ground clear controls. | 116 | 56.63 | 737.05
8056 | TIN-INTERP | Interpolated Ground | 51560.03 | -5.35 | 693.28 | 0 | 52.33 | 0 | OK | Ground clear controls. | 116 | 56.63 | 745.61
8057 | TIN-INTERP | Interpolated Ground | 51560.04 | 7.43 | 692.79 | 0 | 47.07 | 0 | OK | Ground clear controls. | 116 | 56.63 | 739.86
8058 | TIN-INTERP | Interpolated Ground | 51560.07 | -7.49 | 693.23 | 0 | 46.36 | 0 | OK | Ground clear controls. | 116 | 56.63 | 739.59
8059 | TIN-INTERP | Interpolated Ground | 51560.07 | 5.3 | 692.84 | 0 | 53.35 | 0 | OK | Ground clear controls. | 116 | 56.63 | 746.19
8060 | TIN-INTERP | Interpolated Ground | 51560.11 | -6 | 693.27 | 0 | 40.7 | 0 | OK | Ground clear controls. | 116 | 56.63 | 733.97
8061 | TIN-INTERP | Interpolated Ground | 51560.11 | 5.92 | 692.83 | 0 | 41.55 | 0 | OK | Ground clear controls. | 116 | 56.63 | 734.38
8062 | TIN-INTERP | Interpolated Ground | 51600.03 | -5.26 | 693.38 | 0 | 50.4 | 0 | OK | Ground clear controls. | 116 | 56.63 | 743.78
8063 | TIN-INTERP | Interpolated Ground | 51600.04 | 7.3 | 693.25 | 0 | 44.88 | 0 | OK | Ground clear controls. | 116 | 56.63 | 738.13
8064 | TIN-INTERP | Interpolated Ground | 51600.07 | -7.39 | 693.34 | 0 | 44.46 | 0 | OK | Ground clear controls. | 116 | 56.63 | 737.8
8065 | TIN-INTERP | Interpolated Ground | 51600.07 | 5.18 | 693.23 | 0 | 51.21 | 0 | OK | Ground clear controls. | 116 | 56.63 | 744.44
8066 | TIN-INTERP | Interpolated Ground | 51600.11 | -5.9 | 693.37 | 0 | 38.86 | 0 | OK | Ground clear controls. | 116 | 56.63 | 732.23
8067 | TIN-INTERP | Interpolated Ground | 51600.11 | 5.8 | 693.21 | 0 | 39.51 | 0 | OK | Ground clear controls. | 116 | 56.63 | 732.72
8068 | TIN-INTERP | Interpolated Ground | 51640.03 | -5.16 | 693.46 | 0 | 49.5 | 0 | OK | Ground clear controls. | 116 | 56.63 | 742.96
8069 | TIN-INTERP | Interpolated Ground | 51640.04 | 7.17 | 693.13 | 0 | 44.28 | 0 | OK | Ground clear controls. | 116 | 56.63 | 737.41
8070 | TIN-INTERP | Interpolated Ground | 51640.07 | -7.29 | 693.46 | 0 | 43.57 | 0 | OK | Ground clear controls. | 116 | 56.63 | 737.03
8071 | TIN-INTERP | Interpolated Ground | 51640.07 | 5.07 | 693.23 | 0 | 50.48 | 0 | OK | Ground clear controls. | 116 | 56.63 | 743.71
8072 | TIN-INTERP | Interpolated Ground | 51640.11 | -5.81 | 693.48 | 0 | 38.03 | 0 | OK | Ground clear controls. | 116 | 56.63 | 731.51
8073 | TIN-INTERP | Interpolated Ground | 51640.11 | 5.67 | 693.23 | 0 | 38.83 | 0 | OK | Ground clear controls. | 116 | 56.63 | 732.06
8074 | TIN-INTERP | Interpolated Ground | 51680.03 | -5.07 | 693.39 | 0 | 49.8 | 0 | OK | Ground clear controls. | 116 | 56.63 | 743.19
8075 | TIN-INTERP | Interpolated Ground | 51680.04 | 7.04 | 692.74 | 0 | 44.98 | 0 | OK | Ground clear controls. | 116 | 56.63 | 737.72
8076 | TIN-INTERP | Interpolated Ground | 51680.07 | -7.19 | 693.4 | 0 | 43.89 | 0 | OK | Ground clear controls. | 116 | 56.63 | 737.29
8077 | TIN-INTERP | Interpolated Ground | 51680.07 | 4.95 | 692.85 | 0 | 51.14 | 0 | OK | Ground clear controls. | 116 | 56.63 | 743.99
8078 | TIN-INTERP | Interpolated Ground | 51680.11 | -5.71 | 693.43 | 0 | 38.39 | 0 | OK | Ground clear controls. | 116 | 56.63 | 731.82
8079 | TIN-INTERP | Interpolated Ground | 51680.11 | 5.54 | 692.83 | 0 | 39.6 | 0 | OK | Ground clear controls. | 116 | 56.63 | 732.43
8080 | TIN-INTERP | Interpolated Ground | 51720.03 | -4.98 | 698.73 | 0 | 45.72 | 0 | OK | Ground clear controls. | 116 | 56.63 | 744.45
8081 | TIN-INTERP | Interpolated Ground | 51720.04 | 6.91 | 693.45 | 0 | 45.61 | 0 | OK | Ground clear controls. | 116 | 56.63 | 739.06
8082 | TIN-INTERP | Interpolated Ground | 51720.07 | -7.09 | 699.93 | 0 | 38.65 | 0 | OK | Ground clear controls. | 116 | 56.63 | 738.58
8083 | TIN-INTERP | Interpolated Ground | 51720.07 | 4.84 | 693.53 | 0 | 51.75 | 0 | OK | Ground clear controls. | 116 | 56.63 | 745.28
8084 | TIN-INTERP | Interpolated Ground | 51720.11 | -5.61 | 699.14 | 0 | 34.01 | 0 | OK | Ground clear controls. | 116 | 56.63 | 733.15
8085 | TIN-INTERP | Interpolated Ground | 51720.11 | 5.41 | 693.48 | 0 | 40.31 | 0 | OK | Ground clear controls. | 116 | 56.63 | 733.79
8086 | TIN-INTERP | Interpolated Ground | 51760.03 | -4.89 | 718.44 | 0 | 28.28 | 0 | OK | Ground clear controls. | 116 | 56.63 | 746.72
8087 | TIN-INTERP | Interpolated Ground | 51760.04 | 6.79 | 719.27 | 0 | 22.14 | 0 | OK | Ground clear controls. | 116 | 56.63 | 741.41
8088 | TIN-INTERP | Interpolated Ground | 51760.07 | -6.99 | 718.85 | 0 | 22.05 | 0 | OK | Ground clear controls. | 116 | 56.63 | 740.9
8089 | TIN-INTERP | Interpolated Ground | 51760.07 | 4.72 | 719.3 | 0 | 28.27 | 0 | OK | Ground clear controls. | 116 | 56.63 | 747.57
8090 | TIN-INTERP | Interpolated Ground | 51760.11 | -5.51 | 718.6 | 0 | 16.9 | 0 | OK | Ground clear controls. | 116 | 56.63 | 735.5
8091 | TIN-INTERP | Interpolated Ground | 51760.11 | 5.28 | 719.29 | 0 | 16.87 | 0 | OK | Ground clear controls. | 116 | 56.63 | 736.16
8092 | TIN-INTERP | Interpolated Ground | 51800.03 | -4.8 | 719.1 | 0 | 30.95 | 0 | OK | Ground clear controls. | 116 | 56.63 | 750.05
8093 | TIN-INTERP | Interpolated Ground | 51800.04 | 6.66 | 718.93 | 0 | 25.87 | 0 | OK | Ground clear controls. | 116 | 56.63 | 744.8
8094 | TIN-INTERP | Interpolated Ground | 51800.07 | -6.88 | 719.09 | 0 | 25.17 | 0 | OK | Ground clear controls. | 116 | 56.63 | 744.26
8095 | TIN-INTERP | Interpolated Ground | 51800.07 | 4.61 | 718.99 | 0 | 31.91 | 0 | OK | Ground clear controls. | 116 | 56.63 | 750.9
8096 | TIN-INTERP | Interpolated Ground | 51800.11 | -5.42 | 719.11 | 0 | 19.76 | 0 | OK | Ground clear controls. | 116 | 56.63 | 738.87
8097 | TIN-INTERP | Interpolated Ground | 51800.11 | 5.15 | 718.97 | 0 | 20.58 | 0 | OK | Ground clear controls. | 116 | 56.63 | 739.55
8098 | TIN-INTERP | Interpolated Ground | 51840.03 | -4.71 | 698.86 | 0 | 55.53 | 0 | OK | Ground clear controls. | 116 | 56.63 | 754.39
8099 | TIN-INTERP | Interpolated Ground | 51840.04 | 6.53 | 698.86 | 0 | 50.35 | 0 | OK | Ground clear controls. | 116 | 56.63 | 749.21
8100 | TIN-INTERP | Interpolated Ground | 51840.07 | -6.78 | 698.9 | 0 | 49.74 | 0 | OK | Ground clear controls. | 116 | 56.63 | 748.64
8101 | TIN-INTERP | Interpolated Ground | 51840.07 | 4.49 | 698.59 | 0 | 56.63 | 0 | OK | Ground clear controls. | 116 | 56.63 | 755.22
8102 | TIN-INTERP | Interpolated Ground | 51840.11 | -5.32 | 698.91 | 0 | 44.37 | 0 | OK | Ground clear controls. | 116 | 49 | 743.28
8103 | TIN-INTERP | Interpolated Ground | 51840.11 | 5.03 | 698.58 | 0 | 45.37 | 0 | OK | Ground clear controls. | 116 | 49 | 743.95
8104 | TIN-INTERP | Interpolated Ground | 51880.03 | -4.62 | 719.1 | 0 | 40.67 | 0 | OK | Ground clear controls. | 116 | 49 | 759.77
8105 | TIN-INTERP | Interpolated Ground | 51880.04 | 6.4 | 718.95 | 0 | 35.7 | 0 | OK | Ground clear controls. | 116 | 49 | 754.65
8106 | TIN-INTERP | Interpolated Ground | 51880.07 | -6.68 | 718.92 | 0 | 35.14 | 0 | OK | Ground clear controls. | 116 | 49 | 754.06
8107 | TIN-INTERP | Interpolated Ground | 51880.07 | 4.38 | 718.94 | 0 | 41.61 | 0 | OK | Ground clear controls. | 116 | 49 | 760.55
8108 | TIN-INTERP | Interpolated Ground | 51880.11 | -5.22 | 719.15 | 0 | 29.54 | 0 | OK | Ground clear controls. | 116 | 49 | 748.69
8109 | TIN-INTERP | Interpolated Ground | 51880.11 | 4.9 | 718.94 | 0 | 30.43 | 0 | OK | Ground clear controls. | 116 | 49 | 749.37
8110 | TIN-INTERP | Interpolated Ground | 51920.03 | -4.53 | 717.94 | 0 | 48.26 | 0 | OK | Ground clear controls. | 116 | 49 | 766.2
8111 | TIN-INTERP | Interpolated Ground | 51920.04 | 6.27 | 718.04 | 0 | 43.08 | 0 | OK | Ground clear controls. | 116 | 49 | 761.12
8112 | TIN-INTERP | Interpolated Ground | 51920.07 | -6.58 | 718.1 | 0 | 42.42 | 0 | OK | Ground clear controls. | 116 | 49 | 760.52
8113 | TIN-INTERP | Interpolated Ground | 51920.07 | 4.26 | 717.91 | 0 | 49 | 0 | OK | Ground clear controls. | 116 | 49 | 766.91
8114 | TIN-INTERP | Interpolated Ground | 51920.1 | -5.12 | 717.99 | 0 | 37.17 | 0 | OK | Ground clear controls. | 116 | 38.52 | 755.16
8115 | TIN-INTERP | Interpolated Ground | 51920.11 | 4.77 | 717.92 | 0 | 37.89 | 0 | OK | Ground clear controls. | 116 | 38.52 | 755.81
8116 | TIN-INTERP | Interpolated Ground | 51960.03 | -4.44 | 736.25 | 0 | 37.41 | 0 | OK | Ground clear controls. | 116 | 38.52 | 773.66
8117 | TIN-INTERP | Interpolated Ground | 51960.04 | 6.14 | 735.52 | 0 | 33.12 | 0 | OK | Ground clear controls. | 116 | 38.52 | 768.64
8118 | TIN-INTERP | Interpolated Ground | 51960.07 | -6.48 | 737.13 | 0 | 30.89 | 0 | OK | Ground clear controls. | 116 | 38.52 | 768.02
8119 | TIN-INTERP | Interpolated Ground | 51960.07 | 4.15 | 735.78 | 0 | 38.52 | 0 | OK | Ground clear controls. | 116 | 38.52 | 774.3
8120 | TIN-INTERP | Interpolated Ground | 51960.1 | -5.03 | 736.67 | 0 | 25.99 | 0 | OK | Ground clear controls. | 116 | 32.11 | 762.66
8121 | TIN-INTERP | Interpolated Ground | 51960.11 | 4.64 | 735.74 | 0 | 27.53 | 0 | OK | Ground clear controls. | 116 | 32.11 | 763.27
8122 | TIN-INTERP | Interpolated Ground | 52000.03 | -4.34 | 752.96 | 0 | 29.21 | 0 | OK | Ground clear controls. | 116 | 32.11 | 782.17
8123 | TIN-INTERP | Interpolated Ground | 52000.04 | 6.01 | 752.21 | 0 | 24.99 | 0 | OK | Ground clear controls. | 116 | 32.11 | 777.2
8124 | TIN-INTERP | Interpolated Ground | 52000.07 | -6.38 | 752.88 | 0 | 23.68 | 0 | OK | Ground clear controls. | 116 | 32.11 | 776.56
8125 | TIN-INTERP | Interpolated Ground | 52000.07 | 4.03 | 752.31 | 0 | 30.4 | 0 | OK | Ground clear controls. | 116 | 32.11 | 782.71
8126 | TIN-INTERP | Interpolated Ground | 52000.1 | -4.93 | 752.99 | 0 | 18.21 | 0 | OK | Ground clear controls. | 116 | 32.11 | 771.2
8127 | TIN-INTERP | Interpolated Ground | 52000.11 | 4.51 | 752.31 | 0 | 19.46 | 0 | OK | Ground clear controls. | 116 | 32.11 | 771.77
8128 | TIN-INTERP | Interpolated Ground | 52040.03 | -4.25 | 759.64 | 0 | 32.11 | 0 | OK | Ground clear controls. | 116 | 32.11 | 791.75
8129 | TIN-INTERP | Interpolated Ground | 52040.07 | -6.28 | 759.63 | 0 | 26.54 | 0 | OK | Ground clear controls. | 116 | 31.84 | 786.17
8130 | TIN-INTERP | Interpolated Ground | 52040.07 | 3.92 | 760.32 | 0 | 31.84 | 0 | OK | Ground clear controls. | 116 | 31.84 | 792.16
8131 | TIN-INTERP | Interpolated Ground | 52040.1 | -4.83 | 759.73 | 0 | 21.05 | 0 | OK | Ground clear controls. | 116 | 21.05 | 780.78
8132 | TIN-INTERP | Interpolated Ground | 52047.26 | -6.28 | 760.14 | 0 | 26.81 | 0 | OK | Ground clear controls. | 117 | 50.6 | 786.95
8133 | TIN-INTERP | Interpolated Ground | 52047.4 | -4.21 | 760.13 | 0 | 32.32 | 0 | OK | Ground clear controls. | 117 | 50.6 | 792.45
8134 | TIN-INTERP | Interpolated Ground | 52047.61 | -4.82 | 760.15 | 0 | 21.3 | 0 | OK | Ground clear controls. | 117 | 50.6 | 781.45
8135 | TIN-INTERP | Interpolated Ground | 52049.22 | 3.9 | 760.08 | 0 | 32.36 | 0 | OK | Ground clear controls. | 117 | 50.6 | 792.44
8136 | TIN-INTERP | Interpolated Ground | 52049.69 | 4.35 | 759.95 | 0 | 21.51 | 0 | OK | Ground clear controls. | 117 | 50.6 | 781.46
8137 | TIN-INTERP | Interpolated Ground | 52050 | 5.82 | 759.69 | 0 | 27.26 | 0 | OK | Ground clear controls. | 117 | 50.6 | 786.95
8138 | TIN-INTERP | Interpolated Ground | 52087.26 | -6.31 | 760.89 | 0 | 19.44 | 0 | OK | Ground clear controls. | 117 | 50.6 | 780.33
8139 | TIN-INTERP | Interpolated Ground | 52087.4 | -4.24 | 760.3 | 0 | 25.49 | 0 | OK | Ground clear controls. | 117 | 50.6 | 785.79
8140 | TIN-INTERP | Interpolated Ground | 52087.61 | -4.85 | 760.56 | 0 | 14.29 | 0 | OK | Ground clear controls. | 117 | 50.6 | 774.85
8141 | TIN-INTERP | Interpolated Ground | 52089.22 | 3.94 | 758.47 | 0 | 27.25 | 0 | OK | Ground clear controls. | 117 | 50.6 | 785.72
8142 | TIN-INTERP | Interpolated Ground | 52089.69 | 4.39 | 758.51 | 0 | 16.36 | 0 | OK | Ground clear controls. | 117 | 50.6 | 774.87
8143 | TIN-INTERP | Interpolated Ground | 52090 | 5.87 | 758.35 | 0 | 21.96 | 0 | OK | Ground clear controls. | 117 | 50.6 | 780.31
8144 | TIN-INTERP | Interpolated Ground | 52127.26 | -6.33 | 759.59 | 0 | 15.1 | 0 | OK | Ground clear controls. | 117 | 50.6 | 774.69
8145 | TIN-INTERP | Interpolated Ground | 52127.4 | -4.27 | 759.12 | 0 | 21.02 | 0 | OK | Ground clear controls. | 117 | 50.6 | 780.14
8146 | TIN-INTERP | Interpolated Ground | 52127.61 | -4.87 | 759.18 | 0 | 10.06 | 0 | OK | Ground clear controls. | 117 | 50.6 | 769.24
8147 | TIN-INTERP | Interpolated Ground | 52129.22 | 3.98 | 757.8 | 0 | 22.21 | 0 | OK | Ground clear controls. | 117 | 50.6 | 780.01
8148 | TIN-INTERP | Interpolated Ground | 52129.69 | 4.44 | 757.63 | 0 | 11.65 | 0 | OK | Ground clear controls. | 117 | 50.6 | 769.28
8149 | TIN-INTERP | Interpolated Ground | 52130 | 5.91 | 757.25 | 0 | 17.42 | 0 | OK | Ground clear controls. | 117 | 50.6 | 774.67
8150 | TIN-INTERP | Interpolated Ground | 52167.26 | -6.36 | 752.36 | 0 | 17.69 | 0 | OK | Ground clear controls. | 117 | 50.6 | 770.05
8151 | TIN-INTERP | Interpolated Ground | 52167.4 | -4.3 | 752.05 | 0 | 23.42 | 0 | OK | Ground clear controls. | 117 | 50.6 | 775.47
8152 | TIN-INTERP | Interpolated Ground | 52167.61 | -4.89 | 752.08 | 0 | 12.53 | 0 | OK | Ground clear controls. | 117 | 50.6 | 764.61
8153 | TIN-INTERP | Interpolated Ground | 52169.22 | 4.03 | 750.27 | 0 | 25.02 | 0 | OK | Ground clear controls. | 117 | 50.6 | 775.29
8154 | TIN-INTERP | Interpolated Ground | 52169.69 | 4.49 | 750.15 | 0 | 14.52 | 0 | OK | Ground clear controls. | 117 | 50.6 | 764.67
8155 | TIN-INTERP | Interpolated Ground | 52170 | 5.96 | 749.87 | 0 | 20.15 | 0 | OK | Ground clear controls. | 117 | 50.6 | 770.02
8156 | TIN-INTERP | Interpolated Ground | 52207.26 | -6.39 | 740.36 | 0 | 26.03 | 0 | OK | Ground clear controls. | 117 | 50.6 | 766.39
8157 | TIN-INTERP | Interpolated Ground | 52207.4 | -4.33 | 740.36 | 0 | 31.42 | 0 | OK | Ground clear controls. | 117 | 50.6 | 771.78
8158 | TIN-INTERP | Interpolated Ground | 52207.61 | -4.92 | 740.28 | 0 | 20.68 | 0 | OK | Ground clear controls. | 117 | 50.6 | 760.96
8159 | TIN-INTERP | Interpolated Ground | 52209.22 | 4.07 | 740.09 | 0 | 31.49 | 0 | OK | Ground clear controls. | 117 | 50.6 | 771.58
8160 | TIN-INTERP | Interpolated Ground | 52209.69 | 4.53 | 740.03 | 0 | 21.01 | 0 | OK | Ground clear controls. | 117 | 50.6 | 761.04
8161 | TIN-INTERP | Interpolated Ground | 52210 | 6.01 | 740.07 | 0 | 26.29 | 0 | OK | Ground clear controls. | 117 | 50.6 | 766.36
8162 | TIN-INTERP | Interpolated Ground | 52247.26 | -6.41 | 727.87 | 0 | 35.84 | 0 | OK | Ground clear controls. | 117 | 50.6 | 763.71
8163 | TIN-INTERP | Interpolated Ground | 52247.4 | -4.36 | 728.02 | 0 | 41.07 | 0 | OK | Ground clear controls. | 117 | 50.6 | 769.09
8164 | TIN-INTERP | Interpolated Ground | 52247.61 | -4.94 | 727.96 | 0 | 30.33 | 0 | OK | Ground clear controls. | 117 | 50.6 | 758.29
8165 | TIN-INTERP | Interpolated Ground | 52249.22 | 4.11 | 727.83 | 0 | 41.05 | 0 | OK | Ground clear controls. | 117 | 50.6 | 768.88
8166 | TIN-INTERP | Interpolated Ground | 52249.69 | 4.58 | 727.74 | 0 | 30.65 | 0 | OK | Ground clear controls. | 117 | 50.6 | 758.39
8167 | TIN-INTERP | Interpolated Ground | 52250 | 6.06 | 727.53 | 0 | 36.16 | 0 | OK | Ground clear controls. | 117 | 50.6 | 763.69
8168 | TIN-INTERP | Interpolated Ground | 52287.26 | -6.44 | 716.66 | 0 | 45.35 | 0 | OK | Ground clear controls. | 117 | 50.6 | 762.01
8169 | TIN-INTERP | Interpolated Ground | 52287.4 | -4.4 | 716.78 | 0 | 50.6 | 0 | OK | Ground clear controls. | 117 | 50.6 | 767.38
8170 | TIN-INTERP | Interpolated Ground | 52287.61 | -4.97 | 716.63 | 0 | 39.97 | 0 | OK | Ground clear controls. | 117 | 50.43 | 756.6
8171 | TIN-INTERP | Interpolated Ground | 52289.22 | 4.15 | 716.74 | 0 | 50.43 | 0 | OK | Ground clear controls. | 117 | 50.43 | 767.17
8172 | TIN-INTERP | Interpolated Ground | 52289.69 | 4.63 | 716.62 | 0 | 40.1 | 0 | OK | Ground clear controls. | 117 | 47.87 | 756.72
8173 | TIN-INTERP | Interpolated Ground | 52290 | 6.11 | 716.5 | 0 | 45.51 | 0 | OK | Ground clear controls. | 117 | 47.87 | 762.01
8174 | TIN-INTERP | Interpolated Ground | 52327.26 | -6.47 | 718.83 | 0 | 42.46 | 0 | OK | Ground clear controls. | 117 | 47.87 | 761.29
8175 | TIN-INTERP | Interpolated Ground | 52327.4 | -4.43 | 718.79 | 0 | 47.87 | 0 | OK | Ground clear controls. | 117 | 47.87 | 766.66
8176 | TIN-INTERP | Interpolated Ground | 52327.61 | -4.99 | 718.79 | 0 | 37.09 | 0 | OK | Ground clear controls. | 117 | 47.83 | 755.88
8177 | TIN-INTERP | Interpolated Ground | 52329.22 | 4.2 | 719.25 | 0 | 47.21 | 0 | OK | Ground clear controls. | 117 | 47.83 | 766.46
8178 | TIN-INTERP | Interpolated Ground | 52329.69 | 4.67 | 719.25 | 0 | 36.78 | 0 | OK | Ground clear controls. | 117 | 47.83 | 756.03
8179 | TIN-INTERP | Interpolated Ground | 52330 | 6.16 | 719.2 | 0 | 42.12 | 0 | OK | Ground clear controls. | 117 | 47.83 | 761.32
8180 | TIN-INTERP | Interpolated Ground | 52367.26 | -6.49 | 719.63 | 0 | 41.93 | 0 | OK | Ground clear controls. | 117 | 47.83 | 761.56
8181 | TIN-INTERP | Interpolated Ground | 52367.4 | -4.46 | 719.52 | 0 | 47.41 | 0 | OK | Ground clear controls. | 117 | 47.83 | 766.93
8182 | TIN-INTERP | Interpolated Ground | 52367.61 | -5.01 | 719.54 | 0 | 36.61 | 0 | OK | Ground clear controls. | 117 | 47.83 | 756.15
8183 | TIN-INTERP | Interpolated Ground | 52369.22 | 4.24 | 719.42 | 0 | 47.33 | 0 | OK | Ground clear controls. | 117 | 47.83 | 766.75
8184 | TIN-INTERP | Interpolated Ground | 52369.69 | 4.72 | 719.45 | 0 | 36.87 | 0 | OK | Ground clear controls. | 117 | 47.83 | 756.32
8185 | TIN-INTERP | Interpolated Ground | 52370 | 6.2 | 719.38 | 0 | 42.24 | 0 | OK | Ground clear controls. | 117 | 47.83 | 761.62
8186 | TIN-INTERP | Interpolated Ground | 52407.26 | -6.52 | 720.6 | 0 | 42.19 | 0 | OK | Ground clear controls. | 117 | 47.83 | 762.79
8187 | TIN-INTERP | Interpolated Ground | 52407.4 | -4.49 | 720.5 | 0 | 47.67 | 0 | OK | Ground clear controls. | 117 | 47.83 | 768.17
8188 | TIN-INTERP | Interpolated Ground | 52407.61 | -5.04 | 720.53 | 0 | 36.86 | 0 | OK | Ground clear controls. | 117 | 47.83 | 757.39
8189 | TIN-INTERP | Interpolated Ground | 52409.22 | 4.28 | 720.2 | 0 | 47.83 | 0 | OK | Ground clear controls. | 117 | 47.83 | 768.03
8190 | TIN-INTERP | Interpolated Ground | 52409.69 | 4.76 | 720.23 | 0 | 37.35 | 0 | OK | Ground clear controls. | 117 | 45.15 | 757.58
8191 | TIN-INTERP | Interpolated Ground | 52410 | 6.25 | 720.2 | 0 | 42.69 | 0 | OK | Ground clear controls. | 117 | 45.15 | 762.89
8192 | TIN-INTERP | Interpolated Ground | 52447.26 | -6.54 | 725.37 | 0 | 39.65 | 0 | OK | Ground clear controls. | 117 | 45.15 | 765.02
8193 | TIN-INTERP | Interpolated Ground | 52447.4 | -4.52 | 725.26 | 0 | 45.15 | 0 | OK | Ground clear controls. | 117 | 45.15 | 770.41
8194 | TIN-INTERP | Interpolated Ground | 52447.61 | -5.06 | 725.33 | 0 | 34.28 | 0 | OK | Ground clear controls. | 117 | 44.84 | 759.61
8195 | TIN-INTERP | Interpolated Ground | 52449.22 | 4.32 | 725.48 | 0 | 44.84 | 0 | OK | Ground clear controls. | 117 | 44.84 | 770.32
8196 | TIN-INTERP | Interpolated Ground | 52449.69 | 4.81 | 725.56 | 0 | 34.27 | 0 | OK | Ground clear controls. | 117 | 41.18 | 759.83
8197 | TIN-INTERP | Interpolated Ground | 52450 | 6.3 | 725.6 | 0 | 39.56 | 0 | OK | Ground clear controls. | 117 | 41.18 | 765.16
8198 | TIN-INTERP | Interpolated Ground | 52487.26 | -6.57 | 732.42 | 0 | 35.79 | 0 | OK | Ground clear controls. | 117 | 41.18 | 768.21
8199 | TIN-INTERP | Interpolated Ground | 52487.4 | -4.55 | 732.44 | 0 | 41.18 | 0 | OK | Ground clear controls. | 117 | 41.18 | 773.62
8200 | TIN-INTERP | Interpolated Ground | 52487.61 | -5.08 | 732.5 | 0 | 30.3 | 0 | OK | Ground clear controls. | 117 | 40.77 | 762.8
8201 | TIN-INTERP | Interpolated Ground | 52489.22 | 4.37 | 732.83 | 0 | 40.77 | 0 | OK | Ground clear controls. | 117 | 40.77 | 773.6
8202 | TIN-INTERP | Interpolated Ground | 52489.69 | 4.86 | 732.98 | 0 | 30.08 | 0 | OK | Ground clear controls. | 117 | 35.8 | 763.06
8203 | TIN-INTERP | Interpolated Ground | 52490 | 6.35 | 733 | 0 | 35.42 | 0 | OK | Ground clear controls. | 117 | 35.8 | 768.42
8204 | TIN-INTERP | Interpolated Ground | 52527.26 | -6.6 | 743.21 | 0 | 29.19 | 0 | OK | Ground clear controls. | 117 | 35.8 | 772.4
8205 | TIN-INTERP | Interpolated Ground | 52527.4 | -4.58 | 742.87 | 0 | 34.96 | 0 | OK | Ground clear controls. | 117 | 35.8 | 777.83
8206 | TIN-INTERP | Interpolated Ground | 52527.61 | -5.11 | 742.99 | 0 | 23.99 | 0 | OK | Ground clear controls. | 117 | 35.8 | 766.98
8207 | TIN-INTERP | Interpolated Ground | 52529.22 | 4.41 | 742.09 | 0 | 35.8 | 0 | OK | Ground clear controls. | 117 | 35.8 | 777.89
8208 | TIN-INTERP | Interpolated Ground | 52529.69 | 4.9 | 742.1 | 0 | 25.16 | 0 | OK | Ground clear controls. | 117 | 31.51 | 767.26
8209 | TIN-INTERP | Interpolated Ground | 52530 | 6.4 | 742.27 | 0 | 30.4 | 0 | OK | Ground clear controls. | 117 | 31.51 | 772.67
8210 | TIN-INTERP | Interpolated Ground | 52567.26 | -6.62 | 752.53 | 0 | 25.03 | 0 | OK | Ground clear controls. | 117 | 31.51 | 777.56
8211 | TIN-INTERP | Interpolated Ground | 52567.4 | -4.61 | 752.61 | 0 | 30.42 | 0 | OK | Ground clear controls. | 117 | 31.51 | 783.03
8212 | TIN-INTERP | Interpolated Ground | 52567.61 | -5.13 | 752.66 | 0 | 19.48 | 0 | OK | Ground clear controls. | 117 | 31.51 | 772.14
8213 | TIN-INTERP | Interpolated Ground | 52569.22 | 4.45 | 751.67 | 0 | 31.51 | 0 | OK | Ground clear controls. | 117 | 31.51 | 783.18
8214 | TIN-INTERP | Interpolated Ground | 52569.69 | 4.95 | 751.7 | 0 | 20.76 | 0 | OK | Ground clear controls. | 117 | 30.74 | 772.46
8215 | TIN-INTERP | Interpolated Ground | 52570 | 6.44 | 751.93 | 0 | 25.98 | 0 | OK | Ground clear controls. | 117 | 30.74 | 777.91
8216 | TIN-INTERP | Interpolated Ground | 52607.26 | -6.65 | 759.63 | 0 | 24.09 | 0 | OK | Ground clear controls. | 117 | 30.74 | 783.72
8217 | TIN-INTERP | Interpolated Ground | 52607.4 | -4.65 | 759.64 | 0 | 29.58 | 0 | OK | Ground clear controls. | 117 | 30.74 | 789.22
8218 | TIN-INTERP | Interpolated Ground | 52607.61 | -5.15 | 759.7 | 0 | 18.59 | 0 | OK | Ground clear controls. | 117 | 30.74 | 778.29
8219 | TIN-INTERP | Interpolated Ground | 52609.22 | 4.5 | 758.73 | 0 | 30.74 | 0 | OK | Ground clear controls. | 117 | 30.74 | 789.47
8220 | TIN-INTERP | Interpolated Ground | 52609.69 | 4.99 | 758.58 | 0 | 20.06 | 0 | OK | Ground clear controls. | 117 | 25.98 | 778.64
8221 | TIN-INTERP | Interpolated Ground | 52610 | 6.49 | 758.17 | 0 | 25.98 | 0 | OK | Ground clear controls. | 117 | 25.98 | 784.15
8222 | TIN-INTERP | Interpolated Ground | 52632.91 | -6.67 | 761.27 | 0 | 26.92 | 0 | OK | Ground clear controls. | 118 | 58.33 | 788.19
8223 | TIN-INTERP | Interpolated Ground | 52632.95 | -4.67 | 760.93 | 0 | 32.76 | 0 | OK | Ground clear controls. | 118 | 58.33 | 793.69
8224 | TIN-INTERP | Interpolated Ground | 52632.96 | -5.17 | 761 | 0 | 21.69 | 0 | OK | Ground clear controls. | 118 | 58.33 | 782.69
8225 | TIN-INTERP | Interpolated Ground | 52632.98 | 4.52 | 758.67 | 0 | 35.02 | 0 | OK | Ground clear controls. | 118 | 58.33 | 793.69
8226 | TIN-INTERP | Interpolated Ground | 52632.99 | 6.52 | 758.3 | 0 | 29.89 | 0 | OK | Ground clear controls. | 118 | 58.33 | 788.19
8227 | TIN-INTERP | Interpolated Ground | 52633.02 | 5.02 | 758.6 | 0 | 24.1 | 0 | OK | Ground clear controls. | 118 | 58.33 | 782.7
8228 | TIN-INTERP | Interpolated Ground | 52672.91 | -6.66 | 761.41 | 0 | 19.93 | 0 | OK | Ground clear controls. | 118 | 58.33 | 781.34
8229 | TIN-INTERP | Interpolated Ground | 52672.95 | -4.65 | 761.02 | 0 | 25.81 | 0 | OK | Ground clear controls. | 118 | 58.33 | 786.83
8230 | TIN-INTERP | Interpolated Ground | 52672.96 | -5.16 | 761.1 | 0 | 14.79 | 0 | OK | Ground clear controls. | 118 | 58.33 | 775.89
8231 | TIN-INTERP | Interpolated Ground | 52672.98 | 4.53 | 758.18 | 0 | 28.55 | 0 | OK | Ground clear controls. | 118 | 58.33 | 786.73
8232 | TIN-INTERP | Interpolated Ground | 52672.99 | 6.53 | 757.81 | 0 | 23.48 | 0 | OK | Ground clear controls. | 118 | 58.33 | 781.29
8233 | TIN-INTERP | Interpolated Ground | 52673.02 | 5.03 | 758.06 | 0 | 17.81 | 0 | OK | Ground clear controls. | 118 | 58.33 | 775.87
8234 | TIN-INTERP | Interpolated Ground | 52712.91 | -6.64 | 756.13 | 0 | 19.34 | 0 | OK | Ground clear controls. | 118 | 58.33 | 775.47
8235 | TIN-INTERP | Interpolated Ground | 52712.95 | -4.64 | 755.81 | 0 | 25.16 | 0 | OK | Ground clear controls. | 118 | 58.33 | 780.97
8236 | TIN-INTERP | Interpolated Ground | 52712.96 | -5.14 | 755.86 | 0 | 14.2 | 0 | OK | Ground clear controls. | 118 | 58.33 | 770.06
8237 | TIN-INTERP | Interpolated Ground | 52712.98 | 4.55 | 754.04 | 0 | 26.74 | 0 | OK | Ground clear controls. | 118 | 58.33 | 780.78
8238 | TIN-INTERP | Interpolated Ground | 52712.99 | 6.55 | 753.33 | 0 | 22.06 | 0 | OK | Ground clear controls. | 118 | 58.33 | 775.39
8239 | TIN-INTERP | Interpolated Ground | 52713.02 | 5.05 | 753.9 | 0 | 16.14 | 0 | OK | Ground clear controls. | 118 | 58.33 | 770.04
8240 | TIN-INTERP | Interpolated Ground | 52752.91 | -6.63 | 746.18 | 0 | 24.41 | 0 | OK | Ground clear controls. | 118 | 58.33 | 770.59
8241 | TIN-INTERP | Interpolated Ground | 52752.95 | -4.63 | 746.01 | 0 | 30.08 | 0 | OK | Ground clear controls. | 118 | 58.33 | 776.09
8242 | TIN-INTERP | Interpolated Ground | 52752.96 | -5.13 | 746.03 | 0 | 19.18 | 0 | OK | Ground clear controls. | 118 | 58.33 | 765.21
8243 | TIN-INTERP | Interpolated Ground | 52752.98 | 4.56 | 743.97 | 0 | 31.87 | 0 | OK | Ground clear controls. | 118 | 58.33 | 775.84
8244 | TIN-INTERP | Interpolated Ground | 52752.99 | 6.56 | 743.23 | 0 | 27.25 | 0 | OK | Ground clear controls. | 118 | 58.33 | 770.48
8245 | TIN-INTERP | Interpolated Ground | 52753.02 | 5.06 | 743.78 | 0 | 21.4 | 0 | OK | Ground clear controls. | 118 | 58.33 | 765.18
8246 | TIN-INTERP | Interpolated Ground | 52792.91 | -6.62 | 727.69 | 0 | 39.01 | 0 | OK | Ground clear controls. | 118 | 58.33 | 766.7
8247 | TIN-INTERP | Interpolated Ground | 52792.95 | -4.62 | 727.26 | 0 | 44.92 | 0 | OK | Ground clear controls. | 118 | 58.33 | 772.18
8248 | TIN-INTERP | Interpolated Ground | 52792.96 | -5.12 | 727.43 | 0 | 33.91 | 0 | OK | Ground clear controls. | 118 | 58.33 | 761.34
8249 | TIN-INTERP | Interpolated Ground | 52792.98 | 4.57 | 725.48 | 0 | 46.42 | 0 | OK | Ground clear controls. | 118 | 58.33 | 771.9
8250 | TIN-INTERP | Interpolated Ground | 52792.99 | 6.57 | 725.07 | 0 | 41.49 | 0 | OK | Ground clear controls. | 118 | 58.33 | 766.56
8251 | TIN-INTERP | Interpolated Ground | 52793.02 | 5.07 | 725.33 | 0 | 35.95 | 0 | OK | Ground clear controls. | 118 | 58.33 | 761.28
8252 | TIN-INTERP | Interpolated Ground | 52832.91 | -6.61 | 710.55 | 0 | 53.23 | 0 | OK | Ground clear controls. | 118 | 58.33 | 763.78
8253 | TIN-INTERP | Interpolated Ground | 52832.95 | -4.61 | 711.02 | 0 | 58.25 | 0 | OK | Ground clear controls. | 118 | 58.33 | 769.27
8254 | TIN-INTERP | Interpolated Ground | 52832.96 | -5.11 | 710.89 | 0 | 47.53 | 0 | OK | Ground clear controls. | 118 | 58.33 | 758.42
8255 | TIN-INTERP | Interpolated Ground | 52832.98 | 4.58 | 710.61 | 0 | 58.33 | 0 | OK | Ground clear controls. | 118 | 58.33 | 768.94
8256 | TIN-INTERP | Interpolated Ground | 52832.99 | 6.58 | 710.89 | 0 | 52.73 | 0 | OK | Ground clear controls. | 118 | 52.73 | 763.62
8257 | TIN-INTERP | Interpolated Ground | 52833.02 | 5.08 | 710.63 | 0 | 47.75 | 0 | OK | Ground clear controls. | 118 | 47.75 | 758.38
8258 | TIN-INTERP | Interpolated Ground | 52872.91 | -6.6 | 725.44 | 0 | 36.41 | 0 | OK | Ground clear controls. | 118 | 47.5 | 761.85
8259 | TIN-INTERP | Interpolated Ground | 52872.95 | -4.6 | 725.02 | 0 | 42.3 | 0 | OK | Ground clear controls. | 118 | 47.5 | 767.32
8260 | TIN-INTERP | Interpolated Ground | 52872.96 | -5.1 | 725.13 | 0 | 31.36 | 0 | OK | Ground clear controls. | 118 | 47.5 | 756.49
8261 | TIN-INTERP | Interpolated Ground | 52872.98 | 4.6 | 724.84 | 0 | 42.15 | 0 | OK | Ground clear controls. | 118 | 47.5 | 766.99
8262 | TIN-INTERP | Interpolated Ground | 52872.99 | 6.6 | 724.84 | 0 | 36.84 | 0 | OK | Ground clear controls. | 118 | 47.5 | 761.68
8263 | TIN-INTERP | Interpolated Ground | 52873.02 | 5.1 | 724.83 | 0 | 31.61 | 0 | OK | Ground clear controls. | 118 | 47.5 | 756.44
8264 | TIN-INTERP | Interpolated Ground | 52912.91 | -6.58 | 722.33 | 0 | 38.55 | 0 | OK | Ground clear controls. | 118 | 47.5 | 760.88
8265 | TIN-INTERP | Interpolated Ground | 52912.95 | -4.58 | 722.01 | 0 | 44.35 | 0 | OK | Ground clear controls. | 118 | 47.5 | 766.36
8266 | TIN-INTERP | Interpolated Ground | 52912.96 | -5.08 | 722.15 | 0 | 33.38 | 0 | OK | Ground clear controls. | 118 | 47.5 | 755.53
8267 | TIN-INTERP | Interpolated Ground | 52912.98 | 4.61 | 719.07 | 0 | 46.96 | 0 | OK | Ground clear controls. | 118 | 47.5 | 766.03
8268 | TIN-INTERP | Interpolated Ground | 52912.99 | 6.61 | 719.1 | 0 | 41.63 | 0 | OK | Ground clear controls. | 118 | 47.5 | 760.73
8269 | TIN-INTERP | Interpolated Ground | 52913.02 | 5.11 | 719.07 | 0 | 36.4 | 0 | OK | Ground clear controls. | 118 | 47.5 | 755.47
8270 | TIN-INTERP | Interpolated Ground | 52952.91 | -6.57 | 719.15 | 0 | 41.75 | 0 | OK | Ground clear controls. | 118 | 47.5 | 760.9
8271 | TIN-INTERP | Interpolated Ground | 52952.95 | -4.57 | 719.14 | 0 | 47.24 | 0 | OK | Ground clear controls. | 118 | 47.5 | 766.38
8272 | TIN-INTERP | Interpolated Ground | 52952.96 | -5.07 | 719.15 | 0 | 36.38 | 0 | OK | Ground clear controls. | 118 | 47.5 | 755.53
8273 | TIN-INTERP | Interpolated Ground | 52952.98 | 4.62 | 718.57 | 0 | 47.5 | 0 | OK | Ground clear controls. | 118 | 47.5 | 766.07
8274 | TIN-INTERP | Interpolated Ground | 52952.99 | 6.62 | 718.68 | 0 | 42.07 | 0 | OK | Ground clear controls. | 118 | 42.07 | 760.75
8275 | TIN-INTERP | Interpolated Ground | 52953.02 | 5.12 | 718.56 | 0 | 36.92 | 0 | OK | Ground clear controls. | 118 | 40.68 | 755.48
8276 | TIN-INTERP | Interpolated Ground | 52992.91 | -6.56 | 726.71 | 0 | 35.17 | 0 | OK | Ground clear controls. | 118 | 40.68 | 761.88
8277 | TIN-INTERP | Interpolated Ground | 52992.95 | -4.56 | 726.69 | 0 | 40.68 | 0 | OK | Ground clear controls. | 118 | 40.68 | 767.37
8278 | TIN-INTERP | Interpolated Ground | 52992.96 | -5.06 | 726.6 | 0 | 29.9 | 0 | OK | Ground clear controls. | 118 | 40.27 | 756.5
8279 | TIN-INTERP | Interpolated Ground | 52992.98 | 4.63 | 726.83 | 0 | 40.27 | 0 | OK | Ground clear controls. | 118 | 40.27 | 767.1
8280 | TIN-INTERP | Interpolated Ground | 52992.99 | 6.63 | 726.51 | 0 | 35.24 | 0 | OK | Ground clear controls. | 118 | 36.23 | 761.75
8281 | TIN-INTERP | Interpolated Ground | 52993.02 | 5.13 | 726.7 | 0 | 29.76 | 0 | OK | Ground clear controls. | 118 | 36.23 | 756.46
8282 | TIN-INTERP | Interpolated Ground | 53032.91 | -6.55 | 733.24 | 0 | 30.61 | 0 | OK | Ground clear controls. | 118 | 36.23 | 763.85
8283 | TIN-INTERP | Interpolated Ground | 53032.95 | -4.55 | 733.11 | 0 | 36.23 | 0 | OK | Ground clear controls. | 118 | 36.23 | 769.34
8284 | TIN-INTERP | Interpolated Ground | 53032.96 | -5.05 | 733.13 | 0 | 25.31 | 0 | OK | Ground clear controls. | 118 | 36.12 | 758.44
8285 | TIN-INTERP | Interpolated Ground | 53032.98 | 4.65 | 733 | 0 | 36.12 | 0 | OK | Ground clear controls. | 118 | 36.12 | 769.12
8286 | TIN-INTERP | Interpolated Ground | 53032.99 | 6.65 | 732.94 | 0 | 30.81 | 0 | OK | Ground clear controls. | 118 | 30.81 | 763.75
8287 | TIN-INTERP | Interpolated Ground | 53033.02 | 5.15 | 732.94 | 0 | 25.47 | 0 | OK | Ground clear controls. | 118 | 29.36 | 758.41
8288 | TIN-INTERP | Interpolated Ground | 53072.91 | -6.54 | 743.19 | 0 | 23.61 | 0 | OK | Ground clear controls. | 118 | 29.36 | 766.8
8289 | TIN-INTERP | Interpolated Ground | 53072.95 | -4.54 | 743.21 | 0 | 29.08 | 0 | OK | Ground clear controls. | 118 | 29.36 | 772.29
8290 | TIN-INTERP | Interpolated Ground | 53072.96 | -5.04 | 743.19 | 0 | 18.17 | 0 | OK | Ground clear controls. | 118 | 29.36 | 761.36
8291 | TIN-INTERP | Interpolated Ground | 53072.98 | 4.66 | 742.8 | 0 | 29.36 | 0 | OK | Ground clear controls. | 118 | 29.36 | 772.16
8292 | TIN-INTERP | Interpolated Ground | 53072.99 | 6.66 | 742.69 | 0 | 24.04 | 0 | OK | Ground clear controls. | 118 | 28.88 | 766.73
8293 | TIN-INTERP | Interpolated Ground | 53073.02 | 5.16 | 742.74 | 0 | 18.59 | 0 | OK | Ground clear controls. | 118 | 28.88 | 761.33
8294 | TIN-INTERP | Interpolated Ground | 53112.91 | -6.53 | 747.71 | 0 | 23.01 | 0 | OK | Ground clear controls. | 118 | 28.88 | 770.72
8295 | TIN-INTERP | Interpolated Ground | 53112.95 | -4.53 | 747.4 | 0 | 28.83 | 0 | OK | Ground clear controls. | 118 | 28.88 | 776.23
8296 | TIN-INTERP | Interpolated Ground | 53112.96 | -5.03 | 747.47 | 0 | 17.77 | 0 | OK | Ground clear controls. | 118 | 28.88 | 765.24
8297 | TIN-INTERP | Interpolated Ground | 53112.98 | 4.67 | 747.29 | 0 | 28.88 | 0 | OK | Ground clear controls. | 118 | 28.88 | 776.17
8298 | TIN-INTERP | Interpolated Ground | 53112.99 | 6.67 | 747.45 | 0 | 23.24 | 0 | OK | Ground clear controls. | 118 | 23.24 | 770.69
8299 | TIN-INTERP | Interpolated Ground | 53113.02 | 5.17 | 747.33 | 0 | 17.9 | 0 | OK | Ground clear controls. | 118 | 17.9 | 765.23
8300 | TIN-INTERP | Interpolated Ground | 53125.16 | -6.52 | 747.72 | 0 | 24.4 | 0 | OK | Ground clear controls. | 119 | 42.6 | 772.12
8301 | TIN-INTERP | Interpolated Ground | 53125.21 | -5.02 | 747.65 | 0 | 18.97 | 0 | OK | Ground clear controls. | 119 | 42.6 | 766.62
8302 | TIN-INTERP | Interpolated Ground | 53125.22 | -4.52 | 747.62 | 0 | 30 | 0 | OK | Ground clear controls. | 119 | 42.6 | 777.62
8303 | TIN-INTERP | Interpolated Ground | 53125.34 | 5.18 | 747.27 | 0 | 19.35 | 0 | OK | Ground clear controls. | 119 | 42.6 | 766.62
8304 | TIN-INTERP | Interpolated Ground | 53125.38 | 6.68 | 747.19 | 0 | 24.93 | 0 | OK | Ground clear controls. | 119 | 42.6 | 772.12
8305 | TIN-INTERP | Interpolated Ground | 53125.41 | 4.68 | 747.29 | 0 | 30.33 | 0 | OK | Ground clear controls. | 119 | 42.6 | 777.62
8306 | TIN-INTERP | Interpolated Ground | 53165.16 | -6.53 | 745.17 | 0 | 24.92 | 0 | OK | Ground clear controls. | 119 | 42.6 | 770.09
8307 | TIN-INTERP | Interpolated Ground | 53165.21 | -5.03 | 745.14 | 0 | 19.49 | 0 | OK | Ground clear controls. | 119 | 42.6 | 764.63
8308 | TIN-INTERP | Interpolated Ground | 53165.22 | -4.53 | 745.13 | 0 | 30.46 | 0 | OK | Ground clear controls. | 119 | 42.6 | 775.59
8309 | TIN-INTERP | Interpolated Ground | 53165.34 | 5.17 | 744.58 | 0 | 20.03 | 0 | OK | Ground clear controls. | 119 | 42.6 | 764.61
8310 | TIN-INTERP | Interpolated Ground | 53165.38 | 6.67 | 744.75 | 0 | 25.31 | 0 | OK | Ground clear controls. | 119 | 42.6 | 770.06
8311 | TIN-INTERP | Interpolated Ground | 53165.41 | 4.67 | 744.53 | 0 | 31.01 | 0 | OK | Ground clear controls. | 119 | 42.6 | 775.54
8312 | TIN-INTERP | Interpolated Ground | 53205.16 | -6.54 | 731.83 | 0 | 37.19 | 0 | OK | Ground clear controls. | 119 | 42.6 | 769.02
8313 | TIN-INTERP | Interpolated Ground | 53205.21 | -5.04 | 732.08 | 0 | 31.51 | 0 | OK | Ground clear controls. | 119 | 42.6 | 763.59
8314 | TIN-INTERP | Interpolated Ground | 53205.22 | -4.54 | 732.3 | 0 | 42.23 | 0 | OK | Ground clear controls. | 119 | 42.6 | 774.53
8315 | TIN-INTERP | Interpolated Ground | 53205.34 | 5.16 | 732.02 | 0 | 31.54 | 0 | OK | Ground clear controls. | 119 | 42.6 | 763.56
8316 | TIN-INTERP | Interpolated Ground | 53205.38 | 6.66 | 732.61 | 0 | 36.38 | 0 | OK | Ground clear controls. | 119 | 42.6 | 768.99
8317 | TIN-INTERP | Interpolated Ground | 53205.41 | 4.66 | 731.84 | 0 | 42.6 | 0 | OK | Ground clear controls. | 119 | 42.6 | 774.44
8318 | TIN-INTERP | Interpolated Ground | 53245.16 | -6.54 | 737.07 | 0 | 31.87 | 0 | OK | Ground clear controls. | 119 | 41.54 | 768.94
8319 | TIN-INTERP | Interpolated Ground | 53245.21 | -5.04 | 736.52 | 0 | 27 | 0 | OK | Ground clear controls. | 119 | 41.54 | 763.52
8320 | TIN-INTERP | Interpolated Ground | 53245.22 | -4.54 | 736.36 | 0 | 38.09 | 0 | OK | Ground clear controls. | 119 | 41.54 | 774.45
8321 | TIN-INTERP | Interpolated Ground | 53245.34 | 5.15 | 732.59 | 0 | 30.91 | 0 | OK | Ground clear controls. | 119 | 41.54 | 763.5
8322 | TIN-INTERP | Interpolated Ground | 53245.38 | 6.65 | 732.03 | 0 | 36.86 | 0 | OK | Ground clear controls. | 119 | 41.54 | 768.89
8323 | TIN-INTERP | Interpolated Ground | 53245.41 | 4.65 | 732.8 | 0 | 41.54 | 0 | OK | Ground clear controls. | 119 | 41.54 | 774.34
8324 | TIN-INTERP | Interpolated Ground | 53285.16 | -6.55 | 742.69 | 0 | 27.15 | 0 | OK | Ground clear controls. | 119 | 41.31 | 769.84
8325 | TIN-INTERP | Interpolated Ground | 53285.21 | -5.05 | 742.09 | 0 | 22.34 | 0 | OK | Ground clear controls. | 119 | 41.31 | 764.43
8326 | TIN-INTERP | Interpolated Ground | 53285.22 | -4.55 | 741.9 | 0 | 33.45 | 0 | OK | Ground clear controls. | 119 | 41.31 | 775.35
8327 | TIN-INTERP | Interpolated Ground | 53285.34 | 5.14 | 736.47 | 0 | 27.93 | 0 | OK | Ground clear controls. | 119 | 41.31 | 764.4
8328 | TIN-INTERP | Interpolated Ground | 53285.38 | 6.64 | 735.43 | 0 | 34.35 | 0 | OK | Ground clear controls. | 119 | 41.31 | 769.78
8329 | TIN-INTERP | Interpolated Ground | 53285.41 | 4.64 | 736.77 | 0 | 38.45 | 0 | OK | Ground clear controls. | 119 | 41.31 | 775.22
8330 | TIN-INTERP | Interpolated Ground | 53325.16 | -6.56 | 748.31 | 0 | 23.39 | 0 | OK | Ground clear controls. | 119 | 41.31 | 771.7
8331 | TIN-INTERP | Interpolated Ground | 53325.21 | -5.06 | 747.67 | 0 | 18.63 | 0 | OK | Ground clear controls. | 119 | 41.31 | 766.3
8332 | TIN-INTERP | Interpolated Ground | 53325.22 | -4.56 | 747.63 | 0 | 29.59 | 0 | OK | Ground clear controls. | 119 | 41.31 | 777.22
8333 | TIN-INTERP | Interpolated Ground | 53325.34 | 5.13 | 747.43 | 0 | 18.84 | 0 | OK | Ground clear controls. | 119 | 41.31 | 766.27
8334 | TIN-INTERP | Interpolated Ground | 53325.38 | 6.63 | 747.47 | 0 | 24.18 | 0 | OK | Ground clear controls. | 119 | 41.31 | 771.65
8335 | TIN-INTERP | Interpolated Ground | 53325.41 | 4.63 | 747.42 | 0 | 29.67 | 0 | OK | Ground clear controls. | 119 | 41.31 | 777.09
8336 | TIN-INTERP | Interpolated Ground | 53365.16 | -6.56 | 752.37 | 0 | 22.18 | 0 | OK | Ground clear controls. | 119 | 41.31 | 774.55
8337 | TIN-INTERP | Interpolated Ground | 53365.21 | -5.06 | 752.02 | 0 | 17.12 | 0 | OK | Ground clear controls. | 119 | 41.31 | 769.14
8338 | TIN-INTERP | Interpolated Ground | 53365.22 | -4.57 | 751.93 | 0 | 28.13 | 0 | OK | Ground clear controls. | 119 | 41.31 | 780.06
8339 | TIN-INTERP | Interpolated Ground | 53365.34 | 5.12 | 749.42 | 0 | 19.69 | 0 | OK | Ground clear controls. | 119 | 41.31 | 769.11
8340 | TIN-INTERP | Interpolated Ground | 53365.38 | 6.62 | 749.18 | 0 | 25.33 | 0 | OK | Ground clear controls. | 119 | 41.31 | 774.51
8341 | TIN-INTERP | Interpolated Ground | 53365.41 | 4.62 | 749.49 | 0 | 30.46 | 0 | OK | Ground clear controls. | 119 | 41.31 | 779.95
8342 | TIN-INTERP | Interpolated Ground | 53405.16 | -6.57 | 750.56 | 0 | 27.82 | 0 | OK | Ground clear controls. | 119 | 41.31 | 778.38
8343 | TIN-INTERP | Interpolated Ground | 53405.21 | -5.07 | 750.03 | 0 | 22.92 | 0 | OK | Ground clear controls. | 119 | 41.31 | 772.95
8344 | TIN-INTERP | Interpolated Ground | 53405.22 | -4.57 | 749.85 | 0 | 34.05 | 0 | OK | Ground clear controls. | 119 | 41.31 | 783.9
8345 | TIN-INTERP | Interpolated Ground | 53405.34 | 5.11 | 747.44 | 0 | 25.49 | 0 | OK | Ground clear controls. | 119 | 41.31 | 772.93
8346 | TIN-INTERP | Interpolated Ground | 53405.38 | 6.61 | 747.17 | 0 | 31.18 | 0 | OK | Ground clear controls. | 119 | 41.31 | 778.35
8347 | TIN-INTERP | Interpolated Ground | 53405.41 | 4.61 | 747.56 | 0 | 36.26 | 0 | OK | Ground clear controls. | 119 | 41.31 | 783.82
8348 | TIN-INTERP | Interpolated Ground | 53445.16 | -6.58 | 749.54 | 0 | 33.65 | 0 | OK | Ground clear controls. | 119 | 41.31 | 783.19
8349 | TIN-INTERP | Interpolated Ground | 53445.21 | -5.08 | 749.07 | 0 | 28.66 | 0 | OK | Ground clear controls. | 119 | 41.31 | 777.73
8350 | TIN-INTERP | Interpolated Ground | 53445.22 | -4.58 | 748.93 | 0 | 39.77 | 0 | OK | Ground clear controls. | 119 | 41.31 | 788.7
8351 | TIN-INTERP | Interpolated Ground | 53445.34 | 5.1 | 747.22 | 0 | 30.49 | 0 | OK | Ground clear controls. | 119 | 41.31 | 777.71
8352 | TIN-INTERP | Interpolated Ground | 53445.38 | 6.6 | 746.96 | 0 | 36.21 | 0 | OK | Ground clear controls. | 119 | 41.31 | 783.17
8353 | TIN-INTERP | Interpolated Ground | 53445.41 | 4.6 | 747.35 | 0 | 41.31 | 0 | OK | Ground clear controls. | 119 | 41.31 | 788.66
8354 | TIN-INTERP | Interpolated Ground | 53479.91 | -6.58 | 750.25 | 0 | 37.92 | 0 | OK | Ground clear controls. | 120 | 58.7 | 788.17
8355 | TIN-INTERP | Interpolated Ground | 53479.92 | -5.08 | 749.93 | 0 | 32.74 | 0 | OK | Ground clear controls. | 120 | 58.7 | 782.67
8356 | TIN-INTERP | Interpolated Ground | 53479.94 | -4.59 | 749.8 | 0 | 43.87 | 0 | OK | Ground clear controls. | 120 | 58.7 | 793.67
8357 | TIN-INTERP | Interpolated Ground | 53480.1 | 5.1 | 748.93 | 0 | 33.74 | 0 | OK | Ground clear controls. | 120 | 58.7 | 782.67
8358 | TIN-INTERP | Interpolated Ground | 53480.11 | 4.59 | 748.93 | 0 | 44.74 | 0 | OK | Ground clear controls. | 120 | 58.7 | 793.67
8359 | TIN-INTERP | Interpolated Ground | 53480.14 | 6.59 | 748.94 | 0 | 39.23 | 0 | OK | Ground clear controls. | 120 | 58.7 | 788.17
8360 | TIN-INTERP | Interpolated Ground | 53519.91 | -6.51 | 735.25 | 0 | 45.85 | 0 | OK | Ground clear controls. | 120 | 58.7 | 781.1
8361 | TIN-INTERP | Interpolated Ground | 53519.92 | -5 | 735.66 | 0 | 39.99 | 0 | OK | Ground clear controls. | 120 | 58.7 | 775.65
8362 | TIN-INTERP | Interpolated Ground | 53519.94 | -4.52 | 735.9 | 0 | 50.68 | 0 | OK | Ground clear controls. | 120 | 58.7 | 786.58
8363 | TIN-INTERP | Interpolated Ground | 53520.1 | 5.08 | 741.19 | 0 | 34.39 | 0 | OK | Ground clear controls. | 120 | 58.7 | 775.58
8364 | TIN-INTERP | Interpolated Ground | 53520.11 | 4.56 | 740.82 | 0 | 45.63 | 0 | OK | Ground clear controls. | 120 | 58.7 | 786.45
8365 | TIN-INTERP | Interpolated Ground | 53520.14 | 6.57 | 742.18 | 0 | 38.8 | 0 | OK | Ground clear controls. | 120 | 58.7 | 780.98
8366 | TIN-INTERP | Interpolated Ground | 53559.91 | -6.43 | 741.93 | 0 | 33.07 | 0 | OK | Ground clear controls. | 120 | 58.7 | 775
8367 | TIN-INTERP | Interpolated Ground | 53559.92 | -4.92 | 741.39 | 0 | 28.22 | 0 | OK | Ground clear controls. | 120 | 58.7 | 769.61
8368 | TIN-INTERP | Interpolated Ground | 53559.94 | -4.46 | 741.2 | 0 | 39.28 | 0 | OK | Ground clear controls. | 120 | 58.7 | 780.48
8369 | TIN-INTERP | Interpolated Ground | 53560.1 | 5.06 | 736.56 | 0 | 32.91 | 0 | OK | Ground clear controls. | 120 | 58.7 | 769.47
8370 | TIN-INTERP | Interpolated Ground | 53560.11 | 4.52 | 736.79 | 0 | 43.44 | 0 | OK | Ground clear controls. | 120 | 58.7 | 780.23
8371 | TIN-INTERP | Interpolated Ground | 53560.14 | 6.54 | 735.98 | 0 | 38.81 | 0 | OK | Ground clear controls. | 120 | 58.7 | 774.79
8372 | TIN-INTERP | Interpolated Ground | 53599.91 | -6.35 | 745.64 | 0 | 24.27 | 0 | OK | Ground clear controls. | 120 | 58.7 | 769.91
8373 | TIN-INTERP | Interpolated Ground | 53599.92 | -4.84 | 745.38 | 0 | 19.17 | 0 | OK | Ground clear controls. | 120 | 58.7 | 764.55
8374 | TIN-INTERP | Interpolated Ground | 53599.94 | -4.39 | 745.22 | 0 | 30.15 | 0 | OK | Ground clear controls. | 120 | 58.7 | 775.37
8375 | TIN-INTERP | Interpolated Ground | 53600.1 | 5.04 | 743.75 | 0 | 20.6 | 0 | OK | Ground clear controls. | 120 | 58.7 | 764.35
8376 | TIN-INTERP | Interpolated Ground | 53600.11 | 4.49 | 743.79 | 0 | 31.22 | 0 | OK | Ground clear controls. | 120 | 58.7 | 775.01
8377 | TIN-INTERP | Interpolated Ground | 53600.14 | 6.52 | 743.64 | 0 | 25.96 | 0 | OK | Ground clear controls. | 120 | 58.7 | 769.6
8378 | TIN-INTERP | Interpolated Ground | 53639.91 | -6.27 | 745.41 | 0 | 20.39 | 0 | OK | Ground clear controls. | 120 | 58.7 | 765.8
8379 | TIN-INTERP | Interpolated Ground | 53639.92 | -4.77 | 745.12 | 0 | 15.36 | 0 | OK | Ground clear controls. | 120 | 58.7 | 760.48
8380 | TIN-INTERP | Interpolated Ground | 53639.94 | -4.33 | 745.03 | 0 | 26.21 | 0 | OK | Ground clear controls. | 120 | 58.7 | 771.24
8381 | TIN-INTERP | Interpolated Ground | 53640.1 | 5.03 | 743.05 | 0 | 17.16 | 0 | OK | Ground clear controls. | 120 | 58.7 | 760.21
8382 | TIN-INTERP | Interpolated Ground | 53640.11 | 4.45 | 743.26 | 0 | 27.53 | 0 | OK | Ground clear controls. | 120 | 58.7 | 770.79
8383 | TIN-INTERP | Interpolated Ground | 53640.14 | 6.49 | 743.1 | 0 | 22.3 | 0 | OK | Ground clear controls. | 120 | 58.7 | 765.4
8384 | TIN-INTERP | Interpolated Ground | 53679.91 | -6.19 | 742.42 | 0 | 20.25 | 0 | OK | Ground clear controls. | 120 | 58.7 | 762.67
8385 | TIN-INTERP | Interpolated Ground | 53679.92 | -4.69 | 742.24 | 0 | 15.14 | 0 | OK | Ground clear controls. | 120 | 58.7 | 757.38
8386 | TIN-INTERP | Interpolated Ground | 53679.94 | -4.26 | 742.18 | 0 | 25.92 | 0 | OK | Ground clear controls. | 120 | 58.7 | 768.1
8387 | TIN-INTERP | Interpolated Ground | 53680.1 | 5.01 | 741.41 | 0 | 15.64 | 0 | OK | Ground clear controls. | 120 | 58.7 | 757.05
8388 | TIN-INTERP | Interpolated Ground | 53680.11 | 4.42 | 741.42 | 0 | 26.16 | 0 | OK | Ground clear controls. | 120 | 58.7 | 767.58
8389 | TIN-INTERP | Interpolated Ground | 53680.14 | 6.47 | 741.39 | 0 | 20.8 | 0 | OK | Ground clear controls. | 120 | 58.7 | 762.19
8390 | TIN-INTERP | Interpolated Ground | 53719.91 | -6.12 | 734.96 | 0 | 25.57 | 0 | OK | Ground clear controls. | 120 | 58.7 | 760.53
8391 | TIN-INTERP | Interpolated Ground | 53719.92 | -4.61 | 734.71 | 0 | 20.55 | 0 | OK | Ground clear controls. | 120 | 58.7 | 755.26
8392 | TIN-INTERP | Interpolated Ground | 53719.94 | -4.19 | 734.74 | 0 | 31.21 | 0 | OK | Ground clear controls. | 120 | 58.7 | 765.95
8393 | TIN-INTERP | Interpolated Ground | 53720.1 | 4.99 | 736 | 0 | 18.88 | 0 | OK | Ground clear controls. | 120 | 58.7 | 754.88
8394 | TIN-INTERP | Interpolated Ground | 53720.11 | 4.38 | 736.04 | 0 | 29.32 | 0 | OK | Ground clear controls. | 120 | 58.7 | 765.36
8395 | TIN-INTERP | Interpolated Ground | 53720.14 | 6.44 | 735.9 | 0 | 24.07 | 0 | OK | Ground clear controls. | 120 | 58.7 | 759.97
8396 | TIN-INTERP | Interpolated Ground | 53759.91 | -6.04 | 721.22 | 0 | 38.15 | 0 | OK | Ground clear controls. | 120 | 58.7 | 759.37
8397 | TIN-INTERP | Interpolated Ground | 53759.92 | -4.53 | 722.58 | 0 | 31.52 | 0 | OK | Ground clear controls. | 120 | 58.7 | 754.1
8398 | TIN-INTERP | Interpolated Ground | 53759.94 | -4.13 | 722.91 | 0 | 41.87 | 0 | OK | Ground clear controls. | 120 | 58.7 | 764.78
8399 | TIN-INTERP | Interpolated Ground | 53760.1 | 4.98 | 726.46 | 0 | 27.21 | 0 | OK | Ground clear controls. | 120 | 58.7 | 753.67
8400 | TIN-INTERP | Interpolated Ground | 53760.11 | 4.34 | 726.25 | 0 | 37.87 | 0 | OK | Ground clear controls. | 120 | 58.7 | 764.12
8401 | TIN-INTERP | Interpolated Ground | 53760.14 | 6.42 | 727.16 | 0 | 31.58 | 0 | OK | Ground clear controls. | 120 | 58.7 | 758.74
8402 | TIN-INTERP | Interpolated Ground | 53799.91 | -5.96 | 707.7 | 0 | 51.5 | 0 | OK | Ground clear controls. | 120 | 58.7 | 759.2
8403 | TIN-INTERP | Interpolated Ground | 53799.92 | -4.45 | 707.95 | 0 | 45.98 | 0 | OK | Ground clear controls. | 120 | 58.7 | 753.93
8404 | TIN-INTERP | Interpolated Ground | 53799.94 | -4.06 | 708 | 0 | 56.6 | 0 | OK | Ground clear controls. | 120 | 58.7 | 764.6
8405 | TIN-INTERP | Interpolated Ground | 53800.1 | 4.96 | 707.21 | 0 | 46.24 | 0 | OK | Ground clear controls. | 120 | 58.7 | 753.45
8406 | TIN-INTERP | Interpolated Ground | 53800.11 | 4.31 | 707.25 | 0 | 56.63 | 0 | OK | Ground clear controls. | 120 | 58.7 | 763.88
8407 | TIN-INTERP | Interpolated Ground | 53800.14 | 6.39 | 707.05 | 0 | 51.45 | 0 | OK | Ground clear controls. | 120 | 58.7 | 758.5
8408 | TIN-INTERP | Interpolated Ground | 53839.91 | -5.88 | 710.92 | 0 | 49.08 | 0 | OK | Ground clear controls. | 120 | 58.7 | 760
8409 | TIN-INTERP | Interpolated Ground | 53839.92 | -4.37 | 710.47 | 0 | 44.25 | 0 | OK | Ground clear controls. | 120 | 58.7 | 754.72
8410 | TIN-INTERP | Interpolated Ground | 53839.94 | -4 | 710.4 | 0 | 54.98 | 0 | OK | Ground clear controls. | 120 | 58.7 | 765.38
8411 | TIN-INTERP | Interpolated Ground | 53840.1 | 4.94 | 709.68 | 0 | 44.52 | 0 | OK | Ground clear controls. | 120 | 58.7 | 754.2
8412 | TIN-INTERP | Interpolated Ground | 53840.11 | 4.27 | 709.75 | 0 | 54.89 | 0 | OK | Ground clear controls. | 120 | 58.7 | 764.64
8413 | TIN-INTERP | Interpolated Ground | 53840.14 | 6.37 | 709.6 | 0 | 49.65 | 0 | OK | Ground clear controls. | 120 | 58.7 | 759.25
8414 | TIN-INTERP | Interpolated Ground | 53879.91 | -5.81 | 713.23 | 0 | 48.56 | 0 | OK | Ground clear controls. | 120 | 58.7 | 761.79
8415 | TIN-INTERP | Interpolated Ground | 53879.92 | -4.29 | 712.87 | 0 | 43.63 | 0 | OK | Ground clear controls. | 120 | 58.7 | 756.5
8416 | TIN-INTERP | Interpolated Ground | 53879.94 | -3.93 | 712.79 | 0 | 54.37 | 0 | OK | Ground clear controls. | 120 | 58.7 | 767.16
8417 | TIN-INTERP | Interpolated Ground | 53880.1 | 4.92 | 711.47 | 0 | 44.46 | 0 | OK | Ground clear controls. | 120 | 58.7 | 755.93
8418 | TIN-INTERP | Interpolated Ground | 53880.11 | 4.24 | 711.51 | 0 | 54.88 | 0 | OK | Ground clear controls. | 120 | 58.7 | 766.39
8419 | TIN-INTERP | Interpolated Ground | 53880.14 | 6.34 | 711.21 | 0 | 49.77 | 0 | OK | Ground clear controls. | 120 | 58.7 | 760.98
8420 | TIN-INTERP | Interpolated Ground | 53919.91 | -5.73 | 713.24 | 0 | 51.31 | 0 | OK | Ground clear controls. | 120 | 58.7 | 764.55
8421 | TIN-INTERP | Interpolated Ground | 53919.92 | -4.21 | 712.27 | 0 | 46.97 | 0 | OK | Ground clear controls. | 120 | 58.7 | 759.24
8422 | TIN-INTERP | Interpolated Ground | 53919.94 | -3.87 | 712.05 | 0 | 57.86 | 0 | OK | Ground clear controls. | 120 | 58.7 | 769.91
8423 | TIN-INTERP | Interpolated Ground | 53920.1 | 4.91 | 710.49 | 0 | 48.14 | 0 | OK | Ground clear controls. | 120 | 58.7 | 758.63
8424 | TIN-INTERP | Interpolated Ground | 53920.11 | 4.2 | 710.43 | 0 | 58.7 | 0 | OK | Ground clear controls. | 120 | 58.7 | 769.13
8425 | TIN-INTERP | Interpolated Ground | 53920.14 | 6.31 | 710.93 | 0 | 52.77 | 0 | OK | Ground clear controls. | 120 | 52.77 | 763.7
8426 | TIN-INTERP | Interpolated Ground | 53959.91 | -5.65 | 720.87 | 0 | 47.45 | 0 | OK | Ground clear controls. | 120 | 52.44 | 768.32
8427 | TIN-INTERP | Interpolated Ground | 53959.92 | -4.13 | 721.15 | 0 | 41.82 | 0 | OK | Ground clear controls. | 120 | 52.44 | 762.97
8428 | TIN-INTERP | Interpolated Ground | 53959.94 | -3.8 | 721.22 | 0 | 52.44 | 0 | OK | Ground clear controls. | 120 | 52.44 | 773.66
8429 | TIN-INTERP | Interpolated Ground | 53960.1 | 4.89 | 722.97 | 0 | 39.36 | 0 | OK | Ground clear controls. | 120 | 50.08 | 762.33
8430 | TIN-INTERP | Interpolated Ground | 53960.11 | 4.17 | 722.79 | 0 | 50.08 | 0 | OK | Ground clear controls. | 120 | 50.08 | 772.87
8431 | TIN-INTERP | Interpolated Ground | 53960.14 | 6.29 | 723.26 | 0 | 44.16 | 0 | OK | Ground clear controls. | 120 | 45.35 | 767.42
8432 | TIN-INTERP | Interpolated Ground | 53999.91 | -5.57 | 732.75 | 0 | 40.31 | 0 | OK | Ground clear controls. | 120 | 45.35 | 773.06
8433 | TIN-INTERP | Interpolated Ground | 53999.92 | -4.05 | 732.98 | 0 | 34.69 | 0 | OK | Ground clear controls. | 120 | 45.35 | 767.67
8434 | TIN-INTERP | Interpolated Ground | 53999.94 | -3.74 | 733.03 | 0 | 45.35 | 0 | OK | Ground clear controls. | 120 | 45.35 | 778.38
8435 | TIN-INTERP | Interpolated Ground | 54000.1 | 4.87 | 733.31 | 0 | 33.68 | 0 | OK | Ground clear controls. | 120 | 44.28 | 766.99
8436 | TIN-INTERP | Interpolated Ground | 54000.11 | 4.13 | 733.33 | 0 | 44.28 | 0 | OK | Ground clear controls. | 120 | 44.28 | 777.61
8437 | TIN-INTERP | Interpolated Ground | 54000.14 | 6.26 | 733.28 | 0 | 38.85 | 0 | OK | Ground clear controls. | 120 | 40.07 | 772.13
8438 | TIN-INTERP | Interpolated Ground | 54039.91 | -5.49 | 744.21 | 0 | 34.58 | 0 | OK | Ground clear controls. | 120 | 40.07 | 778.79
8439 | TIN-INTERP | Interpolated Ground | 54039.92 | -3.97 | 744.07 | 0 | 29.28 | 0 | OK | Ground clear controls. | 120 | 40.07 | 773.35
8440 | TIN-INTERP | Interpolated Ground | 54039.94 | -3.67 | 744.04 | 0 | 40.07 | 0 | OK | Ground clear controls. | 120 | 40.07 | 784.11
8441 | TIN-INTERP | Interpolated Ground | 54040.1 | 4.85 | 743.72 | 0 | 28.94 | 0 | OK | Ground clear controls. | 120 | 39.57 | 772.66
8442 | TIN-INTERP | Interpolated Ground | 54040.11 | 4.1 | 743.78 | 0 | 39.57 | 0 | OK | Ground clear controls. | 120 | 39.57 | 783.35
8443 | TIN-INTERP | Interpolated Ground | 54040.14 | 6.24 | 743.7 | 0 | 34.13 | 0 | OK | Ground clear controls. | 120 | 35.1 | 777.83
8444 | TIN-INTERP | Interpolated Ground | 54079.91 | -5.42 | 755.67 | 0 | 29.85 | 0 | OK | Ground clear controls. | 120 | 35.1 | 785.52
8445 | TIN-INTERP | Interpolated Ground | 54079.92 | -3.89 | 755.75 | 0 | 24.28 | 0 | OK | Ground clear controls. | 120 | 35.1 | 780.03
8446 | TIN-INTERP | Interpolated Ground | 54079.94 | -3.61 | 755.72 | 0 | 35.1 | 0 | OK | Ground clear controls. | 120 | 35.1 | 790.82
8447 | TIN-INTERP | Interpolated Ground | 54080.1 | 4.84 | 754.92 | 0 | 24.37 | 0 | OK | Ground clear controls. | 120 | 35.03 | 779.29
8448 | TIN-INTERP | Interpolated Ground | 54080.11 | 4.06 | 755.06 | 0 | 35.03 | 0 | OK | Ground clear controls. | 120 | 35.03 | 790.09
8449 | TIN-INTERP | Interpolated Ground | 54080.14 | 6.21 | 754.69 | 0 | 29.84 | 0 | OK | Ground clear controls. | 120 | 33.43 | 784.53
8450 | TIN-INTERP | Interpolated Ground | 54119.91 | -5.34 | 765.59 | 0 | 27.64 | 0 | OK | Ground clear controls. | 120 | 33.43 | 793.23
8451 | TIN-INTERP | Interpolated Ground | 54119.92 | -3.81 | 765.16 | 0 | 22.52 | 0 | OK | Ground clear controls. | 120 | 33.43 | 787.68
8452 | TIN-INTERP | Interpolated Ground | 54119.94 | -3.54 | 765.09 | 0 | 33.43 | 0 | OK | Ground clear controls. | 120 | 33.43 | 798.52
8453 | TIN-INTERP | Interpolated Ground | 54120.1 | 4.82 | 764.55 | 0 | 22.39 | 0 | OK | Ground clear controls. | 120 | 33.19 | 786.94
8454 | TIN-INTERP | Interpolated Ground | 54120.11 | 4.02 | 764.66 | 0 | 33.19 | 0 | OK | Ground clear controls. | 120 | 33.19 | 797.85
8455 | TIN-INTERP | Interpolated Ground | 54120.14 | 6.19 | 764.3 | 0 | 27.95 | 0 | OK | Ground clear controls. | 120 | 27.95 | 792.25
8456 | TIN-INTERP | Interpolated Ground | 54149.27 | 6.19 | 766.69 | 0 | 31.5 | 0 | OK | Ground clear controls. | 121 | 50.35 | 798.19
8457 | TIN-INTERP | Interpolated Ground | 54149.86 | 4 | 766.55 | 0 | 37.11 | 0 | OK | Ground clear controls. | 121 | 50.35 | 803.66
8458 | TIN-INTERP | Interpolated Ground | 54149.9 | 4.83 | 766.54 | 0 | 26.15 | 0 | OK | Ground clear controls. | 121 | 50.35 | 792.69
8459 | TIN-INTERP | Interpolated Ground | 54153.15 | -3.52 | 767.43 | 0 | 36.24 | 0 | OK | Ground clear controls. | 121 | 50.35 | 803.67
8460 | TIN-INTERP | Interpolated Ground | 54153.57 | -3.73 | 767.54 | 0 | 25.16 | 0 | OK | Ground clear controls. | 121 | 50.35 | 792.7
8461 | TIN-INTERP | Interpolated Ground | 54154.14 | -5.33 | 768.07 | 0 | 30.12 | 0 | OK | Ground clear controls. | 121 | 50.35 | 798.19
8462 | TIN-INTERP | Interpolated Ground | 54189.27 | 6.25 | 764.21 | 0 | 30.01 | 0 | OK | Ground clear controls. | 121 | 50.35 | 794.22
8463 | TIN-INTERP | Interpolated Ground | 54189.86 | 4.08 | 764.44 | 0 | 34.81 | 0 | OK | Ground clear controls. | 121 | 50.35 | 799.25
8464 | TIN-INTERP | Interpolated Ground | 54189.9 | 4.87 | 764.38 | 0 | 24.33 | 0 | OK | Ground clear controls. | 121 | 50.35 | 788.71
8465 | TIN-INTERP | Interpolated Ground | 54193.15 | -3.63 | 765.09 | 0 | 34.29 | 0 | OK | Ground clear controls. | 121 | 50.35 | 799.38
8466 | TIN-INTERP | Interpolated Ground | 54193.57 | -3.87 | 765.09 | 0 | 23.82 | 0 | OK | Ground clear controls. | 121 | 50.35 | 788.91
8467 | TIN-INTERP | Interpolated Ground | 54194.14 | -5.46 | 765.38 | 0 | 28.85 | 0 | OK | Ground clear controls. | 121 | 50.35 | 794.23
8468 | TIN-INTERP | Interpolated Ground | 54229.27 | 6.3 | 755.28 | 0 | 35.87 | 0 | OK | Ground clear controls. | 121 | 50.35 | 791.15
8469 | TIN-INTERP | Interpolated Ground | 54229.86 | 4.16 | 755.81 | 0 | 40.05 | 0 | OK | Ground clear controls. | 121 | 50.35 | 795.86
8470 | TIN-INTERP | Interpolated Ground | 54229.9 | 4.91 | 755.65 | 0 | 29.97 | 0 | OK | Ground clear controls. | 121 | 50.35 | 785.62
8471 | TIN-INTERP | Interpolated Ground | 54233.15 | -3.74 | 755.82 | 0 | 40.28 | 0 | OK | Ground clear controls. | 121 | 50.35 | 796.1
8472 | TIN-INTERP | Interpolated Ground | 54233.57 | -4.01 | 755.78 | 0 | 30.21 | 0 | OK | Ground clear controls. | 121 | 50.35 | 785.99
8473 | TIN-INTERP | Interpolated Ground | 54234.14 | -5.6 | 755.99 | 0 | 35.2 | 0 | OK | Ground clear controls. | 121 | 50.35 | 791.19
8474 | TIN-INTERP | Interpolated Ground | 54269.27 | 6.36 | 748.56 | 0 | 40.43 | 0 | OK | Ground clear controls. | 121 | 50.35 | 788.99
8475 | TIN-INTERP | Interpolated Ground | 54269.86 | 4.23 | 749.19 | 0 | 44.3 | 0 | OK | Ground clear controls. | 121 | 50.35 | 793.49
8476 | TIN-INTERP | Interpolated Ground | 54269.9 | 4.95 | 749.01 | 0 | 34.44 | 0 | OK | Ground clear controls. | 121 | 50.35 | 783.45
8477 | TIN-INTERP | Interpolated Ground | 54273.15 | -3.85 | 751.21 | 0 | 42.6 | 0 | OK | Ground clear controls. | 121 | 50.35 | 793.81
8478 | TIN-INTERP | Interpolated Ground | 54273.57 | -4.16 | 751.32 | 0 | 32.61 | 0 | OK | Ground clear controls. | 121 | 50.35 | 783.93
8479 | TIN-INTERP | Interpolated Ground | 54274.14 | -5.73 | 752.11 | 0 | 36.94 | 0 | OK | Ground clear controls. | 121 | 50.35 | 789.05
8480 | TIN-INTERP | Interpolated Ground | 54309.27 | 6.41 | 749.86 | 0 | 37.86 | 0 | OK | Ground clear controls. | 121 | 50.35 | 787.72
8481 | TIN-INTERP | Interpolated Ground | 54309.86 | 4.31 | 750.65 | 0 | 41.49 | 0 | OK | Ground clear controls. | 121 | 50.35 | 792.14
8482 | TIN-INTERP | Interpolated Ground | 54309.9 | 4.99 | 750.51 | 0 | 31.66 | 0 | OK | Ground clear controls. | 121 | 50.35 | 782.17
8483 | TIN-INTERP | Interpolated Ground | 54313.15 | -3.96 | 753.84 | 0 | 38.66 | 0 | OK | Ground clear controls. | 121 | 50.35 | 792.5
8484 | TIN-INTERP | Interpolated Ground | 54313.57 | -4.3 | 753.93 | 0 | 28.8 | 0 | OK | Ground clear controls. | 121 | 50.35 | 782.73
8485 | TIN-INTERP | Interpolated Ground | 54314.14 | -5.86 | 754.37 | 0 | 33.45 | 0 | OK | Ground clear controls. | 121 | 50.35 | 787.82
8486 | TIN-INTERP | Interpolated Ground | 54349.27 | 6.47 | 746.66 | 0 | 40.69 | 0 | OK | Ground clear controls. | 121 | 50.35 | 787.35
8487 | TIN-INTERP | Interpolated Ground | 54349.86 | 4.39 | 747.32 | 0 | 44.47 | 0 | OK | Ground clear controls. | 121 | 50.35 | 791.79
8488 | TIN-INTERP | Interpolated Ground | 54349.9 | 5.03 | 747.06 | 0 | 34.76 | 0 | OK | Ground clear controls. | 121 | 50.35 | 781.82
8489 | TIN-INTERP | Interpolated Ground | 54353.15 | -4.07 | 750.76 | 0 | 41.43 | 0 | OK | Ground clear controls. | 121 | 50.35 | 792.19
8490 | TIN-INTERP | Interpolated Ground | 54353.57 | -4.44 | 750.88 | 0 | 31.51 | 0 | OK | Ground clear controls. | 121 | 50.35 | 782.39
8491 | TIN-INTERP | Interpolated Ground | 54354.14 | -5.99 | 751.59 | 0 | 35.92 | 0 | OK | Ground clear controls. | 121 | 50.35 | 787.51
8492 | TIN-INTERP | Interpolated Ground | 54389.27 | 6.52 | 741.39 | 0 | 46.5 | 0 | OK | Ground clear controls. | 121 | 50.35 | 787.89
8493 | TIN-INTERP | Interpolated Ground | 54389.86 | 4.46 | 742.12 | 0 | 50.35 | 0 | OK | Ground clear controls. | 121 | 50.35 | 792.47
8494 | TIN-INTERP | Interpolated Ground | 54389.9 | 5.07 | 742.08 | 0 | 40.28 | 0 | OK | Ground clear controls. | 121 | 47.03 | 782.36
8495 | TIN-INTERP | Interpolated Ground | 54393.15 | -4.19 | 745.84 | 0 | 47.03 | 0 | OK | Ground clear controls. | 121 | 47.03 | 792.87
8496 | TIN-INTERP | Interpolated Ground | 54393.57 | -4.59 | 746.14 | 0 | 36.78 | 0 | OK | Ground clear controls. | 121 | 41.37 | 782.92
8497 | TIN-INTERP | Interpolated Ground | 54394.14 | -6.12 | 746.73 | 0 | 41.37 | 0 | OK | Ground clear controls. | 121 | 41.37 | 788.1
8498 | TIN-INTERP | Interpolated Ground | 54429.27 | 6.58 | 758.54 | 0 | 30.78 | 0 | OK | Ground clear controls. | 121 | 35.06 | 789.32
8499 | TIN-INTERP | Interpolated Ground | 54429.86 | 4.54 | 759.1 | 0 | 35.06 | 0 | OK | Ground clear controls. | 121 | 35.06 | 794.16
8500 | TIN-INTERP | Interpolated Ground | 54429.9 | 5.11 | 759.03 | 0 | 24.79 | 0 | OK | Ground clear controls. | 121 | 31.63 | 783.82
8501 | TIN-INTERP | Interpolated Ground | 54433.15 | -4.3 | 762.92 | 0 | 31.63 | 0 | OK | Ground clear controls. | 121 | 31.63 | 794.55
8502 | TIN-INTERP | Interpolated Ground | 54433.57 | -4.73 | 763.12 | 0 | 21.19 | 0 | OK | Ground clear controls. | 121 | 27.32 | 784.31
8503 | TIN-INTERP | Interpolated Ground | 54434.13 | -6.26 | 763.43 | 0 | 26.15 | 0 | OK | Ground clear controls. | 121 | 27.32 | 789.58
8504 | TIN-INTERP | Interpolated Ground | 54469.27 | 6.63 | 768.93 | 0 | 22.71 | 0 | OK | Ground clear controls. | 121 | 27.32 | 791.64
8505 | TIN-INTERP | Interpolated Ground | 54469.86 | 4.62 | 769.56 | 0 | 27.32 | 0 | OK | Ground clear controls. | 121 | 27.32 | 796.88
8506 | TIN-INTERP | Interpolated Ground | 54469.9 | 5.15 | 769.43 | 0 | 16.74 | 0 | OK | Ground clear controls. | 121 | 25.32 | 786.17
8507 | TIN-INTERP | Interpolated Ground | 54473.15 | -4.41 | 771.9 | 0 | 25.32 | 0 | OK | Ground clear controls. | 121 | 25.32 | 797.22
8508 | TIN-INTERP | Interpolated Ground | 54473.57 | -4.87 | 772.09 | 0 | 14.47 | 0 | OK | Ground clear controls. | 121 | 19.62 | 786.56
8509 | TIN-INTERP | Interpolated Ground | 54474.13 | -6.39 | 772.37 | 0 | 19.62 | 0 | OK | Ground clear controls. | 121 | 19.62 | 791.99
8510 | TIN-INTERP | Interpolated Ground | 54496.56 | 6.67 | 773.59 | 0 | 20.16 | 0 | OK | Ground clear controls. | 122 | 61.75 | 793.75
8511 | TIN-INTERP | Interpolated Ground | 54496.57 | 5.18 | 773.76 | 0 | 14.49 | 0 | OK | Ground clear controls. | 122 | 61.75 | 788.25
8512 | TIN-INTERP | Interpolated Ground | 54496.6 | 4.67 | 773.77 | 0 | 25.49 | 0 | OK | Ground clear controls. | 122 | 61.75 | 799.26
8513 | TIN-INTERP | Interpolated Ground | 54496.64 | -4.96 | 774.05 | 0 | 14.2 | 0 | OK | Ground clear controls. | 122 | 61.75 | 788.25
8514 | TIN-INTERP | Interpolated Ground | 54496.7 | -4.47 | 774.02 | 0 | 25.23 | 0 | OK | Ground clear controls. | 122 | 61.75 | 799.25
8515 | TIN-INTERP | Interpolated Ground | 54496.76 | -6.46 | 773.93 | 0 | 19.83 | 0 | OK | Ground clear controls. | 122 | 61.75 | 793.76
8516 | TIN-INTERP | Interpolated Ground | 54536.56 | 6.66 | 764.65 | 0 | 26.15 | 0 | OK | Ground clear controls. | 122 | 61.75 | 790.8
8517 | TIN-INTERP | Interpolated Ground | 54536.57 | 5.16 | 764.51 | 0 | 20.76 | 0 | OK | Ground clear controls. | 122 | 61.75 | 785.27
8518 | TIN-INTERP | Interpolated Ground | 54536.6 | 4.66 | 764.45 | 0 | 31.42 | 0 | OK | Ground clear controls. | 122 | 61.75 | 795.87
8519 | TIN-INTERP | Interpolated Ground | 54536.64 | -4.98 | 760.52 | 0 | 24.91 | 0 | OK | Ground clear controls. | 122 | 61.75 | 785.43
8520 | TIN-INTERP | Interpolated Ground | 54536.7 | -4.49 | 760.76 | 0 | 35.21 | 0 | OK | Ground clear controls. | 122 | 61.75 | 795.97
8521 | TIN-INTERP | Interpolated Ground | 54536.76 | -6.48 | 759.75 | 0 | 31.04 | 0 | OK | Ground clear controls. | 122 | 61.75 | 790.79
8522 | TIN-INTERP | Interpolated Ground | 54576.56 | 6.65 | 738.61 | 0 | 50.14 | 0 | OK | Ground clear controls. | 122 | 61.75 | 788.75
8523 | TIN-INTERP | Interpolated Ground | 54576.57 | 5.15 | 737.72 | 0 | 45.48 | 0 | OK | Ground clear controls. | 122 | 61.75 | 783.2
8524 | TIN-INTERP | Interpolated Ground | 54576.6 | 4.64 | 737.61 | 0 | 55.9 | 0 | OK | Ground clear controls. | 122 | 61.75 | 793.51
8525 | TIN-INTERP | Interpolated Ground | 54576.64 | -5 | 735.72 | 0 | 47.76 | 0 | OK | Ground clear controls. | 122 | 61.75 | 783.48
8526 | TIN-INTERP | Interpolated Ground | 54576.7 | -4.51 | 735.56 | 0 | 58.12 | 0 | OK | Ground clear controls. | 122 | 61.75 | 793.68
8527 | TIN-INTERP | Interpolated Ground | 54576.76 | -6.5 | 735.64 | 0 | 53.09 | 0 | OK | Ground clear controls. | 122 | 61.75 | 788.73
8528 | TIN-INTERP | Interpolated Ground | 54616.56 | 6.63 | 729.7 | 0 | 57.89 | 0 | OK | Ground clear controls. | 122 | 61.75 | 787.59
8529 | TIN-INTERP | Interpolated Ground | 54616.57 | 5.14 | 730.2 | 0 | 51.83 | 0 | OK | Ground clear controls. | 122 | 61.75 | 782.03
8530 | TIN-INTERP | Interpolated Ground | 54616.6 | 4.63 | 730.41 | 0 | 61.75 | 0 | OK | Ground clear controls. | 122 | 61.75 | 792.16
8531 | TIN-INTERP | Interpolated Ground | 54616.64 | -5.02 | 734.75 | 0 | 47.64 | 0 | OK | Ground clear controls. | 122 | 57.94 | 782.39
8532 | TIN-INTERP | Interpolated Ground | 54616.7 | -4.53 | 734.43 | 0 | 57.94 | 0 | OK | Ground clear controls. | 122 | 57.94 | 792.37
8533 | TIN-INTERP | Interpolated Ground | 54616.76 | -6.52 | 735.6 | 0 | 51.97 | 0 | OK | Ground clear controls. | 122 | 51.97 | 787.57
8534 | TIN-INTERP | Interpolated Ground | 54656.56 | 6.62 | 752.98 | 0 | 34.35 | 0 | OK | Ground clear controls. | 122 | 44.54 | 787.33
8535 | TIN-INTERP | Interpolated Ground | 54656.57 | 5.12 | 752.44 | 0 | 29.33 | 0 | OK | Ground clear controls. | 122 | 44.54 | 781.77
8536 | TIN-INTERP | Interpolated Ground | 54656.6 | 4.62 | 752.22 | 0 | 39.6 | 0 | OK | Ground clear controls. | 122 | 44.54 | 791.82
8537 | TIN-INTERP | Interpolated Ground | 54656.64 | -5.04 | 747.19 | 0 | 34.96 | 0 | OK | Ground clear controls. | 122 | 44.54 | 782.15
8538 | TIN-INTERP | Interpolated Ground | 54656.7 | -4.54 | 747.51 | 0 | 44.54 | 0 | OK | Ground clear controls. | 122 | 44.54 | 792.05
8539 | TIN-INTERP | Interpolated Ground | 54656.76 | -6.54 | 746.25 | 0 | 41.05 | 0 | OK | Ground clear controls. | 122 | 41.05 | 787.3
8540 | TIN-INTERP | Interpolated Ground | 54696.56 | 6.61 | 757.1 | 0 | 30.87 | 0 | OK | Ground clear controls. | 122 | 36.21 | 787.97
8541 | TIN-INTERP | Interpolated Ground | 54696.57 | 5.11 | 756.95 | 0 | 25.46 | 0 | OK | Ground clear controls. | 122 | 36.21 | 782.41
8542 | TIN-INTERP | Interpolated Ground | 54696.6 | 4.61 | 756.9 | 0 | 35.59 | 0 | OK | Ground clear controls. | 122 | 36.21 | 792.49
8543 | TIN-INTERP | Interpolated Ground | 54696.64 | -5.06 | 756.27 | 0 | 26.51 | 0 | OK | Ground clear controls. | 122 | 36.21 | 782.78
8544 | TIN-INTERP | Interpolated Ground | 54696.7 | -4.56 | 756.5 | 0 | 36.21 | 0 | OK | Ground clear controls. | 122 | 36.21 | 792.71
8545 | TIN-INTERP | Interpolated Ground | 54696.76 | -6.56 | 755.87 | 0 | 32.08 | 0 | OK | Ground clear controls. | 122 | 32.08 | 787.95
8546 | TIN-INTERP | Interpolated Ground | 54736.56 | 6.59 | 765.51 | 0 | 24 | 0 | OK | Ground clear controls. | 122 | 28.76 | 789.51
8547 | TIN-INTERP | Interpolated Ground | 54736.57 | 5.1 | 765.63 | 0 | 18.32 | 0 | OK | Ground clear controls. | 122 | 28.76 | 783.95
8548 | TIN-INTERP | Interpolated Ground | 54736.6 | 4.6 | 765.67 | 0 | 28.5 | 0 | OK | Ground clear controls. | 122 | 28.76 | 794.17
8549 | TIN-INTERP | Interpolated Ground | 54736.64 | -5.08 | 765.47 | 0 | 18.8 | 0 | OK | Ground clear controls. | 122 | 28.76 | 784.27
8550 | TIN-INTERP | Interpolated Ground | 54736.7 | -4.58 | 765.6 | 0 | 28.76 | 0 | OK | Ground clear controls. | 122 | 28.76 | 794.36
8551 | TIN-INTERP | Interpolated Ground | 54736.76 | -6.58 | 765.4 | 0 | 24.09 | 0 | OK | Ground clear controls. | 122 | 27.46 | 789.49
8552 | TIN-INTERP | Interpolated Ground | 54776.56 | 6.58 | 768.87 | 0 | 23.06 | 0 | OK | Ground clear controls. | 122 | 27.46 | 791.93
8553 | TIN-INTERP | Interpolated Ground | 54776.57 | 5.08 | 769.98 | 0 | 16.41 | 0 | OK | Ground clear controls. | 122 | 27.46 | 786.39
8554 | TIN-INTERP | Interpolated Ground | 54776.6 | 4.59 | 770.27 | 0 | 26.59 | 0 | OK | Ground clear controls. | 122 | 27.46 | 796.86
8555 | TIN-INTERP | Interpolated Ground | 54776.64 | -5.1 | 772.41 | 0 | 14.21 | 0 | OK | Ground clear controls. | 122 | 27.46 | 786.62
8556 | TIN-INTERP | Interpolated Ground | 54776.7 | -4.6 | 772.5 | 0 | 24.5 | 0 | OK | Ground clear controls. | 122 | 27.46 | 797
8557 | TIN-INTERP | Interpolated Ground | 54776.76 | -6.6 | 772.22 | 0 | 19.71 | 0 | OK | Ground clear controls. | 122 | 27.46 | 791.93
8558 | TIN-INTERP | Interpolated Ground | 54816.56 | 6.57 | 772.16 | 0 | 23.1 | 0 | OK | Ground clear controls. | 122 | 27.46 | 795.26
8559 | TIN-INTERP | Interpolated Ground | 54816.57 | 5.07 | 772.85 | 0 | 16.9 | 0 | OK | Ground clear controls. | 122 | 27.46 | 789.75
8560 | TIN-INTERP | Interpolated Ground | 54816.6 | 4.58 | 773.1 | 0 | 27.46 | 0 | OK | Ground clear controls. | 122 | 27.46 | 800.56
8561 | TIN-INTERP | Interpolated Ground | 54816.64 | -5.12 | 776 | 0 | 13.84 | 0 | OK | Ground clear controls. | 122 | 24.63 | 789.84
8562 | TIN-INTERP | Interpolated Ground | 54816.7 | -4.62 | 775.98 | 0 | 24.63 | 0 | OK | Ground clear controls. | 122 | 24.63 | 800.61
8563 | TIN-INTERP | Interpolated Ground | 54816.76 | -6.62 | 776.09 | 0 | 19.19 | 0 | OK | Ground clear controls. | 122 | 19.19 | 795.28
8564 | TIN-INTERP | Interpolated Ground | 54834.56 | -5.13 | 777.23 | 0 | 14.33 | 0 | OK | Ground clear controls. | 123 | 44.06 | 791.56
8565 | TIN-INTERP | Interpolated Ground | 54834.62 | -6.63 | 777.44 | 0 | 19.62 | 0 | OK | Ground clear controls. | 123 | 44.06 | 797.06
8566 | TIN-INTERP | Interpolated Ground | 54834.65 | 6.56 | 775 | 0 | 22.06 | 0 | OK | Ground clear controls. | 123 | 44.06 | 797.06
8567 | TIN-INTERP | Interpolated Ground | 54834.65 | -4.62 | 777.16 | 0 | 25.4 | 0 | OK | Ground clear controls. | 123 | 44.06 | 802.56
8568 | TIN-INTERP | Interpolated Ground | 54834.65 | 4.57 | 775.25 | 0 | 27.31 | 0 | OK | Ground clear controls. | 123 | 44.06 | 802.56
8569 | TIN-INTERP | Interpolated Ground | 54834.67 | 5.06 | 775.14 | 0 | 16.42 | 0 | OK | Ground clear controls. | 123 | 44.06 | 791.56
8570 | TIN-INTERP | Interpolated Ground | 54874.56 | -5.25 | 765.19 | 0 | 23.84 | 0 | OK | Ground clear controls. | 123 | 44.06 | 789.03
8571 | TIN-INTERP | Interpolated Ground | 54874.62 | -6.74 | 765.71 | 0 | 28.75 | 0 | OK | Ground clear controls. | 123 | 44.06 | 794.46
8572 | TIN-INTERP | Interpolated Ground | 54874.65 | -4.73 | 764.87 | 0 | 34.94 | 0 | OK | Ground clear controls. | 123 | 44.06 | 799.81
8573 | TIN-INTERP | Interpolated Ground | 54874.65 | 6.44 | 759.74 | 0 | 34.74 | 0 | OK | Ground clear controls. | 123 | 44.06 | 794.48
8574 | TIN-INTERP | Interpolated Ground | 54874.65 | 4.45 | 760.38 | 0 | 39.39 | 0 | OK | Ground clear controls. | 123 | 44.06 | 799.77
8575 | TIN-INTERP | Interpolated Ground | 54874.67 | 4.94 | 760.24 | 0 | 28.73 | 0 | OK | Ground clear controls. | 123 | 44.06 | 788.97
8576 | TIN-INTERP | Interpolated Ground | 54914.56 | -5.36 | 754.09 | 0 | 33.29 | 0 | OK | Ground clear controls. | 123 | 44.06 | 787.38
8577 | TIN-INTERP | Interpolated Ground | 54914.62 | -6.85 | 754.15 | 0 | 38.62 | 0 | OK | Ground clear controls. | 123 | 44.06 | 792.77
8578 | TIN-INTERP | Interpolated Ground | 54914.65 | -4.84 | 754.17 | 0 | 43.89 | 0 | OK | Ground clear controls. | 123 | 44.06 | 798.06
8579 | TIN-INTERP | Interpolated Ground | 54914.65 | 6.31 | 753.29 | 0 | 39.51 | 0 | OK | Ground clear controls. | 123 | 44.06 | 792.8
8580 | TIN-INTERP | Interpolated Ground | 54914.65 | 4.34 | 753.94 | 0 | 44.06 | 0 | OK | Ground clear controls. | 123 | 44.06 | 798
8581 | TIN-INTERP | Interpolated Ground | 54914.67 | 4.81 | 753.8 | 0 | 33.49 | 0 | OK | Ground clear controls. | 123 | 33.49 | 787.29
8582 | TIN-INTERP | Interpolated Ground | 54954.56 | -5.48 | 774.62 | 0 | 11.96 | 0 | OK | Ground clear controls. | 123 | 26.79 | 786.58
8583 | TIN-INTERP | Interpolated Ground | 54954.62 | -6.96 | 775.07 | 0 | 16.92 | 0 | OK | Ground clear controls. | 123 | 26.79 | 791.99
8584 | TIN-INTERP | Interpolated Ground | 54954.65 | -4.94 | 774.5 | 0 | 22.78 | 0 | OK | Ground clear controls. | 123 | 26.79 | 797.28
8585 | TIN-INTERP | Interpolated Ground | 54954.65 | 6.18 | 770.64 | 0 | 21.38 | 0 | OK | Ground clear controls. | 123 | 26.79 | 792.02
8586 | TIN-INTERP | Interpolated Ground | 54954.65 | 4.22 | 771.14 | 0 | 26.09 | 0 | OK | Ground clear controls. | 123 | 26.79 | 797.23
8587 | TIN-INTERP | Interpolated Ground | 54954.66 | 4.68 | 771.04 | 0 | 15.47 | 0 | OK | Ground clear controls. | 123 | 26.79 | 786.51
8588 | TIN-INTERP | Interpolated Ground | 54994.56 | -5.59 | 775.4 | 0 | 11.26 | 0 | OK | Ground clear controls. | 123 | 26.79 | 786.66
8589 | TIN-INTERP | Interpolated Ground | 54994.62 | -7.08 | 776.53 | 0 | 15.57 | 0 | OK | Ground clear controls. | 123 | 26.79 | 792.1
8590 | TIN-INTERP | Interpolated Ground | 54994.65 | -5.05 | 774.95 | 0 | 22.54 | 0 | OK | Ground clear controls. | 123 | 26.79 | 797.49
8591 | TIN-INTERP | Interpolated Ground | 54994.65 | 6.05 | 770.04 | 0 | 22.1 | 0 | OK | Ground clear controls. | 123 | 26.79 | 792.14
8592 | TIN-INTERP | Interpolated Ground | 54994.65 | 4.1 | 770.69 | 0 | 26.79 | 0 | OK | Ground clear controls. | 123 | 26.79 | 797.48
8593 | TIN-INTERP | Interpolated Ground | 54994.66 | 4.56 | 770.54 | 0 | 16.09 | 0 | OK | Ground clear controls. | 123 | 16.09 | 786.63
8594 | TIN-INTERP | Interpolated Ground | 55021.12 | 4.02 | 768.23 | 0 | 29.97 | 0 | OK | Ground clear controls. | 124 | 37.98 | 798.2
8595 | TIN-INTERP | Interpolated Ground | 55021.13 | 4.47 | 768.24 | 0 | 18.97 | 0 | OK | Ground clear controls. | 124 | 37.98 | 787.21
8596 | TIN-INTERP | Interpolated Ground | 55021.2 | 5.97 | 768.19 | 0 | 24.52 | 0 | OK | Ground clear controls. | 124 | 37.98 | 792.71
8597 | TIN-INTERP | Interpolated Ground | 55021.61 | -5.11 | 771.79 | 0 | 26.4 | 0 | OK | Ground clear controls. | 124 | 37.98 | 798.19
8598 | TIN-INTERP | Interpolated Ground | 55021.72 | -5.67 | 772.58 | 0 | 14.62 | 0 | OK | Ground clear controls. | 124 | 37.98 | 787.2
8599 | TIN-INTERP | Interpolated Ground | 55021.79 | -7.14 | 774.6 | 0 | 18.09 | 0 | OK | Ground clear controls. | 124 | 37.98 | 792.69
8600 | TIN-INTERP | Interpolated Ground | 55060.98 | 4.45 | 757.68 | 0 | 25.95 | 0 | OK | Ground clear controls. | 124 | 37.98 | 783.63
8601 | TIN-INTERP | Interpolated Ground | 55060.98 | 4 | 757.94 | 0 | 36.42 | 0 | OK | Ground clear controls. | 124 | 37.98 | 794.36
8602 | TIN-INTERP | Interpolated Ground | 55061 | 5.94 | 756.82 | 0 | 32.34 | 0 | OK | Ground clear controls. | 124 | 37.98 | 789.16
8603 | TIN-INTERP | Interpolated Ground | 55061.61 | -4.95 | 762.97 | 0 | 31.45 | 0 | OK | Ground clear controls. | 124 | 37.98 | 794.42
8604 | TIN-INTERP | Interpolated Ground | 55061.72 | -5.51 | 763.11 | 0 | 20.6 | 0 | OK | Ground clear controls. | 124 | 37.98 | 783.71
8605 | TIN-INTERP | Interpolated Ground | 55061.79 | -6.98 | 764.04 | 0 | 25.08 | 0 | OK | Ground clear controls. | 124 | 37.98 | 789.12
8606 | TIN-INTERP | Interpolated Ground | 55100.98 | 4.44 | 757.91 | 0 | 23.05 | 0 | OK | Ground clear controls. | 124 | 37.98 | 780.96
8607 | TIN-INTERP | Interpolated Ground | 55100.98 | 3.98 | 757.87 | 0 | 33.67 | 0 | OK | Ground clear controls. | 124 | 37.98 | 791.54
8608 | TIN-INTERP | Interpolated Ground | 55101 | 5.93 | 758.11 | 0 | 28.39 | 0 | OK | Ground clear controls. | 124 | 37.98 | 786.5
8609 | TIN-INTERP | Interpolated Ground | 55101.61 | -4.79 | 759.86 | 0 | 31.78 | 0 | OK | Ground clear controls. | 124 | 37.98 | 791.64
8610 | TIN-INTERP | Interpolated Ground | 55101.71 | -5.36 | 760.21 | 0 | 20.89 | 0 | OK | Ground clear controls. | 124 | 37.98 | 781.1
8611 | TIN-INTERP | Interpolated Ground | 55101.79 | -6.82 | 760.64 | 0 | 25.82 | 0 | OK | Ground clear controls. | 124 | 37.98 | 786.46
8612 | TIN-INTERP | Interpolated Ground | 55140.98 | 4.43 | 760.25 | 0 | 18.96 | 0 | OK | Ground clear controls. | 124 | 37.98 | 779.21
8613 | TIN-INTERP | Interpolated Ground | 55140.98 | 3.97 | 760.44 | 0 | 29.31 | 0 | OK | Ground clear controls. | 124 | 37.98 | 789.75
8614 | TIN-INTERP | Interpolated Ground | 55141 | 5.92 | 759.79 | 0 | 24.97 | 0 | OK | Ground clear controls. | 124 | 37.98 | 784.76
8615 | TIN-INTERP | Interpolated Ground | 55141.61 | -4.62 | 763.82 | 0 | 26.03 | 0 | OK | Ground clear controls. | 124 | 37.98 | 789.85
8616 | TIN-INTERP | Interpolated Ground | 55141.71 | -5.2 | 764.02 | 0 | 15.34 | 0 | OK | Ground clear controls. | 124 | 37.98 | 779.36
8617 | TIN-INTERP | Interpolated Ground | 55141.79 | -6.66 | 764.46 | 0 | 20.24 | 0 | OK | Ground clear controls. | 124 | 37.98 | 784.7
8618 | TIN-INTERP | Interpolated Ground | 55180.98 | 4.42 | 750.94 | 0 | 27.43 | 0 | OK | Ground clear controls. | 124 | 37.98 | 778.37
8619 | TIN-INTERP | Interpolated Ground | 55180.98 | 3.95 | 751 | 0 | 37.98 | 0 | OK | Ground clear controls. | 124 | 37.98 | 788.98
8620 | TIN-INTERP | Interpolated Ground | 55181 | 5.91 | 750.5 | 0 | 33.41 | 0 | OK | Ground clear controls. | 124 | 34.51 | 783.91
8621 | TIN-INTERP | Interpolated Ground | 55181.61 | -4.46 | 754.54 | 0 | 34.51 | 0 | OK | Ground clear controls. | 124 | 34.51 | 789.05
8622 | TIN-INTERP | Interpolated Ground | 55181.71 | -5.04 | 754.93 | 0 | 23.56 | 0 | OK | Ground clear controls. | 124 | 27.95 | 778.49
8623 | TIN-INTERP | Interpolated Ground | 55181.79 | -6.49 | 755.9 | 0 | 27.95 | 0 | OK | Ground clear controls. | 124 | 27.95 | 783.85
8624 | TIN-INTERP | Interpolated Ground | 55220.98 | 4.41 | 761.69 | 0 | 16.75 | 0 | OK | Ground clear controls. | 124 | 27.44 | 778.44
8625 | TIN-INTERP | Interpolated Ground | 55220.98 | 3.94 | 761.8 | 0 | 27.44 | 0 | OK | Ground clear controls. | 124 | 27.44 | 789.24
8626 | TIN-INTERP | Interpolated Ground | 55221 | 5.9 | 761.34 | 0 | 22.62 | 0 | OK | Ground clear controls. | 124 | 24.33 | 783.96
8627 | TIN-INTERP | Interpolated Ground | 55221.61 | -4.3 | 764.92 | 0 | 24.33 | 0 | OK | Ground clear controls. | 124 | 24.33 | 789.25
8628 | TIN-INTERP | Interpolated Ground | 55221.71 | -4.89 | 765.39 | 0 | 13.09 | 0 | OK | Ground clear controls. | 124 | 17.51 | 778.48
8629 | TIN-INTERP | Interpolated Ground | 55221.79 | -6.33 | 766.39 | 0 | 17.51 | 0 | OK | Ground clear controls. | 124 | 17.51 | 783.9
8630 | TIN-INTERP | Interpolated Ground | 55252.8 | -6.24 | 761.73 | 0 | 22.9 | 0 | OK | Ground clear controls. | 125 | 53.98 | 784.63
8631 | TIN-INTERP | Interpolated Ground | 55253.01 | -4.19 | 760.94 | 0 | 29.17 | 0 | OK | Ground clear controls. | 125 | 53.98 | 790.11
8632 | TIN-INTERP | Interpolated Ground | 55253.2 | -4.79 | 761.01 | 0 | 18.1 | 0 | OK | Ground clear controls. | 125 | 53.98 | 779.11
8633 | TIN-INTERP | Interpolated Ground | 55254.59 | 3.96 | 760.78 | 0 | 29.33 | 0 | OK | Ground clear controls. | 125 | 53.98 | 790.11
8634 | TIN-INTERP | Interpolated Ground | 55254.9 | 4.46 | 760.9 | 0 | 18.21 | 0 | OK | Ground clear controls. | 125 | 53.98 | 779.11
8635 | TIN-INTERP | Interpolated Ground | 55255.14 | 5.94 | 760.81 | 0 | 23.82 | 0 | OK | Ground clear controls. | 125 | 53.98 | 784.63
8636 | TIN-INTERP | Interpolated Ground | 55292.8 | -6.24 | 755.88 | 0 | 31.38 | 0 | OK | Ground clear controls. | 125 | 53.98 | 787.26
8637 | TIN-INTERP | Interpolated Ground | 55293.01 | -4.19 | 754.42 | 0 | 38.07 | 0 | OK | Ground clear controls. | 125 | 53.98 | 792.49
8638 | TIN-INTERP | Interpolated Ground | 55293.2 | -4.79 | 754.49 | 0 | 27.07 | 0 | OK | Ground clear controls. | 125 | 53.98 | 781.56
8639 | TIN-INTERP | Interpolated Ground | 55294.59 | 3.95 | 751.89 | 0 | 40.49 | 0 | OK | Ground clear controls. | 125 | 53.98 | 792.38
8640 | TIN-INTERP | Interpolated Ground | 55294.9 | 4.45 | 751.61 | 0 | 29.91 | 0 | OK | Ground clear controls. | 125 | 53.98 | 781.52
8641 | TIN-INTERP | Interpolated Ground | 55295.14 | 5.93 | 751 | 0 | 36.18 | 0 | OK | Ground clear controls. | 125 | 53.98 | 787.18
8642 | TIN-INTERP | Interpolated Ground | 55332.8 | -6.24 | 747 | 0 | 43.73 | 0 | OK | Ground clear controls. | 125 | 53.98 | 790.73
8643 | TIN-INTERP | Interpolated Ground | 55333.01 | -4.2 | 747.14 | 0 | 48.62 | 0 | OK | Ground clear controls. | 125 | 53.98 | 795.76
8644 | TIN-INTERP | Interpolated Ground | 55333.2 | -4.8 | 747.09 | 0 | 37.8 | 0 | OK | Ground clear controls. | 125 | 53.98 | 784.89
8645 | TIN-INTERP | Interpolated Ground | 55334.59 | 3.94 | 748.9 | 0 | 46.7 | 0 | OK | Ground clear controls. | 125 | 53.98 | 795.6
8646 | TIN-INTERP | Interpolated Ground | 55334.9 | 4.43 | 749.22 | 0 | 35.62 | 0 | OK | Ground clear controls. | 125 | 53.98 | 784.84
8647 | TIN-INTERP | Interpolated Ground | 55335.14 | 5.92 | 749.86 | 0 | 40.77 | 0 | OK | Ground clear controls. | 125 | 53.98 | 790.63
8648 | TIN-INTERP | Interpolated Ground | 55372.8 | -6.25 | 753.9 | 0 | 41.17 | 0 | OK | Ground clear controls. | 125 | 53.98 | 795.07
8649 | TIN-INTERP | Interpolated Ground | 55373.01 | -4.2 | 755.23 | 0 | 44.71 | 0 | OK | Ground clear controls. | 125 | 53.98 | 799.94
8650 | TIN-INTERP | Interpolated Ground | 55373.2 | -4.8 | 754.75 | 0 | 34.36 | 0 | OK | Ground clear controls. | 125 | 53.98 | 789.11
8651 | TIN-INTERP | Interpolated Ground | 55374.59 | 3.93 | 761 | 0 | 38.75 | 0 | OK | Ground clear controls. | 125 | 53.98 | 799.75
8652 | TIN-INTERP | Interpolated Ground | 55374.9 | 4.42 | 761.13 | 0 | 27.96 | 0 | OK | Ground clear controls. | 125 | 53.98 | 789.09
8653 | TIN-INTERP | Interpolated Ground | 55375.14 | 5.91 | 762 | 0 | 32.96 | 0 | OK | Ground clear controls. | 125 | 53.98 | 794.96
8654 | TIN-INTERP | Interpolated Ground | 55412.8 | -6.25 | 755.19 | 0 | 45.07 | 0 | OK | Ground clear controls. | 125 | 53.98 | 800.26
8655 | TIN-INTERP | Interpolated Ground | 55413.01 | -4.21 | 756.83 | 0 | 48.19 | 0 | OK | Ground clear controls. | 125 | 53.98 | 805.02
8656 | TIN-INTERP | Interpolated Ground | 55413.2 | -4.81 | 756.35 | 0 | 37.89 | 0 | OK | Ground clear controls. | 125 | 53.98 | 794.24
8657 | TIN-INTERP | Interpolated Ground | 55414.59 | 3.92 | 763.02 | 0 | 41.83 | 0 | OK | Ground clear controls. | 125 | 53.98 | 804.85
8658 | TIN-INTERP | Interpolated Ground | 55414.9 | 4.41 | 763.39 | 0 | 30.87 | 0 | OK | Ground clear controls. | 125 | 53.98 | 794.26
8659 | TIN-INTERP | Interpolated Ground | 55415.14 | 5.9 | 764.54 | 0 | 35.65 | 0 | OK | Ground clear controls. | 125 | 53.98 | 800.19
8660 | TIN-INTERP | Interpolated Ground | 55452.8 | -6.26 | 760.36 | 0 | 45.95 | 0 | OK | Ground clear controls. | 125 | 53.98 | 806.31
8661 | TIN-INTERP | Interpolated Ground | 55453.01 | -4.21 | 761.77 | 0 | 49.26 | 0 | OK | Ground clear controls. | 125 | 53.98 | 811.03
8662 | TIN-INTERP | Interpolated Ground | 55453.2 | -4.81 | 761.29 | 0 | 38.97 | 0 | OK | Ground clear controls. | 125 | 53.98 | 800.26
8663 | TIN-INTERP | Interpolated Ground | 55454.59 | 3.91 | 767.73 | 0 | 43.16 | 0 | OK | Ground clear controls. | 125 | 53.98 | 810.89
8664 | TIN-INTERP | Interpolated Ground | 55454.9 | 4.4 | 768.02 | 0 | 32.32 | 0 | OK | Ground clear controls. | 125 | 53.98 | 800.34
8665 | TIN-INTERP | Interpolated Ground | 55455.14 | 5.89 | 769.27 | 0 | 37.07 | 0 | OK | Ground clear controls. | 125 | 53.98 | 806.34
8666 | TIN-INTERP | Interpolated Ground | 55492.8 | -6.26 | 768.66 | 0 | 44.57 | 0 | OK | Ground clear controls. | 125 | 53.98 | 813.23
8667 | TIN-INTERP | Interpolated Ground | 55493.01 | -4.22 | 767.47 | 0 | 50.47 | 0 | OK | Ground clear controls. | 125 | 53.98 | 817.94
8668 | TIN-INTERP | Interpolated Ground | 55493.2 | -4.82 | 767.91 | 0 | 39.28 | 0 | OK | Ground clear controls. | 125 | 53.98 | 807.19
8669 | TIN-INTERP | Interpolated Ground | 55494.59 | 3.9 | 763.9 | 0 | 53.98 | 0 | OK | Ground clear controls. | 125 | 53.98 | 817.88
8670 | TIN-INTERP | Interpolated Ground | 55494.9 | 4.38 | 763.8 | 0 | 43.56 | 0 | OK | Ground clear controls. | 125 | 51.44 | 807.36
8671 | TIN-INTERP | Interpolated Ground | 55495.14 | 5.88 | 763.58 | 0 | 49.8 | 0 | OK | Ground clear controls. | 125 | 51.44 | 813.38
8672 | TIN-INTERP | Interpolated Ground | 55532.8 | -6.26 | 781.62 | 0 | 39.4 | 0 | OK | Ground clear controls. | 125 | 51.44 | 821.02
8673 | TIN-INTERP | Interpolated Ground | 55533.01 | -4.22 | 780.44 | 0 | 45.32 | 0 | OK | Ground clear controls. | 125 | 51.44 | 825.76
8674 | TIN-INTERP | Interpolated Ground | 55533.2 | -4.82 | 780.86 | 0 | 34.16 | 0 | OK | Ground clear controls. | 125 | 51.44 | 815.02
8675 | TIN-INTERP | Interpolated Ground | 55534.59 | 3.89 | 774.39 | 0 | 51.44 | 0 | OK | Ground clear controls. | 125 | 51.44 | 825.83
8676 | TIN-INTERP | Interpolated Ground | 55534.9 | 4.37 | 774.1 | 0 | 41.22 | 0 | OK | Ground clear controls. | 125 | 48.29 | 815.32
8677 | TIN-INTERP | Interpolated Ground | 55535.14 | 5.87 | 773.03 | 0 | 48.29 | 0 | OK | Ground clear controls. | 125 | 48.29 | 821.32
8678 | TIN-INTERP | Interpolated Ground | 55572.8 | -6.27 | 798.36 | 0 | 31.32 | 0 | OK | Ground clear controls. | 125 | 45.6 | 829.68
8679 | TIN-INTERP | Interpolated Ground | 55573.01 | -4.23 | 797.01 | 0 | 37.5 | 0 | OK | Ground clear controls. | 125 | 45.6 | 834.51
8680 | TIN-INTERP | Interpolated Ground | 55573.2 | -4.83 | 797.52 | 0 | 26.25 | 0 | OK | Ground clear controls. | 125 | 45.6 | 823.77
8681 | TIN-INTERP | Interpolated Ground | 55574.59 | 3.88 | 792.73 | 0 | 42.01 | 0 | OK | Ground clear controls. | 125 | 45.6 | 834.74
8682 | TIN-INTERP | Interpolated Ground | 55574.9 | 4.36 | 792.6 | 0 | 31.61 | 0 | OK | Ground clear controls. | 125 | 45.6 | 824.21
8683 | TIN-INTERP | Interpolated Ground | 55575.14 | 5.86 | 791.77 | 0 | 38.4 | 0 | OK | Ground clear controls. | 125 | 45.6 | 830.17
8684 | TIN-INTERP | Interpolated Ground | 55612.8 | -6.27 | 806.17 | 0 | 33.04 | 0 | OK | Ground clear controls. | 125 | 45.6 | 839.21
8685 | TIN-INTERP | Interpolated Ground | 55613.01 | -4.23 | 804.8 | 0 | 39.39 | 0 | OK | Ground clear controls. | 125 | 45.6 | 844.19
8686 | TIN-INTERP | Interpolated Ground | 55613.2 | -4.83 | 805.29 | 0 | 28.13 | 0 | OK | Ground clear controls. | 125 | 45.6 | 833.42
8687 | TIN-INTERP | Interpolated Ground | 55614.59 | 3.87 | 799 | 0 | 45.6 | 0 | OK | Ground clear controls. | 125 | 45.6 | 844.6
8688 | TIN-INTERP | Interpolated Ground | 55614.9 | 4.34 | 798.74 | 0 | 35.3 | 0 | OK | Ground clear controls. | 125 | 44.61 | 834.04
8689 | TIN-INTERP | Interpolated Ground | 55615.14 | 5.85 | 797.65 | 0 | 42.29 | 0 | OK | Ground clear controls. | 125 | 44.61 | 839.94
8690 | TIN-INTERP | Interpolated Ground | 55652.8 | -6.28 | 809.89 | 0 | 39.73 | 0 | OK | Ground clear controls. | 125 | 44.61 | 849.62
8691 | TIN-INTERP | Interpolated Ground | 55653.01 | -4.24 | 810.19 | 0 | 44.61 | 0 | OK | Ground clear controls. | 125 | 44.61 | 854.8
8692 | TIN-INTERP | Interpolated Ground | 55653.2 | -4.84 | 810.18 | 0 | 33.82 | 0 | OK | Ground clear controls. | 125 | 41.62 | 844
8693 | TIN-INTERP | Interpolated Ground | 55654.59 | 3.86 | 813.81 | 0 | 41.62 | 0 | OK | Ground clear controls. | 125 | 41.62 | 855.43
8694 | TIN-INTERP | Interpolated Ground | 55654.9 | 4.33 | 814.12 | 0 | 30.7 | 0 | OK | Ground clear controls. | 125 | 35.95 | 844.82
8695 | TIN-INTERP | Interpolated Ground | 55655.14 | 5.84 | 814.68 | 0 | 35.95 | 0 | OK | Ground clear controls. | 125 | 35.95 | 850.63
8696 | TIN-INTERP | Interpolated Ground | 55692.8 | -6.28 | 834.53 | 0 | 26.39 | 0 | OK | Ground clear controls. | 125 | 31.83 | 860.92
8697 | TIN-INTERP | Interpolated Ground | 55693.01 | -4.24 | 834.51 | 0 | 31.83 | 0 | OK | Ground clear controls. | 125 | 31.83 | 866.34
8698 | TIN-INTERP | Interpolated Ground | 55693.2 | -4.84 | 834.66 | 0 | 20.84 | 0 | OK | Ground clear controls. | 125 | 31.69 | 855.5
8699 | TIN-INTERP | Interpolated Ground | 55694.59 | 3.85 | 835.54 | 0 | 31.69 | 0 | OK | Ground clear controls. | 125 | 31.69 | 867.23
8700 | TIN-INTERP | Interpolated Ground | 55694.9 | 4.32 | 835.83 | 0 | 20.71 | 0 | OK | Ground clear controls. | 125 | 26.58 | 856.54
8701 | TIN-INTERP | Interpolated Ground | 55695.14 | 5.83 | 835.66 | 0 | 26.58 | 0 | OK | Ground clear controls. | 125 | 26.58 | 862.24
8702 | TIN-INTERP | Interpolated Ground | 55725.41 | -6.26 | 847.42 | 0 | 22.26 | 0 | OK | Ground clear controls. | 126 | 59.38 | 869.68
8703 | TIN-INTERP | Interpolated Ground | 55725.79 | -4.23 | 847.47 | 0 | 27.7 | 0 | OK | Ground clear controls. | 126 | 59.38 | 875.17
8704 | TIN-INTERP | Interpolated Ground | 55725.97 | -4.86 | 847.46 | 0 | 16.71 | 0 | OK | Ground clear controls. | 126 | 59.38 | 864.17
8705 | TIN-INTERP | Interpolated Ground | 55727.9 | 3.8 | 847.11 | 0 | 28.06 | 0 | OK | Ground clear controls. | 126 | 59.38 | 875.17
8706 | TIN-INTERP | Interpolated Ground | 55728.39 | 4.23 | 847.11 | 0 | 17.06 | 0 | OK | Ground clear controls. | 126 | 59.38 | 864.17
8707 | TIN-INTERP | Interpolated Ground | 55728.66 | 5.72 | 847.05 | 0 | 22.63 | 0 | OK | Ground clear controls. | 126 | 59.38 | 869.68
8708 | TIN-INTERP | Interpolated Ground | 55765.41 | -6.29 | 831.09 | 0 | 30.37 | 0 | OK | Ground clear controls. | 126 | 59.38 | 861.46
8709 | TIN-INTERP | Interpolated Ground | 55765.79 | -4.26 | 831.07 | 0 | 35.79 | 0 | OK | Ground clear controls. | 126 | 59.38 | 866.86
8710 | TIN-INTERP | Interpolated Ground | 55765.97 | -4.88 | 830.93 | 0 | 25 | 0 | OK | Ground clear controls. | 126 | 59.38 | 855.93
8711 | TIN-INTERP | Interpolated Ground | 55767.9 | 3.87 | 831.81 | 0 | 35.06 | 0 | OK | Ground clear controls. | 126 | 59.38 | 866.87
8712 | TIN-INTERP | Interpolated Ground | 55768.39 | 4.31 | 831.79 | 0 | 24.17 | 0 | OK | Ground clear controls. | 126 | 59.38 | 855.96
8713 | TIN-INTERP | Interpolated Ground | 55768.66 | 5.79 | 831.74 | 0 | 29.69 | 0 | OK | Ground clear controls. | 126 | 59.38 | 861.43
8714 | TIN-INTERP | Interpolated Ground | 55805.41 | -6.32 | 816.1 | 0 | 38.08 | 0 | OK | Ground clear controls. | 126 | 59.38 | 854.18
8715 | TIN-INTERP | Interpolated Ground | 55805.79 | -4.3 | 815.12 | 0 | 44.4 | 0 | OK | Ground clear controls. | 126 | 59.38 | 859.52
8716 | TIN-INTERP | Interpolated Ground | 55805.97 | -4.9 | 815.29 | 0 | 33.34 | 0 | OK | Ground clear controls. | 126 | 59.38 | 848.63
8717 | TIN-INTERP | Interpolated Ground | 55807.9 | 3.94 | 817.72 | 0 | 41.81 | 0 | OK | Ground clear controls. | 126 | 59.38 | 859.53
8718 | TIN-INTERP | Interpolated Ground | 55808.39 | 4.38 | 817.66 | 0 | 31.03 | 0 | OK | Ground clear controls. | 126 | 59.38 | 848.69
8719 | TIN-INTERP | Interpolated Ground | 55808.66 | 5.86 | 818.2 | 0 | 35.92 | 0 | OK | Ground clear controls. | 126 | 59.38 | 854.12
8720 | TIN-INTERP | Interpolated Ground | 55845.41 | -6.35 | 796.42 | 0 | 51.42 | 0 | OK | Ground clear controls. | 126 | 59.38 | 847.84
8721 | TIN-INTERP | Interpolated Ground | 55845.79 | -4.33 | 794.65 | 0 | 58.48 | 0 | OK | Ground clear controls. | 126 | 59.38 | 853.13
8722 | TIN-INTERP | Interpolated Ground | 55845.97 | -4.92 | 794.87 | 0 | 47.41 | 0 | OK | Ground clear controls. | 126 | 59.38 | 842.28
8723 | TIN-INTERP | Interpolated Ground | 55847.9 | 4 | 793.77 | 0 | 59.38 | 0 | OK | Ground clear controls. | 126 | 59.38 | 853.15
8724 | TIN-INTERP | Interpolated Ground | 55848.39 | 4.45 | 793.69 | 0 | 48.68 | 0 | OK | Ground clear controls. | 126 | 53.23 | 842.37
8725 | TIN-INTERP | Interpolated Ground | 55848.66 | 5.94 | 794.54 | 0 | 53.23 | 0 | OK | Ground clear controls. | 126 | 53.23 | 847.77
8726 | TIN-INTERP | Interpolated Ground | 55885.41 | -6.37 | 799.4 | 0 | 43.04 | 0 | OK | Ground clear controls. | 126 | 52.75 | 842.44
8727 | TIN-INTERP | Interpolated Ground | 55885.79 | -4.36 | 798.44 | 0 | 49.26 | 0 | OK | Ground clear controls. | 126 | 52.75 | 847.7
8728 | TIN-INTERP | Interpolated Ground | 55885.97 | -4.94 | 798.68 | 0 | 38.19 | 0 | OK | Ground clear controls. | 126 | 52.75 | 836.87
8729 | TIN-INTERP | Interpolated Ground | 55887.9 | 4.07 | 794.98 | 0 | 52.75 | 0 | OK | Ground clear controls. | 126 | 52.75 | 847.73
8730 | TIN-INTERP | Interpolated Ground | 55888.39 | 4.52 | 794.78 | 0 | 42.2 | 0 | OK | Ground clear controls. | 126 | 48.49 | 836.98
8731 | TIN-INTERP | Interpolated Ground | 55888.66 | 6.01 | 793.88 | 0 | 48.49 | 0 | OK | Ground clear controls. | 126 | 48.49 | 842.37
8732 | TIN-INTERP | Interpolated Ground | 55925.41 | -6.4 | 799.34 | 0 | 38.64 | 0 | OK | Ground clear controls. | 126 | 45.65 | 837.98
8733 | TIN-INTERP | Interpolated Ground | 55925.79 | -4.39 | 799.52 | 0 | 43.7 | 0 | OK | Ground clear controls. | 126 | 45.65 | 843.22
8734 | TIN-INTERP | Interpolated Ground | 55925.97 | -4.96 | 799.6 | 0 | 32.81 | 0 | OK | Ground clear controls. | 126 | 45.65 | 832.41
8735 | TIN-INTERP | Interpolated Ground | 55927.9 | 4.13 | 797.61 | 0 | 45.65 | 0 | OK | Ground clear controls. | 126 | 45.65 | 843.26
8736 | TIN-INTERP | Interpolated Ground | 55928.39 | 4.6 | 797.53 | 0 | 35 | 0 | OK | Ground clear controls. | 126 | 40.84 | 832.53
8737 | TIN-INTERP | Interpolated Ground | 55928.66 | 6.09 | 797.07 | 0 | 40.84 | 0 | OK | Ground clear controls. | 126 | 40.84 | 837.91
8738 | TIN-INTERP | Interpolated Ground | 55965.41 | -6.43 | 805.27 | 0 | 29.18 | 0 | OK | Ground clear controls. | 126 | 39.71 | 834.45
8739 | TIN-INTERP | Interpolated Ground | 55965.79 | -4.42 | 804.16 | 0 | 35.51 | 0 | OK | Ground clear controls. | 126 | 39.71 | 839.67
8740 | TIN-INTERP | Interpolated Ground | 55965.97 | -4.98 | 804.43 | 0 | 24.44 | 0 | OK | Ground clear controls. | 126 | 39.71 | 828.87
8741 | TIN-INTERP | Interpolated Ground | 55967.9 | 4.2 | 800.84 | 0 | 38.89 | 0 | OK | Ground clear controls. | 126 | 39.71 | 839.73
8742 | TIN-INTERP | Interpolated Ground | 55968.39 | 4.67 | 800.64 | 0 | 28.37 | 0 | OK | Ground clear controls. | 126 | 39.71 | 829.01
8743 | TIN-INTERP | Interpolated Ground | 55968.66 | 6.16 | 799.99 | 0 | 34.4 | 0 | OK | Ground clear controls. | 126 | 39.71 | 834.39
8744 | TIN-INTERP | Interpolated Ground | 56005.41 | -6.46 | 802.65 | 0 | 29.2 | 0 | OK | Ground clear controls. | 126 | 39.71 | 831.85
8745 | TIN-INTERP | Interpolated Ground | 56005.79 | -4.45 | 802.05 | 0 | 35.04 | 0 | OK | Ground clear controls. | 126 | 39.71 | 837.09
8746 | TIN-INTERP | Interpolated Ground | 56005.97 | -5 | 802.25 | 0 | 24.03 | 0 | OK | Ground clear controls. | 126 | 39.71 | 826.28
8747 | TIN-INTERP | Interpolated Ground | 56007.9 | 4.27 | 797.44 | 0 | 39.71 | 0 | OK | Ground clear controls. | 126 | 39.71 | 837.15
8748 | TIN-INTERP | Interpolated Ground | 56008.39 | 4.74 | 797.01 | 0 | 29.41 | 0 | OK | Ground clear controls. | 126 | 38.25 | 826.42
8749 | TIN-INTERP | Interpolated Ground | 56008.66 | 6.23 | 795.88 | 0 | 35.93 | 0 | OK | Ground clear controls. | 126 | 38.25 | 831.81
8750 | TIN-INTERP | Interpolated Ground | 56045.41 | -6.49 | 800.37 | 0 | 29.81 | 0 | OK | Ground clear controls. | 126 | 38.25 | 830.18
8751 | TIN-INTERP | Interpolated Ground | 56045.79 | -4.48 | 799.86 | 0 | 35.58 | 0 | OK | Ground clear controls. | 126 | 38.25 | 835.44
8752 | TIN-INTERP | Interpolated Ground | 56045.97 | -5.02 | 800.02 | 0 | 24.6 | 0 | OK | Ground clear controls. | 126 | 38.25 | 824.62
8753 | TIN-INTERP | Interpolated Ground | 56047.9 | 4.33 | 797.27 | 0 | 38.25 | 0 | OK | Ground clear controls. | 126 | 38.25 | 835.52
8754 | TIN-INTERP | Interpolated Ground | 56048.39 | 4.81 | 797.08 | 0 | 27.68 | 0 | OK | Ground clear controls. | 126 | 33.96 | 824.76
8755 | TIN-INTERP | Interpolated Ground | 56048.66 | 6.31 | 796.2 | 0 | 33.96 | 0 | OK | Ground clear controls. | 126 | 33.96 | 830.16
8756 | TIN-INTERP | Interpolated Ground | 56085.41 | -6.52 | 811.84 | 0 | 17.59 | 0 | OK | Ground clear controls. | 126 | 32.11 | 829.43
8757 | TIN-INTERP | Interpolated Ground | 56085.79 | -4.51 | 810.92 | 0 | 23.83 | 0 | OK | Ground clear controls. | 126 | 32.11 | 834.75
8758 | TIN-INTERP | Interpolated Ground | 56085.97 | -5.04 | 811.18 | 0 | 12.71 | 0 | OK | Ground clear controls. | 126 | 32.11 | 823.89
8759 | TIN-INTERP | Interpolated Ground | 56087.9 | 4.4 | 806.77 | 0 | 28.07 | 0 | OK | Ground clear controls. | 126 | 32.11 | 834.84
8760 | TIN-INTERP | Interpolated Ground | 56088.39 | 4.88 | 806.42 | 0 | 17.62 | 0 | OK | Ground clear controls. | 126 | 32.11 | 824.04
8761 | TIN-INTERP | Interpolated Ground | 56088.66 | 6.38 | 805.55 | 0 | 23.92 | 0 | OK | Ground clear controls. | 126 | 32.11 | 829.47
8762 | TIN-INTERP | Interpolated Ground | 56125.41 | -6.55 | 809.6 | 0 | 20.01 | 0 | OK | Ground clear controls. | 126 | 32.11 | 829.61
8763 | TIN-INTERP | Interpolated Ground | 56125.79 | -4.54 | 809.48 | 0 | 25.52 | 0 | OK | Ground clear controls. | 126 | 32.11 | 835
8764 | TIN-INTERP | Interpolated Ground | 56125.97 | -5.06 | 809.56 | 0 | 14.53 | 0 | OK | Ground clear controls. | 126 | 32.11 | 824.09
8765 | TIN-INTERP | Interpolated Ground | 56127.9 | 4.47 | 802.98 | 0 | 32.11 | 0 | OK | Ground clear controls. | 126 | 32.11 | 835.09
8766 | TIN-INTERP | Interpolated Ground | 56128.39 | 4.96 | 802.61 | 0 | 21.63 | 0 | OK | Ground clear controls. | 126 | 30.63 | 824.24
8767 | TIN-INTERP | Interpolated Ground | 56128.66 | 6.46 | 801.65 | 0 | 28.04 | 0 | OK | Ground clear controls. | 126 | 30.63 | 829.69
8768 | TIN-INTERP | Interpolated Ground | 56165.41 | -6.58 | 807.63 | 0 | 23.09 | 0 | OK | Ground clear controls. | 126 | 30.63 | 830.72
8769 | TIN-INTERP | Interpolated Ground | 56165.79 | -4.58 | 806.41 | 0 | 29.78 | 0 | OK | Ground clear controls. | 126 | 30.63 | 836.19
8770 | TIN-INTERP | Interpolated Ground | 56165.97 | -5.09 | 806.69 | 0 | 18.54 | 0 | OK | Ground clear controls. | 126 | 30.63 | 825.23
8771 | TIN-INTERP | Interpolated Ground | 56167.9 | 4.53 | 805.66 | 0 | 30.63 | 0 | OK | Ground clear controls. | 126 | 30.63 | 836.29
8772 | TIN-INTERP | Interpolated Ground | 56168.39 | 5.03 | 805.57 | 0 | 19.8 | 0 | OK | Ground clear controls. | 126 | 26.2 | 825.37
8773 | TIN-INTERP | Interpolated Ground | 56168.66 | 6.53 | 804.66 | 0 | 26.2 | 0 | OK | Ground clear controls. | 126 | 26.2 | 830.86
8774 | TIN-INTERP | Interpolated Ground | 56192.82 | -6.6 | 806.86 | 0 | 25.16 | 0 | OK | Ground clear controls. | 127 | 45.26 | 832.02
8775 | TIN-INTERP | Interpolated Ground | 56192.82 | 5.07 | 802.35 | 0 | 24.17 | 0 | OK | Ground clear controls. | 127 | 45.26 | 826.52
8776 | TIN-INTERP | Interpolated Ground | 56192.84 | -5.1 | 805.79 | 0 | 20.73 | 0 | OK | Ground clear controls. | 127 | 45.26 | 826.52
8777 | TIN-INTERP | Interpolated Ground | 56192.84 | 4.58 | 802.4 | 0 | 35.12 | 0 | OK | Ground clear controls. | 127 | 45.26 | 837.52
8778 | TIN-INTERP | Interpolated Ground | 56192.85 | -4.6 | 805.44 | 0 | 32.08 | 0 | OK | Ground clear controls. | 127 | 45.26 | 837.52
8779 | TIN-INTERP | Interpolated Ground | 56192.87 | 6.57 | 802.18 | 0 | 29.84 | 0 | OK | Ground clear controls. | 127 | 45.26 | 832.02
8780 | TIN-INTERP | Interpolated Ground | 56232.82 | -6.6 | 802.28 | 0 | 23.74 | 0 | OK | Ground clear controls. | 127 | 45.26 | 826.02
8781 | TIN-INTERP | Interpolated Ground | 56232.82 | 5.07 | 796.3 | 0 | 24.21 | 0 | OK | Ground clear controls. | 127 | 45.26 | 820.51
8782 | TIN-INTERP | Interpolated Ground | 56232.84 | 4.58 | 796.18 | 0 | 35.26 | 0 | OK | Ground clear controls. | 127 | 45.26 | 831.44
8783 | TIN-INTERP | Interpolated Ground | 56232.84 | -5.1 | 801.36 | 0 | 19.14 | 0 | OK | Ground clear controls. | 127 | 45.26 | 820.5
8784 | TIN-INTERP | Interpolated Ground | 56232.85 | -4.6 | 801.06 | 0 | 30.39 | 0 | OK | Ground clear controls. | 127 | 45.26 | 831.45
8785 | TIN-INTERP | Interpolated Ground | 56232.86 | 6.57 | 796.5 | 0 | 29.49 | 0 | OK | Ground clear controls. | 127 | 45.26 | 825.99
8786 | TIN-INTERP | Interpolated Ground | 56272.82 | -6.6 | 782.26 | 0 | 38.69 | 0 | OK | Ground clear controls. | 127 | 45.26 | 820.95
8787 | TIN-INTERP | Interpolated Ground | 56272.82 | 5.08 | 780.92 | 0 | 34.52 | 0 | OK | Ground clear controls. | 127 | 45.26 | 815.44
8788 | TIN-INTERP | Interpolated Ground | 56272.84 | 4.58 | 781.06 | 0 | 45.26 | 0 | OK | Ground clear controls. | 127 | 45.26 | 826.32
8789 | TIN-INTERP | Interpolated Ground | 56272.84 | -5.1 | 781.52 | 0 | 33.9 | 0 | OK | Ground clear controls. | 127 | 45.06 | 815.42
8790 | TIN-INTERP | Interpolated Ground | 56272.85 | -4.6 | 781.27 | 0 | 45.06 | 0 | OK | Ground clear controls. | 127 | 45.06 | 826.33
8791 | TIN-INTERP | Interpolated Ground | 56272.86 | 6.58 | 780.69 | 0 | 40.22 | 0 | OK | Ground clear controls. | 127 | 44.49 | 820.91
8792 | TIN-INTERP | Interpolated Ground | 56312.82 | -6.6 | 798.29 | 0 | 18.53 | 0 | OK | Ground clear controls. | 127 | 44.49 | 816.82
8793 | TIN-INTERP | Interpolated Ground | 56312.82 | 5.08 | 794.37 | 0 | 16.94 | 0 | OK | Ground clear controls. | 127 | 44.49 | 811.31
8794 | TIN-INTERP | Interpolated Ground | 56312.84 | 4.58 | 794.56 | 0 | 27.59 | 0 | OK | Ground clear controls. | 127 | 44.49 | 822.15
8795 | TIN-INTERP | Interpolated Ground | 56312.84 | -5.1 | 797.55 | 0 | 13.73 | 0 | OK | Ground clear controls. | 127 | 44.49 | 811.28
8796 | TIN-INTERP | Interpolated Ground | 56312.85 | -4.6 | 797.37 | 0 | 24.79 | 0 | OK | Ground clear controls. | 127 | 44.49 | 822.16
8797 | TIN-INTERP | Interpolated Ground | 56312.86 | 6.58 | 793.96 | 0 | 22.8 | 0 | OK | Ground clear controls. | 127 | 44.49 | 816.76
8798 | TIN-INTERP | Interpolated Ground | 56352.82 | -6.6 | 794.49 | 0 | 19.15 | 0 | OK | Ground clear controls. | 127 | 44.49 | 813.64
8799 | TIN-INTERP | Interpolated Ground | 56352.82 | 5.08 | 788.13 | 0 | 19.99 | 0 | OK | Ground clear controls. | 127 | 44.49 | 808.12
8800 | TIN-INTERP | Interpolated Ground | 56352.84 | 4.58 | 788.31 | 0 | 30.63 | 0 | OK | Ground clear controls. | 127 | 44.49 | 818.94
8801 | TIN-INTERP | Interpolated Ground | 56352.84 | -5.11 | 793.46 | 0 | 14.63 | 0 | OK | Ground clear controls. | 127 | 44.49 | 808.09
8802 | TIN-INTERP | Interpolated Ground | 56352.85 | -4.6 | 793.12 | 0 | 25.84 | 0 | OK | Ground clear controls. | 127 | 44.49 | 818.96
8803 | TIN-INTERP | Interpolated Ground | 56352.86 | 6.58 | 787.58 | 0 | 25.99 | 0 | OK | Ground clear controls. | 127 | 44.49 | 813.57
8804 | TIN-INTERP | Interpolated Ground | 56392.82 | -6.61 | 796.17 | 0 | 15.22 | 0 | OK | Ground clear controls. | 127 | 44.49 | 811.39
8805 | TIN-INTERP | Interpolated Ground | 56392.82 | 5.08 | 790.28 | 0 | 15.59 | 0 | OK | Ground clear controls. | 127 | 44.49 | 805.87
8806 | TIN-INTERP | Interpolated Ground | 56392.84 | 4.58 | 790.45 | 0 | 26.22 | 0 | OK | Ground clear controls. | 127 | 44.49 | 816.67
8807 | TIN-INTERP | Interpolated Ground | 56392.84 | -5.11 | 795.3 | 0 | 10.54 | 0 | OK | Ground clear controls. | 127 | 44.49 | 805.84
8808 | TIN-INTERP | Interpolated Ground | 56392.85 | -4.61 | 794.96 | 0 | 21.73 | 0 | OK | Ground clear controls. | 127 | 44.49 | 816.69
8809 | TIN-INTERP | Interpolated Ground | 56392.86 | 6.58 | 789.77 | 0 | 21.55 | 0 | OK | Ground clear controls. | 127 | 44.49 | 811.32
8810 | TIN-INTERP | Interpolated Ground | 56432.82 | -6.61 | 779.81 | 0 | 30.26 | 0 | OK | Ground clear controls. | 127 | 44.49 | 810.07
8811 | TIN-INTERP | Interpolated Ground | 56432.82 | 5.08 | 781.05 | 0 | 23.5 | 0 | OK | Ground clear controls. | 127 | 44.49 | 804.55
8812 | TIN-INTERP | Interpolated Ground | 56432.84 | 4.58 | 780.86 | 0 | 34.5 | 0 | OK | Ground clear controls. | 127 | 44.49 | 815.36
8813 | TIN-INTERP | Interpolated Ground | 56432.84 | -5.11 | 779.24 | 0 | 25.28 | 0 | OK | Ground clear controls. | 127 | 44.49 | 804.52
8814 | TIN-INTERP | Interpolated Ground | 56432.85 | -4.61 | 779.02 | 0 | 36.36 | 0 | OK | Ground clear controls. | 127 | 44.49 | 815.38
8815 | TIN-INTERP | Interpolated Ground | 56432.86 | 6.58 | 781.55 | 0 | 28.46 | 0 | OK | Ground clear controls. | 127 | 44.49 | 810.01
8816 | TIN-INTERP | Interpolated Ground | 56472.82 | -6.61 | 775.34 | 0 | 34.35 | 0 | OK | Ground clear controls. | 127 | 44.49 | 809.69
8817 | TIN-INTERP | Interpolated Ground | 56472.82 | 5.08 | 770.28 | 0 | 33.89 | 0 | OK | Ground clear controls. | 127 | 44.49 | 804.17
8818 | TIN-INTERP | Interpolated Ground | 56472.84 | 4.58 | 770.51 | 0 | 44.49 | 0 | OK | Ground clear controls. | 127 | 44.49 | 815
8819 | TIN-INTERP | Interpolated Ground | 56472.84 | -5.11 | 775.26 | 0 | 28.88 | 0 | OK | Ground clear controls. | 127 | 40.01 | 804.14
8820 | TIN-INTERP | Interpolated Ground | 56472.85 | -4.61 | 775.11 | 0 | 39.91 | 0 | OK | Ground clear controls. | 127 | 40.01 | 815.02
8821 | TIN-INTERP | Interpolated Ground | 56472.86 | 6.58 | 769.62 | 0 | 40.01 | 0 | OK | Ground clear controls. | 127 | 40.01 | 809.63
8822 | TIN-INTERP | Interpolated Ground | 56512.82 | -6.61 | 784.67 | 0 | 25.56 | 0 | OK | Ground clear controls. | 127 | 32.14 | 810.23
8823 | TIN-INTERP | Interpolated Ground | 56512.82 | 5.08 | 783.52 | 0 | 21.2 | 0 | OK | Ground clear controls. | 127 | 32.14 | 804.72
8824 | TIN-INTERP | Interpolated Ground | 56512.84 | 4.58 | 783.44 | 0 | 32.14 | 0 | OK | Ground clear controls. | 127 | 32.14 | 815.58
8825 | TIN-INTERP | Interpolated Ground | 56512.84 | -5.11 | 784.51 | 0 | 20.19 | 0 | OK | Ground clear controls. | 127 | 31.28 | 804.7
8826 | TIN-INTERP | Interpolated Ground | 56512.85 | -4.61 | 784.32 | 0 | 31.28 | 0 | OK | Ground clear controls. | 127 | 31.28 | 815.6
8827 | TIN-INTERP | Interpolated Ground | 56512.86 | 6.58 | 783.52 | 0 | 26.66 | 0 | OK | Ground clear controls. | 127 | 26.66 | 810.18
8828 | TIN-INTERP | Interpolated Ground | 56552.82 | -6.61 | 795.52 | 0 | 16.2 | 0 | OK | Ground clear controls. | 127 | 25.3 | 811.72
8829 | TIN-INTERP | Interpolated Ground | 56552.82 | 5.08 | 792.6 | 0 | 13.61 | 0 | OK | Ground clear controls. | 127 | 25.3 | 806.21
8830 | TIN-INTERP | Interpolated Ground | 56552.84 | 4.58 | 792.78 | 0 | 24.34 | 0 | OK | Ground clear controls. | 127 | 25.3 | 817.12
8831 | TIN-INTERP | Interpolated Ground | 56552.84 | -5.11 | 795.26 | 0 | 10.93 | 0 | OK | Ground clear controls. | 127 | 25.3 | 806.19
8832 | TIN-INTERP | Interpolated Ground | 56552.85 | -4.61 | 795.18 | 0 | 21.95 | 0 | OK | Ground clear controls. | 127 | 25.3 | 817.13
8833 | TIN-INTERP | Interpolated Ground | 56552.86 | 6.58 | 792.08 | 0 | 19.61 | 0 | OK | Ground clear controls. | 127 | 25.3 | 811.69
8834 | TIN-INTERP | Interpolated Ground | 56592.82 | -6.61 | 796.99 | 0 | 17.14 | 0 | OK | Ground clear controls. | 127 | 25.3 | 814.13
8835 | TIN-INTERP | Interpolated Ground | 56592.82 | 5.08 | 794.16 | 0 | 14.48 | 0 | OK | Ground clear controls. | 127 | 25.3 | 808.64
8836 | TIN-INTERP | Interpolated Ground | 56592.84 | 4.58 | 794.3 | 0 | 25.3 | 0 | OK | Ground clear controls. | 127 | 25.3 | 819.6
8837 | TIN-INTERP | Interpolated Ground | 56592.84 | -5.11 | 796.7 | 0 | 11.93 | 0 | OK | Ground clear controls. | 127 | 23 | 808.63
8838 | TIN-INTERP | Interpolated Ground | 56592.85 | -4.61 | 796.6 | 0 | 23 | 0 | OK | Ground clear controls. | 127 | 23 | 819.6
8839 | TIN-INTERP | Interpolated Ground | 56592.86 | 6.58 | 793.75 | 0 | 20.38 | 0 | OK | Ground clear controls. | 127 | 20.38 | 814.13
8840 | TIN-INTERP | Interpolated Ground | 56611.69 | 5.08 | 793.87 | 0 | 16.23 | 0 | OK | Ground clear controls. | 128 | 44.91 | 810.1
8841 | TIN-INTERP | Interpolated Ground | 56611.7 | -5.12 | 795.23 | 0 | 14.87 | 0 | OK | Ground clear controls. | 128 | 44.91 | 810.1
8842 | TIN-INTERP | Interpolated Ground | 56611.7 | 4.58 | 793.94 | 0 | 27.16 | 0 | OK | Ground clear controls. | 128 | 44.91 | 821.1
8843 | TIN-INTERP | Interpolated Ground | 56611.72 | -6.62 | 795.45 | 0 | 20.15 | 0 | OK | Ground clear controls. | 128 | 44.91 | 815.6
8844 | TIN-INTERP | Interpolated Ground | 56611.72 | 6.58 | 793.5 | 0 | 22.1 | 0 | OK | Ground clear controls. | 128 | 44.91 | 815.6
8845 | TIN-INTERP | Interpolated Ground | 56611.74 | -4.62 | 795.16 | 0 | 25.94 | 0 | OK | Ground clear controls. | 128 | 44.91 | 821.1
8846 | TIN-INTERP | Interpolated Ground | 56651.69 | 5.08 | 785.05 | 0 | 19.72 | 0 | OK | Ground clear controls. | 128 | 44.91 | 804.77
8847 | TIN-INTERP | Interpolated Ground | 56651.69 | -5.11 | 781.05 | 0 | 23.72 | 0 | OK | Ground clear controls. | 128 | 44.91 | 804.77
8848 | TIN-INTERP | Interpolated Ground | 56651.7 | 4.58 | 784.92 | 0 | 30.8 | 0 | OK | Ground clear controls. | 128 | 44.91 | 815.72
8849 | TIN-INTERP | Interpolated Ground | 56651.71 | -6.61 | 780.28 | 0 | 30 | 0 | OK | Ground clear controls. | 128 | 44.91 | 810.28
8850 | TIN-INTERP | Interpolated Ground | 56651.72 | 6.58 | 785.06 | 0 | 25.2 | 0 | OK | Ground clear controls. | 128 | 44.91 | 810.26
8851 | TIN-INTERP | Interpolated Ground | 56651.74 | -4.61 | 781.27 | 0 | 34.46 | 0 | OK | Ground clear controls. | 128 | 44.91 | 815.73
8852 | TIN-INTERP | Interpolated Ground | 56691.69 | 5.09 | 768.08 | 0 | 32.31 | 0 | OK | Ground clear controls. | 128 | 44.91 | 800.39
8853 | TIN-INTERP | Interpolated Ground | 56691.69 | -5.11 | 767.39 | 0 | 32.98 | 0 | OK | Ground clear controls. | 128 | 44.91 | 800.37
8854 | TIN-INTERP | Interpolated Ground | 56691.7 | 4.59 | 767.93 | 0 | 43.37 | 0 | OK | Ground clear controls. | 128 | 44.91 | 811.3
8855 | TIN-INTERP | Interpolated Ground | 56691.71 | -6.61 | 767.75 | 0 | 38.16 | 0 | OK | Ground clear controls. | 128 | 44.91 | 805.91
8856 | TIN-INTERP | Interpolated Ground | 56691.72 | 6.59 | 768.81 | 0 | 37.07 | 0 | OK | Ground clear controls. | 128 | 44.91 | 805.88
8857 | TIN-INTERP | Interpolated Ground | 56691.74 | -4.61 | 767.26 | 0 | 44.07 | 0 | OK | Ground clear controls. | 128 | 44.91 | 811.33
8858 | TIN-INTERP | Interpolated Ground | 56731.69 | 5.09 | 773.55 | 0 | 23.4 | 0 | OK | Ground clear controls. | 128 | 44.91 | 796.95
8859 | TIN-INTERP | Interpolated Ground | 56731.69 | -5.11 | 774.82 | 0 | 22.12 | 0 | OK | Ground clear controls. | 128 | 44.91 | 796.94
8860 | TIN-INTERP | Interpolated Ground | 56731.7 | 4.59 | 773.6 | 0 | 34.25 | 0 | OK | Ground clear controls. | 128 | 44.91 | 807.85
8861 | TIN-INTERP | Interpolated Ground | 56731.71 | -6.61 | 775.17 | 0 | 27.31 | 0 | OK | Ground clear controls. | 128 | 44.91 | 802.48
8862 | TIN-INTERP | Interpolated Ground | 56731.72 | 6.59 | 773.4 | 0 | 29.04 | 0 | OK | Ground clear controls. | 128 | 44.91 | 802.44
8863 | TIN-INTERP | Interpolated Ground | 56731.74 | -4.61 | 774.67 | 0 | 33.21 | 0 | OK | Ground clear controls. | 128 | 44.91 | 807.88
8864 | TIN-INTERP | Interpolated Ground | 56771.69 | 5.09 | 771.68 | 0 | 22.77 | 0 | OK | Ground clear controls. | 128 | 44.91 | 794.45
8865 | TIN-INTERP | Interpolated Ground | 56771.69 | -5.11 | 773.08 | 0 | 21.36 | 0 | OK | Ground clear controls. | 128 | 44.91 | 794.44
8866 | TIN-INTERP | Interpolated Ground | 56771.7 | 4.59 | 771.75 | 0 | 33.59 | 0 | OK | Ground clear controls. | 128 | 44.91 | 805.34
8867 | TIN-INTERP | Interpolated Ground | 56771.71 | -6.61 | 773.48 | 0 | 26.51 | 0 | OK | Ground clear controls. | 128 | 44.91 | 799.99
8868 | TIN-INTERP | Interpolated Ground | 56771.72 | 6.59 | 771.47 | 0 | 28.47 | 0 | OK | Ground clear controls. | 128 | 44.91 | 799.94
8869 | TIN-INTERP | Interpolated Ground | 56771.74 | -4.61 | 772.94 | 0 | 32.44 | 0 | OK | Ground clear controls. | 128 | 44.91 | 805.38
8870 | TIN-INTERP | Interpolated Ground | 56811.69 | 5.09 | 773.31 | 0 | 19.59 | 0 | OK | Ground clear controls. | 128 | 44.91 | 792.9
8871 | TIN-INTERP | Interpolated Ground | 56811.69 | -5.11 | 774.12 | 0 | 18.77 | 0 | OK | Ground clear controls. | 128 | 44.91 | 792.89
8872 | TIN-INTERP | Interpolated Ground | 56811.7 | 4.59 | 773.36 | 0 | 30.44 | 0 | OK | Ground clear controls. | 128 | 44.91 | 803.8
8873 | TIN-INTERP | Interpolated Ground | 56811.71 | -6.61 | 774.49 | 0 | 23.95 | 0 | OK | Ground clear controls. | 128 | 44.91 | 798.44
8874 | TIN-INTERP | Interpolated Ground | 56811.72 | 6.59 | 773.03 | 0 | 25.37 | 0 | OK | Ground clear controls. | 128 | 44.91 | 798.4
8875 | TIN-INTERP | Interpolated Ground | 56811.74 | -4.61 | 774.02 | 0 | 29.82 | 0 | OK | Ground clear controls. | 128 | 44.91 | 803.84
8876 | TIN-INTERP | Interpolated Ground | 56851.69 | 5.09 | 758.02 | 0 | 34.28 | 0 | OK | Ground clear controls. | 128 | 44.91 | 792.3
8877 | TIN-INTERP | Interpolated Ground | 56851.69 | -5.11 | 760.35 | 0 | 31.94 | 0 | OK | Ground clear controls. | 128 | 44.91 | 792.29
8878 | TIN-INTERP | Interpolated Ground | 56851.7 | 4.59 | 758.3 | 0 | 44.91 | 0 | OK | Ground clear controls. | 128 | 44.91 | 803.21
8879 | TIN-INTERP | Interpolated Ground | 56851.71 | -6.61 | 760.34 | 0 | 37.48 | 0 | OK | Ground clear controls. | 128 | 42.87 | 797.82
8880 | TIN-INTERP | Interpolated Ground | 56851.72 | 6.59 | 757.28 | 0 | 40.51 | 0 | OK | Ground clear controls. | 128 | 42.87 | 797.79
8881 | TIN-INTERP | Interpolated Ground | 56851.74 | -4.61 | 760.38 | 0 | 42.87 | 0 | OK | Ground clear controls. | 128 | 42.87 | 803.25
8882 | TIN-INTERP | Interpolated Ground | 56891.69 | 5.09 | 773.87 | 0 | 18.77 | 0 | OK | Ground clear controls. | 128 | 29.59 | 792.64
8883 | TIN-INTERP | Interpolated Ground | 56891.69 | -5.11 | 775.61 | 0 | 17.01 | 0 | OK | Ground clear controls. | 128 | 29.59 | 792.62
8884 | TIN-INTERP | Interpolated Ground | 56891.7 | 4.59 | 773.99 | 0 | 29.59 | 0 | OK | Ground clear controls. | 128 | 29.59 | 803.58
8885 | TIN-INTERP | Interpolated Ground | 56891.71 | -6.61 | 775.65 | 0 | 22.5 | 0 | OK | Ground clear controls. | 128 | 27.99 | 798.15
8886 | TIN-INTERP | Interpolated Ground | 56891.72 | 6.59 | 773.42 | 0 | 24.72 | 0 | OK | Ground clear controls. | 128 | 27.99 | 798.14
8887 | TIN-INTERP | Interpolated Ground | 56891.74 | -4.61 | 775.61 | 0 | 27.99 | 0 | OK | Ground clear controls. | 128 | 27.99 | 803.6
8888 | TIN-INTERP | Interpolated Ground | 56931.69 | 5.09 | 779.69 | 0 | 14.22 | 0 | OK | Ground clear controls. | 128 | 25.06 | 793.91
8889 | TIN-INTERP | Interpolated Ground | 56931.69 | -5.11 | 781.97 | 0 | 11.94 | 0 | OK | Ground clear controls. | 128 | 25.06 | 793.91
8890 | TIN-INTERP | Interpolated Ground | 56931.7 | 4.59 | 779.84 | 0 | 25.06 | 0 | OK | Ground clear controls. | 128 | 25.06 | 804.9
8891 | TIN-INTERP | Interpolated Ground | 56931.71 | -6.61 | 782.83 | 0 | 16.58 | 0 | OK | Ground clear controls. | 128 | 23.22 | 799.41
8892 | TIN-INTERP | Interpolated Ground | 56931.72 | 6.59 | 779.03 | 0 | 20.38 | 0 | OK | Ground clear controls. | 128 | 23.22 | 799.41
8893 | TIN-INTERP | Interpolated Ground | 56931.74 | -4.61 | 781.69 | 0 | 23.22 | 0 | OK | Ground clear controls. | 128 | 23.22 | 804.91
8894 | TIN-INTERP | Interpolated Ground | 56938.89 | -6.61 | 783.05 | 0 | 16.69 | 0 | OK | Ground clear controls. | 129 | 47.02 | 799.74
8895 | TIN-INTERP | Interpolated Ground | 56938.89 | 6.59 | 779.77 | 0 | 19.97 | 0 | OK | Ground clear controls. | 129 | 47.02 | 799.74
8896 | TIN-INTERP | Interpolated Ground | 56938.89 | 5.09 | 779.85 | 0 | 14.39 | 0 | OK | Ground clear controls. | 129 | 47.02 | 794.24
8897 | TIN-INTERP | Interpolated Ground | 56938.91 | -4.61 | 782.35 | 0 | 22.89 | 0 | OK | Ground clear controls. | 129 | 47.02 | 805.24
8898 | TIN-INTERP | Interpolated Ground | 56938.92 | -5.11 | 782.58 | 0 | 11.66 | 0 | OK | Ground clear controls. | 129 | 47.02 | 794.24
8899 | TIN-INTERP | Interpolated Ground | 56938.95 | 4.59 | 779.88 | 0 | 25.36 | 0 | OK | Ground clear controls. | 129 | 47.02 | 805.24
8900 | TIN-INTERP | Interpolated Ground | 56978.89 | 6.59 | 772.45 | 0 | 23.32 | 0 | OK | Ground clear controls. | 129 | 47.02 | 795.77
8901 | TIN-INTERP | Interpolated Ground | 56978.89 | -6.61 | 776.89 | 0 | 18.9 | 0 | OK | Ground clear controls. | 129 | 47.02 | 795.79
8902 | TIN-INTERP | Interpolated Ground | 56978.89 | 5.09 | 772.92 | 0 | 17.35 | 0 | OK | Ground clear controls. | 129 | 47.02 | 790.27
8903 | TIN-INTERP | Interpolated Ground | 56978.91 | -4.61 | 776.5 | 0 | 24.74 | 0 | OK | Ground clear controls. | 129 | 47.02 | 801.24
8904 | TIN-INTERP | Interpolated Ground | 56978.92 | -5.11 | 776.87 | 0 | 13.41 | 0 | OK | Ground clear controls. | 129 | 47.02 | 790.28
8905 | TIN-INTERP | Interpolated Ground | 56978.95 | 4.59 | 773.07 | 0 | 28.17 | 0 | OK | Ground clear controls. | 129 | 47.02 | 801.24
8906 | TIN-INTERP | Interpolated Ground | 57018.89 | 6.59 | 768.6 | 0 | 24.15 | 0 | OK | Ground clear controls. | 129 | 47.02 | 792.75
8907 | TIN-INTERP | Interpolated Ground | 57018.89 | -6.62 | 771.38 | 0 | 21.41 | 0 | OK | Ground clear controls. | 129 | 47.02 | 792.79
8908 | TIN-INTERP | Interpolated Ground | 57018.89 | 5.09 | 768.96 | 0 | 18.3 | 0 | OK | Ground clear controls. | 129 | 47.02 | 787.26
8909 | TIN-INTERP | Interpolated Ground | 57018.91 | -4.62 | 770.94 | 0 | 27.26 | 0 | OK | Ground clear controls. | 129 | 47.02 | 798.2
8910 | TIN-INTERP | Interpolated Ground | 57018.92 | -5.12 | 771.05 | 0 | 16.22 | 0 | OK | Ground clear controls. | 129 | 47.02 | 787.27
8911 | TIN-INTERP | Interpolated Ground | 57018.95 | 4.59 | 768.98 | 0 | 29.21 | 0 | OK | Ground clear controls. | 129 | 47.02 | 798.19
8912 | TIN-INTERP | Interpolated Ground | 57058.89 | 6.59 | 764.9 | 0 | 25.78 | 0 | OK | Ground clear controls. | 129 | 47.02 | 790.68
8913 | TIN-INTERP | Interpolated Ground | 57058.89 | -6.62 | 766.61 | 0 | 24.12 | 0 | OK | Ground clear controls. | 129 | 47.02 | 790.73
8914 | TIN-INTERP | Interpolated Ground | 57058.89 | 5.09 | 764.94 | 0 | 20.25 | 0 | OK | Ground clear controls. | 129 | 47.02 | 785.19
8915 | TIN-INTERP | Interpolated Ground | 57058.91 | -4.62 | 766.13 | 0 | 29.99 | 0 | OK | Ground clear controls. | 129 | 47.02 | 796.12
8916 | TIN-INTERP | Interpolated Ground | 57058.92 | -5.12 | 766.25 | 0 | 18.95 | 0 | OK | Ground clear controls. | 129 | 47.02 | 785.2
8917 | TIN-INTERP | Interpolated Ground | 57058.95 | 4.59 | 764.96 | 0 | 31.14 | 0 | OK | Ground clear controls. | 129 | 47.02 | 796.1
8918 | TIN-INTERP | Interpolated Ground | 57098.89 | 6.59 | 764.21 | 0 | 25.35 | 0 | OK | Ground clear controls. | 129 | 47.02 | 789.56
8919 | TIN-INTERP | Interpolated Ground | 57098.89 | -6.63 | 766.69 | 0 | 22.92 | 0 | OK | Ground clear controls. | 129 | 47.02 | 789.61
8920 | TIN-INTERP | Interpolated Ground | 57098.89 | 5.09 | 764.66 | 0 | 19.41 | 0 | OK | Ground clear controls. | 129 | 47.02 | 784.07
8921 | TIN-INTERP | Interpolated Ground | 57098.91 | -4.62 | 766.27 | 0 | 28.71 | 0 | OK | Ground clear controls. | 129 | 47.02 | 794.98
8922 | TIN-INTERP | Interpolated Ground | 57098.92 | -5.13 | 766.32 | 0 | 17.75 | 0 | OK | Ground clear controls. | 129 | 47.02 | 784.07
8923 | TIN-INTERP | Interpolated Ground | 57098.95 | 4.59 | 764.81 | 0 | 30.15 | 0 | OK | Ground clear controls. | 129 | 47.02 | 794.96
8924 | TIN-INTERP | Interpolated Ground | 57138.89 | 6.59 | 746.99 | 0 | 42.39 | 0 | OK | Ground clear controls. | 129 | 47.02 | 789.38
8925 | TIN-INTERP | Interpolated Ground | 57138.89 | -6.63 | 751.28 | 0 | 38.14 | 0 | OK | Ground clear controls. | 129 | 47.02 | 789.42
8926 | TIN-INTERP | Interpolated Ground | 57138.89 | 5.09 | 747.55 | 0 | 36.34 | 0 | OK | Ground clear controls. | 129 | 47.02 | 783.89
8927 | TIN-INTERP | Interpolated Ground | 57138.91 | -4.63 | 751.21 | 0 | 43.58 | 0 | OK | Ground clear controls. | 129 | 47.02 | 794.79
8928 | TIN-INTERP | Interpolated Ground | 57138.92 | -5.13 | 751.31 | 0 | 32.59 | 0 | OK | Ground clear controls. | 129 | 47.02 | 783.9
8929 | TIN-INTERP | Interpolated Ground | 57138.95 | 4.59 | 747.75 | 0 | 47.02 | 0 | OK | Ground clear controls. | 129 | 47.02 | 794.77
8930 | TIN-INTERP | Interpolated Ground | 57178.89 | 6.59 | 760.26 | 0 | 29.88 | 0 | OK | Ground clear controls. | 129 | 37.46 | 790.14
8931 | TIN-INTERP | Interpolated Ground | 57178.89 | -6.64 | 757.78 | 0 | 32.41 | 0 | OK | Ground clear controls. | 129 | 37.46 | 790.19
8932 | TIN-INTERP | Interpolated Ground | 57178.89 | 5.09 | 760.11 | 0 | 24.54 | 0 | OK | Ground clear controls. | 129 | 37.46 | 784.65
8933 | TIN-INTERP | Interpolated Ground | 57178.91 | -4.63 | 758.1 | 0 | 37.46 | 0 | OK | Ground clear controls. | 129 | 37.46 | 795.56
8934 | TIN-INTERP | Interpolated Ground | 57178.92 | -5.13 | 758.08 | 0 | 26.58 | 0 | OK | Ground clear controls. | 129 | 35.48 | 784.66
8935 | TIN-INTERP | Interpolated Ground | 57178.95 | 4.59 | 760.05 | 0 | 35.48 | 0 | OK | Ground clear controls. | 129 | 35.48 | 795.53
8936 | TIN-INTERP | Interpolated Ground | 57218.89 | 6.59 | 770.05 | 0 | 21.79 | 0 | OK | Ground clear controls. | 129 | 28.34 | 791.84
8937 | TIN-INTERP | Interpolated Ground | 57218.89 | -6.64 | 769.96 | 0 | 21.93 | 0 | OK | Ground clear controls. | 129 | 28.34 | 791.89
8938 | TIN-INTERP | Interpolated Ground | 57218.89 | 5.09 | 770.16 | 0 | 16.2 | 0 | OK | Ground clear controls. | 129 | 28.34 | 786.36
8939 | TIN-INTERP | Interpolated Ground | 57218.91 | -4.64 | 770.11 | 0 | 27.17 | 0 | OK | Ground clear controls. | 129 | 28.34 | 797.28
8940 | TIN-INTERP | Interpolated Ground | 57218.92 | -5.14 | 770.07 | 0 | 16.3 | 0 | OK | Ground clear controls. | 129 | 28.34 | 786.37
8941 | TIN-INTERP | Interpolated Ground | 57218.95 | 4.59 | 770.19 | 0 | 27.07 | 0 | OK | Ground clear controls. | 129 | 28.34 | 797.26
8942 | TIN-INTERP | Interpolated Ground | 57258.89 | 6.59 | 774.35 | 0 | 20.14 | 0 | OK | Ground clear controls. | 129 | 28.34 | 794.49
8943 | TIN-INTERP | Interpolated Ground | 57258.89 | -6.65 | 772.68 | 0 | 21.85 | 0 | OK | Ground clear controls. | 129 | 28.34 | 794.53
8944 | TIN-INTERP | Interpolated Ground | 57258.89 | 5.09 | 773.99 | 0 | 15.01 | 0 | OK | Ground clear controls. | 129 | 28.34 | 789
8945 | TIN-INTERP | Interpolated Ground | 57258.91 | -4.64 | 772.72 | 0 | 27.23 | 0 | OK | Ground clear controls. | 129 | 28.34 | 799.95
8946 | TIN-INTERP | Interpolated Ground | 57258.92 | -5.14 | 772.71 | 0 | 16.3 | 0 | OK | Ground clear controls. | 129 | 28.34 | 789.01
8947 | TIN-INTERP | Interpolated Ground | 57258.95 | 4.59 | 773.9 | 0 | 26.03 | 0 | OK | Ground clear controls. | 129 | 28.34 | 799.93
8948 | TIN-INTERP | Interpolated Ground | 57298.89 | 6.59 | 774.9 | 0 | 23.19 | 0 | OK | Ground clear controls. | 129 | 28.34 | 798.09
8949 | TIN-INTERP | Interpolated Ground | 57298.89 | -6.65 | 775.54 | 0 | 22.57 | 0 | OK | Ground clear controls. | 129 | 28.34 | 798.11
8950 | TIN-INTERP | Interpolated Ground | 57298.89 | 5.09 | 775.16 | 0 | 17.44 | 0 | OK | Ground clear controls. | 129 | 28.34 | 792.6
8951 | TIN-INTERP | Interpolated Ground | 57298.91 | -4.65 | 775.63 | 0 | 27.94 | 0 | OK | Ground clear controls. | 129 | 28.34 | 803.57
8952 | TIN-INTERP | Interpolated Ground | 57298.92 | -5.15 | 775.61 | 0 | 17 | 0 | OK | Ground clear controls. | 129 | 28.34 | 792.61
8953 | TIN-INTERP | Interpolated Ground | 57298.95 | 4.59 | 775.22 | 0 | 28.34 | 0 | OK | Ground clear controls. | 129 | 28.34 | 803.56
8954 | TIN-INTERP | Interpolated Ground | 57334.9 | -5.15 | 773.19 | 0 | 23.46 | 0 | OK | Ground clear controls. | 130 | 45.56 | 796.65
8955 | TIN-INTERP | Interpolated Ground | 57334.94 | -6.65 | 773.45 | 0 | 28.7 | 0 | OK | Ground clear controls. | 130 | 45.56 | 802.15
8956 | TIN-INTERP | Interpolated Ground | 57334.96 | -4.65 | 773.07 | 0 | 34.58 | 0 | OK | Ground clear controls. | 130 | 45.56 | 807.65
8957 | TIN-INTERP | Interpolated Ground | 57334.98 | 6.59 | 770.78 | 0 | 31.37 | 0 | OK | Ground clear controls. | 130 | 45.56 | 802.15
8958 | TIN-INTERP | Interpolated Ground | 57334.99 | 4.59 | 771.22 | 0 | 36.43 | 0 | OK | Ground clear controls. | 130 | 45.56 | 807.65
8959 | TIN-INTERP | Interpolated Ground | 57335 | 5.09 | 771.08 | 0 | 25.57 | 0 | OK | Ground clear controls. | 130 | 45.56 | 796.65
8960 | TIN-INTERP | Interpolated Ground | 57374.9 | -5.38 | 769.55 | 0 | 22.24 | 0 | OK | Ground clear controls. | 130 | 45.56 | 791.79
8961 | TIN-INTERP | Interpolated Ground | 57374.94 | -6.89 | 769.79 | 0 | 27.57 | 0 | OK | Ground clear controls. | 130 | 45.56 | 797.36
8962 | TIN-INTERP | Interpolated Ground | 57374.96 | -4.87 | 769.28 | 0 | 33.58 | 0 | OK | Ground clear controls. | 130 | 45.56 | 802.86
8963 | TIN-INTERP | Interpolated Ground | 57374.98 | 6.55 | 766.26 | 0 | 31.06 | 0 | OK | Ground clear controls. | 130 | 45.56 | 797.32
8964 | TIN-INTERP | Interpolated Ground | 57374.99 | 4.54 | 766.35 | 0 | 36.48 | 0 | OK | Ground clear controls. | 130 | 45.56 | 802.83
8965 | TIN-INTERP | Interpolated Ground | 57375 | 5.06 | 766.26 | 0 | 25.56 | 0 | OK | Ground clear controls. | 130 | 45.56 | 791.82
8966 | TIN-INTERP | Interpolated Ground | 57414.9 | -5.61 | 758.36 | 0 | 29.51 | 0 | OK | Ground clear controls. | 130 | 45.56 | 787.87
8967 | TIN-INTERP | Interpolated Ground | 57414.94 | -7.12 | 758.95 | 0 | 34.55 | 0 | OK | Ground clear controls. | 130 | 45.56 | 793.5
8968 | TIN-INTERP | Interpolated Ground | 57414.96 | -5.08 | 758.05 | 0 | 40.96 | 0 | OK | Ground clear controls. | 130 | 45.56 | 799.01
8969 | TIN-INTERP | Interpolated Ground | 57414.98 | 6.51 | 752.97 | 0 | 40.45 | 0 | OK | Ground clear controls. | 130 | 45.56 | 793.42
8970 | TIN-INTERP | Interpolated Ground | 57414.99 | 4.49 | 753.4 | 0 | 45.56 | 0 | OK | Ground clear controls. | 130 | 45.56 | 798.96
8971 | TIN-INTERP | Interpolated Ground | 57415 | 5.02 | 753.28 | 0 | 34.64 | 0 | OK | Ground clear controls. | 130 | 34.83 | 787.92
8972 | TIN-INTERP | Interpolated Ground | 57454.9 | -5.84 | 763.91 | 0 | 21 | 0 | OK | Ground clear controls. | 130 | 34.83 | 784.91
8973 | TIN-INTERP | Interpolated Ground | 57454.94 | -7.36 | 763.78 | 0 | 26.81 | 0 | OK | Ground clear controls. | 130 | 34.83 | 790.59
8974 | TIN-INTERP | Interpolated Ground | 57454.96 | -5.3 | 763.96 | 0 | 32.17 | 0 | OK | Ground clear controls. | 130 | 34.83 | 796.13
8975 | TIN-INTERP | Interpolated Ground | 57454.98 | 6.47 | 763.99 | 0 | 26.48 | 0 | OK | Ground clear controls. | 130 | 34.83 | 790.47
8976 | TIN-INTERP | Interpolated Ground | 57454.99 | 4.44 | 763.99 | 0 | 32.06 | 0 | OK | Ground clear controls. | 130 | 34.83 | 796.05
8977 | TIN-INTERP | Interpolated Ground | 57455 | 4.98 | 763.99 | 0 | 20.98 | 0 | OK | Ground clear controls. | 130 | 34.83 | 784.97
8978 | TIN-INTERP | Interpolated Ground | 57494.9 | -6.06 | 764.87 | 0 | 18.02 | 0 | OK | Ground clear controls. | 130 | 34.83 | 782.89
8979 | TIN-INTERP | Interpolated Ground | 57494.93 | -7.59 | 764.79 | 0 | 23.84 | 0 | OK | Ground clear controls. | 130 | 34.83 | 788.63
8980 | TIN-INTERP | Interpolated Ground | 57494.96 | -5.52 | 764.92 | 0 | 29.26 | 0 | OK | Ground clear controls. | 130 | 34.83 | 794.18
8981 | TIN-INTERP | Interpolated Ground | 57494.98 | 6.43 | 763.61 | 0 | 24.85 | 0 | OK | Ground clear controls. | 130 | 34.83 | 788.46
8982 | TIN-INTERP | Interpolated Ground | 57494.99 | 4.38 | 763.96 | 0 | 30.12 | 0 | OK | Ground clear controls. | 130 | 34.83 | 794.08
8983 | TIN-INTERP | Interpolated Ground | 57495 | 4.94 | 763.84 | 0 | 19.11 | 0 | OK | Ground clear controls. | 130 | 34.83 | 782.95
8984 | TIN-INTERP | Interpolated Ground | 57534.9 | -6.29 | 765.94 | 0 | 15.9 | 0 | OK | Ground clear controls. | 130 | 34.83 | 781.84
8985 | TIN-INTERP | Interpolated Ground | 57534.93 | -7.82 | 765.96 | 0 | 21.64 | 0 | OK | Ground clear controls. | 130 | 34.83 | 787.6
8986 | TIN-INTERP | Interpolated Ground | 57534.96 | -5.73 | 765.89 | 0 | 27.31 | 0 | OK | Ground clear controls. | 130 | 34.83 | 793.2
8987 | TIN-INTERP | Interpolated Ground | 57534.98 | 6.39 | 764.77 | 0 | 22.64 | 0 | OK | Ground clear controls. | 130 | 34.83 | 787.41
8988 | TIN-INTERP | Interpolated Ground | 57534.99 | 4.33 | 764.81 | 0 | 28.27 | 0 | OK | Ground clear controls. | 130 | 34.83 | 793.08
8989 | TIN-INTERP | Interpolated Ground | 57535 | 4.9 | 764.8 | 0 | 17.08 | 0 | OK | Ground clear controls. | 130 | 34.83 | 781.88
8990 | TIN-INTERP | Interpolated Ground | 57574.9 | -6.52 | 768.41 | 0 | 13.31 | 0 | OK | Ground clear controls. | 130 | 34.83 | 781.72
8991 | TIN-INTERP | Interpolated Ground | 57574.93 | -8.06 | 768.68 | 0 | 18.84 | 0 | OK | Ground clear controls. | 130 | 34.83 | 787.52
8992 | TIN-INTERP | Interpolated Ground | 57574.96 | -5.95 | 768.28 | 0 | 24.89 | 0 | OK | Ground clear controls. | 130 | 34.83 | 793.17
8993 | TIN-INTERP | Interpolated Ground | 57574.98 | 6.35 | 766.18 | 0 | 21.11 | 0 | OK | Ground clear controls. | 130 | 34.83 | 787.29
8994 | TIN-INTERP | Interpolated Ground | 57574.99 | 4.28 | 766.58 | 0 | 26.42 | 0 | OK | Ground clear controls. | 130 | 34.83 | 793
8995 | TIN-INTERP | Interpolated Ground | 57575 | 4.86 | 766.49 | 0 | 15.26 | 0 | OK | Ground clear controls. | 130 | 34.83 | 781.75
8996 | TIN-INTERP | Interpolated Ground | 57614.9 | -6.75 | 770 | 0 | 12.55 | 0 | OK | Ground clear controls. | 130 | 34.83 | 782.55
8997 | TIN-INTERP | Interpolated Ground | 57614.93 | -8.29 | 770.33 | 0 | 18.05 | 0 | OK | Ground clear controls. | 130 | 34.83 | 788.38
8998 | TIN-INTERP | Interpolated Ground | 57614.96 | -6.17 | 769.88 | 0 | 24.2 | 0 | OK | Ground clear controls. | 130 | 34.83 | 794.08
8999 | TIN-INTERP | Interpolated Ground | 57614.98 | 6.31 | 768.42 | 0 | 19.69 | 0 | OK | Ground clear controls. | 130 | 34.83 | 788.11
9000 | TIN-INTERP | Interpolated Ground | 57614.99 | 4.23 | 768.57 | 0 | 25.33 | 0 | OK | Ground clear controls. | 130 | 34.83 | 793.9
9001 | TIN-INTERP | Interpolated Ground | 57615 | 4.82 | 768.53 | 0 | 14.03 | 0 | OK | Ground clear controls. | 130 | 34.83 | 782.56
9002 | TIN-INTERP | Interpolated Ground | 57654.9 | -6.98 | 772.68 | 0 | 11.65 | 0 | OK | Ground clear controls. | 130 | 34.83 | 784.33
9003 | TIN-INTERP | Interpolated Ground | 57654.93 | -8.52 | 772.96 | 0 | 17.22 | 0 | OK | Ground clear controls. | 130 | 34.83 | 790.18
9004 | TIN-INTERP | Interpolated Ground | 57654.96 | -6.38 | 772.56 | 0 | 23.38 | 0 | OK | Ground clear controls. | 130 | 34.83 | 795.94
9005 | TIN-INTERP | Interpolated Ground | 57654.98 | 6.27 | 771.48 | 0 | 18.39 | 0 | OK | Ground clear controls. | 130 | 34.83 | 789.87
9006 | TIN-INTERP | Interpolated Ground | 57654.99 | 4.18 | 771.45 | 0 | 24.28 | 0 | OK | Ground clear controls. | 130 | 34.83 | 795.73
9007 | TIN-INTERP | Interpolated Ground | 57655 | 4.78 | 771.49 | 0 | 12.8 | 0 | OK | Ground clear controls. | 130 | 34.83 | 784.29
9008 | TIN-INTERP | Interpolated Ground | 57694.9 | -7.21 | 774.75 | 0 | 12.31 | 0 | OK | Ground clear controls. | 130 | 34.83 | 787.06
9009 | TIN-INTERP | Interpolated Ground | 57694.93 | -8.76 | 775.04 | 0 | 17.89 | 0 | OK | Ground clear controls. | 130 | 34.83 | 792.93
9010 | TIN-INTERP | Interpolated Ground | 57694.96 | -6.6 | 774.67 | 0 | 24.1 | 0 | OK | Ground clear controls. | 130 | 34.83 | 798.77
9011 | TIN-INTERP | Interpolated Ground | 57694.98 | 6.23 | 773.71 | 0 | 18.87 | 0 | OK | Ground clear controls. | 130 | 34.83 | 792.58
9012 | TIN-INTERP | Interpolated Ground | 57694.99 | 4.12 | 773.87 | 0 | 24.66 | 0 | OK | Ground clear controls. | 130 | 34.83 | 798.53
9013 | TIN-INTERP | Interpolated Ground | 57695 | 4.74 | 773.82 | 0 | 13.16 | 0 | OK | Ground clear controls. | 130 | 34.83 | 786.98
9014 | TIN-INTERP | Interpolated Ground | 57734.9 | -7.43 | 775.82 | 0 | 14.92 | 0 | OK | Ground clear controls. | 130 | 34.83 | 790.74
9015 | TIN-INTERP | Interpolated Ground | 57734.93 | -8.99 | 776.14 | 0 | 20.47 | 0 | OK | Ground clear controls. | 130 | 34.83 | 796.61
9016 | TIN-INTERP | Interpolated Ground | 57734.96 | -6.82 | 775.73 | 0 | 26.8 | 0 | OK | Ground clear controls. | 130 | 34.83 | 802.53
9017 | TIN-INTERP | Interpolated Ground | 57734.98 | 6.19 | 774.25 | 0 | 21.99 | 0 | OK | Ground clear controls. | 130 | 34.83 | 796.24
9018 | TIN-INTERP | Interpolated Ground | 57734.99 | 4.07 | 774.31 | 0 | 27.96 | 0 | OK | Ground clear controls. | 130 | 34.83 | 802.27
9019 | TIN-INTERP | Interpolated Ground | 57735 | 4.71 | 774.26 | 0 | 16.35 | 0 | OK | Ground clear controls. | 130 | 34.83 | 790.61
9020 | TIN-INTERP | Interpolated Ground | 57774.9 | -7.66 | 779.32 | 0 | 16.05 | 0 | OK | Ground clear controls. | 130 | 34.83 | 795.37
9021 | TIN-INTERP | Interpolated Ground | 57774.93 | -9.23 | 779.58 | 0 | 21.67 | 0 | OK | Ground clear controls. | 130 | 34.83 | 801.25
9022 | TIN-INTERP | Interpolated Ground | 57774.96 | -7.03 | 779.28 | 0 | 27.98 | 0 | OK | Ground clear controls. | 130 | 34.83 | 807.26
9023 | TIN-INTERP | Interpolated Ground | 57774.98 | 6.15 | 778.43 | 0 | 22.41 | 0 | OK | Ground clear controls. | 130 | 34.83 | 800.84
9024 | TIN-INTERP | Interpolated Ground | 57774.99 | 4.02 | 778.56 | 0 | 28.41 | 0 | OK | Ground clear controls. | 130 | 34.83 | 806.97
9025 | TIN-INTERP | Interpolated Ground | 57775 | 4.67 | 778.52 | 0 | 16.65 | 0 | OK | Ground clear controls. | 130 | 34.83 | 795.17
9026 | TIN-INTERP | Interpolated Ground | 57814.89 | -7.89 | 782.32 | 0 | 18.64 | 0 | OK | Ground clear controls. | 130 | 34.83 | 800.96
9027 | TIN-INTERP | Interpolated Ground | 57814.93 | -9.46 | 782.79 | 0 | 24.05 | 0 | OK | Ground clear controls. | 130 | 34.83 | 806.84
9028 | TIN-INTERP | Interpolated Ground | 57814.95 | -7.25 | 782.19 | 0 | 30.75 | 0 | OK | Ground clear controls. | 130 | 34.83 | 812.94
9029 | TIN-INTERP | Interpolated Ground | 57814.98 | 6.11 | 781.19 | 0 | 25.19 | 0 | OK | Ground clear controls. | 130 | 34.83 | 806.38
9030 | TIN-INTERP | Interpolated Ground | 57814.99 | 3.97 | 781.16 | 0 | 31.46 | 0 | OK | Ground clear controls. | 130 | 34.83 | 812.62
9031 | TIN-INTERP | Interpolated Ground | 57815 | 4.63 | 781.18 | 0 | 19.51 | 0 | OK | Ground clear controls. | 130 | 34.83 | 800.69
9032 | TIN-INTERP | Interpolated Ground | 57854.89 | -8.12 | 784.76 | 0 | 22.76 | 0 | OK | Ground clear controls. | 130 | 34.83 | 807.52
9033 | TIN-INTERP | Interpolated Ground | 57854.93 | -9.69 | 784.89 | 0 | 28.48 | 0 | OK | Ground clear controls. | 130 | 34.83 | 813.37
9034 | TIN-INTERP | Interpolated Ground | 57854.95 | -7.47 | 784.76 | 0 | 34.83 | 0 | OK | Ground clear controls. | 130 | 34.83 | 819.59
9035 | TIN-INTERP | Interpolated Ground | 57854.98 | 6.07 | 785.57 | 0 | 27.32 | 0 | OK | Ground clear controls. | 130 | 33.97 | 812.89
9036 | TIN-INTERP | Interpolated Ground | 57854.99 | 3.92 | 785.27 | 0 | 33.97 | 0 | OK | Ground clear controls. | 130 | 33.97 | 819.24
9037 | TIN-INTERP | Interpolated Ground | 57855 | 4.59 | 785.41 | 0 | 21.75 | 0 | OK | Ground clear controls. | 130 | 21.75 | 807.16
9038 | TIN-INTERP | Interpolated Ground | 57856.99 | -9.71 | 784.9 | 0 | 28.83 | 0 | OK | Ground clear controls. | 131 | 45.35 | 813.73
9039 | TIN-INTERP | Interpolated Ground | 57857.27 | -8.13 | 784.86 | 0 | 23.07 | 0 | OK | Ground clear controls. | 131 | 45.35 | 807.93
9040 | TIN-INTERP | Interpolated Ground | 57857.39 | -7.48 | 784.93 | 0 | 35.09 | 0 | OK | Ground clear controls. | 131 | 45.35 | 820.02
9041 | TIN-INTERP | Interpolated Ground | 57858.9 | 3.97 | 785.15 | 0 | 34.91 | 0 | OK | Ground clear controls. | 131 | 45.35 | 820.06
9042 | TIN-INTERP | Interpolated Ground | 57858.9 | 4.65 | 785.19 | 0 | 22.78 | 0 | OK | Ground clear controls. | 131 | 45.35 | 807.97
9043 | TIN-INTERP | Interpolated Ground | 57858.9 | 6.16 | 785.28 | 0 | 28.49 | 0 | OK | Ground clear controls. | 131 | 45.35 | 813.77
9044 | TIN-INTERP | Interpolated Ground | 57897.72 | 6.08 | 784.34 | 0 | 19.83 | 0 | OK | Ground clear controls. | 131 | 45.35 | 804.17
9045 | TIN-INTERP | Interpolated Ground | 57897.99 | 4.59 | 784.37 | 0 | 14.05 | 0 | OK | Ground clear controls. | 131 | 45.35 | 798.42
9046 | TIN-INTERP | Interpolated Ground | 57898.14 | 3.95 | 784.37 | 0 | 25.95 | 0 | OK | Ground clear controls. | 131 | 45.35 | 810.32
9047 | TIN-INTERP | Interpolated Ground | 57900.18 | -6.98 | 782.18 | 0 | 28.03 | 0 | OK | Ground clear controls. | 131 | 45.35 | 810.21
9048 | TIN-INTERP | Interpolated Ground | 57900.3 | -7.65 | 782.15 | 0 | 16.13 | 0 | OK | Ground clear controls. | 131 | 45.35 | 798.28
9049 | TIN-INTERP | Interpolated Ground | 57900.61 | -9.18 | 782.07 | 0 | 21.99 | 0 | OK | Ground clear controls. | 131 | 45.35 | 804.06
9050 | TIN-INTERP | Interpolated Ground | 57937.72 | 6.11 | 775.44 | 0 | 20.11 | 0 | OK | Ground clear controls. | 131 | 45.35 | 795.55
9051 | TIN-INTERP | Interpolated Ground | 57937.99 | 4.62 | 775.17 | 0 | 14.66 | 0 | OK | Ground clear controls. | 131 | 45.35 | 789.83
9052 | TIN-INTERP | Interpolated Ground | 57938.14 | 3.99 | 775.1 | 0 | 26.48 | 0 | OK | Ground clear controls. | 131 | 45.35 | 801.58
9053 | TIN-INTERP | Interpolated Ground | 57940.18 | -6.45 | 772.08 | 0 | 29.32 | 0 | OK | Ground clear controls. | 131 | 45.35 | 801.4
9054 | TIN-INTERP | Interpolated Ground | 57940.3 | -7.13 | 771.71 | 0 | 17.93 | 0 | OK | Ground clear controls. | 131 | 45.35 | 789.64
9055 | TIN-INTERP | Interpolated Ground | 57940.61 | -8.62 | 771 | 0 | 24.39 | 0 | OK | Ground clear controls. | 131 | 45.35 | 795.39
9056 | TIN-INTERP | Interpolated Ground | 57977.72 | 6.14 | 762.22 | 0 | 25.68 | 0 | OK | Ground clear controls. | 131 | 45.35 | 787.9
9057 | TIN-INTERP | Interpolated Ground | 57977.99 | 4.65 | 761.56 | 0 | 20.66 | 0 | OK | Ground clear controls. | 131 | 45.35 | 782.22
9058 | TIN-INTERP | Interpolated Ground | 57978.14 | 4.04 | 761.27 | 0 | 32.52 | 0 | OK | Ground clear controls. | 131 | 45.35 | 793.79
9059 | TIN-INTERP | Interpolated Ground | 57980.18 | -5.91 | 756.51 | 0 | 37.08 | 0 | OK | Ground clear controls. | 131 | 45.35 | 793.59
9060 | TIN-INTERP | Interpolated Ground | 57980.3 | -6.61 | 756.12 | 0 | 25.86 | 0 | OK | Ground clear controls. | 131 | 45.35 | 781.98
9061 | TIN-INTERP | Interpolated Ground | 57980.6 | -8.05 | 754.79 | 0 | 32.9 | 0 | OK | Ground clear controls. | 131 | 45.35 | 787.69
9062 | TIN-INTERP | Interpolated Ground | 58017.72 | 6.17 | 739.72 | 0 | 41.49 | 0 | OK | Ground clear controls. | 131 | 45.35 | 781.21
9063 | TIN-INTERP | Interpolated Ground | 58017.99 | 4.68 | 741.11 | 0 | 34.46 | 0 | OK | Ground clear controls. | 131 | 45.35 | 775.57
9064 | TIN-INTERP | Interpolated Ground | 58018.14 | 4.08 | 741.64 | 0 | 45.35 | 0 | OK | Ground clear controls. | 131 | 45.35 | 786.99
9065 | TIN-INTERP | Interpolated Ground | 58020.17 | -5.38 | 747.07 | 0 | 39.69 | 0 | OK | Ground clear controls. | 131 | 44.53 | 786.76
9066 | TIN-INTERP | Interpolated Ground | 58020.29 | -6.09 | 747.37 | 0 | 27.94 | 0 | OK | Ground clear controls. | 131 | 44.53 | 775.31
9067 | TIN-INTERP | Interpolated Ground | 58020.6 | -7.49 | 748 | 0 | 32.97 | 0 | OK | Ground clear controls. | 131 | 44.53 | 780.97
9068 | TIN-INTERP | Interpolated Ground | 58057.72 | 6.2 | 738.94 | 0 | 36.54 | 0 | OK | Ground clear controls. | 131 | 44.53 | 775.48
9069 | TIN-INTERP | Interpolated Ground | 58057.99 | 4.71 | 739.67 | 0 | 30.22 | 0 | OK | Ground clear controls. | 131 | 44.53 | 769.89
9070 | TIN-INTERP | Interpolated Ground | 58058.14 | 4.13 | 740.01 | 0 | 41.14 | 0 | OK | Ground clear controls. | 131 | 44.53 | 781.15
9071 | TIN-INTERP | Interpolated Ground | 58060.17 | -4.84 | 745.42 | 0 | 35.5 | 0 | OK | Ground clear controls. | 131 | 44.53 | 780.92
9072 | TIN-INTERP | Interpolated Ground | 58060.29 | -5.56 | 745.86 | 0 | 23.76 | 0 | OK | Ground clear controls. | 131 | 44.53 | 769.62
9073 | TIN-INTERP | Interpolated Ground | 58060.6 | -6.93 | 746.65 | 0 | 28.58 | 0 | OK | Ground clear controls. | 131 | 44.53 | 775.23
9074 | TIN-INTERP | Interpolated Ground | 58097.72 | 6.24 | 730.41 | 0 | 40.3 | 0 | OK | Ground clear controls. | 131 | 44.53 | 770.71
9075 | TIN-INTERP | Interpolated Ground | 58097.99 | 4.74 | 731.41 | 0 | 33.74 | 0 | OK | Ground clear controls. | 131 | 44.53 | 765.15
9076 | TIN-INTERP | Interpolated Ground | 58098.14 | 4.18 | 731.76 | 0 | 44.53 | 0 | OK | Ground clear controls. | 131 | 44.53 | 776.29
9077 | TIN-INTERP | Interpolated Ground | 58100.17 | -4.3 | 733.58 | 0 | 42.49 | 0 | OK | Ground clear controls. | 131 | 42.49 | 776.07
9078 | TIN-INTERP | Interpolated Ground | 58100.29 | -5.04 | 733.45 | 0 | 31.48 | 0 | OK | Ground clear controls. | 131 | 36.83 | 764.93
9079 | TIN-INTERP | Interpolated Ground | 58100.59 | -6.37 | 733.63 | 0 | 36.83 | 0 | OK | Ground clear controls. | 131 | 36.83 | 770.46
9080 | TIN-INTERP | Interpolated Ground | 58135.9 | -4.08 | 742.86 | 0 | 29.73 | 0 | OK | Ground clear controls. | 132 | 48.27 | 772.59
9081 | TIN-INTERP | Interpolated Ground | 58135.96 | 4.23 | 742.12 | 0 | 30.46 | 0 | OK | Ground clear controls. | 132 | 48.27 | 772.58
9082 | TIN-INTERP | Interpolated Ground | 58136.2 | 6.28 | 741.73 | 0 | 25.37 | 0 | OK | Ground clear controls. | 132 | 48.27 | 767.1
9083 | TIN-INTERP | Interpolated Ground | 58136.21 | -6.13 | 742.9 | 0 | 24.2 | 0 | OK | Ground clear controls. | 132 | 48.27 | 767.1
9084 | TIN-INTERP | Interpolated Ground | 58136.3 | -4.63 | 742.92 | 0 | 18.69 | 0 | OK | Ground clear controls. | 132 | 48.27 | 761.61
9085 | TIN-INTERP | Interpolated Ground | 58136.31 | 4.78 | 742.04 | 0 | 19.57 | 0 | OK | Ground clear controls. | 132 | 48.27 | 761.61
9086 | TIN-INTERP | Interpolated Ground | 58175.9 | -4.13 | 734.22 | 0 | 33.23 | 0 | OK | Ground clear controls. | 132 | 48.27 | 767.45
9087 | TIN-INTERP | Interpolated Ground | 58175.96 | 4.27 | 729.59 | 0 | 37.76 | 0 | OK | Ground clear controls. | 132 | 48.27 | 767.35
9088 | TIN-INTERP | Interpolated Ground | 58176.2 | 6.31 | 728.67 | 0 | 33.44 | 0 | OK | Ground clear controls. | 132 | 48.27 | 762.11
9089 | TIN-INTERP | Interpolated Ground | 58176.21 | -6.18 | 736.06 | 0 | 25.95 | 0 | OK | Ground clear controls. | 132 | 48.27 | 762.01
9090 | TIN-INTERP | Interpolated Ground | 58176.3 | -4.67 | 734.48 | 0 | 22.17 | 0 | OK | Ground clear controls. | 132 | 48.27 | 756.65
9091 | TIN-INTERP | Interpolated Ground | 58176.31 | 4.81 | 729.4 | 0 | 27.31 | 0 | OK | Ground clear controls. | 132 | 48.27 | 756.71
9092 | TIN-INTERP | Interpolated Ground | 58215.9 | -4.19 | 723.85 | 0 | 39.42 | 0 | OK | Ground clear controls. | 132 | 48.27 | 763.27
9093 | TIN-INTERP | Interpolated Ground | 58215.96 | 4.31 | 718.39 | 0 | 44.7 | 0 | OK | Ground clear controls. | 132 | 48.27 | 763.09
9094 | TIN-INTERP | Interpolated Ground | 58216.2 | 6.34 | 717.48 | 0 | 40.58 | 0 | OK | Ground clear controls. | 132 | 48.27 | 758.06
9095 | TIN-INTERP | Interpolated Ground | 58216.21 | -6.22 | 723.9 | 0 | 33.99 | 0 | OK | Ground clear controls. | 132 | 48.27 | 757.89
9096 | TIN-INTERP | Interpolated Ground | 58216.3 | -4.72 | 723.95 | 0 | 28.68 | 0 | OK | Ground clear controls. | 132 | 48.27 | 752.63
9097 | TIN-INTERP | Interpolated Ground | 58216.31 | 4.85 | 718.26 | 0 | 34.48 | 0 | OK | Ground clear controls. | 132 | 48.27 | 752.74
9098 | TIN-INTERP | Interpolated Ground | 58255.9 | -4.24 | 718.29 | 0 | 41.78 | 0 | OK | Ground clear controls. | 132 | 48.27 | 760.07
9099 | TIN-INTERP | Interpolated Ground | 58255.96 | 4.35 | 711.94 | 0 | 47.89 | 0 | OK | Ground clear controls. | 132 | 48.27 | 759.83
9100 | TIN-INTERP | Interpolated Ground | 58256.2 | 6.37 | 710.95 | 0 | 43.99 | 0 | OK | Ground clear controls. | 132 | 48.27 | 754.94
9101 | TIN-INTERP | Interpolated Ground | 58256.21 | -6.27 | 719.77 | 0 | 34.95 | 0 | OK | Ground clear controls. | 132 | 48.27 | 754.72
9102 | TIN-INTERP | Interpolated Ground | 58256.3 | -4.77 | 718.48 | 0 | 31.07 | 0 | OK | Ground clear controls. | 132 | 48.27 | 749.55
9103 | TIN-INTERP | Interpolated Ground | 58256.31 | 4.88 | 711.5 | 0 | 38.19 | 0 | OK | Ground clear controls. | 132 | 48.27 | 749.69
9104 | TIN-INTERP | Interpolated Ground | 58295.9 | -4.3 | 722.15 | 0 | 35.68 | 0 | OK | Ground clear controls. | 132 | 48.27 | 757.83
9105 | TIN-INTERP | Interpolated Ground | 58295.96 | 4.4 | 718.8 | 0 | 38.74 | 0 | OK | Ground clear controls. | 132 | 48.27 | 757.54
9106 | TIN-INTERP | Interpolated Ground | 58296.2 | 6.41 | 718.31 | 0 | 34.47 | 0 | OK | Ground clear controls. | 132 | 48.27 | 752.78
9107 | TIN-INTERP | Interpolated Ground | 58296.21 | -6.32 | 722.74 | 0 | 29.77 | 0 | OK | Ground clear controls. | 132 | 48.27 | 752.51
9108 | TIN-INTERP | Interpolated Ground | 58296.3 | -4.82 | 722.29 | 0 | 25.12 | 0 | OK | Ground clear controls. | 132 | 48.27 | 747.41
9109 | TIN-INTERP | Interpolated Ground | 58296.31 | 4.91 | 718.53 | 0 | 29.05 | 0 | OK | Ground clear controls. | 132 | 48.27 | 747.58
9110 | TIN-INTERP | Interpolated Ground | 58335.9 | -4.35 | 713.88 | 0 | 42.69 | 0 | OK | Ground clear controls. | 132 | 48.27 | 756.57
9111 | TIN-INTERP | Interpolated Ground | 58335.96 | 4.44 | 707.98 | 0 | 48.27 | 0 | OK | Ground clear controls. | 132 | 48.27 | 756.25
9112 | TIN-INTERP | Interpolated Ground | 58336.2 | 6.44 | 706.52 | 0 | 45.04 | 0 | OK | Ground clear controls. | 132 | 47.29 | 751.56
9113 | TIN-INTERP | Interpolated Ground | 58336.21 | -6.37 | 714.82 | 0 | 36.45 | 0 | OK | Ground clear controls. | 132 | 47.29 | 751.27
9114 | TIN-INTERP | Interpolated Ground | 58336.3 | -4.86 | 713.97 | 0 | 32.24 | 0 | OK | Ground clear controls. | 132 | 47.29 | 746.21
9115 | TIN-INTERP | Interpolated Ground | 58336.31 | 4.95 | 707.54 | 0 | 38.86 | 0 | OK | Ground clear controls. | 132 | 47.29 | 746.4
9116 | TIN-INTERP | Interpolated Ground | 58375.9 | -4.41 | 708.99 | 0 | 47.29 | 0 | OK | Ground clear controls. | 132 | 47.29 | 756.28
9117 | TIN-INTERP | Interpolated Ground | 58375.96 | 4.48 | 709.8 | 0 | 46.15 | 0 | OK | Ground clear controls. | 132 | 46.15 | 755.95
9118 | TIN-INTERP | Interpolated Ground | 58376.2 | 6.47 | 711.56 | 0 | 39.74 | 0 | OK | Ground clear controls. | 132 | 41.98 | 751.3
9119 | TIN-INTERP | Interpolated Ground | 58376.21 | -6.41 | 708.99 | 0 | 41.98 | 0 | OK | Ground clear controls. | 132 | 41.98 | 750.97
9120 | TIN-INTERP | Interpolated Ground | 58376.3 | -4.91 | 709.15 | 0 | 36.81 | 0 | OK | Ground clear controls. | 132 | 38.68 | 745.96
9121 | TIN-INTERP | Interpolated Ground | 58376.31 | 4.98 | 710.43 | 0 | 35.72 | 0 | OK | Ground clear controls. | 132 | 38.68 | 746.15
9122 | TIN-INTERP | Interpolated Ground | 58415.9 | -4.46 | 718.28 | 0 | 38.68 | 0 | OK | Ground clear controls. | 132 | 38.68 | 756.96
9123 | TIN-INTERP | Interpolated Ground | 58415.96 | 4.52 | 719.46 | 0 | 37.16 | 0 | OK | Ground clear controls. | 132 | 37.16 | 756.62
9124 | TIN-INTERP | Interpolated Ground | 58416.2 | 6.5 | 719.64 | 0 | 32.32 | 0 | OK | Ground clear controls. | 132 | 33.68 | 751.96
9125 | TIN-INTERP | Interpolated Ground | 58416.21 | -6.46 | 718.32 | 0 | 33.33 | 0 | OK | Ground clear controls. | 132 | 33.68 | 751.65
9126 | TIN-INTERP | Interpolated Ground | 58416.3 | -4.96 | 718.43 | 0 | 28.19 | 0 | OK | Ground clear controls. | 132 | 33.68 | 746.62
9127 | TIN-INTERP | Interpolated Ground | 58416.31 | 5.02 | 719.55 | 0 | 27.29 | 0 | OK | Ground clear controls. | 132 | 33.68 | 746.84
9128 | TIN-INTERP | Interpolated Ground | 58455.9 | -4.52 | 725.37 | 0 | 33.24 | 0 | OK | Ground clear controls. | 132 | 33.68 | 758.61
9129 | TIN-INTERP | Interpolated Ground | 58455.96 | 4.57 | 724.59 | 0 | 33.68 | 0 | OK | Ground clear controls. | 132 | 33.68 | 758.27
9130 | TIN-INTERP | Interpolated Ground | 58456.2 | 6.54 | 724.54 | 0 | 29.04 | 0 | OK | Ground clear controls. | 132 | 31.42 | 753.58
9131 | TIN-INTERP | Interpolated Ground | 58456.21 | -6.51 | 725.42 | 0 | 27.84 | 0 | OK | Ground clear controls. | 132 | 31.42 | 753.26
9132 | TIN-INTERP | Interpolated Ground | 58456.3 | -5.01 | 725.46 | 0 | 22.78 | 0 | OK | Ground clear controls. | 132 | 31.42 | 748.24
9133 | TIN-INTERP | Interpolated Ground | 58456.31 | 5.05 | 724.59 | 0 | 23.85 | 0 | OK | Ground clear controls. | 132 | 31.42 | 748.44
9134 | TIN-INTERP | Interpolated Ground | 58495.9 | -4.57 | 729.8 | 0 | 31.42 | 0 | OK | Ground clear controls. | 132 | 31.42 | 761.22
9135 | TIN-INTERP | Interpolated Ground | 58495.96 | 4.61 | 730.38 | 0 | 30.53 | 0 | OK | Ground clear controls. | 132 | 30.53 | 760.91
9136 | TIN-INTERP | Interpolated Ground | 58496.2 | 6.57 | 730.7 | 0 | 25.44 | 0 | OK | Ground clear controls. | 132 | 28.26 | 756.14
9137 | TIN-INTERP | Interpolated Ground | 58496.21 | -6.56 | 729.79 | 0 | 26.06 | 0 | OK | Ground clear controls. | 132 | 28.26 | 755.85
9138 | TIN-INTERP | Interpolated Ground | 58496.3 | -5.05 | 729.82 | 0 | 20.97 | 0 | OK | Ground clear controls. | 132 | 28.26 | 750.79
9139 | TIN-INTERP | Interpolated Ground | 58496.31 | 5.09 | 730.52 | 0 | 20.46 | 0 | OK | Ground clear controls. | 132 | 28.26 | 750.98
9140 | TIN-INTERP | Interpolated Ground | 58535.9 | -4.63 | 738.86 | 0 | 25.95 | 0 | OK | Ground clear controls. | 132 | 28.26 | 764.81
9141 | TIN-INTERP | Interpolated Ground | 58535.96 | 4.65 | 739.72 | 0 | 24.82 | 0 | OK | Ground clear controls. | 132 | 28.26 | 764.54
9142 | TIN-INTERP | Interpolated Ground | 58536.2 | 6.6 | 739.96 | 0 | 19.7 | 0 | OK | Ground clear controls. | 132 | 28.26 | 759.66
9143 | TIN-INTERP | Interpolated Ground | 58536.21 | -6.6 | 738.1 | 0 | 21.29 | 0 | OK | Ground clear controls. | 132 | 28.26 | 759.39
9144 | TIN-INTERP | Interpolated Ground | 58536.3 | -5.1 | 738.78 | 0 | 15.51 | 0 | OK | Ground clear controls. | 132 | 28.26 | 754.29
9145 | TIN-INTERP | Interpolated Ground | 58536.31 | 5.12 | 739.82 | 0 | 14.63 | 0 | OK | Ground clear controls. | 132 | 28.26 | 754.45
9146 | TIN-INTERP | Interpolated Ground | 58575.9 | -4.68 | 741.13 | 0 | 28.26 | 0 | OK | Ground clear controls. | 132 | 28.26 | 769.39
9147 | TIN-INTERP | Interpolated Ground | 58575.96 | 4.69 | 742.55 | 0 | 26.61 | 0 | OK | Ground clear controls. | 132 | 27.5 | 769.16
9148 | TIN-INTERP | Interpolated Ground | 58576.2 | 6.63 | 742.97 | 0 | 21.14 | 0 | OK | Ground clear controls. | 132 | 27.5 | 764.11
9149 | TIN-INTERP | Interpolated Ground | 58576.21 | -6.65 | 740.93 | 0 | 22.97 | 0 | OK | Ground clear controls. | 132 | 27.5 | 763.9
9150 | TIN-INTERP | Interpolated Ground | 58576.3 | -5.15 | 741.11 | 0 | 17.61 | 0 | OK | Ground clear controls. | 132 | 27.5 | 758.72
9151 | TIN-INTERP | Interpolated Ground | 58576.31 | 5.15 | 742.69 | 0 | 16.17 | 0 | OK | Ground clear controls. | 132 | 27.5 | 758.86
9152 | TIN-INTERP | Interpolated Ground | 58615.9 | -4.74 | 747.42 | 0 | 27.5 | 0 | OK | Ground clear controls. | 132 | 27.5 | 774.92
9153 | TIN-INTERP | Interpolated Ground | 58615.96 | 4.74 | 748.23 | 0 | 26.53 | 0 | OK | Ground clear controls. | 132 | 26.53 | 774.76
9154 | TIN-INTERP | Interpolated Ground | 58616.2 | 6.67 | 748.64 | 0 | 20.88 | 0 | OK | Ground clear controls. | 132 | 26.47 | 769.52
9155 | TIN-INTERP | Interpolated Ground | 58616.21 | -6.7 | 747.3 | 0 | 22.06 | 0 | OK | Ground clear controls. | 132 | 26.47 | 769.36
9156 | TIN-INTERP | Interpolated Ground | 58616.3 | -5.2 | 747.47 | 0 | 16.62 | 0 | OK | Ground clear controls. | 132 | 26.47 | 764.09
9157 | TIN-INTERP | Interpolated Ground | 58616.31 | 5.19 | 748.43 | 0 | 15.76 | 0 | OK | Ground clear controls. | 132 | 26.47 | 764.19
9158 | TIN-INTERP | Interpolated Ground | 58655.9 | -4.79 | 754.97 | 0 | 26.47 | 0 | OK | Ground clear controls. | 132 | 26.47 | 781.44
9159 | TIN-INTERP | Interpolated Ground | 58655.96 | 4.78 | 757.97 | 0 | 23.4 | 0 | OK | Ground clear controls. | 132 | 23.4 | 781.37
9160 | TIN-INTERP | Interpolated Ground | 58656.2 | 6.7 | 758.71 | 0 | 17.16 | 0 | OK | Ground clear controls. | 132 | 22.35 | 775.87
9161 | TIN-INTERP | Interpolated Ground | 58656.21 | -6.75 | 753.44 | 0 | 22.35 | 0 | OK | Ground clear controls. | 132 | 22.35 | 775.79
9162 | TIN-INTERP | Interpolated Ground | 58656.3 | -5.24 | 754.6 | 0 | 15.83 | 0 | OK | Ground clear controls. | 132 | 15.83 | 770.43
9163 | TIN-INTERP | Interpolated Ground | 58656.31 | 5.22 | 758.29 | 0 | 12.19 | 0 | OK | Ground clear controls. | 132 | 12.19 | 770.48
9164 | TIN-INTERP | Interpolated Ground | 58691.9 | -6.79 | 758.29 | 0 | 24.07 | 0 | OK | Ground clear controls. | 133 | 37.64 | 782.36
9165 | TIN-INTERP | Interpolated Ground | 58691.91 | -4.84 | 758.17 | 0 | 29.98 | 0 | OK | Ground clear controls. | 133 | 37.64 | 788.15
9166 | TIN-INTERP | Interpolated Ground | 58691.91 | 6.73 | 761.06 | 0 | 21.3 | 0 | OK | Ground clear controls. | 133 | 37.64 | 782.36
9167 | TIN-INTERP | Interpolated Ground | 58691.93 | 5.25 | 760.43 | 0 | 16.43 | 0 | OK | Ground clear controls. | 133 | 37.64 | 776.86
9168 | TIN-INTERP | Interpolated Ground | 58691.93 | 4.82 | 760.06 | 0 | 28.1 | 0 | OK | Ground clear controls. | 133 | 37.64 | 788.16
9169 | TIN-INTERP | Interpolated Ground | 58691.99 | -5.29 | 758.23 | 0 | 18.64 | 0 | OK | Ground clear controls. | 133 | 37.64 | 776.87
9170 | TIN-INTERP | Interpolated Ground | 58731.9 | -6.77 | 752.68 | 0 | 32.36 | 0 | OK | Ground clear controls. | 133 | 37.64 | 785.04
9171 | TIN-INTERP | Interpolated Ground | 58731.91 | -4.82 | 753.11 | 0 | 37.64 | 0 | OK | Ground clear controls. | 133 | 37.64 | 790.75
9172 | TIN-INTERP | Interpolated Ground | 58731.91 | 6.68 | 758.17 | 0 | 26.9 | 0 | OK | Ground clear controls. | 133 | 33.87 | 785.07
9173 | TIN-INTERP | Interpolated Ground | 58731.93 | 5.2 | 757.12 | 0 | 22.47 | 0 | OK | Ground clear controls. | 133 | 33.87 | 779.59
9174 | TIN-INTERP | Interpolated Ground | 58731.93 | 4.75 | 756.86 | 0 | 33.87 | 0 | OK | Ground clear controls. | 133 | 33.87 | 790.73
9175 | TIN-INTERP | Interpolated Ground | 58731.99 | -5.27 | 753.06 | 0 | 26.54 | 0 | OK | Ground clear controls. | 133 | 33.54 | 779.6
9176 | TIN-INTERP | Interpolated Ground | 58771.9 | -6.76 | 759.89 | 0 | 28.78 | 0 | OK | Ground clear controls. | 133 | 33.54 | 788.67
9177 | TIN-INTERP | Interpolated Ground | 58771.91 | -4.79 | 760.76 | 0 | 33.54 | 0 | OK | Ground clear controls. | 133 | 33.54 | 794.3
9178 | TIN-INTERP | Interpolated Ground | 58771.91 | 6.63 | 766.36 | 0 | 22.34 | 0 | OK | Ground clear controls. | 133 | 32.12 | 788.7
9179 | TIN-INTERP | Interpolated Ground | 58771.93 | 5.14 | 764.99 | 0 | 18.25 | 0 | OK | Ground clear controls. | 133 | 32.12 | 783.24
9180 | TIN-INTERP | Interpolated Ground | 58771.93 | 4.68 | 764.32 | 0 | 29.95 | 0 | OK | Ground clear controls. | 133 | 32.12 | 794.27
9181 | TIN-INTERP | Interpolated Ground | 58771.99 | -5.26 | 760.54 | 0 | 22.71 | 0 | OK | Ground clear controls. | 133 | 32.12 | 783.25
9182 | TIN-INTERP | Interpolated Ground | 58811.9 | -6.75 | 765.82 | 0 | 27.42 | 0 | OK | Ground clear controls. | 133 | 32.12 | 793.24
9183 | TIN-INTERP | Interpolated Ground | 58811.91 | -4.77 | 766.69 | 0 | 32.12 | 0 | OK | Ground clear controls. | 133 | 32.12 | 798.81
9184 | TIN-INTERP | Interpolated Ground | 58811.91 | 6.58 | 770.55 | 0 | 22.7 | 0 | OK | Ground clear controls. | 133 | 29.92 | 793.25
9185 | TIN-INTERP | Interpolated Ground | 58811.93 | 5.09 | 769.29 | 0 | 18.51 | 0 | OK | Ground clear controls. | 133 | 29.92 | 787.8
9186 | TIN-INTERP | Interpolated Ground | 58811.93 | 4.62 | 768.86 | 0 | 29.92 | 0 | OK | Ground clear controls. | 133 | 29.92 | 798.78
9187 | TIN-INTERP | Interpolated Ground | 58811.99 | -5.25 | 766.56 | 0 | 21.27 | 0 | OK | Ground clear controls. | 133 | 29.67 | 787.83
9188 | TIN-INTERP | Interpolated Ground | 58851.9 | -6.73 | 774.34 | 0 | 24.42 | 0 | OK | Ground clear controls. | 133 | 29.67 | 798.76
9189 | TIN-INTERP | Interpolated Ground | 58851.91 | -4.75 | 774.61 | 0 | 29.67 | 0 | OK | Ground clear controls. | 133 | 29.67 | 804.28
9190 | TIN-INTERP | Interpolated Ground | 58851.91 | 6.53 | 777.83 | 0 | 20.93 | 0 | OK | Ground clear controls. | 133 | 27.05 | 798.76
9191 | TIN-INTERP | Interpolated Ground | 58851.93 | 5.04 | 777.33 | 0 | 15.95 | 0 | OK | Ground clear controls. | 133 | 27.05 | 793.28
9192 | TIN-INTERP | Interpolated Ground | 58851.93 | 4.55 | 777.2 | 0 | 27.05 | 0 | OK | Ground clear controls. | 133 | 27.05 | 804.25
9193 | TIN-INTERP | Interpolated Ground | 58851.99 | -5.24 | 774.56 | 0 | 18.76 | 0 | OK | Ground clear controls. | 133 | 18.76 | 793.32
9194 | TIN-INTERP | Interpolated Ground | 58869.73 | -5.23 | 777.14 | 0 | 18.92 | 0 | OK | Ground clear controls. | 134 | 42.71 | 796.06
9195 | TIN-INTERP | Interpolated Ground | 58869.97 | -6.73 | 776.8 | 0 | 24.77 | 0 | OK | Ground clear controls. | 134 | 42.71 | 801.57
9196 | TIN-INTERP | Interpolated Ground | 58869.99 | -4.73 | 777.23 | 0 | 29.84 | 0 | OK | Ground clear controls. | 134 | 42.71 | 807.07
9197 | TIN-INTERP | Interpolated Ground | 58870.04 | 5.01 | 777.85 | 0 | 18.21 | 0 | OK | Ground clear controls. | 134 | 42.71 | 796.06
9198 | TIN-INTERP | Interpolated Ground | 58870.1 | 4.52 | 777.63 | 0 | 29.44 | 0 | OK | Ground clear controls. | 134 | 42.71 | 807.07
9199 | TIN-INTERP | Interpolated Ground | 58870.13 | 6.51 | 778.97 | 0 | 22.6 | 0 | OK | Ground clear controls. | 134 | 42.71 | 801.57
9200 | TIN-INTERP | Interpolated Ground | 58909.73 | -5.33 | 767.64 | 0 | 31.75 | 0 | OK | Ground clear controls. | 134 | 42.71 | 799.39
9201 | TIN-INTERP | Interpolated Ground | 58909.97 | -6.83 | 767.11 | 0 | 37.75 | 0 | OK | Ground clear controls. | 134 | 42.71 | 804.86
9202 | TIN-INTERP | Interpolated Ground | 58909.99 | -4.83 | 767.72 | 0 | 42.6 | 0 | OK | Ground clear controls. | 134 | 42.71 | 810.32
9203 | TIN-INTERP | Interpolated Ground | 58910.04 | 4.91 | 774.11 | 0 | 25.32 | 0 | OK | Ground clear controls. | 134 | 42.71 | 799.43
9204 | TIN-INTERP | Interpolated Ground | 58910.1 | 4.42 | 773.73 | 0 | 36.53 | 0 | OK | Ground clear controls. | 134 | 42.71 | 810.26
9205 | TIN-INTERP | Interpolated Ground | 58910.13 | 6.4 | 774.93 | 0 | 29.96 | 0 | OK | Ground clear controls. | 134 | 42.71 | 804.89
9206 | TIN-INTERP | Interpolated Ground | 58949.73 | -5.42 | 784.25 | 0 | 19.4 | 0 | OK | Ground clear controls. | 134 | 42.71 | 803.65
9207 | TIN-INTERP | Interpolated Ground | 58949.97 | -6.92 | 784.06 | 0 | 25.01 | 0 | OK | Ground clear controls. | 134 | 42.71 | 809.07
9208 | TIN-INTERP | Interpolated Ground | 58949.99 | -4.93 | 784.43 | 0 | 30.07 | 0 | OK | Ground clear controls. | 134 | 42.71 | 814.5
9209 | TIN-INTERP | Interpolated Ground | 58950.04 | 4.8 | 783.99 | 0 | 19.71 | 0 | OK | Ground clear controls. | 134 | 42.71 | 803.7
9210 | TIN-INTERP | Interpolated Ground | 58950.1 | 4.32 | 784.08 | 0 | 30.33 | 0 | OK | Ground clear controls. | 134 | 42.71 | 814.41
9211 | TIN-INTERP | Interpolated Ground | 58950.13 | 6.3 | 783.66 | 0 | 25.47 | 0 | OK | Ground clear controls. | 134 | 42.71 | 809.13
9212 | TIN-INTERP | Interpolated Ground | 58989.73 | -5.52 | 776.67 | 0 | 32.15 | 0 | OK | Ground clear controls. | 134 | 42.71 | 808.82
9213 | TIN-INTERP | Interpolated Ground | 58989.97 | -7.02 | 775.76 | 0 | 38.48 | 0 | OK | Ground clear controls. | 134 | 42.71 | 814.24
9214 | TIN-INTERP | Interpolated Ground | 58989.99 | -5.02 | 776.94 | 0 | 42.71 | 0 | OK | Ground clear controls. | 134 | 42.71 | 819.65
9215 | TIN-INTERP | Interpolated Ground | 58990.04 | 4.7 | 782.49 | 0 | 26.4 | 0 | OK | Ground clear controls. | 134 | 40.23 | 808.89
9216 | TIN-INTERP | Interpolated Ground | 58990.1 | 4.21 | 782.17 | 0 | 37.35 | 0 | OK | Ground clear controls. | 134 | 40.23 | 819.52
9217 | TIN-INTERP | Interpolated Ground | 58990.13 | 6.19 | 783.45 | 0 | 30.86 | 0 | OK | Ground clear controls. | 134 | 40.23 | 814.31
9218 | TIN-INTERP | Interpolated Ground | 59029.73 | -5.62 | 787.9 | 0 | 27.03 | 0 | OK | Ground clear controls. | 134 | 40.23 | 814.93
9219 | TIN-INTERP | Interpolated Ground | 59029.97 | -7.12 | 788.31 | 0 | 32.04 | 0 | OK | Ground clear controls. | 134 | 40.23 | 820.35
9220 | TIN-INTERP | Interpolated Ground | 59029.99 | -5.12 | 787.84 | 0 | 37.91 | 0 | OK | Ground clear controls. | 134 | 40.23 | 825.75
9221 | TIN-INTERP | Interpolated Ground | 59030.04 | 4.59 | 785.05 | 0 | 29.94 | 0 | OK | Ground clear controls. | 134 | 40.23 | 814.99
9222 | TIN-INTERP | Interpolated Ground | 59030.1 | 4.11 | 785.38 | 0 | 40.23 | 0 | OK | Ground clear controls. | 134 | 40.23 | 825.61
9223 | TIN-INTERP | Interpolated Ground | 59030.13 | 6.09 | 784.56 | 0 | 35.84 | 0 | OK | Ground clear controls. | 134 | 35.84 | 820.4
9224 | TIN-INTERP | Interpolated Ground | 59069.73 | -5.71 | 803.3 | 0 | 18.68 | 0 | OK | Ground clear controls. | 134 | 29.33 | 821.98
9225 | TIN-INTERP | Interpolated Ground | 59069.97 | -7.21 | 803.01 | 0 | 24.39 | 0 | OK | Ground clear controls. | 134 | 29.33 | 827.4
9226 | TIN-INTERP | Interpolated Ground | 59069.99 | -5.22 | 803.48 | 0 | 29.33 | 0 | OK | Ground clear controls. | 134 | 29.33 | 832.81
9227 | TIN-INTERP | Interpolated Ground | 59070.04 | 4.49 | 807.81 | 0 | 14.21 | 0 | OK | Ground clear controls. | 134 | 26.63 | 822.02
9228 | TIN-INTERP | Interpolated Ground | 59070.1 | 4.01 | 807.64 | 0 | 25.03 | 0 | OK | Ground clear controls. | 134 | 26.63 | 832.67
9229 | TIN-INTERP | Interpolated Ground | 59070.13 | 5.99 | 808.26 | 0 | 19.18 | 0 | OK | Ground clear controls. | 134 | 26.63 | 827.44
9230 | TIN-INTERP | Interpolated Ground | 59109.73 | -5.81 | 814.02 | 0 | 15.93 | 0 | OK | Ground clear controls. | 134 | 26.63 | 829.95
9231 | TIN-INTERP | Interpolated Ground | 59109.97 | -7.31 | 813.8 | 0 | 21.6 | 0 | OK | Ground clear controls. | 134 | 26.63 | 835.4
9232 | TIN-INTERP | Interpolated Ground | 59109.99 | -5.31 | 814.2 | 0 | 26.63 | 0 | OK | Ground clear controls. | 134 | 26.63 | 840.83
9233 | TIN-INTERP | Interpolated Ground | 59110.04 | 4.38 | 816.56 | 0 | 13.41 | 0 | OK | Ground clear controls. | 134 | 24.25 | 829.97
9234 | TIN-INTERP | Interpolated Ground | 59110.1 | 3.9 | 816.45 | 0 | 24.25 | 0 | OK | Ground clear controls. | 134 | 24.25 | 840.7
9235 | TIN-INTERP | Interpolated Ground | 59110.13 | 5.88 | 816.98 | 0 | 18.42 | 0 | OK | Ground clear controls. | 134 | 23.59 | 835.4
9236 | TIN-INTERP | Interpolated Ground | 59149.73 | -5.91 | 826.18 | 0 | 12.68 | 0 | OK | Ground clear controls. | 134 | 23.59 | 838.86
9237 | TIN-INTERP | Interpolated Ground | 59149.97 | -7.41 | 826.41 | 0 | 17.96 | 0 | OK | Ground clear controls. | 134 | 23.59 | 844.37
9238 | TIN-INTERP | Interpolated Ground | 59149.99 | -5.41 | 826.22 | 0 | 23.59 | 0 | OK | Ground clear controls. | 134 | 23.59 | 849.81
9239 | TIN-INTERP | Interpolated Ground | 59150.04 | 4.28 | 828.13 | 0 | 10.73 | 0 | OK | Ground clear controls. | 134 | 21.82 | 838.86
9240 | TIN-INTERP | Interpolated Ground | 59150.1 | 3.8 | 827.88 | 0 | 21.82 | 0 | OK | Ground clear controls. | 134 | 21.82 | 849.7
9241 | TIN-INTERP | Interpolated Ground | 59150.13 | 5.78 | 828.87 | 0 | 15.44 | 0 | OK | Ground clear controls. | 134 | 15.44 | 844.31
9242 | TIN-INTERP | Interpolated Ground | 59183.06 | 5.71 | 832.23 | 0 | 20.25 | 0 | OK | Ground clear controls. | 135 | 39.42 | 852.48
9243 | TIN-INTERP | Interpolated Ground | 59183.08 | 4.2 | 832.31 | 0 | 14.67 | 0 | OK | Ground clear controls. | 135 | 39.42 | 846.98
9244 | TIN-INTERP | Interpolated Ground | 59183.15 | 3.73 | 832.32 | 0 | 25.65 | 0 | OK | Ground clear controls. | 135 | 39.42 | 857.97
9245 | TIN-INTERP | Interpolated Ground | 59183.37 | -5.98 | 832.55 | 0 | 14.42 | 0 | OK | Ground clear controls. | 135 | 39.42 | 846.97
9246 | TIN-INTERP | Interpolated Ground | 59183.5 | -5.47 | 832.56 | 0 | 25.42 | 0 | OK | Ground clear controls. | 135 | 39.42 | 857.98
9247 | TIN-INTERP | Interpolated Ground | 59183.55 | -7.47 | 832.71 | 0 | 19.76 | 0 | OK | Ground clear controls. | 135 | 39.42 | 852.47
9248 | TIN-INTERP | Interpolated Ground | 59223.06 | 5.72 | 830.31 | 0 | 24.06 | 0 | OK | Ground clear controls. | 135 | 39.42 | 854.37
9249 | TIN-INTERP | Interpolated Ground | 59223.08 | 4.21 | 830.44 | 0 | 18.44 | 0 | OK | Ground clear controls. | 135 | 39.42 | 848.88
9250 | TIN-INTERP | Interpolated Ground | 59223.15 | 3.74 | 830.4 | 0 | 29.38 | 0 | OK | Ground clear controls. | 135 | 39.42 | 859.78
9251 | TIN-INTERP | Interpolated Ground | 59223.37 | -5.97 | 831.28 | 0 | 17.56 | 0 | OK | Ground clear controls. | 135 | 39.42 | 848.84
9252 | TIN-INTERP | Interpolated Ground | 59223.5 | -5.46 | 830.89 | 0 | 28.99 | 0 | OK | Ground clear controls. | 135 | 39.42 | 859.88
9253 | TIN-INTERP | Interpolated Ground | 59223.55 | -7.46 | 832.19 | 0 | 22.15 | 0 | OK | Ground clear controls. | 135 | 39.42 | 854.34
9254 | TIN-INTERP | Interpolated Ground | 59263.06 | 5.73 | 822.13 | 0 | 35.01 | 0 | OK | Ground clear controls. | 135 | 39.42 | 857.14
9255 | TIN-INTERP | Interpolated Ground | 59263.08 | 4.22 | 822.86 | 0 | 28.82 | 0 | OK | Ground clear controls. | 135 | 39.42 | 851.68
9256 | TIN-INTERP | Interpolated Ground | 59263.15 | 3.75 | 823.11 | 0 | 39.42 | 0 | OK | Ground clear controls. | 135 | 39.42 | 862.53
9257 | TIN-INTERP | Interpolated Ground | 59263.37 | -5.96 | 826.69 | 0 | 24.94 | 0 | OK | Ground clear controls. | 135 | 38.59 | 851.63
9258 | TIN-INTERP | Interpolated Ground | 59263.5 | -5.45 | 826.42 | 0 | 36.29 | 0 | OK | Ground clear controls. | 135 | 38.59 | 862.71
9259 | TIN-INTERP | Interpolated Ground | 59263.55 | -7.45 | 827.16 | 0 | 29.97 | 0 | OK | Ground clear controls. | 135 | 38.59 | 857.13
9260 | TIN-INTERP | Interpolated Ground | 59303.06 | 5.73 | 828.89 | 0 | 31.94 | 0 | OK | Ground clear controls. | 135 | 38.59 | 860.83
9261 | TIN-INTERP | Interpolated Ground | 59303.08 | 4.23 | 829.34 | 0 | 26.03 | 0 | OK | Ground clear controls. | 135 | 38.59 | 855.37
9262 | TIN-INTERP | Interpolated Ground | 59303.15 | 3.76 | 829.5 | 0 | 36.72 | 0 | OK | Ground clear controls. | 135 | 38.59 | 866.22
9263 | TIN-INTERP | Interpolated Ground | 59303.37 | -5.95 | 832.39 | 0 | 22.95 | 0 | OK | Ground clear controls. | 135 | 38.59 | 855.34
9264 | TIN-INTERP | Interpolated Ground | 59303.5 | -5.43 | 832.28 | 0 | 34.19 | 0 | OK | Ground clear controls. | 135 | 38.59 | 866.47
9265 | TIN-INTERP | Interpolated Ground | 59303.55 | -7.44 | 832.81 | 0 | 28.03 | 0 | OK | Ground clear controls. | 135 | 38.59 | 860.84
9266 | TIN-INTERP | Interpolated Ground | 59343.06 | 5.74 | 836.21 | 0 | 29.22 | 0 | OK | Ground clear controls. | 135 | 38.59 | 865.43
9267 | TIN-INTERP | Interpolated Ground | 59343.08 | 4.24 | 836.47 | 0 | 23.49 | 0 | OK | Ground clear controls. | 135 | 38.59 | 859.96
9268 | TIN-INTERP | Interpolated Ground | 59343.15 | 3.77 | 836.56 | 0 | 34.29 | 0 | OK | Ground clear controls. | 135 | 38.59 | 870.85
9269 | TIN-INTERP | Interpolated Ground | 59343.37 | -5.94 | 837.79 | 0 | 22.17 | 0 | OK | Ground clear controls. | 135 | 38.59 | 859.96
9270 | TIN-INTERP | Interpolated Ground | 59343.5 | -5.42 | 837.78 | 0 | 33.4 | 0 | OK | Ground clear controls. | 135 | 38.59 | 871.18
9271 | TIN-INTERP | Interpolated Ground | 59343.55 | -7.43 | 837.87 | 0 | 27.62 | 0 | OK | Ground clear controls. | 135 | 38.59 | 865.49
9272 | TIN-INTERP | Interpolated Ground | 59383.06 | 5.75 | 839.02 | 0 | 31.9 | 0 | OK | Ground clear controls. | 135 | 38.59 | 870.92
9273 | TIN-INTERP | Interpolated Ground | 59383.08 | 4.25 | 839.19 | 0 | 26.25 | 0 | OK | Ground clear controls. | 135 | 38.59 | 865.44
9274 | TIN-INTERP | Interpolated Ground | 59383.15 | 3.78 | 839.16 | 0 | 37.26 | 0 | OK | Ground clear controls. | 135 | 38.59 | 876.42
9275 | TIN-INTERP | Interpolated Ground | 59383.37 | -5.93 | 838.11 | 0 | 27.39 | 0 | OK | Ground clear controls. | 135 | 38.59 | 865.5
9276 | TIN-INTERP | Interpolated Ground | 59383.5 | -5.41 | 838.22 | 0 | 38.59 | 0 | OK | Ground clear controls. | 135 | 38.59 | 876.81
9277 | TIN-INTERP | Interpolated Ground | 59383.55 | -7.42 | 837.7 | 0 | 33.34 | 0 | OK | Ground clear controls. | 135 | 33.34 | 871.04
9278 | TIN-INTERP | Interpolated Ground | 59390.38 | 4.26 | 838.89 | 0 | 27.69 | 0 | OK | Ground clear controls. | 136 | 59.88 | 866.58
9279 | TIN-INTERP | Interpolated Ground | 59390.38 | 5.76 | 838.76 | 0 | 33.33 | 0 | OK | Ground clear controls. | 136 | 59.88 | 872.09
9280 | TIN-INTERP | Interpolated Ground | 59390.42 | 3.79 | 838.86 | 0 | 38.72 | 0 | OK | Ground clear controls. | 136 | 59.88 | 877.58
9281 | TIN-INTERP | Interpolated Ground | 59390.79 | -5.39 | 837.38 | 0 | 40.5 | 0 | OK | Ground clear controls. | 136 | 59.88 | 877.88
9282 | TIN-INTERP | Interpolated Ground | 59390.86 | -7.4 | 837.18 | 0 | 34.9 | 0 | OK | Ground clear controls. | 136 | 59.88 | 872.08
9283 | TIN-INTERP | Interpolated Ground | 59390.9 | -5.9 | 837.3 | 0 | 29.29 | 0 | OK | Ground clear controls. | 136 | 59.88 | 866.59
9284 | TIN-INTERP | Interpolated Ground | 59430.35 | 5.81 | 834.46 | 0 | 35.76 | 0 | OK | Ground clear controls. | 136 | 59.88 | 870.22
9285 | TIN-INTERP | Interpolated Ground | 59430.35 | 4.31 | 834.5 | 0 | 30.25 | 0 | OK | Ground clear controls. | 136 | 59.88 | 864.75
9286 | TIN-INTERP | Interpolated Ground | 59430.42 | 3.83 | 834.44 | 0 | 41.07 | 0 | OK | Ground clear controls. | 136 | 59.88 | 875.51
9287 | TIN-INTERP | Interpolated Ground | 59430.79 | -5.27 | 833.33 | 0 | 42.56 | 0 | OK | Ground clear controls. | 136 | 59.88 | 875.89
9288 | TIN-INTERP | Interpolated Ground | 59430.86 | -7.28 | 832.5 | 0 | 37.68 | 0 | OK | Ground clear controls. | 136 | 59.88 | 870.18
9289 | TIN-INTERP | Interpolated Ground | 59430.9 | -5.79 | 833.09 | 0 | 31.68 | 0 | OK | Ground clear controls. | 136 | 59.88 | 864.77
9290 | TIN-INTERP | Interpolated Ground | 59470.35 | 5.85 | 835.77 | 0 | 33.46 | 0 | OK | Ground clear controls. | 136 | 59.88 | 869.23
9291 | TIN-INTERP | Interpolated Ground | 59470.35 | 4.35 | 835.91 | 0 | 27.88 | 0 | OK | Ground clear controls. | 136 | 59.88 | 863.79
9292 | TIN-INTERP | Interpolated Ground | 59470.42 | 3.86 | 835.96 | 0 | 38.4 | 0 | OK | Ground clear controls. | 136 | 59.88 | 874.36
9293 | TIN-INTERP | Interpolated Ground | 59470.79 | -5.16 | 836.66 | 0 | 38.16 | 0 | OK | Ground clear controls. | 136 | 59.88 | 874.82
9294 | TIN-INTERP | Interpolated Ground | 59470.86 | -7.17 | 837.25 | 0 | 31.93 | 0 | OK | Ground clear controls. | 136 | 59.88 | 869.18
9295 | TIN-INTERP | Interpolated Ground | 59470.9 | -5.67 | 836.82 | 0 | 27 | 0 | OK | Ground clear controls. | 136 | 59.88 | 863.82
9296 | TIN-INTERP | Interpolated Ground | 59510.35 | 5.89 | 833.8 | 0 | 35.34 | 0 | OK | Ground clear controls. | 136 | 59.88 | 869.14
9297 | TIN-INTERP | Interpolated Ground | 59510.35 | 4.4 | 834.26 | 0 | 29.48 | 0 | OK | Ground clear controls. | 136 | 59.88 | 863.74
9298 | TIN-INTERP | Interpolated Ground | 59510.42 | 3.9 | 834.42 | 0 | 39.7 | 0 | OK | Ground clear controls. | 136 | 59.88 | 874.12
9299 | TIN-INTERP | Interpolated Ground | 59510.79 | -5.04 | 836.56 | 0 | 38.09 | 0 | OK | Ground clear controls. | 136 | 59.88 | 874.65
9300 | TIN-INTERP | Interpolated Ground | 59510.86 | -7.05 | 836.87 | 0 | 32.21 | 0 | OK | Ground clear controls. | 136 | 59.88 | 869.08
9301 | TIN-INTERP | Interpolated Ground | 59510.9 | -5.55 | 836.61 | 0 | 27.16 | 0 | OK | Ground clear controls. | 136 | 59.88 | 863.77
9302 | TIN-INTERP | Interpolated Ground | 59550.35 | 5.93 | 829.67 | 0 | 40.27 | 0 | OK | Ground clear controls. | 136 | 59.88 | 869.94
9303 | TIN-INTERP | Interpolated Ground | 59550.35 | 4.45 | 830.16 | 0 | 34.39 | 0 | OK | Ground clear controls. | 136 | 59.88 | 864.55
9304 | TIN-INTERP | Interpolated Ground | 59550.42 | 3.94 | 830.31 | 0 | 44.51 | 0 | OK | Ground clear controls. | 136 | 59.88 | 874.82
9305 | TIN-INTERP | Interpolated Ground | 59550.79 | -4.93 | 834.28 | 0 | 41.12 | 0 | OK | Ground clear controls. | 136 | 59.88 | 875.4
9306 | TIN-INTERP | Interpolated Ground | 59550.86 | -6.93 | 834.26 | 0 | 35.63 | 0 | OK | Ground clear controls. | 136 | 59.88 | 869.89
9307 | TIN-INTERP | Interpolated Ground | 59550.9 | -5.43 | 834.3 | 0 | 30.31 | 0 | OK | Ground clear controls. | 136 | 59.88 | 864.61
9308 | TIN-INTERP | Interpolated Ground | 59590.35 | 5.98 | 816.68 | 0 | 54.94 | 0 | OK | Ground clear controls. | 136 | 59.88 | 871.62
9309 | TIN-INTERP | Interpolated Ground | 59590.35 | 4.5 | 816.38 | 0 | 49.86 | 0 | OK | Ground clear controls. | 136 | 59.88 | 866.24
9310 | TIN-INTERP | Interpolated Ground | 59590.42 | 3.98 | 816.56 | 0 | 59.88 | 0 | OK | Ground clear controls. | 136 | 59.88 | 876.44
9311 | TIN-INTERP | Interpolated Ground | 59590.79 | -4.81 | 821.97 | 0 | 55.08 | 0 | OK | Ground clear controls. | 136 | 55.08 | 877.05
9312 | TIN-INTERP | Interpolated Ground | 59590.86 | -6.81 | 823.93 | 0 | 47.66 | 0 | OK | Ground clear controls. | 136 | 47.66 | 871.59
9313 | TIN-INTERP | Interpolated Ground | 59590.9 | -5.31 | 822.5 | 0 | 43.83 | 0 | OK | Ground clear controls. | 136 | 43.83 | 866.33
9314 | TIN-INTERP | Interpolated Ground | 59630.35 | 6.02 | 838.08 | 0 | 36.12 | 0 | OK | Ground clear controls. | 136 | 40.41 | 874.2
9315 | TIN-INTERP | Interpolated Ground | 59630.35 | 4.55 | 838.43 | 0 | 30.4 | 0 | OK | Ground clear controls. | 136 | 40.41 | 868.83
9316 | TIN-INTERP | Interpolated Ground | 59630.42 | 4.01 | 838.57 | 0 | 40.41 | 0 | OK | Ground clear controls. | 136 | 40.41 | 878.98
9317 | TIN-INTERP | Interpolated Ground | 59630.79 | -4.7 | 839.44 | 0 | 40.18 | 0 | OK | Ground clear controls. | 136 | 40.18 | 879.62
9318 | TIN-INTERP | Interpolated Ground | 59630.86 | -6.7 | 840.07 | 0 | 34.13 | 0 | OK | Ground clear controls. | 136 | 38.15 | 874.2
9319 | TIN-INTERP | Interpolated Ground | 59630.9 | -5.2 | 839.61 | 0 | 29.34 | 0 | OK | Ground clear controls. | 136 | 38.15 | 868.95
9320 | TIN-INTERP | Interpolated Ground | 59670.35 | 6.06 | 843.42 | 0 | 34.23 | 0 | OK | Ground clear controls. | 136 | 38.15 | 877.65
9321 | TIN-INTERP | Interpolated Ground | 59670.35 | 4.59 | 844.07 | 0 | 28.23 | 0 | OK | Ground clear controls. | 136 | 38.15 | 872.3
9322 | TIN-INTERP | Interpolated Ground | 59670.42 | 4.05 | 844.3 | 0 | 38.15 | 0 | OK | Ground clear controls. | 136 | 38.15 | 882.45
9323 | TIN-INTERP | Interpolated Ground | 59670.79 | -4.58 | 848.78 | 0 | 34.32 | 0 | OK | Ground clear controls. | 136 | 35.86 | 883.1
9324 | TIN-INTERP | Interpolated Ground | 59670.86 | -6.58 | 849.8 | 0 | 27.9 | 0 | OK | Ground clear controls. | 136 | 35.86 | 877.7
9325 | TIN-INTERP | Interpolated Ground | 59670.9 | -5.08 | 849.13 | 0 | 23.32 | 0 | OK | Ground clear controls. | 136 | 35.86 | 872.45
9326 | TIN-INTERP | Interpolated Ground | 59710.35 | 6.11 | 850.99 | 0 | 31.01 | 0 | OK | Ground clear controls. | 136 | 35.86 | 882
9327 | TIN-INTERP | Interpolated Ground | 59710.35 | 4.64 | 850.86 | 0 | 25.79 | 0 | OK | Ground clear controls. | 136 | 35.86 | 876.65
9328 | TIN-INTERP | Interpolated Ground | 59710.42 | 4.09 | 850.98 | 0 | 35.86 | 0 | OK | Ground clear controls. | 136 | 35.86 | 886.84
9329 | TIN-INTERP | Interpolated Ground | 59710.79 | -4.47 | 852.57 | 0 | 34.92 | 0 | OK | Ground clear controls. | 136 | 34.92 | 887.49
9330 | TIN-INTERP | Interpolated Ground | 59710.86 | -6.46 | 852.85 | 0 | 29.27 | 0 | OK | Ground clear controls. | 136 | 33.51 | 882.12
9331 | TIN-INTERP | Interpolated Ground | 59710.9 | -4.96 | 852.67 | 0 | 24.18 | 0 | OK | Ground clear controls. | 136 | 33.51 | 876.85
9332 | TIN-INTERP | Interpolated Ground | 59750.35 | 6.15 | 867.56 | 0 | 19.7 | 0 | OK | Ground clear controls. | 136 | 33.51 | 887.26
9333 | TIN-INTERP | Interpolated Ground | 59750.35 | 4.69 | 867.69 | 0 | 14.22 | 0 | OK | Ground clear controls. | 136 | 33.51 | 881.91
9334 | TIN-INTERP | Interpolated Ground | 59750.42 | 4.13 | 867.76 | 0 | 24.41 | 0 | OK | Ground clear controls. | 136 | 33.51 | 892.17
9335 | TIN-INTERP | Interpolated Ground | 59750.79 | -4.35 | 868.41 | 0 | 24.39 | 0 | OK | Ground clear controls. | 136 | 33.51 | 892.8
9336 | TIN-INTERP | Interpolated Ground | 59750.86 | -6.34 | 867.47 | 0 | 19.98 | 0 | OK | Ground clear controls. | 136 | 33.51 | 887.45
9337 | TIN-INTERP | Interpolated Ground | 59750.9 | -4.84 | 868.37 | 0 | 13.78 | 0 | OK | Ground clear controls. | 136 | 33.51 | 882.15
9338 | TIN-INTERP | Interpolated Ground | 59790.35 | 6.19 | 872.79 | 0 | 20.6 | 0 | OK | Ground clear controls. | 136 | 33.51 | 893.39
9339 | TIN-INTERP | Interpolated Ground | 59790.35 | 4.74 | 871.67 | 0 | 16.37 | 0 | OK | Ground clear controls. | 136 | 33.51 | 888.04
9340 | TIN-INTERP | Interpolated Ground | 59790.42 | 4.16 | 871.13 | 0 | 27.29 | 0 | OK | Ground clear controls. | 136 | 33.51 | 898.42
9341 | TIN-INTERP | Interpolated Ground | 59790.79 | -4.23 | 868.08 | 0 | 30.94 | 0 | OK | Ground clear controls. | 136 | 33.51 | 899.02
9342 | TIN-INTERP | Interpolated Ground | 59790.86 | -6.23 | 867.31 | 0 | 26.37 | 0 | OK | Ground clear controls. | 136 | 33.51 | 893.68
9343 | TIN-INTERP | Interpolated Ground | 59790.9 | -4.73 | 867.94 | 0 | 20.4 | 0 | OK | Ground clear controls. | 136 | 33.51 | 888.34
9344 | TIN-INTERP | Interpolated Ground | 59830.35 | 6.23 | 874.94 | 0 | 25.5 | 0 | OK | Ground clear controls. | 136 | 33.51 | 900.44
9345 | TIN-INTERP | Interpolated Ground | 59830.35 | 4.79 | 874.88 | 0 | 20.19 | 0 | OK | Ground clear controls. | 136 | 33.51 | 895.07
9346 | TIN-INTERP | Interpolated Ground | 59830.42 | 4.2 | 874.96 | 0 | 30.66 | 0 | OK | Ground clear controls. | 136 | 33.51 | 905.62
9347 | TIN-INTERP | Interpolated Ground | 59830.79 | -4.12 | 873.93 | 0 | 32.23 | 0 | OK | Ground clear controls. | 136 | 33.51 | 906.16
9348 | TIN-INTERP | Interpolated Ground | 59830.85 | -6.11 | 873.63 | 0 | 27.19 | 0 | OK | Ground clear controls. | 136 | 33.51 | 900.82
9349 | TIN-INTERP | Interpolated Ground | 59830.9 | -4.61 | 873.86 | 0 | 21.57 | 0 | OK | Ground clear controls. | 136 | 33.51 | 895.43
9350 | TIN-INTERP | Interpolated Ground | 59870.35 | 6.28 | 882.02 | 0 | 26.37 | 0 | OK | Ground clear controls. | 136 | 33.51 | 908.39
9351 | TIN-INTERP | Interpolated Ground | 59870.35 | 4.83 | 882.18 | 0 | 20.83 | 0 | OK | Ground clear controls. | 136 | 33.51 | 903.01
9352 | TIN-INTERP | Interpolated Ground | 59870.42 | 4.24 | 882.23 | 0 | 31.53 | 0 | OK | Ground clear controls. | 136 | 33.51 | 913.76
9353 | TIN-INTERP | Interpolated Ground | 59870.79 | -4 | 880.73 | 0 | 33.51 | 0 | OK | Ground clear controls. | 136 | 33.51 | 914.24
9354 | TIN-INTERP | Interpolated Ground | 59870.85 | -5.99 | 880.25 | 0 | 28.64 | 0 | OK | Ground clear controls. | 136 | 28.64 | 908.89
9355 | TIN-INTERP | Interpolated Ground | 59870.9 | -4.49 | 880.65 | 0 | 22.78 | 0 | OK | Ground clear controls. | 136 | 22.78 | 903.43
9356 | TIN-INTERP | Interpolated Ground | 59906.92 | 6.26 | 882.48 | 0 | 33.05 | 0 | OK | Ground clear controls. | 137 | 62.83 | 915.53
9357 | TIN-INTERP | Interpolated Ground | 59907.09 | 4.2 | 882.59 | 0 | 38.43 | 0 | OK | Ground clear controls. | 137 | 62.83 | 921.02
9358 | TIN-INTERP | Interpolated Ground | 59907.34 | 4.81 | 882.62 | 0 | 27.44 | 0 | OK | Ground clear controls. | 137 | 62.83 | 910.06
9359 | TIN-INTERP | Interpolated Ground | 59908.79 | -3.92 | 882.76 | 0 | 38.3 | 0 | OK | Ground clear controls. | 137 | 62.83 | 921.06
9360 | TIN-INTERP | Interpolated Ground | 59909.23 | -4.4 | 882.75 | 0 | 27.32 | 0 | OK | Ground clear controls. | 137 | 62.83 | 910.07
9361 | TIN-INTERP | Interpolated Ground | 59909.36 | -5.9 | 882.94 | 0 | 32.64 | 0 | OK | Ground clear controls. | 137 | 62.83 | 915.58
9362 | TIN-INTERP | Interpolated Ground | 59946.92 | 6.19 | 885.42 | 0 | 25.61 | 0 | OK | Ground clear controls. | 137 | 62.83 | 911.03
9363 | TIN-INTERP | Interpolated Ground | 59947.09 | 4.16 | 885.47 | 0 | 30.94 | 0 | OK | Ground clear controls. | 137 | 62.83 | 916.41
9364 | TIN-INTERP | Interpolated Ground | 59947.34 | 4.74 | 885.5 | 0 | 20.53 | 0 | OK | Ground clear controls. | 137 | 62.83 | 906.03
9365 | TIN-INTERP | Interpolated Ground | 59948.79 | -3.94 | 885.78 | 0 | 31.23 | 0 | OK | Ground clear controls. | 137 | 62.83 | 917.01
9366 | TIN-INTERP | Interpolated Ground | 59949.23 | -4.44 | 885.83 | 0 | 20.4 | 0 | OK | Ground clear controls. | 137 | 62.83 | 906.23
9367 | TIN-INTERP | Interpolated Ground | 59949.36 | -5.94 | 885.9 | 0 | 25.87 | 0 | OK | Ground clear controls. | 137 | 62.83 | 911.77
9368 | TIN-INTERP | Interpolated Ground | 59986.92 | 6.12 | 873.59 | 0 | 34.13 | 0 | OK | Ground clear controls. | 137 | 62.83 | 907.72
9369 | TIN-INTERP | Interpolated Ground | 59987.09 | 4.12 | 873.91 | 0 | 39.11 | 0 | OK | Ground clear controls. | 137 | 62.83 | 913.02
9370 | TIN-INTERP | Interpolated Ground | 59987.34 | 4.68 | 873.76 | 0 | 29.34 | 0 | OK | Ground clear controls. | 137 | 62.83 | 903.1
9371 | TIN-INTERP | Interpolated Ground | 59988.79 | -3.97 | 876.51 | 0 | 37.56 | 0 | OK | Ground clear controls. | 137 | 62.83 | 914.07
9372 | TIN-INTERP | Interpolated Ground | 59989.23 | -4.48 | 876.67 | 0 | 26.79 | 0 | OK | Ground clear controls. | 137 | 62.83 | 903.46
9373 | TIN-INTERP | Interpolated Ground | 59989.36 | -5.97 | 877.23 | 0 | 31.81 | 0 | OK | Ground clear controls. | 137 | 62.83 | 909.04
9374 | TIN-INTERP | Interpolated Ground | 60026.92 | 6.06 | 874.35 | 0 | 31.27 | 0 | OK | Ground clear controls. | 137 | 62.83 | 905.62
9375 | TIN-INTERP | Interpolated Ground | 60027.09 | 4.08 | 874.4 | 0 | 36.45 | 0 | OK | Ground clear controls. | 137 | 62.83 | 910.85
9376 | TIN-INTERP | Interpolated Ground | 60027.34 | 4.61 | 874.35 | 0 | 26.94 | 0 | OK | Ground clear controls. | 137 | 62.83 | 901.29
9377 | TIN-INTERP | Interpolated Ground | 60028.79 | -3.99 | 874.15 | 0 | 38.09 | 0 | OK | Ground clear controls. | 137 | 62.83 | 912.24
9378 | TIN-INTERP | Interpolated Ground | 60029.23 | -4.52 | 874.09 | 0 | 27.67 | 0 | OK | Ground clear controls. | 137 | 62.83 | 901.76
9379 | TIN-INTERP | Interpolated Ground | 60029.36 | -6 | 874.19 | 0 | 33.17 | 0 | OK | Ground clear controls. | 137 | 62.83 | 907.36
9380 | TIN-INTERP | Interpolated Ground | 60066.92 | 5.99 | 856.42 | 0 | 48.31 | 0 | OK | Ground clear controls. | 137 | 62.83 | 904.73
9381 | TIN-INTERP | Interpolated Ground | 60067.09 | 4.04 | 855.97 | 0 | 53.94 | 0 | OK | Ground clear controls. | 137 | 62.83 | 909.91
9382 | TIN-INTERP | Interpolated Ground | 60067.34 | 4.55 | 855.91 | 0 | 44.68 | 0 | OK | Ground clear controls. | 137 | 62.83 | 900.59
9383 | TIN-INTERP | Interpolated Ground | 60068.79 | -4.01 | 856.87 | 0 | 54.66 | 0 | OK | Ground clear controls. | 137 | 62.83 | 911.53
9384 | TIN-INTERP | Interpolated Ground | 60069.23 | -4.57 | 857.03 | 0 | 44.11 | 0 | OK | Ground clear controls. | 137 | 62.83 | 901.14
9385 | TIN-INTERP | Interpolated Ground | 60069.36 | -6.04 | 857.57 | 0 | 49.18 | 0 | OK | Ground clear controls. | 137 | 62.83 | 906.75
9386 | TIN-INTERP | Interpolated Ground | 60106.92 | 5.93 | 857.1 | 0 | 47.93 | 0 | OK | Ground clear controls. | 137 | 62.83 | 905.03
9387 | TIN-INTERP | Interpolated Ground | 60107.09 | 4 | 859.06 | 0 | 51.11 | 0 | OK | Ground clear controls. | 137 | 62.83 | 910.17
9388 | TIN-INTERP | Interpolated Ground | 60107.34 | 4.48 | 858.6 | 0 | 42.4 | 0 | OK | Ground clear controls. | 137 | 62.83 | 901
9389 | TIN-INTERP | Interpolated Ground | 60108.79 | -4.04 | 863.03 | 0 | 48.89 | 0 | OK | Ground clear controls. | 137 | 62.83 | 911.92
9390 | TIN-INTERP | Interpolated Ground | 60109.23 | -4.61 | 863.27 | 0 | 38.32 | 0 | OK | Ground clear controls. | 137 | 62.83 | 901.59
9391 | TIN-INTERP | Interpolated Ground | 60109.36 | -6.07 | 863.99 | 0 | 43.21 | 0 | OK | Ground clear controls. | 137 | 62.83 | 907.2
9392 | TIN-INTERP | Interpolated Ground | 60146.92 | 5.86 | 848.01 | 0 | 58.52 | 0 | OK | Ground clear controls. | 137 | 62.83 | 906.53
9393 | TIN-INTERP | Interpolated Ground | 60147.09 | 3.96 | 848.83 | 0 | 62.83 | 0 | OK | Ground clear controls. | 137 | 62.83 | 911.66
9394 | TIN-INTERP | Interpolated Ground | 60147.34 | 4.42 | 848.79 | 0 | 53.73 | 0 | OK | Ground clear controls. | 137 | 61.61 | 902.52
9395 | TIN-INTERP | Interpolated Ground | 60148.79 | -4.06 | 854.3 | 0 | 59.12 | 0 | OK | Ground clear controls. | 137 | 61.61 | 913.42
9396 | TIN-INTERP | Interpolated Ground | 60149.23 | -4.65 | 855.14 | 0 | 47.97 | 0 | OK | Ground clear controls. | 137 | 61.61 | 903.11
9397 | TIN-INTERP | Interpolated Ground | 60149.36 | -6.1 | 856.28 | 0 | 52.43 | 0 | OK | Ground clear controls. | 137 | 61.61 | 908.71
9398 | TIN-INTERP | Interpolated Ground | 60186.92 | 5.8 | 850.81 | 0 | 58.42 | 0 | OK | Ground clear controls. | 137 | 61.61 | 909.23
9399 | TIN-INTERP | Interpolated Ground | 60187.09 | 3.91 | 852.76 | 0 | 61.61 | 0 | OK | Ground clear controls. | 137 | 61.61 | 914.37
9400 | TIN-INTERP | Interpolated Ground | 60187.34 | 4.35 | 852.42 | 0 | 52.74 | 0 | OK | Ground clear controls. | 137 | 61 | 905.16
9401 | TIN-INTERP | Interpolated Ground | 60188.79 | -4.08 | 858.41 | 0 | 57.62 | 0 | OK | Ground clear controls. | 137 | 61 | 916.03
9402 | TIN-INTERP | Interpolated Ground | 60189.23 | -4.69 | 858.88 | 0 | 46.82 | 0 | OK | Ground clear controls. | 137 | 61 | 905.7
9403 | TIN-INTERP | Interpolated Ground | 60189.36 | -6.13 | 859.51 | 0 | 51.78 | 0 | OK | Ground clear controls. | 137 | 61 | 911.29
9404 | TIN-INTERP | Interpolated Ground | 60226.92 | 5.73 | 857.19 | 0 | 55.95 | 0 | OK | Ground clear controls. | 137 | 61 | 913.14
9405 | TIN-INTERP | Interpolated Ground | 60227.09 | 3.87 | 857.3 | 0 | 61 | 0 | OK | Ground clear controls. | 137 | 61 | 918.3
9406 | TIN-INTERP | Interpolated Ground | 60227.34 | 4.29 | 857.5 | 0 | 51.41 | 0 | OK | Ground clear controls. | 137 | 60.81 | 908.91
9407 | TIN-INTERP | Interpolated Ground | 60228.79 | -4.11 | 858.96 | 0 | 60.81 | 0 | OK | Ground clear controls. | 137 | 60.81 | 919.77
9408 | TIN-INTERP | Interpolated Ground | 60229.23 | -4.73 | 859.17 | 0 | 50.2 | 0 | OK | Ground clear controls. | 137 | 55.81 | 909.37
9409 | TIN-INTERP | Interpolated Ground | 60229.36 | -6.17 | 859.13 | 0 | 55.81 | 0 | OK | Ground clear controls. | 137 | 55.81 | 914.94
9410 | TIN-INTERP | Interpolated Ground | 60266.92 | 5.67 | 872.97 | 0 | 45.29 | 0 | OK | Ground clear controls. | 137 | 50.03 | 918.26
9411 | TIN-INTERP | Interpolated Ground | 60267.09 | 3.83 | 873.43 | 0 | 50.03 | 0 | OK | Ground clear controls. | 137 | 50.03 | 923.46
9412 | TIN-INTERP | Interpolated Ground | 60267.34 | 4.22 | 873.37 | 0 | 40.41 | 0 | OK | Ground clear controls. | 137 | 47.08 | 913.78
9413 | TIN-INTERP | Interpolated Ground | 60268.79 | -4.13 | 877.53 | 0 | 47.08 | 0 | OK | Ground clear controls. | 137 | 47.08 | 924.61
9414 | TIN-INTERP | Interpolated Ground | 60269.23 | -4.77 | 878 | 0 | 36.11 | 0 | OK | Ground clear controls. | 137 | 41.29 | 914.11
9415 | TIN-INTERP | Interpolated Ground | 60269.36 | -6.2 | 878.37 | 0 | 41.29 | 0 | OK | Ground clear controls. | 137 | 41.29 | 919.66
9416 | TIN-INTERP | Interpolated Ground | 60306.92 | 5.6 | 889.9 | 0 | 34.68 | 0 | OK | Ground clear controls. | 137 | 39.9 | 924.58
9417 | TIN-INTERP | Interpolated Ground | 60307.09 | 3.79 | 889.94 | 0 | 39.9 | 0 | OK | Ground clear controls. | 137 | 39.9 | 929.84
9418 | TIN-INTERP | Interpolated Ground | 60307.34 | 4.16 | 890.02 | 0 | 29.75 | 0 | OK | Ground clear controls. | 137 | 39.84 | 919.77
9419 | TIN-INTERP | Interpolated Ground | 60308.79 | -4.15 | 890.74 | 0 | 39.84 | 0 | OK | Ground clear controls. | 137 | 39.84 | 930.58
9420 | TIN-INTERP | Interpolated Ground | 60309.23 | -4.81 | 891.17 | 0 | 28.77 | 0 | OK | Ground clear controls. | 137 | 33.92 | 919.94
9421 | TIN-INTERP | Interpolated Ground | 60309.36 | -6.23 | 891.53 | 0 | 33.92 | 0 | OK | Ground clear controls. | 137 | 33.92 | 925.45
9422 | TIN-INTERP | Interpolated Ground | 60346.92 | 5.54 | 907.97 | 0 | 24.15 | 0 | OK | Ground clear controls. | 137 | 28.8 | 932.12
9423 | TIN-INTERP | Interpolated Ground | 60347.09 | 3.75 | 908.66 | 0 | 28.8 | 0 | OK | Ground clear controls. | 137 | 28.8 | 937.46
9424 | TIN-INTERP | Interpolated Ground | 60347.34 | 4.09 | 908.83 | 0 | 18.06 | 0 | OK | Ground clear controls. | 137 | 27.35 | 926.89
9425 | TIN-INTERP | Interpolated Ground | 60348.79 | -4.18 | 910.32 | 0 | 27.35 | 0 | OK | Ground clear controls. | 137 | 27.35 | 937.67
9426 | TIN-INTERP | Interpolated Ground | 60349.23 | -4.86 | 910.72 | 0 | 16.14 | 0 | OK | Ground clear controls. | 137 | 21.61 | 926.86
9427 | TIN-INTERP | Interpolated Ground | 60349.36 | -6.27 | 910.7 | 0 | 21.61 | 0 | OK | Ground clear controls. | 137 | 21.61 | 932.31
9428 | TIN-INTERP | Interpolated Ground | 60369.89 | -6.23 | 913.48 | 0 | 21.75 | 0 | OK | Ground clear controls. | 138 | 99.33 | 935.23
9429 | TIN-INTERP | Interpolated Ground | 60370.43 | -4.25 | 913.13 | 0 | 27.6 | 0 | OK | Ground clear controls. | 138 | 99.33 | 940.73
9430 | TIN-INTERP | Interpolated Ground | 60370.46 | -4.84 | 913.16 | 0 | 16.58 | 0 | OK | Ground clear controls. | 138 | 99.33 | 929.74
9431 | TIN-INTERP | Interpolated Ground | 60372.93 | 3.57 | 912.93 | 0 | 27.79 | 0 | OK | Ground clear controls. | 138 | 99.33 | 940.72
9432 | TIN-INTERP | Interpolated Ground | 60373.26 | 3.94 | 912.95 | 0 | 16.78 | 0 | OK | Ground clear controls. | 138 | 99.33 | 929.73
9433 | TIN-INTERP | Interpolated Ground | 60373.6 | 5.45 | 912.99 | 0 | 22.23 | 0 | OK | Ground clear controls. | 138 | 99.33 | 935.22
9434 | TIN-INTERP | Interpolated Ground | 60409.89 | -6.33 | 900.21 | 0 | 22.41 | 0 | OK | Ground clear controls. | 138 | 99.33 | 922.62
9435 | TIN-INTERP | Interpolated Ground | 60410.43 | -4.34 | 899.4 | 0 | 28.61 | 0 | OK | Ground clear controls. | 138 | 99.33 | 928.01
9436 | TIN-INTERP | Interpolated Ground | 60410.46 | -4.93 | 899.55 | 0 | 17.56 | 0 | OK | Ground clear controls. | 138 | 99.33 | 917.11
9437 | TIN-INTERP | Interpolated Ground | 60412.93 | 3.65 | 896.06 | 0 | 31.85 | 0 | OK | Ground clear controls. | 138 | 99.33 | 927.91
9438 | TIN-INTERP | Interpolated Ground | 60413.26 | 4.03 | 895.83 | 0 | 21.2 | 0 | OK | Ground clear controls. | 138 | 99.33 | 917.03
9439 | TIN-INTERP | Interpolated Ground | 60413.6 | 5.55 | 895.49 | 0 | 26.91 | 0 | OK | Ground clear controls. | 138 | 99.33 | 922.4
9440 | TIN-INTERP | Interpolated Ground | 60449.89 | -6.42 | 884.85 | 0 | 26.19 | 0 | OK | Ground clear controls. | 138 | 99.33 | 911.04
9441 | TIN-INTERP | Interpolated Ground | 60450.43 | -4.42 | 884.58 | 0 | 31.74 | 0 | OK | Ground clear controls. | 138 | 99.33 | 916.32
9442 | TIN-INTERP | Interpolated Ground | 60450.46 | -5.02 | 884.61 | 0 | 20.9 | 0 | OK | Ground clear controls. | 138 | 99.33 | 905.51
9443 | TIN-INTERP | Interpolated Ground | 60452.93 | 3.72 | 883.23 | 0 | 32.9 | 0 | OK | Ground clear controls. | 138 | 99.33 | 916.13
9444 | TIN-INTERP | Interpolated Ground | 60453.26 | 4.12 | 883.04 | 0 | 22.31 | 0 | OK | Ground clear controls. | 138 | 99.33 | 905.35
9445 | TIN-INTERP | Interpolated Ground | 60453.6 | 5.64 | 882.64 | 0 | 27.97 | 0 | OK | Ground clear controls. | 138 | 99.33 | 910.61
9446 | TIN-INTERP | Interpolated Ground | 60489.89 | -6.52 | 870.23 | 0 | 30.3 | 0 | OK | Ground clear controls. | 138 | 99.33 | 900.53
9447 | TIN-INTERP | Interpolated Ground | 60490.43 | -4.51 | 869.16 | 0 | 36.57 | 0 | OK | Ground clear controls. | 138 | 99.33 | 905.73
9448 | TIN-INTERP | Interpolated Ground | 60490.46 | -5.11 | 869.35 | 0 | 25.65 | 0 | OK | Ground clear controls. | 138 | 99.33 | 895
9449 | TIN-INTERP | Interpolated Ground | 60492.93 | 3.8 | 865.79 | 0 | 39.67 | 0 | OK | Ground clear controls. | 138 | 99.33 | 905.46
9450 | TIN-INTERP | Interpolated Ground | 60493.26 | 4.22 | 865.67 | 0 | 29.1 | 0 | OK | Ground clear controls. | 138 | 99.33 | 894.77
9451 | TIN-INTERP | Interpolated Ground | 60493.6 | 5.73 | 865.89 | 0 | 34.05 | 0 | OK | Ground clear controls. | 138 | 99.33 | 899.94
9452 | TIN-INTERP | Interpolated Ground | 60529.89 | -6.61 | 862.85 | 0 | 28.19 | 0 | OK | Ground clear controls. | 138 | 99.33 | 891.04
9453 | TIN-INTERP | Interpolated Ground | 60530.43 | -4.6 | 864.42 | 0 | 31.74 | 0 | OK | Ground clear controls. | 138 | 99.33 | 896.16
9454 | TIN-INTERP | Interpolated Ground | 60530.46 | -5.2 | 864 | 0 | 21.5 | 0 | OK | Ground clear controls. | 138 | 99.33 | 885.5
9455 | TIN-INTERP | Interpolated Ground | 60532.93 | 3.88 | 868.43 | 0 | 27.41 | 0 | OK | Ground clear controls. | 138 | 99.33 | 895.84
9456 | TIN-INTERP | Interpolated Ground | 60533.26 | 4.31 | 868.62 | 0 | 16.61 | 0 | OK | Ground clear controls. | 138 | 99.33 | 885.23
9457 | TIN-INTERP | Interpolated Ground | 60533.6 | 5.82 | 869.39 | 0 | 20.91 | 0 | OK | Ground clear controls. | 138 | 99.33 | 890.3
9458 | TIN-INTERP | Interpolated Ground | 60569.89 | -6.71 | 854.77 | 0 | 27.82 | 0 | OK | Ground clear controls. | 138 | 99.33 | 882.59
9459 | TIN-INTERP | Interpolated Ground | 60570.43 | -4.68 | 855.57 | 0 | 32.1 | 0 | OK | Ground clear controls. | 138 | 99.33 | 887.67
9460 | TIN-INTERP | Interpolated Ground | 60570.46 | -5.29 | 855.25 | 0 | 21.79 | 0 | OK | Ground clear controls. | 138 | 99.33 | 877.04
9461 | TIN-INTERP | Interpolated Ground | 60572.93 | 3.96 | 858.57 | 0 | 28.72 | 0 | OK | Ground clear controls. | 138 | 99.33 | 887.29
9462 | TIN-INTERP | Interpolated Ground | 60573.26 | 4.4 | 858.65 | 0 | 18.09 | 0 | OK | Ground clear controls. | 138 | 99.33 | 876.74
9463 | TIN-INTERP | Interpolated Ground | 60573.6 | 5.91 | 859.3 | 0 | 22.45 | 0 | OK | Ground clear controls. | 138 | 99.33 | 881.75
9464 | TIN-INTERP | Interpolated Ground | 60609.89 | -6.8 | 839.18 | 0 | 36.01 | 0 | OK | Ground clear controls. | 138 | 99.33 | 875.19
9465 | TIN-INTERP | Interpolated Ground | 60610.43 | -4.77 | 839.82 | 0 | 40.4 | 0 | OK | Ground clear controls. | 138 | 99.33 | 880.22
9466 | TIN-INTERP | Interpolated Ground | 60610.46 | -5.38 | 839.65 | 0 | 29.98 | 0 | OK | Ground clear controls. | 138 | 99.33 | 869.63
9467 | TIN-INTERP | Interpolated Ground | 60612.93 | 4.04 | 841.66 | 0 | 38.14 | 0 | OK | Ground clear controls. | 138 | 99.33 | 879.8
9468 | TIN-INTERP | Interpolated Ground | 60613.26 | 4.49 | 841.74 | 0 | 27.55 | 0 | OK | Ground clear controls. | 138 | 99.33 | 869.29
9469 | TIN-INTERP | Interpolated Ground | 60613.6 | 6 | 842.26 | 0 | 31.98 | 0 | OK | Ground clear controls. | 138 | 99.33 | 874.24
9470 | TIN-INTERP | Interpolated Ground | 60649.89 | -6.9 | 832.56 | 0 | 36.22 | 0 | OK | Ground clear controls. | 138 | 99.33 | 868.78
9471 | TIN-INTERP | Interpolated Ground | 60650.43 | -4.85 | 833.13 | 0 | 40.65 | 0 | OK | Ground clear controls. | 138 | 99.33 | 873.78
9472 | TIN-INTERP | Interpolated Ground | 60650.46 | -5.47 | 832.9 | 0 | 30.32 | 0 | OK | Ground clear controls. | 138 | 99.33 | 863.22
9473 | TIN-INTERP | Interpolated Ground | 60652.93 | 4.12 | 835.93 | 0 | 37.4 | 0 | OK | Ground clear controls. | 138 | 99.33 | 873.33
9474 | TIN-INTERP | Interpolated Ground | 60653.26 | 4.58 | 835.98 | 0 | 26.87 | 0 | OK | Ground clear controls. | 138 | 99.33 | 862.85
9475 | TIN-INTERP | Interpolated Ground | 60653.6 | 6.1 | 836.45 | 0 | 31.3 | 0 | OK | Ground clear controls. | 138 | 99.33 | 867.75
9476 | TIN-INTERP | Interpolated Ground | 60689.89 | -6.99 | 819.6 | 0 | 43.84 | 0 | OK | Ground clear controls. | 138 | 99.33 | 863.44
9477 | TIN-INTERP | Interpolated Ground | 60690.43 | -4.94 | 819.21 | 0 | 49.2 | 0 | OK | Ground clear controls. | 138 | 99.33 | 868.41
9478 | TIN-INTERP | Interpolated Ground | 60690.46 | -5.56 | 819.21 | 0 | 38.65 | 0 | OK | Ground clear controls. | 138 | 99.33 | 857.86
9479 | TIN-INTERP | Interpolated Ground | 60692.93 | 4.2 | 816.37 | 0 | 51.57 | 0 | OK | Ground clear controls. | 138 | 99.33 | 867.94
9480 | TIN-INTERP | Interpolated Ground | 60693.26 | 4.68 | 815.88 | 0 | 41.61 | 0 | OK | Ground clear controls. | 138 | 99.33 | 857.49
9481 | TIN-INTERP | Interpolated Ground | 60693.6 | 6.19 | 815.53 | 0 | 46.82 | 0 | OK | Ground clear controls. | 138 | 99.33 | 862.35
9482 | TIN-INTERP | Interpolated Ground | 60729.89 | -7.09 | 795.12 | 0 | 63.98 | 0 | OK | Ground clear controls. | 138 | 99.33 | 859.1
9483 | TIN-INTERP | Interpolated Ground | 60730.43 | -5.03 | 794.1 | 0 | 69.96 | 0 | OK | Ground clear controls. | 138 | 99.33 | 864.06
9484 | TIN-INTERP | Interpolated Ground | 60730.46 | -5.65 | 794.28 | 0 | 59.24 | 0 | OK | Ground clear controls. | 138 | 99.33 | 853.52
9485 | TIN-INTERP | Interpolated Ground | 60732.93 | 4.28 | 790.4 | 0 | 73.17 | 0 | OK | Ground clear controls. | 138 | 99.33 | 863.57
9486 | TIN-INTERP | Interpolated Ground | 60733.26 | 4.77 | 789.96 | 0 | 63.17 | 0 | OK | Ground clear controls. | 138 | 99.33 | 853.13
9487 | TIN-INTERP | Interpolated Ground | 60733.6 | 6.28 | 789.16 | 0 | 68.8 | 0 | OK | Ground clear controls. | 138 | 99.33 | 857.96
9488 | TIN-INTERP | Interpolated Ground | 60769.89 | -7.18 | 779.24 | 0 | 76.52 | 0 | OK | Ground clear controls. | 138 | 99.33 | 855.76
9489 | TIN-INTERP | Interpolated Ground | 60770.43 | -5.11 | 779.68 | 0 | 81.05 | 0 | OK | Ground clear controls. | 138 | 99.33 | 860.73
9490 | TIN-INTERP | Interpolated Ground | 60770.46 | -5.74 | 779.63 | 0 | 70.54 | 0 | OK | Ground clear controls. | 138 | 99.33 | 850.17
9491 | TIN-INTERP | Interpolated Ground | 60772.93 | 4.36 | 783.41 | 0 | 76.84 | 0 | OK | Ground clear controls. | 138 | 99.33 | 860.25
9492 | TIN-INTERP | Interpolated Ground | 60773.26 | 4.86 | 783.75 | 0 | 66.05 | 0 | OK | Ground clear controls. | 138 | 99.33 | 849.8
9493 | TIN-INTERP | Interpolated Ground | 60773.6 | 6.37 | 784.39 | 0 | 70.23 | 0 | OK | Ground clear controls. | 138 | 99.33 | 854.62
9494 | TIN-INTERP | Interpolated Ground | 60809.89 | -7.28 | 787.52 | 0 | 65.94 | 0 | OK | Ground clear controls. | 138 | 99.33 | 853.46
9495 | TIN-INTERP | Interpolated Ground | 60810.43 | -5.2 | 788.15 | 0 | 70.3 | 0 | OK | Ground clear controls. | 138 | 99.33 | 858.45
9496 | TIN-INTERP | Interpolated Ground | 60810.46 | -5.83 | 787.91 | 0 | 59.96 | 0 | OK | Ground clear controls. | 138 | 99.33 | 847.87
9497 | TIN-INTERP | Interpolated Ground | 60812.93 | 4.43 | 793.18 | 0 | 64.8 | 0 | OK | Ground clear controls. | 138 | 99.33 | 857.98
9498 | TIN-INTERP | Interpolated Ground | 60813.25 | 4.95 | 793.56 | 0 | 53.94 | 0 | OK | Ground clear controls. | 138 | 99.33 | 847.5
9499 | TIN-INTERP | Interpolated Ground | 60813.6 | 6.46 | 794.68 | 0 | 57.64 | 0 | OK | Ground clear controls. | 138 | 99.33 | 852.32
9500 | TIN-INTERP | Interpolated Ground | 60849.89 | -7.37 | 801.07 | 0 | 51.09 | 0 | OK | Ground clear controls. | 138 | 99.33 | 852.16
9501 | TIN-INTERP | Interpolated Ground | 60850.43 | -5.28 | 801.71 | 0 | 55.46 | 0 | OK | Ground clear controls. | 138 | 99.33 | 857.17
9502 | TIN-INTERP | Interpolated Ground | 60850.46 | -5.93 | 801.67 | 0 | 44.88 | 0 | OK | Ground clear controls. | 138 | 99.33 | 846.55
9503 | TIN-INTERP | Interpolated Ground | 60852.93 | 4.51 | 803.96 | 0 | 52.75 | 0 | OK | Ground clear controls. | 138 | 99.33 | 856.71
9504 | TIN-INTERP | Interpolated Ground | 60853.25 | 5.04 | 804.09 | 0 | 42.12 | 0 | OK | Ground clear controls. | 138 | 99.33 | 846.21
9505 | TIN-INTERP | Interpolated Ground | 60853.6 | 6.55 | 804.27 | 0 | 46.77 | 0 | OK | Ground clear controls. | 138 | 99.33 | 851.04
9506 | TIN-INTERP | Interpolated Ground | 60889.89 | -7.47 | 795.17 | 0 | 56.7 | 0 | OK | Ground clear controls. | 138 | 99.33 | 851.87
9507 | TIN-INTERP | Interpolated Ground | 60890.43 | -5.37 | 794.49 | 0 | 62.43 | 0 | OK | Ground clear controls. | 138 | 99.33 | 856.92
9508 | TIN-INTERP | Interpolated Ground | 60890.46 | -6.02 | 794.64 | 0 | 51.63 | 0 | OK | Ground clear controls. | 138 | 99.33 | 846.27
9509 | TIN-INTERP | Interpolated Ground | 60892.93 | 4.59 | 789.72 | 0 | 66.79 | 0 | OK | Ground clear controls. | 138 | 99.33 | 856.51
9510 | TIN-INTERP | Interpolated Ground | 60893.25 | 5.14 | 789.41 | 0 | 56.55 | 0 | OK | Ground clear controls. | 138 | 99.33 | 845.96
9511 | TIN-INTERP | Interpolated Ground | 60893.6 | 6.65 | 788.56 | 0 | 62.25 | 0 | OK | Ground clear controls. | 138 | 99.33 | 850.81
9512 | TIN-INTERP | Interpolated Ground | 60929.89 | -7.56 | 771.76 | 0 | 80.85 | 0 | OK | Ground clear controls. | 138 | 99.33 | 852.61
9513 | TIN-INTERP | Interpolated Ground | 60930.43 | -5.46 | 770.52 | 0 | 87.2 | 0 | OK | Ground clear controls. | 138 | 99.33 | 857.72
9514 | TIN-INTERP | Interpolated Ground | 60930.46 | -6.11 | 770.67 | 0 | 76.33 | 0 | OK | Ground clear controls. | 138 | 99.33 | 847
9515 | TIN-INTERP | Interpolated Ground | 60932.93 | 4.67 | 764.9 | 0 | 92.42 | 0 | OK | Ground clear controls. | 138 | 99.33 | 857.32
9516 | TIN-INTERP | Interpolated Ground | 60933.25 | 5.23 | 764.45 | 0 | 82.28 | 0 | OK | Ground clear controls. | 138 | 99.33 | 846.73
9517 | TIN-INTERP | Interpolated Ground | 60933.6 | 6.74 | 763.56 | 0 | 88.05 | 0 | OK | Ground clear controls. | 138 | 99.33 | 851.61
9518 | TIN-INTERP | Interpolated Ground | 60969.89 | -7.66 | 763.98 | 0 | 90.35 | 0 | OK | Ground clear controls. | 138 | 99.33 | 854.33
9519 | TIN-INTERP | Interpolated Ground | 60970.43 | -5.54 | 764.46 | 0 | 95.04 | 0 | OK | Ground clear controls. | 138 | 99.33 | 859.5
9520 | TIN-INTERP | Interpolated Ground | 60970.46 | -6.2 | 764.35 | 0 | 84.37 | 0 | OK | Ground clear controls. | 138 | 99.33 | 848.72
9521 | TIN-INTERP | Interpolated Ground | 60972.93 | 4.75 | 767.52 | 0 | 91.65 | 0 | OK | Ground clear controls. | 138 | 99.33 | 859.17
9522 | TIN-INTERP | Interpolated Ground | 60973.25 | 5.32 | 767.63 | 0 | 80.87 | 0 | OK | Ground clear controls. | 138 | 99.33 | 848.5
9523 | TIN-INTERP | Interpolated Ground | 60973.6 | 6.83 | 767.92 | 0 | 85.49 | 0 | OK | Ground clear controls. | 138 | 99.33 | 853.41
9524 | TIN-INTERP | Interpolated Ground | 61009.89 | -7.75 | 770.69 | 0 | 86.4 | 0 | OK | Ground clear controls. | 138 | 99.33 | 857.09
9525 | TIN-INTERP | Interpolated Ground | 61010.43 | -5.63 | 771.56 | 0 | 90.78 | 0 | OK | Ground clear controls. | 138 | 99.33 | 862.34
9526 | TIN-INTERP | Interpolated Ground | 61010.46 | -6.29 | 771.11 | 0 | 80.37 | 0 | OK | Ground clear controls. | 138 | 99.33 | 851.48
9527 | TIN-INTERP | Interpolated Ground | 61012.93 | 4.83 | 776.12 | 0 | 85.96 | 0 | OK | Ground clear controls. | 138 | 99.33 | 862.08
9528 | TIN-INTERP | Interpolated Ground | 61013.25 | 5.41 | 776.24 | 0 | 75.08 | 0 | OK | Ground clear controls. | 138 | 99.33 | 851.32
9529 | TIN-INTERP | Interpolated Ground | 61013.6 | 6.92 | 776.78 | 0 | 79.52 | 0 | OK | Ground clear controls. | 138 | 99.33 | 856.3
9530 | TIN-INTERP | Interpolated Ground | 61049.89 | -7.85 | 776.71 | 0 | 84.15 | 0 | OK | Ground clear controls. | 138 | 99.33 | 860.86
9531 | TIN-INTERP | Interpolated Ground | 61050.43 | -5.71 | 777.7 | 0 | 88.5 | 0 | OK | Ground clear controls. | 138 | 99.33 | 866.2
9532 | TIN-INTERP | Interpolated Ground | 61050.46 | -6.38 | 777.47 | 0 | 77.78 | 0 | OK | Ground clear controls. | 138 | 99.33 | 855.25
9533 | TIN-INTERP | Interpolated Ground | 61052.93 | 4.91 | 780.92 | 0 | 85.09 | 0 | OK | Ground clear controls. | 138 | 99.33 | 866.01
9534 | TIN-INTERP | Interpolated Ground | 61053.25 | 5.51 | 781.25 | 0 | 73.9 | 0 | OK | Ground clear controls. | 138 | 99.33 | 855.15
9535 | TIN-INTERP | Interpolated Ground | 61053.6 | 7.01 | 781.85 | 0 | 78.34 | 0 | OK | Ground clear controls. | 138 | 99.33 | 860.19
9536 | TIN-INTERP | Interpolated Ground | 61089.89 | -7.94 | 787.97 | 0 | 77.66 | 0 | OK | Ground clear controls. | 138 | 99.33 | 865.63
9537 | TIN-INTERP | Interpolated Ground | 61090.43 | -5.8 | 788.48 | 0 | 82.59 | 0 | OK | Ground clear controls. | 138 | 99.33 | 871.07
9538 | TIN-INTERP | Interpolated Ground | 61090.46 | -6.47 | 788.27 | 0 | 71.75 | 0 | OK | Ground clear controls. | 138 | 99.33 | 860.02
9539 | TIN-INTERP | Interpolated Ground | 61092.93 | 4.99 | 796 | 0 | 74.96 | 0 | OK | Ground clear controls. | 138 | 99.33 | 870.96
9540 | TIN-INTERP | Interpolated Ground | 61093.25 | 5.6 | 796.08 | 0 | 63.93 | 0 | OK | Ground clear controls. | 138 | 99.33 | 860.01
9541 | TIN-INTERP | Interpolated Ground | 61093.6 | 7.1 | 796.78 | 0 | 68.34 | 0 | OK | Ground clear controls. | 138 | 99.33 | 865.12
9542 | TIN-INTERP | Interpolated Ground | 61129.89 | -8.04 | 776.56 | 0 | 94.9 | 0 | OK | Ground clear controls. | 138 | 99.33 | 871.46
9543 | TIN-INTERP | Interpolated Ground | 61130.43 | -5.89 | 777.69 | 0 | 99.33 | 0 | OK | Ground clear controls. | 138 | 99.33 | 877.02
9544 | TIN-INTERP | Interpolated Ground | 61130.46 | -6.56 | 777.44 | 0 | 88.4 | 0 | OK | Ground clear controls. | 138 | 92.23 | 865.84
9545 | TIN-INTERP | Interpolated Ground | 61132.93 | 5.07 | 784.76 | 0 | 92.23 | 0 | OK | Ground clear controls. | 138 | 92.23 | 876.99
9546 | TIN-INTERP | Interpolated Ground | 61133.25 | 5.69 | 785.38 | 0 | 80.54 | 0 | OK | Ground clear controls. | 138 | 91.97 | 865.92
9547 | TIN-INTERP | Interpolated Ground | 61133.6 | 7.2 | 786.35 | 0 | 84.77 | 0 | OK | Ground clear controls. | 138 | 91.97 | 871.12
9548 | TIN-INTERP | Interpolated Ground | 61169.89 | -8.13 | 792.14 | 0 | 86.15 | 0 | OK | Ground clear controls. | 138 | 91.97 | 878.29
9549 | TIN-INTERP | Interpolated Ground | 61170.43 | -5.97 | 792.01 | 0 | 91.97 | 0 | OK | Ground clear controls. | 138 | 91.97 | 883.98
9550 | TIN-INTERP | Interpolated Ground | 61170.46 | -6.65 | 792.14 | 0 | 80.52 | 0 | OK | Ground clear controls. | 138 | 91.43 | 872.66
9551 | TIN-INTERP | Interpolated Ground | 61172.93 | 5.15 | 792.61 | 0 | 91.43 | 0 | OK | Ground clear controls. | 138 | 91.43 | 884.04
9552 | TIN-INTERP | Interpolated Ground | 61173.25 | 5.78 | 792.69 | 0 | 80.14 | 0 | OK | Ground clear controls. | 138 | 85.41 | 872.83
9553 | TIN-INTERP | Interpolated Ground | 61173.6 | 7.29 | 792.72 | 0 | 85.41 | 0 | OK | Ground clear controls. | 138 | 85.41 | 878.13
9554 | TIN-INTERP | Interpolated Ground | 61209.89 | -8.23 | 810.52 | 0 | 75.62 | 0 | OK | Ground clear controls. | 138 | 81.35 | 886.14
9555 | TIN-INTERP | Interpolated Ground | 61210.43 | -6.06 | 810.62 | 0 | 81.35 | 0 | OK | Ground clear controls. | 138 | 81.35 | 891.97
9556 | TIN-INTERP | Interpolated Ground | 61210.46 | -6.74 | 810.72 | 0 | 69.8 | 0 | OK | Ground clear controls. | 138 | 80.65 | 880.52
9557 | TIN-INTERP | Interpolated Ground | 61212.93 | 5.22 | 811.51 | 0 | 80.65 | 0 | OK | Ground clear controls. | 138 | 80.65 | 892.16
9558 | TIN-INTERP | Interpolated Ground | 61213.25 | 5.87 | 811.73 | 0 | 69.08 | 0 | OK | Ground clear controls. | 138 | 74.04 | 880.81
9559 | TIN-INTERP | Interpolated Ground | 61213.6 | 7.38 | 812.18 | 0 | 74.04 | 0 | OK | Ground clear controls. | 138 | 74.04 | 886.22
9560 | TIN-INTERP | Interpolated Ground | 61249.89 | -8.32 | 832.24 | 0 | 62.82 | 0 | OK | Ground clear controls. | 138 | 68.53 | 895.06
9561 | TIN-INTERP | Interpolated Ground | 61250.43 | -6.14 | 832.5 | 0 | 68.53 | 0 | OK | Ground clear controls. | 138 | 68.53 | 901.03
9562 | TIN-INTERP | Interpolated Ground | 61250.46 | -6.83 | 832.53 | 0 | 56.9 | 0 | OK | Ground clear controls. | 138 | 67.27 | 889.43
9563 | TIN-INTERP | Interpolated Ground | 61252.93 | 5.3 | 834.07 | 0 | 67.27 | 0 | OK | Ground clear controls. | 138 | 67.27 | 901.34
9564 | TIN-INTERP | Interpolated Ground | 61253.25 | 5.97 | 834.16 | 0 | 55.66 | 0 | OK | Ground clear controls. | 138 | 61.21 | 889.82
9565 | TIN-INTERP | Interpolated Ground | 61253.6 | 7.47 | 834.15 | 0 | 61.21 | 0 | OK | Ground clear controls. | 138 | 61.21 | 895.36
9566 | TIN-INTERP | Interpolated Ground | 61289.89 | -8.42 | 854.17 | 0 | 50.79 | 0 | OK | Ground clear controls. | 138 | 57.92 | 904.96
9567 | TIN-INTERP | Interpolated Ground | 61290.43 | -6.23 | 853.92 | 0 | 57.19 | 0 | OK | Ground clear controls. | 138 | 57.92 | 911.11
9568 | TIN-INTERP | Interpolated Ground | 61290.46 | -6.92 | 854.09 | 0 | 45.25 | 0 | OK | Ground clear controls. | 138 | 57.92 | 899.34
9569 | TIN-INTERP | Interpolated Ground | 61292.93 | 5.38 | 853.66 | 0 | 57.92 | 0 | OK | Ground clear controls. | 138 | 57.92 | 911.58
9570 | TIN-INTERP | Interpolated Ground | 61293.25 | 6.06 | 853.92 | 0 | 45.96 | 0 | OK | Ground clear controls. | 138 | 51.62 | 899.88
9571 | TIN-INTERP | Interpolated Ground | 61293.6 | 7.56 | 853.93 | 0 | 51.62 | 0 | OK | Ground clear controls. | 138 | 51.62 | 905.55
9572 | TIN-INTERP | Interpolated Ground | 61329.89 | -8.51 | 873.17 | 0 | 42.8 | 0 | OK | Ground clear controls. | 138 | 48.04 | 915.97
9573 | TIN-INTERP | Interpolated Ground | 61330.43 | -6.32 | 874.26 | 0 | 48.04 | 0 | OK | Ground clear controls. | 138 | 48.04 | 922.3
9574 | TIN-INTERP | Interpolated Ground | 61330.46 | -7.01 | 874.01 | 0 | 36.33 | 0 | OK | Ground clear controls. | 138 | 44.25 | 910.34
9575 | TIN-INTERP | Interpolated Ground | 61332.93 | 5.46 | 878.66 | 0 | 44.25 | 0 | OK | Ground clear controls. | 138 | 44.25 | 922.91
9576 | TIN-INTERP | Interpolated Ground | 61333.25 | 6.15 | 878.49 | 0 | 32.52 | 0 | OK | Ground clear controls. | 138 | 38.19 | 911.01
9577 | TIN-INTERP | Interpolated Ground | 61333.6 | 7.65 | 878.64 | 0 | 38.19 | 0 | OK | Ground clear controls. | 138 | 38.19 | 916.83
9578 | TIN-INTERP | Interpolated Ground | 61354.51 | 7.71 | 885.21 | 0 | 38.02 | 0 | OK | Ground clear controls. | 139 | 76.8 | 923.23
9579 | TIN-INTERP | Interpolated Ground | 61354.57 | 6.21 | 884.98 | 0 | 32.45 | 0 | OK | Ground clear controls. | 139 | 76.8 | 917.43
9580 | TIN-INTERP | Interpolated Ground | 61354.62 | 5.52 | 884.88 | 0 | 44.66 | 0 | OK | Ground clear controls. | 139 | 76.8 | 929.54
9581 | TIN-INTERP | Interpolated Ground | 61354.82 | -7.06 | 883.73 | 0 | 33.7 | 0 | OK | Ground clear controls. | 139 | 76.8 | 917.43
9582 | TIN-INTERP | Interpolated Ground | 61354.88 | -6.35 | 883.81 | 0 | 45.73 | 0 | OK | Ground clear controls. | 139 | 76.8 | 929.54
9583 | TIN-INTERP | Interpolated Ground | 61354.91 | -8.56 | 883.27 | 0 | 39.97 | 0 | OK | Ground clear controls. | 139 | 76.8 | 923.24
9584 | TIN-INTERP | Interpolated Ground | 61394.51 | 7.86 | 873.05 | 0 | 46.3 | 0 | OK | Ground clear controls. | 139 | 76.8 | 919.35
9585 | TIN-INTERP | Interpolated Ground | 61394.57 | 6.35 | 872.64 | 0 | 40.99 | 0 | OK | Ground clear controls. | 139 | 76.8 | 913.63
9586 | TIN-INTERP | Interpolated Ground | 61394.62 | 5.66 | 872.34 | 0 | 53.36 | 0 | OK | Ground clear controls. | 139 | 76.8 | 925.7
9587 | TIN-INTERP | Interpolated Ground | 61394.82 | -6.9 | 866.37 | 0 | 47.24 | 0 | OK | Ground clear controls. | 139 | 76.8 | 913.61
9588 | TIN-INTERP | Interpolated Ground | 61394.88 | -6.2 | 866.68 | 0 | 59.03 | 0 | OK | Ground clear controls. | 139 | 76.8 | 925.71
9589 | TIN-INTERP | Interpolated Ground | 61394.91 | -8.4 | 865.64 | 0 | 53.82 | 0 | OK | Ground clear controls. | 139 | 76.8 | 919.46
9590 | TIN-INTERP | Interpolated Ground | 61434.51 | 8 | 875.77 | 0 | 40.69 | 0 | OK | Ground clear controls. | 139 | 76.8 | 916.46
9591 | TIN-INTERP | Interpolated Ground | 61434.57 | 6.5 | 875.52 | 0 | 35.29 | 0 | OK | Ground clear controls. | 139 | 76.8 | 910.81
9592 | TIN-INTERP | Interpolated Ground | 61434.62 | 5.8 | 875.44 | 0 | 47.4 | 0 | OK | Ground clear controls. | 139 | 76.8 | 922.84
9593 | TIN-INTERP | Interpolated Ground | 61434.82 | -6.75 | 871.83 | 0 | 38.93 | 0 | OK | Ground clear controls. | 139 | 76.8 | 910.76
9594 | TIN-INTERP | Interpolated Ground | 61434.87 | -6.05 | 872.14 | 0 | 50.73 | 0 | OK | Ground clear controls. | 139 | 76.8 | 922.87
9595 | TIN-INTERP | Interpolated Ground | 61434.91 | -8.24 | 871.23 | 0 | 45.43 | 0 | OK | Ground clear controls. | 139 | 76.8 | 916.66
9596 | TIN-INTERP | Interpolated Ground | 61474.51 | 8.14 | 889.1 | 0 | 25.46 | 0 | OK | Ground clear controls. | 139 | 76.8 | 914.56
9597 | TIN-INTERP | Interpolated Ground | 61474.57 | 6.64 | 888.77 | 0 | 20.2 | 0 | OK | Ground clear controls. | 139 | 76.8 | 908.97
9598 | TIN-INTERP | Interpolated Ground | 61474.61 | 5.95 | 888.61 | 0 | 32.36 | 0 | OK | Ground clear controls. | 139 | 76.8 | 920.97
9599 | TIN-INTERP | Interpolated Ground | 61474.82 | -6.59 | 882.3 | 0 | 26.6 | 0 | OK | Ground clear controls. | 139 | 76.8 | 908.9
9600 | TIN-INTERP | Interpolated Ground | 61474.87 | -5.89 | 882.74 | 0 | 38.28 | 0 | OK | Ground clear controls. | 139 | 76.8 | 921.02
9601 | TIN-INTERP | Interpolated Ground | 61474.91 | -8.08 | 881.46 | 0 | 33.36 | 0 | OK | Ground clear controls. | 139 | 76.8 | 914.82
9602 | TIN-INTERP | Interpolated Ground | 61514.51 | 8.28 | 892.32 | 0 | 21.34 | 0 | OK | Ground clear controls. | 139 | 76.8 | 913.66
9603 | TIN-INTERP | Interpolated Ground | 61514.57 | 6.78 | 891.87 | 0 | 16.24 | 0 | OK | Ground clear controls. | 139 | 76.8 | 908.11
9604 | TIN-INTERP | Interpolated Ground | 61514.61 | 6.09 | 891.58 | 0 | 28.51 | 0 | OK | Ground clear controls. | 139 | 76.8 | 920.09
9605 | TIN-INTERP | Interpolated Ground | 61514.82 | -6.43 | 884.52 | 0 | 23.5 | 0 | OK | Ground clear controls. | 139 | 76.8 | 908.02
9606 | TIN-INTERP | Interpolated Ground | 61514.87 | -5.74 | 885.24 | 0 | 34.89 | 0 | OK | Ground clear controls. | 139 | 76.8 | 920.13
9607 | TIN-INTERP | Interpolated Ground | 61514.91 | -7.93 | 884.31 | 0 | 29.65 | 0 | OK | Ground clear controls. | 139 | 76.8 | 913.96
9608 | TIN-INTERP | Interpolated Ground | 61554.51 | 8.42 | 877.93 | 0 | 35.83 | 0 | OK | Ground clear controls. | 139 | 76.8 | 913.76
9609 | TIN-INTERP | Interpolated Ground | 61554.57 | 6.93 | 877.6 | 0 | 30.62 | 0 | OK | Ground clear controls. | 139 | 76.8 | 908.22
9610 | TIN-INTERP | Interpolated Ground | 61554.61 | 6.23 | 877.4 | 0 | 42.79 | 0 | OK | Ground clear controls. | 139 | 76.8 | 920.19
9611 | TIN-INTERP | Interpolated Ground | 61554.82 | -6.28 | 873.39 | 0 | 34.72 | 0 | OK | Ground clear controls. | 139 | 76.8 | 908.11
9612 | TIN-INTERP | Interpolated Ground | 61554.87 | -5.58 | 873.43 | 0 | 46.79 | 0 | OK | Ground clear controls. | 139 | 76.8 | 920.22
9613 | TIN-INTERP | Interpolated Ground | 61554.91 | -7.77 | 872.9 | 0 | 41.16 | 0 | OK | Ground clear controls. | 139 | 76.8 | 914.06
9614 | TIN-INTERP | Interpolated Ground | 61594.51 | 8.57 | 854.5 | 0 | 60.35 | 0 | OK | Ground clear controls. | 139 | 76.8 | 914.85
9615 | TIN-INTERP | Interpolated Ground | 61594.57 | 7.07 | 853.87 | 0 | 55.45 | 0 | OK | Ground clear controls. | 139 | 76.8 | 909.32
9616 | TIN-INTERP | Interpolated Ground | 61594.61 | 6.38 | 853.5 | 0 | 67.78 | 0 | OK | Ground clear controls. | 139 | 76.8 | 921.28
9617 | TIN-INTERP | Interpolated Ground | 61594.82 | -6.12 | 849.45 | 0 | 59.72 | 0 | OK | Ground clear controls. | 139 | 76.8 | 909.17
9618 | TIN-INTERP | Interpolated Ground | 61594.87 | -5.43 | 849.62 | 0 | 71.67 | 0 | OK | Ground clear controls. | 139 | 76.8 | 921.29
9619 | TIN-INTERP | Interpolated Ground | 61594.91 | -7.61 | 849.02 | 0 | 66.12 | 0 | OK | Ground clear controls. | 139 | 76.8 | 915.14
9620 | TIN-INTERP | Interpolated Ground | 61634.51 | 8.71 | 853.22 | 0 | 63.7 | 0 | OK | Ground clear controls. | 139 | 76.8 | 916.92
9621 | TIN-INTERP | Interpolated Ground | 61634.57 | 7.21 | 851.44 | 0 | 59.95 | 0 | OK | Ground clear controls. | 139 | 76.8 | 911.39
9622 | TIN-INTERP | Interpolated Ground | 61634.61 | 6.52 | 850.85 | 0 | 72.5 | 0 | OK | Ground clear controls. | 139 | 76.8 | 923.35
9623 | TIN-INTERP | Interpolated Ground | 61634.82 | -5.96 | 846.36 | 0 | 64.87 | 0 | OK | Ground clear controls. | 139 | 76.8 | 911.23
9624 | TIN-INTERP | Interpolated Ground | 61634.87 | -5.27 | 846.55 | 0 | 76.8 | 0 | OK | Ground clear controls. | 139 | 76.8 | 923.35
9625 | TIN-INTERP | Interpolated Ground | 61634.91 | -7.45 | 845.99 | 0 | 71.19 | 0 | OK | Ground clear controls. | 139 | 71.19 | 917.18
9626 | TIN-INTERP | Interpolated Ground | 61674.5 | 8.85 | 870.66 | 0 | 49.35 | 0 | OK | Ground clear controls. | 139 | 58.88 | 920.01
9627 | TIN-INTERP | Interpolated Ground | 61674.57 | 7.36 | 870.4 | 0 | 44.05 | 0 | OK | Ground clear controls. | 139 | 58.88 | 914.45
9628 | TIN-INTERP | Interpolated Ground | 61674.61 | 6.66 | 870.16 | 0 | 56.26 | 0 | OK | Ground clear controls. | 139 | 58.88 | 926.42
9629 | TIN-INTERP | Interpolated Ground | 61674.82 | -5.81 | 867.32 | 0 | 46.93 | 0 | OK | Ground clear controls. | 139 | 58.88 | 914.25
9630 | TIN-INTERP | Interpolated Ground | 61674.87 | -5.12 | 867.49 | 0 | 58.88 | 0 | OK | Ground clear controls. | 139 | 58.88 | 926.37
9631 | TIN-INTERP | Interpolated Ground | 61674.91 | -7.3 | 866.41 | 0 | 53.78 | 0 | OK | Ground clear controls. | 139 | 56.63 | 920.19
9632 | TIN-INTERP | Interpolated Ground | 61714.5 | 8.99 | 879.96 | 0 | 44.11 | 0 | OK | Ground clear controls. | 139 | 56.63 | 924.07
9633 | TIN-INTERP | Interpolated Ground | 61714.57 | 7.5 | 879.29 | 0 | 39.19 | 0 | OK | Ground clear controls. | 139 | 56.63 | 918.48
9634 | TIN-INTERP | Interpolated Ground | 61714.61 | 6.81 | 879.15 | 0 | 51.32 | 0 | OK | Ground clear controls. | 139 | 56.63 | 930.47
9635 | TIN-INTERP | Interpolated Ground | 61714.82 | -5.65 | 873.71 | 0 | 44.55 | 0 | OK | Ground clear controls. | 139 | 56.63 | 918.26
9636 | TIN-INTERP | Interpolated Ground | 61714.87 | -4.96 | 873.76 | 0 | 56.63 | 0 | OK | Ground clear controls. | 139 | 56.63 | 930.39
9637 | TIN-INTERP | Interpolated Ground | 61714.91 | -7.14 | 873.58 | 0 | 50.6 | 0 | OK | Ground clear controls. | 139 | 55.96 | 924.18
9638 | TIN-INTERP | Interpolated Ground | 61754.5 | 9.13 | 885.86 | 0 | 43.3 | 0 | OK | Ground clear controls. | 139 | 55.96 | 929.16
9639 | TIN-INTERP | Interpolated Ground | 61754.57 | 7.64 | 885.3 | 0 | 38.21 | 0 | OK | Ground clear controls. | 139 | 55.96 | 923.51
9640 | TIN-INTERP | Interpolated Ground | 61754.61 | 6.95 | 885.03 | 0 | 50.48 | 0 | OK | Ground clear controls. | 139 | 55.96 | 935.51
9641 | TIN-INTERP | Interpolated Ground | 61754.82 | -5.5 | 879 | 0 | 44.26 | 0 | OK | Ground clear controls. | 139 | 55.96 | 923.26
9642 | TIN-INTERP | Interpolated Ground | 61754.87 | -4.81 | 879.42 | 0 | 55.96 | 0 | OK | Ground clear controls. | 139 | 55.96 | 935.38
9643 | TIN-INTERP | Interpolated Ground | 61754.91 | -6.98 | 878.4 | 0 | 50.75 | 0 | OK | Ground clear controls. | 139 | 50.75 | 929.15
9644 | TIN-INTERP | Interpolated Ground | 61794.5 | 9.27 | 895.06 | 0 | 40.17 | 0 | OK | Ground clear controls. | 139 | 47.39 | 935.23
9645 | TIN-INTERP | Interpolated Ground | 61794.57 | 7.78 | 895.36 | 0 | 34.16 | 0 | OK | Ground clear controls. | 139 | 47.39 | 929.52
9646 | TIN-INTERP | Interpolated Ground | 61794.61 | 7.09 | 895.5 | 0 | 46.05 | 0 | OK | Ground clear controls. | 139 | 47.39 | 941.55
9647 | TIN-INTERP | Interpolated Ground | 61794.82 | -5.34 | 894.04 | 0 | 35.2 | 0 | OK | Ground clear controls. | 139 | 47.39 | 929.24
9648 | TIN-INTERP | Interpolated Ground | 61794.87 | -4.66 | 893.98 | 0 | 47.39 | 0 | OK | Ground clear controls. | 139 | 47.39 | 941.37
9649 | TIN-INTERP | Interpolated Ground | 61794.91 | -6.83 | 894.09 | 0 | 41 | 0 | OK | Ground clear controls. | 139 | 44.28 | 935.09
9650 | TIN-INTERP | Interpolated Ground | 61834.5 | 9.42 | 904.4 | 0 | 37.92 | 0 | OK | Ground clear controls. | 139 | 44.28 | 942.32
9651 | TIN-INTERP | Interpolated Ground | 61834.57 | 7.93 | 904.47 | 0 | 32.06 | 0 | OK | Ground clear controls. | 139 | 44.28 | 936.53
9652 | TIN-INTERP | Interpolated Ground | 61834.61 | 7.24 | 904.44 | 0 | 44.15 | 0 | OK | Ground clear controls. | 139 | 44.28 | 948.59
9653 | TIN-INTERP | Interpolated Ground | 61834.82 | -5.18 | 904.24 | 0 | 31.97 | 0 | OK | Ground clear controls. | 139 | 44.28 | 936.21
9654 | TIN-INTERP | Interpolated Ground | 61834.87 | -4.5 | 904.06 | 0 | 44.28 | 0 | OK | Ground clear controls. | 139 | 44.28 | 948.34
9655 | TIN-INTERP | Interpolated Ground | 61834.91 | -6.67 | 904.46 | 0 | 37.54 | 0 | OK | Ground clear controls. | 139 | 37.54 | 942
9656 | TIN-INTERP | Interpolated Ground | 61835.74 | 9.42 | 904.32 | 0 | 38.23 | 0 | OK | Ground clear controls. | 140 | 46.04 | 942.55
9657 | TIN-INTERP | Interpolated Ground | 61835.89 | 7.93 | 904.37 | 0 | 32.4 | 0 | OK | Ground clear controls. | 140 | 46.04 | 936.77
9658 | TIN-INTERP | Interpolated Ground | 61836.04 | 7.24 | 904.34 | 0 | 44.52 | 0 | OK | Ground clear controls. | 140 | 46.04 | 948.86
9659 | TIN-INTERP | Interpolated Ground | 61837.4 | -6.69 | 903.94 | 0 | 38.65 | 0 | OK | Ground clear controls. | 140 | 46.04 | 942.59
9660 | TIN-INTERP | Interpolated Ground | 61837.4 | -5.19 | 904 | 0 | 32.79 | 0 | OK | Ground clear controls. | 140 | 46.04 | 936.79
9661 | TIN-INTERP | Interpolated Ground | 61837.4 | -4.5 | 903.99 | 0 | 44.89 | 0 | OK | Ground clear controls. | 140 | 46.04 | 948.88
9662 | TIN-INTERP | Interpolated Ground | 61875.98 | -6.48 | 892.63 | 0 | 35.97 | 0 | OK | Ground clear controls. | 140 | 46.04 | 928.6
9663 | TIN-INTERP | Interpolated Ground | 61876.25 | -5 | 893.11 | 0 | 29.7 | 0 | OK | Ground clear controls. | 140 | 46.04 | 922.81
9664 | TIN-INTERP | Interpolated Ground | 61876.35 | -4.34 | 893.18 | 0 | 41.55 | 0 | OK | Ground clear controls. | 140 | 46.04 | 934.73
9665 | TIN-INTERP | Interpolated Ground | 61878.34 | 6.83 | 893.89 | 0 | 40.72 | 0 | OK | Ground clear controls. | 140 | 46.04 | 934.61
9666 | TIN-INTERP | Interpolated Ground | 61878.41 | 7.51 | 893.59 | 0 | 29.08 | 0 | OK | Ground clear controls. | 140 | 46.04 | 922.67
9667 | TIN-INTERP | Interpolated Ground | 61878.72 | 8.98 | 892.92 | 0 | 35.48 | 0 | OK | Ground clear controls. | 140 | 46.04 | 928.4
9668 | TIN-INTERP | Interpolated Ground | 61915.98 | -6.43 | 878.45 | 0 | 37.25 | 0 | OK | Ground clear controls. | 140 | 46.04 | 915.7
9669 | TIN-INTERP | Interpolated Ground | 61916.25 | -4.94 | 879.12 | 0 | 30.81 | 0 | OK | Ground clear controls. | 140 | 46.04 | 909.93
9670 | TIN-INTERP | Interpolated Ground | 61916.35 | -4.3 | 879.21 | 0 | 42.47 | 0 | OK | Ground clear controls. | 140 | 46.04 | 921.68
9671 | TIN-INTERP | Interpolated Ground | 61918.34 | 6.36 | 879.81 | 0 | 41.68 | 0 | OK | Ground clear controls. | 140 | 46.04 | 921.49
9672 | TIN-INTERP | Interpolated Ground | 61918.41 | 7.01 | 879.97 | 0 | 29.71 | 0 | OK | Ground clear controls. | 140 | 46.04 | 909.68
9673 | TIN-INTERP | Interpolated Ground | 61918.72 | 8.49 | 880.29 | 0 | 35.08 | 0 | OK | Ground clear controls. | 140 | 46.04 | 915.37
9674 | TIN-INTERP | Interpolated Ground | 61955.98 | -6.37 | 862.5 | 0 | 41.39 | 0 | OK | Ground clear controls. | 140 | 46.04 | 903.89
9675 | TIN-INTERP | Interpolated Ground | 61956.25 | -4.88 | 863.39 | 0 | 34.75 | 0 | OK | Ground clear controls. | 140 | 46.04 | 898.14
9676 | TIN-INTERP | Interpolated Ground | 61956.35 | -4.26 | 863.68 | 0 | 46.04 | 0 | OK | Ground clear controls. | 140 | 46.04 | 909.72
9677 | TIN-INTERP | Interpolated Ground | 61958.34 | 5.88 | 868.24 | 0 | 41.24 | 0 | OK | Ground clear controls. | 140 | 44.52 | 909.48
9678 | TIN-INTERP | Interpolated Ground | 61958.4 | 6.52 | 868.63 | 0 | 29.2 | 0 | OK | Ground clear controls. | 140 | 44.52 | 897.83
9679 | TIN-INTERP | Interpolated Ground | 61958.71 | 8 | 869.45 | 0 | 34.01 | 0 | OK | Ground clear controls. | 140 | 44.52 | 903.46
9680 | TIN-INTERP | Interpolated Ground | 61995.98 | -6.32 | 853.48 | 0 | 39.66 | 0 | OK | Ground clear controls. | 140 | 44.52 | 893.14
9681 | TIN-INTERP | Interpolated Ground | 61996.25 | -4.82 | 854.1 | 0 | 33.33 | 0 | OK | Ground clear controls. | 140 | 44.52 | 887.43
9682 | TIN-INTERP | Interpolated Ground | 61996.35 | -4.23 | 854.34 | 0 | 44.52 | 0 | OK | Ground clear controls. | 140 | 44.52 | 898.86
9683 | TIN-INTERP | Interpolated Ground | 61998.33 | 5.41 | 858.74 | 0 | 39.82 | 0 | OK | Ground clear controls. | 140 | 42.32 | 898.56
9684 | TIN-INTERP | Interpolated Ground | 61998.4 | 6.02 | 859.1 | 0 | 27.97 | 0 | OK | Ground clear controls. | 140 | 42.32 | 887.07
9685 | TIN-INTERP | Interpolated Ground | 61998.71 | 7.5 | 859.94 | 0 | 32.71 | 0 | OK | Ground clear controls. | 140 | 42.32 | 892.65
9686 | TIN-INTERP | Interpolated Ground | 62035.98 | -6.26 | 845.24 | 0 | 38.22 | 0 | OK | Ground clear controls. | 140 | 42.32 | 883.46
9687 | TIN-INTERP | Interpolated Ground | 62036.25 | -4.76 | 846.19 | 0 | 31.6 | 0 | OK | Ground clear controls. | 140 | 42.32 | 877.79
9688 | TIN-INTERP | Interpolated Ground | 62036.35 | -4.19 | 846.75 | 0 | 42.32 | 0 | OK | Ground clear controls. | 140 | 42.32 | 889.07
9689 | TIN-INTERP | Interpolated Ground | 62038.33 | 4.93 | 852.48 | 0 | 36.26 | 0 | OK | Ground clear controls. | 140 | 36.36 | 888.74
9690 | TIN-INTERP | Interpolated Ground | 62038.4 | 5.52 | 852.56 | 0 | 24.85 | 0 | OK | Ground clear controls. | 140 | 36.36 | 877.41
9691 | TIN-INTERP | Interpolated Ground | 62038.71 | 7.01 | 852.71 | 0 | 30.24 | 0 | OK | Ground clear controls. | 140 | 36.36 | 882.95
9692 | TIN-INTERP | Interpolated Ground | 62075.98 | -6.21 | 843.16 | 0 | 31.67 | 0 | OK | Ground clear controls. | 140 | 36.36 | 874.83
9693 | TIN-INTERP | Interpolated Ground | 62076.25 | -4.7 | 843.77 | 0 | 25.46 | 0 | OK | Ground clear controls. | 140 | 36.36 | 869.23
9694 | TIN-INTERP | Interpolated Ground | 62076.35 | -4.15 | 843.99 | 0 | 36.36 | 0 | OK | Ground clear controls. | 140 | 36.36 | 880.35
9695 | TIN-INTERP | Interpolated Ground | 62078.33 | 4.46 | 846.33 | 0 | 33.68 | 0 | OK | Ground clear controls. | 140 | 33.68 | 880.01
9696 | TIN-INTERP | Interpolated Ground | 62078.39 | 5.03 | 846.51 | 0 | 22.33 | 0 | OK | Ground clear controls. | 140 | 26.73 | 868.84
9697 | TIN-INTERP | Interpolated Ground | 62078.71 | 6.52 | 847.61 | 0 | 26.73 | 0 | OK | Ground clear controls. | 140 | 26.73 | 874.34
9698 | TIN-INTERP | Interpolated Ground | 62106.7 | -4.16 | 847 | 0 | 27.58 | 0 | OK | Ground clear controls. | 141 | 133.23 | 874.58
9699 | TIN-INTERP | Interpolated Ground | 62106.73 | 4.14 | 847.6 | 0 | 26.98 | 0 | OK | Ground clear controls. | 141 | 133.23 | 874.58
9700 | TIN-INTERP | Interpolated Ground | 62106.88 | -6.21 | 846.48 | 0 | 22.61 | 0 | OK | Ground clear controls. | 141 | 133.23 | 869.09
9701 | TIN-INTERP | Interpolated Ground | 62106.9 | 6.19 | 848.07 | 0 | 21.03 | 0 | OK | Ground clear controls. | 141 | 133.23 | 869.1
9702 | TIN-INTERP | Interpolated Ground | 62106.94 | 4.69 | 847.68 | 0 | 15.91 | 0 | OK | Ground clear controls. | 141 | 133.23 | 863.59
9703 | TIN-INTERP | Interpolated Ground | 62106.99 | -4.71 | 846.91 | 0 | 16.68 | 0 | OK | Ground clear controls. | 141 | 133.23 | 863.59
9704 | TIN-INTERP | Interpolated Ground | 62146.7 | -4.18 | 819.35 | 0 | 44.23 | 0 | OK | Ground clear controls. | 141 | 133.23 | 863.58
9705 | TIN-INTERP | Interpolated Ground | 62146.73 | 4.17 | 820.52 | 0 | 42.98 | 0 | OK | Ground clear controls. | 141 | 133.23 | 863.5
9706 | TIN-INTERP | Interpolated Ground | 62146.88 | -6.23 | 818.66 | 0 | 39.57 | 0 | OK | Ground clear controls. | 141 | 133.23 | 858.23
9707 | TIN-INTERP | Interpolated Ground | 62146.9 | 6.21 | 820.36 | 0 | 37.78 | 0 | OK | Ground clear controls. | 141 | 133.23 | 858.14
9708 | TIN-INTERP | Interpolated Ground | 62146.94 | 4.71 | 820.37 | 0 | 32.28 | 0 | OK | Ground clear controls. | 141 | 133.23 | 852.65
9709 | TIN-INTERP | Interpolated Ground | 62146.99 | -4.73 | 819.07 | 0 | 33.58 | 0 | OK | Ground clear controls. | 141 | 133.23 | 852.65
9710 | TIN-INTERP | Interpolated Ground | 62186.7 | -4.21 | 792.94 | 0 | 60.64 | 0 | OK | Ground clear controls. | 141 | 133.23 | 853.58
9711 | TIN-INTERP | Interpolated Ground | 62186.73 | 4.19 | 794.48 | 0 | 58.97 | 0 | OK | Ground clear controls. | 141 | 133.23 | 853.45
9712 | TIN-INTERP | Interpolated Ground | 62186.88 | -6.25 | 792.52 | 0 | 55.86 | 0 | OK | Ground clear controls. | 141 | 133.23 | 848.38
9713 | TIN-INTERP | Interpolated Ground | 62186.9 | 6.24 | 795.14 | 0 | 53.05 | 0 | OK | Ground clear controls. | 141 | 133.23 | 848.19
9714 | TIN-INTERP | Interpolated Ground | 62186.94 | 4.74 | 794.55 | 0 | 48.17 | 0 | OK | Ground clear controls. | 141 | 133.23 | 842.72
9715 | TIN-INTERP | Interpolated Ground | 62186.99 | -4.75 | 792.64 | 0 | 50.08 | 0 | OK | Ground clear controls. | 141 | 133.23 | 842.72
9716 | TIN-INTERP | Interpolated Ground | 62226.7 | -4.23 | 788.42 | 0 | 56.19 | 0 | OK | Ground clear controls. | 141 | 133.23 | 844.61
9717 | TIN-INTERP | Interpolated Ground | 62226.73 | 4.22 | 794.13 | 0 | 50.3 | 0 | OK | Ground clear controls. | 141 | 133.23 | 844.43
9718 | TIN-INTERP | Interpolated Ground | 62226.88 | -6.27 | 786.85 | 0 | 52.67 | 0 | OK | Ground clear controls. | 141 | 133.23 | 839.52
9719 | TIN-INTERP | Interpolated Ground | 62226.9 | 6.26 | 795.38 | 0 | 43.89 | 0 | OK | Ground clear controls. | 141 | 133.23 | 839.27
9720 | TIN-INTERP | Interpolated Ground | 62226.94 | 4.76 | 794.49 | 0 | 39.31 | 0 | OK | Ground clear controls. | 141 | 133.23 | 833.8
9721 | TIN-INTERP | Interpolated Ground | 62226.99 | -4.77 | 787.99 | 0 | 45.82 | 0 | OK | Ground clear controls. | 141 | 133.23 | 833.81
9722 | TIN-INTERP | Interpolated Ground | 62266.7 | -4.25 | 789.74 | 0 | 46.93 | 0 | OK | Ground clear controls. | 141 | 133.23 | 836.67
9723 | TIN-INTERP | Interpolated Ground | 62266.73 | 4.25 | 795.04 | 0 | 41.4 | 0 | OK | Ground clear controls. | 141 | 133.23 | 836.44
9724 | TIN-INTERP | Interpolated Ground | 62266.88 | -6.29 | 789.13 | 0 | 42.55 | 0 | OK | Ground clear controls. | 141 | 133.23 | 831.68
9725 | TIN-INTERP | Interpolated Ground | 62266.9 | 6.28 | 796.32 | 0 | 35.04 | 0 | OK | Ground clear controls. | 141 | 133.23 | 831.36
9726 | TIN-INTERP | Interpolated Ground | 62266.94 | 4.78 | 795.45 | 0 | 30.46 | 0 | OK | Ground clear controls. | 141 | 133.23 | 825.91
9727 | TIN-INTERP | Interpolated Ground | 62266.99 | -4.79 | 789.7 | 0 | 36.21 | 0 | OK | Ground clear controls. | 141 | 133.23 | 825.91
9728 | TIN-INTERP | Interpolated Ground | 62306.7 | -4.27 | 788.07 | 0 | 41.68 | 0 | OK | Ground clear controls. | 141 | 133.23 | 829.75
9729 | TIN-INTERP | Interpolated Ground | 62306.73 | 4.27 | 787.67 | 0 | 41.81 | 0 | OK | Ground clear controls. | 141 | 133.23 | 829.48
9730 | TIN-INTERP | Interpolated Ground | 62306.88 | -6.31 | 787.47 | 0 | 37.36 | 0 | OK | Ground clear controls. | 141 | 133.23 | 824.83
9731 | TIN-INTERP | Interpolated Ground | 62306.9 | 6.31 | 787.34 | 0 | 37.13 | 0 | OK | Ground clear controls. | 141 | 133.23 | 824.47
9732 | TIN-INTERP | Interpolated Ground | 62306.94 | 4.81 | 787.47 | 0 | 31.55 | 0 | OK | Ground clear controls. | 141 | 133.23 | 819.02
9733 | TIN-INTERP | Interpolated Ground | 62306.99 | -4.81 | 787.81 | 0 | 31.21 | 0 | OK | Ground clear controls. | 141 | 133.23 | 819.02
9734 | TIN-INTERP | Interpolated Ground | 62346.7 | -4.3 | 761.79 | 0 | 62.04 | 0 | OK | Ground clear controls. | 141 | 133.23 | 823.83
9735 | TIN-INTERP | Interpolated Ground | 62346.73 | 4.3 | 760.65 | 0 | 62.89 | 0 | OK | Ground clear controls. | 141 | 133.23 | 823.54
9736 | TIN-INTERP | Interpolated Ground | 62346.88 | -6.33 | 762.39 | 0 | 56.6 | 0 | OK | Ground clear controls. | 141 | 133.23 | 818.99
9737 | TIN-INTERP | Interpolated Ground | 62346.9 | 6.33 | 760.96 | 0 | 57.62 | 0 | OK | Ground clear controls. | 141 | 133.23 | 818.58
9738 | TIN-INTERP | Interpolated Ground | 62346.94 | 4.83 | 760.6 | 0 | 52.54 | 0 | OK | Ground clear controls. | 141 | 133.23 | 813.14
9739 | TIN-INTERP | Interpolated Ground | 62346.99 | -4.83 | 761.76 | 0 | 51.38 | 0 | OK | Ground clear controls. | 141 | 133.23 | 813.14
9740 | TIN-INTERP | Interpolated Ground | 62386.7 | -4.32 | 746.83 | 0 | 72.1 | 0 | OK | Ground clear controls. | 141 | 133.23 | 818.93
9741 | TIN-INTERP | Interpolated Ground | 62386.73 | 4.32 | 752.47 | 0 | 66.14 | 0 | OK | Ground clear controls. | 141 | 133.23 | 818.61
9742 | TIN-INTERP | Interpolated Ground | 62386.88 | -6.35 | 745.52 | 0 | 68.6 | 0 | OK | Ground clear controls. | 141 | 133.23 | 814.12
9743 | TIN-INTERP | Interpolated Ground | 62386.9 | 6.35 | 754.06 | 0 | 59.64 | 0 | OK | Ground clear controls. | 141 | 133.23 | 813.7
9744 | TIN-INTERP | Interpolated Ground | 62386.94 | 4.85 | 752.86 | 0 | 55.39 | 0 | OK | Ground clear controls. | 141 | 133.23 | 808.25
9745 | TIN-INTERP | Interpolated Ground | 62386.99 | -4.85 | 746.42 | 0 | 61.84 | 0 | OK | Ground clear controls. | 141 | 133.23 | 808.26
9746 | TIN-INTERP | Interpolated Ground | 62426.7 | -4.34 | 735.92 | 0 | 79.1 | 0 | OK | Ground clear controls. | 141 | 133.23 | 815.02
9747 | TIN-INTERP | Interpolated Ground | 62426.73 | 4.35 | 743.78 | 0 | 70.91 | 0 | OK | Ground clear controls. | 141 | 133.23 | 814.69
9748 | TIN-INTERP | Interpolated Ground | 62426.88 | -6.37 | 734.12 | 0 | 76.12 | 0 | OK | Ground clear controls. | 141 | 133.23 | 810.24
9749 | TIN-INTERP | Interpolated Ground | 62426.9 | 6.38 | 745.42 | 0 | 64.39 | 0 | OK | Ground clear controls. | 141 | 133.23 | 809.81
9750 | TIN-INTERP | Interpolated Ground | 62426.94 | 4.88 | 744.25 | 0 | 60.11 | 0 | OK | Ground clear controls. | 141 | 133.23 | 804.36
9751 | TIN-INTERP | Interpolated Ground | 62426.99 | -4.87 | 735.07 | 0 | 69.3 | 0 | OK | Ground clear controls. | 141 | 133.23 | 804.37
9752 | TIN-INTERP | Interpolated Ground | 62466.7 | -4.37 | 717.7 | 0 | 94.43 | 0 | OK | Ground clear controls. | 141 | 133.23 | 812.13
9753 | TIN-INTERP | Interpolated Ground | 62466.73 | 4.38 | 723.16 | 0 | 88.63 | 0 | OK | Ground clear controls. | 141 | 133.23 | 811.79
9754 | TIN-INTERP | Interpolated Ground | 62466.88 | -6.39 | 716.37 | 0 | 90.99 | 0 | OK | Ground clear controls. | 141 | 133.23 | 807.36
9755 | TIN-INTERP | Interpolated Ground | 62466.9 | 6.4 | 724.72 | 0 | 82.2 | 0 | OK | Ground clear controls. | 141 | 133.23 | 806.92
9756 | TIN-INTERP | Interpolated Ground | 62466.94 | 4.9 | 723.46 | 0 | 78.02 | 0 | OK | Ground clear controls. | 141 | 133.23 | 801.48
9757 | TIN-INTERP | Interpolated Ground | 62466.99 | -4.89 | 717.33 | 0 | 84.15 | 0 | OK | Ground clear controls. | 141 | 133.23 | 801.48
9758 | TIN-INTERP | Interpolated Ground | 62506.7 | -4.39 | 690.94 | 0 | 119.29 | 0 | OK | Ground clear controls. | 141 | 133.23 | 810.23
9759 | TIN-INTERP | Interpolated Ground | 62506.73 | 4.4 | 696.74 | 0 | 113.17 | 0 | OK | Ground clear controls. | 141 | 133.23 | 809.91
9760 | TIN-INTERP | Interpolated Ground | 62506.88 | -6.41 | 688.61 | 0 | 116.85 | 0 | OK | Ground clear controls. | 141 | 133.23 | 805.46
9761 | TIN-INTERP | Interpolated Ground | 62506.9 | 6.42 | 697.04 | 0 | 107.98 | 0 | OK | Ground clear controls. | 141 | 133.23 | 805.02
9762 | TIN-INTERP | Interpolated Ground | 62506.94 | 4.92 | 696.71 | 0 | 102.87 | 0 | OK | Ground clear controls. | 141 | 133.23 | 799.58
9763 | TIN-INTERP | Interpolated Ground | 62506.99 | -4.91 | 689.85 | 0 | 109.74 | 0 | OK | Ground clear controls. | 141 | 133.23 | 799.59
9764 | TIN-INTERP | Interpolated Ground | 62546.7 | -4.41 | 676.12 | 0 | 133.23 | 0 | OK | Ground clear controls. | 141 | 133.23 | 809.35
9765 | TIN-INTERP | Interpolated Ground | 62546.73 | 4.43 | 678.09 | 0 | 130.93 | 0 | OK | Ground clear controls. | 141 | 130.93 | 809.02
9766 | TIN-INTERP | Interpolated Ground | 62546.88 | -6.43 | 676.55 | 0 | 127.99 | 0 | OK | Ground clear controls. | 141 | 127.99 | 804.54
9767 | TIN-INTERP | Interpolated Ground | 62546.9 | 6.45 | 678.39 | 0 | 125.74 | 0 | OK | Ground clear controls. | 141 | 125.74 | 804.13
9768 | TIN-INTERP | Interpolated Ground | 62546.94 | 4.95 | 678.31 | 0 | 120.37 | 0 | OK | Ground clear controls. | 141 | 122.44 | 798.68
9769 | TIN-INTERP | Interpolated Ground | 62546.99 | -4.93 | 676.25 | 0 | 122.44 | 0 | OK | Ground clear controls. | 141 | 122.44 | 798.69
9770 | TIN-INTERP | Interpolated Ground | 62586.7 | -4.43 | 694.33 | 0 | 115.11 | 0 | OK | Ground clear controls. | 141 | 115.11 | 809.44
9771 | TIN-INTERP | Interpolated Ground | 62586.73 | 4.45 | 694.78 | 0 | 114.36 | 0 | OK | Ground clear controls. | 141 | 114.36 | 809.14
9772 | TIN-INTERP | Interpolated Ground | 62586.88 | -6.45 | 695.32 | 0 | 109.29 | 0 | OK | Ground clear controls. | 141 | 109.29 | 804.61
9773 | TIN-INTERP | Interpolated Ground | 62586.9 | 6.47 | 695.58 | 0 | 108.63 | 0 | OK | Ground clear controls. | 141 | 108.63 | 804.21
9774 | TIN-INTERP | Interpolated Ground | 62586.94 | 4.97 | 694.99 | 0 | 103.78 | 0 | OK | Ground clear controls. | 141 | 104.07 | 798.77
9775 | TIN-INTERP | Interpolated Ground | 62586.99 | -4.95 | 694.71 | 0 | 104.07 | 0 | OK | Ground clear controls. | 141 | 104.07 | 798.78
9776 | TIN-INTERP | Interpolated Ground | 62626.7 | -4.46 | 718.74 | 0 | 91.8 | 0 | OK | Ground clear controls. | 141 | 96.81 | 810.54
9777 | TIN-INTERP | Interpolated Ground | 62626.73 | 4.48 | 713.46 | 0 | 96.81 | 0 | OK | Ground clear controls. | 141 | 96.81 | 810.27
9778 | TIN-INTERP | Interpolated Ground | 62626.88 | -6.47 | 719.17 | 0 | 86.49 | 0 | OK | Ground clear controls. | 141 | 92.68 | 805.66
9779 | TIN-INTERP | Interpolated Ground | 62626.9 | 6.49 | 712.62 | 0 | 92.68 | 0 | OK | Ground clear controls. | 141 | 92.68 | 805.3
9780 | TIN-INTERP | Interpolated Ground | 62626.94 | 4.99 | 713.31 | 0 | 86.53 | 0 | OK | Ground clear controls. | 141 | 86.53 | 799.84
9781 | TIN-INTERP | Interpolated Ground | 62626.99 | -4.97 | 718.78 | 0 | 81.07 | 0 | OK | Ground clear controls. | 141 | 81.07 | 799.85
9782 | TIN-INTERP | Interpolated Ground | 62666.7 | -4.48 | 742.86 | 0 | 69.78 | 0 | OK | Ground clear controls. | 141 | 71.27 | 812.64
9783 | TIN-INTERP | Interpolated Ground | 62666.73 | 4.51 | 741.13 | 0 | 71.27 | 0 | OK | Ground clear controls. | 141 | 71.27 | 812.4
9784 | TIN-INTERP | Interpolated Ground | 62666.88 | -6.49 | 743.39 | 0 | 64.3 | 0 | OK | Ground clear controls. | 141 | 66.78 | 807.69
9785 | TIN-INTERP | Interpolated Ground | 62666.9 | 6.52 | 740.59 | 0 | 66.78 | 0 | OK | Ground clear controls. | 141 | 66.78 | 807.37
9786 | TIN-INTERP | Interpolated Ground | 62666.94 | 5.02 | 741.05 | 0 | 60.87 | 0 | OK | Ground clear controls. | 141 | 60.87 | 801.92
9787 | TIN-INTERP | Interpolated Ground | 62666.99 | -4.99 | 743.13 | 0 | 58.79 | 0 | OK | Ground clear controls. | 141 | 58.79 | 801.92
9788 | TIN-INTERP | Interpolated Ground | 62706.7 | -4.5 | 765.58 | 0 | 50.17 | 0 | OK | Ground clear controls. | 141 | 50.27 | 815.75
9789 | TIN-INTERP | Interpolated Ground | 62706.73 | 4.53 | 765.29 | 0 | 50.27 | 0 | OK | Ground clear controls. | 141 | 50.27 | 815.56
9790 | TIN-INTERP | Interpolated Ground | 62706.88 | -6.51 | 765.48 | 0 | 45.22 | 0 | OK | Ground clear controls. | 141 | 45.22 | 810.7
9791 | TIN-INTERP | Interpolated Ground | 62706.9 | 6.54 | 765.38 | 0 | 45.07 | 0 | OK | Ground clear controls. | 141 | 45.07 | 810.45
9792 | TIN-INTERP | Interpolated Ground | 62706.94 | 5.04 | 765.36 | 0 | 39.63 | 0 | OK | Ground clear controls. | 141 | 39.63 | 804.99
9793 | TIN-INTERP | Interpolated Ground | 62706.99 | -5.01 | 765.73 | 0 | 39.26 | 0 | OK | Ground clear controls. | 141 | 39.26 | 804.99
9794 | TIN-INTERP | Interpolated Ground | 62746.7 | -4.52 | 786.46 | 0 | 33.4 | 0 | OK | Ground clear controls. | 141 | 36.66 | 819.86
9795 | TIN-INTERP | Interpolated Ground | 62746.73 | 4.56 | 783.06 | 0 | 36.66 | 0 | OK | Ground clear controls. | 141 | 36.66 | 819.72
9796 | TIN-INTERP | Interpolated Ground | 62746.88 | -6.53 | 786.31 | 0 | 28.4 | 0 | OK | Ground clear controls. | 141 | 32.24 | 814.71
9797 | TIN-INTERP | Interpolated Ground | 62746.9 | 6.56 | 782.28 | 0 | 32.24 | 0 | OK | Ground clear controls. | 141 | 32.24 | 814.52
9798 | TIN-INTERP | Interpolated Ground | 62746.94 | 5.06 | 782.87 | 0 | 26.19 | 0 | OK | Ground clear controls. | 141 | 28.92 | 809.06
9799 | TIN-INTERP | Interpolated Ground | 62746.99 | -5.03 | 786.5 | 0 | 22.56 | 0 | OK | Ground clear controls. | 141 | 28.92 | 809.06
9800 | TIN-INTERP | Interpolated Ground | 62786.7 | -4.55 | 796.05 | 0 | 28.92 | 0 | OK | Ground clear controls. | 141 | 28.92 | 824.97
9801 | TIN-INTERP | Interpolated Ground | 62786.73 | 4.58 | 797.34 | 0 | 27.55 | 0 | OK | Ground clear controls. | 141 | 27.55 | 824.89
9802 | TIN-INTERP | Interpolated Ground | 62786.88 | -6.55 | 794.72 | 0 | 24.98 | 0 | OK | Ground clear controls. | 141 | 24.98 | 819.7
9803 | TIN-INTERP | Interpolated Ground | 62786.9 | 6.59 | 797.31 | 0 | 22.28 | 0 | OK | Ground clear controls. | 141 | 23.51 | 819.59
9804 | TIN-INTERP | Interpolated Ground | 62786.94 | 5.09 | 797.34 | 0 | 16.78 | 0 | OK | Ground clear controls. | 141 | 23.51 | 814.12
9805 | TIN-INTERP | Interpolated Ground | 62786.99 | -5.05 | 795.72 | 0 | 18.41 | 0 | OK | Ground clear controls. | 141 | 23.51 | 814.13
9806 | TIN-INTERP | Interpolated Ground | 62826.7 | -4.57 | 807.59 | 0 | 23.51 | 0 | OK | Ground clear controls. | 141 | 23.51 | 831.1
9807 | TIN-INTERP | Interpolated Ground | 62826.73 | 4.61 | 807.67 | 0 | 23.41 | 0 | OK | Ground clear controls. | 141 | 23.41 | 831.08
9808 | TIN-INTERP | Interpolated Ground | 62826.88 | -6.57 | 807.29 | 0 | 18.39 | 0 | OK | Ground clear controls. | 141 | 18.39 | 825.68
9809 | TIN-INTERP | Interpolated Ground | 62826.9 | 6.61 | 807.76 | 0 | 17.9 | 0 | OK | Ground clear controls. | 141 | 17.9 | 825.66
9810 | TIN-INTERP | Interpolated Ground | 62826.94 | 5.11 | 807.74 | 0 | 12.44 | 0 | OK | Ground clear controls. | 141 | 12.62 | 820.18
9811 | TIN-INTERP | Interpolated Ground | 62826.99 | -5.07 | 807.56 | 0 | 12.62 | 0 | OK | Ground clear controls. | 141 | 12.62 | 820.18
9812 | TIN-INTERP | Interpolated Ground | 62840.31 | -5.08 | 807.72 | 0 | 14.69 | 0 | OK | Ground clear controls. | 142 | 49.12 | 822.41
9813 | TIN-INTERP | Interpolated Ground | 62840.33 | 5.12 | 807.67 | 0 | 14.75 | 0 | OK | Ground clear controls. | 142 | 49.12 | 822.42
9814 | TIN-INTERP | Interpolated Ground | 62840.36 | -6.58 | 807.6 | 0 | 20.32 | 0 | OK | Ground clear controls. | 142 | 49.12 | 827.92
9815 | TIN-INTERP | Interpolated Ground | 62840.39 | 6.62 | 807.48 | 0 | 20.44 | 0 | OK | Ground clear controls. | 142 | 49.12 | 827.92
9816 | TIN-INTERP | Interpolated Ground | 62840.4 | 4.62 | 807.73 | 0 | 25.69 | 0 | OK | Ground clear controls. | 142 | 49.12 | 833.42
9817 | TIN-INTERP | Interpolated Ground | 62840.42 | -4.58 | 807.75 | 0 | 25.68 | 0 | OK | Ground clear controls. | 142 | 49.12 | 833.43
9818 | TIN-INTERP | Interpolated Ground | 62880.31 | -5.1 | 796.87 | 0 | 15.78 | 0 | OK | Ground clear controls. | 142 | 49.12 | 812.65
9819 | TIN-INTERP | Interpolated Ground | 62880.33 | 5.12 | 796.74 | 0 | 15.91 | 0 | OK | Ground clear controls. | 142 | 49.12 | 812.65
9820 | TIN-INTERP | Interpolated Ground | 62880.36 | -6.6 | 796.58 | 0 | 21.62 | 0 | OK | Ground clear controls. | 142 | 49.12 | 818.2
9821 | TIN-INTERP | Interpolated Ground | 62880.39 | 6.62 | 796.51 | 0 | 21.66 | 0 | OK | Ground clear controls. | 142 | 49.12 | 818.17
9822 | TIN-INTERP | Interpolated Ground | 62880.4 | 4.62 | 796.79 | 0 | 26.85 | 0 | OK | Ground clear controls. | 142 | 49.12 | 823.64
9823 | TIN-INTERP | Interpolated Ground | 62880.42 | -4.6 | 796.88 | 0 | 26.8 | 0 | OK | Ground clear controls. | 142 | 49.12 | 823.68
9824 | TIN-INTERP | Interpolated Ground | 62920.31 | -5.11 | 787.15 | 0 | 16.74 | 0 | OK | Ground clear controls. | 142 | 49.12 | 803.89
9825 | TIN-INTERP | Interpolated Ground | 62920.33 | 5.12 | 788.26 | 0 | 15.63 | 0 | OK | Ground clear controls. | 142 | 49.12 | 803.89
9826 | TIN-INTERP | Interpolated Ground | 62920.36 | -6.61 | 786.82 | 0 | 22.66 | 0 | OK | Ground clear controls. | 142 | 49.12 | 809.48
9827 | TIN-INTERP | Interpolated Ground | 62920.39 | 6.62 | 788.22 | 0 | 21.22 | 0 | OK | Ground clear controls. | 142 | 49.12 | 809.44
9828 | TIN-INTERP | Interpolated Ground | 62920.4 | 4.62 | 788.27 | 0 | 26.62 | 0 | OK | Ground clear controls. | 142 | 49.12 | 814.89
9829 | TIN-INTERP | Interpolated Ground | 62920.42 | -4.61 | 787.23 | 0 | 27.72 | 0 | OK | Ground clear controls. | 142 | 49.12 | 814.95
9830 | TIN-INTERP | Interpolated Ground | 62960.31 | -5.13 | 778.96 | 0 | 17.19 | 0 | OK | Ground clear controls. | 142 | 49.12 | 796.15
9831 | TIN-INTERP | Interpolated Ground | 62960.33 | 5.12 | 779.48 | 0 | 16.67 | 0 | OK | Ground clear controls. | 142 | 49.12 | 796.15
9832 | TIN-INTERP | Interpolated Ground | 62960.36 | -6.63 | 778.73 | 0 | 23.01 | 0 | OK | Ground clear controls. | 142 | 49.12 | 801.74
9833 | TIN-INTERP | Interpolated Ground | 62960.39 | 6.62 | 779.48 | 0 | 22.22 | 0 | OK | Ground clear controls. | 142 | 49.12 | 801.7
9834 | TIN-INTERP | Interpolated Ground | 62960.4 | 4.62 | 779.42 | 0 | 27.72 | 0 | OK | Ground clear controls. | 142 | 49.12 | 807.14
9835 | TIN-INTERP | Interpolated Ground | 62960.42 | -4.63 | 779.04 | 0 | 28.16 | 0 | OK | Ground clear controls. | 142 | 49.12 | 807.2
9836 | TIN-INTERP | Interpolated Ground | 63000.31 | -5.15 | 768.17 | 0 | 21.23 | 0 | OK | Ground clear controls. | 142 | 49.12 | 789.4
9837 | TIN-INTERP | Interpolated Ground | 63000.33 | 5.12 | 768.08 | 0 | 21.33 | 0 | OK | Ground clear controls. | 142 | 49.12 | 789.41
9838 | TIN-INTERP | Interpolated Ground | 63000.36 | -6.65 | 767.75 | 0 | 27.25 | 0 | OK | Ground clear controls. | 142 | 49.12 | 795
9839 | TIN-INTERP | Interpolated Ground | 63000.39 | 6.62 | 767.82 | 0 | 27.14 | 0 | OK | Ground clear controls. | 142 | 49.12 | 794.96
9840 | TIN-INTERP | Interpolated Ground | 63000.4 | 4.62 | 768.12 | 0 | 32.28 | 0 | OK | Ground clear controls. | 142 | 49.12 | 800.4
9841 | TIN-INTERP | Interpolated Ground | 63000.42 | -4.65 | 768.25 | 0 | 32.21 | 0 | OK | Ground clear controls. | 142 | 49.12 | 800.46
9842 | TIN-INTERP | Interpolated Ground | 63040.31 | -5.17 | 749.43 | 0 | 34.24 | 0 | OK | Ground clear controls. | 142 | 49.12 | 783.67
9843 | TIN-INTERP | Interpolated Ground | 63040.33 | 5.12 | 745.43 | 0 | 38.23 | 0 | OK | Ground clear controls. | 142 | 49.12 | 783.66
9844 | TIN-INTERP | Interpolated Ground | 63040.36 | -6.67 | 750.11 | 0 | 39.12 | 0 | OK | Ground clear controls. | 142 | 49.12 | 789.23
9845 | TIN-INTERP | Interpolated Ground | 63040.39 | 6.62 | 744.88 | 0 | 44.33 | 0 | OK | Ground clear controls. | 142 | 49.12 | 789.21
9846 | TIN-INTERP | Interpolated Ground | 63040.4 | 4.62 | 745.54 | 0 | 49.12 | 0 | OK | Ground clear controls. | 142 | 49.12 | 794.66
9847 | TIN-INTERP | Interpolated Ground | 63040.42 | -4.67 | 749.23 | 0 | 45.48 | 0 | OK | Ground clear controls. | 142 | 45.48 | 794.71
9848 | TIN-INTERP | Interpolated Ground | 63080.31 | -5.18 | 758.62 | 0 | 20.31 | 0 | OK | Ground clear controls. | 142 | 35.59 | 778.93
9849 | TIN-INTERP | Interpolated Ground | 63080.33 | 5.12 | 754.02 | 0 | 24.9 | 0 | OK | Ground clear controls. | 142 | 35.59 | 778.92
9850 | TIN-INTERP | Interpolated Ground | 63080.36 | -6.69 | 759.19 | 0 | 25.26 | 0 | OK | Ground clear controls. | 142 | 35.59 | 784.45
9851 | TIN-INTERP | Interpolated Ground | 63080.39 | 6.62 | 753.32 | 0 | 31.12 | 0 | OK | Ground clear controls. | 142 | 35.59 | 784.44
9852 | TIN-INTERP | Interpolated Ground | 63080.4 | 4.62 | 754.34 | 0 | 35.59 | 0 | OK | Ground clear controls. | 142 | 35.59 | 789.93
9853 | TIN-INTERP | Interpolated Ground | 63080.42 | -4.68 | 758.45 | 0 | 31.49 | 0 | OK | Ground clear controls. | 142 | 31.49 | 789.94
9854 | TIN-INTERP | Interpolated Ground | 63102.94 | 5.12 | 759.56 | 0 | 17.12 | 0 | OK | Ground clear controls. | 143 | 31.53 | 776.68
9855 | TIN-INTERP | Interpolated Ground | 63103.05 | -6.7 | 761.61 | 0 | 20.56 | 0 | OK | Ground clear controls. | 143 | 31.53 | 782.17
9856 | TIN-INTERP | Interpolated Ground | 63103.05 | -5.2 | 761.83 | 0 | 14.84 | 0 | OK | Ground clear controls. | 143 | 31.53 | 776.67
9857 | TIN-INTERP | Interpolated Ground | 63103.11 | -4.69 | 761.89 | 0 | 25.79 | 0 | OK | Ground clear controls. | 143 | 31.53 | 787.68
9858 | TIN-INTERP | Interpolated Ground | 63103.18 | 6.62 | 759.01 | 0 | 23.16 | 0 | OK | Ground clear controls. | 143 | 31.53 | 782.17
9859 | TIN-INTERP | Interpolated Ground | 63103.2 | 4.62 | 759.82 | 0 | 27.86 | 0 | OK | Ground clear controls. | 143 | 31.53 | 787.68
9860 | TIN-INTERP | Interpolated Ground | 63142.94 | 5.34 | 748.25 | 0 | 16.64 | 0 | OK | Ground clear controls. | 143 | 31.53 | 764.89
9861 | TIN-INTERP | Interpolated Ground | 63143.05 | -6.91 | 749.16 | 0 | 21.31 | 0 | OK | Ground clear controls. | 143 | 31.53 | 770.47
9862 | TIN-INTERP | Interpolated Ground | 63143.05 | -5.41 | 748.59 | 0 | 16.29 | 0 | OK | Ground clear controls. | 143 | 31.53 | 764.88
9863 | TIN-INTERP | Interpolated Ground | 63143.11 | -4.89 | 748.43 | 0 | 27.73 | 0 | OK | Ground clear controls. | 143 | 31.53 | 776.16
9864 | TIN-INTERP | Interpolated Ground | 63143.18 | 6.84 | 748.42 | 0 | 22.05 | 0 | OK | Ground clear controls. | 143 | 31.53 | 770.47
9865 | TIN-INTERP | Interpolated Ground | 63143.2 | 4.82 | 748.1 | 0 | 28.05 | 0 | OK | Ground clear controls. | 143 | 31.53 | 776.15
9866 | TIN-INTERP | Interpolated Ground | 63182.94 | 5.56 | 738.81 | 0 | 15.34 | 0 | OK | Ground clear controls. | 143 | 31.53 | 754.15
9867 | TIN-INTERP | Interpolated Ground | 63183.05 | -7.12 | 737.16 | 0 | 22.62 | 0 | OK | Ground clear controls. | 143 | 31.53 | 759.78
9868 | TIN-INTERP | Interpolated Ground | 63183.05 | -5.62 | 737.02 | 0 | 17.09 | 0 | OK | Ground clear controls. | 143 | 31.53 | 754.11
9869 | TIN-INTERP | Interpolated Ground | 63183.11 | -5.09 | 736.99 | 0 | 28.67 | 0 | OK | Ground clear controls. | 143 | 31.53 | 765.66
9870 | TIN-INTERP | Interpolated Ground | 63183.18 | 7.05 | 739.38 | 0 | 20.4 | 0 | OK | Ground clear controls. | 143 | 31.53 | 759.78
9871 | TIN-INTERP | Interpolated Ground | 63183.2 | 5.02 | 738.45 | 0 | 27.19 | 0 | OK | Ground clear controls. | 143 | 31.53 | 765.64
9872 | TIN-INTERP | Interpolated Ground | 63222.94 | 5.77 | 727.26 | 0 | 17.18 | 0 | OK | Ground clear controls. | 143 | 31.53 | 744.44
9873 | TIN-INTERP | Interpolated Ground | 63223.05 | -7.33 | 725.36 | 0 | 24.72 | 0 | OK | Ground clear controls. | 143 | 31.53 | 750.08
9874 | TIN-INTERP | Interpolated Ground | 63223.05 | -5.83 | 724.76 | 0 | 19.61 | 0 | OK | Ground clear controls. | 143 | 31.53 | 744.37
9875 | TIN-INTERP | Interpolated Ground | 63223.11 | -5.29 | 724.62 | 0 | 31.53 | 0 | OK | Ground clear controls. | 143 | 31.53 | 756.15
9876 | TIN-INTERP | Interpolated Ground | 63223.18 | 7.26 | 727.67 | 0 | 22.41 | 0 | OK | Ground clear controls. | 143 | 29.05 | 750.08
9877 | TIN-INTERP | Interpolated Ground | 63223.2 | 5.22 | 727.09 | 0 | 29.05 | 0 | OK | Ground clear controls. | 143 | 29.05 | 756.14
9878 | TIN-INTERP | Interpolated Ground | 63262.94 | 5.99 | 721.92 | 0 | 13.83 | 0 | OK | Ground clear controls. | 143 | 24.81 | 735.75
9879 | TIN-INTERP | Interpolated Ground | 63263.05 | -7.54 | 716.55 | 0 | 24.81 | 0 | OK | Ground clear controls. | 143 | 24.81 | 741.36
9880 | TIN-INTERP | Interpolated Ground | 63263.05 | -6.04 | 717.06 | 0 | 18.56 | 0 | OK | Ground clear controls. | 143 | 18.56 | 735.62
9881 | TIN-INTERP | Interpolated Ground | 63263.08 | -7.54 | 716.55 | 0 | 24.81 | 0 | OK | Ground clear controls. | 144 | 24.81 | 741.36
9882 | TIN-INTERP | Interpolated Ground | 63263.11 | -5.49 | 717.22 | 0 | 30.41 | 0 | OK | Ground clear controls. | 143 | 30.41 | 747.63
9883 | TIN-INTERP | Interpolated Ground | 63263.12 | -5.49 | 717.22 | 0 | 30.41 | 0 | OK | Ground clear controls. | 144 | 30.41 | 747.63
9884 | TIN-INTERP | Interpolated Ground | 63263.18 | 7.47 | 722.91 | 0 | 18.48 | 0 | OK | Ground clear controls. | 143 | 26.29 | 741.39
9885 | TIN-INTERP | Interpolated Ground | 63263.2 | 5.42 | 721.36 | 0 | 26.29 | 0 | OK | Ground clear controls. | 143 | 26.29 | 747.65
9886 | TIN-INTERP | Interpolated Ground | 63263.3 | -6.04 | 717 | 0 | 18.56 | 0 | OK | Ground clear controls. | 144 | 47.52 | 735.56
9887 | TIN-INTERP | Interpolated Ground | 63263.36 | 7.47 | 722.92 | 0 | 18.43 | 0 | OK | Ground clear controls. | 144 | 47.52 | 741.35
9888 | TIN-INTERP | Interpolated Ground | 63263.37 | 5.42 | 721.31 | 0 | 26.31 | 0 | OK | Ground clear controls. | 144 | 47.52 | 747.62
9889 | TIN-INTERP | Interpolated Ground | 63263.78 | 5.99 | 721.74 | 0 | 13.84 | 0 | OK | Ground clear controls. | 144 | 47.52 | 735.58
9890 | TIN-INTERP | Interpolated Ground | 63303.07 | -7.35 | 708.51 | 0 | 23.56 | 0 | OK | Ground clear controls. | 144 | 47.52 | 732.07
9891 | TIN-INTERP | Interpolated Ground | 63303.12 | -5.31 | 710.22 | 0 | 27.91 | 0 | OK | Ground clear controls. | 144 | 47.52 | 738.13
9892 | TIN-INTERP | Interpolated Ground | 63303.3 | -5.85 | 709.7 | 0 | 16.63 | 0 | OK | Ground clear controls. | 144 | 47.52 | 726.33
9893 | TIN-INTERP | Interpolated Ground | 63303.36 | 7.24 | 711.31 | 0 | 20.74 | 0 | OK | Ground clear controls. | 144 | 47.52 | 732.05
9894 | TIN-INTERP | Interpolated Ground | 63303.37 | 5.2 | 712.61 | 0 | 25.49 | 0 | OK | Ground clear controls. | 144 | 47.52 | 738.1
9895 | TIN-INTERP | Interpolated Ground | 63303.78 | 5.76 | 712.01 | 0 | 14.29 | 0 | OK | Ground clear controls. | 144 | 47.52 | 726.3
9896 | TIN-INTERP | Interpolated Ground | 63343.07 | -7.16 | 684.35 | 0 | 39.42 | 0 | OK | Ground clear controls. | 144 | 47.52 | 723.77
9897 | TIN-INTERP | Interpolated Ground | 63343.12 | -5.13 | 683.65 | 0 | 45.98 | 0 | OK | Ground clear controls. | 144 | 47.52 | 729.63
9898 | TIN-INTERP | Interpolated Ground | 63343.3 | -5.65 | 683.86 | 0 | 34.22 | 0 | OK | Ground clear controls. | 144 | 47.52 | 718.08
9899 | TIN-INTERP | Interpolated Ground | 63343.36 | 7.02 | 687.9 | 0 | 35.83 | 0 | OK | Ground clear controls. | 144 | 47.52 | 723.73
9900 | TIN-INTERP | Interpolated Ground | 63343.37 | 4.99 | 686.87 | 0 | 42.72 | 0 | OK | Ground clear controls. | 144 | 47.52 | 729.59
9901 | TIN-INTERP | Interpolated Ground | 63343.78 | 5.53 | 686.95 | 0 | 31.09 | 0 | OK | Ground clear controls. | 144 | 47.52 | 718.04
9902 | TIN-INTERP | Interpolated Ground | 63383.07 | -6.96 | 681.83 | 0 | 34.61 | 0 | OK | Ground clear controls. | 144 | 47.52 | 716.44
9903 | TIN-INTERP | Interpolated Ground | 63383.12 | -4.95 | 680.61 | 0 | 41.51 | 0 | OK | Ground clear controls. | 144 | 47.52 | 722.12
9904 | TIN-INTERP | Interpolated Ground | 63383.3 | -5.46 | 680.97 | 0 | 29.87 | 0 | OK | Ground clear controls. | 144 | 47.52 | 710.84
9905 | TIN-INTERP | Interpolated Ground | 63383.36 | 6.79 | 675.3 | 0 | 41.1 | 0 | OK | Ground clear controls. | 144 | 47.52 | 716.4
9906 | TIN-INTERP | Interpolated Ground | 63383.37 | 4.77 | 674.56 | 0 | 47.52 | 0 | OK | Ground clear controls. | 144 | 47.52 | 722.08
9907 | TIN-INTERP | Interpolated Ground | 63383.77 | 5.29 | 674.43 | 0 | 36.35 | 0 | OK | Ground clear controls. | 144 | 36.35 | 710.78
9908 | TIN-INTERP | Interpolated Ground | 63421.63 | -4.77 | 673.46 | 0 | 42.35 | 0 | OK | Ground clear controls. | 145 | 91.1 | 715.81
9909 | TIN-INTERP | Interpolated Ground | 63421.66 | -6.78 | 673.24 | 0 | 37.07 | 0 | OK | Ground clear controls. | 145 | 91.1 | 710.31
9910 | TIN-INTERP | Interpolated Ground | 63421.68 | 6.57 | 672.61 | 0 | 37.7 | 0 | OK | Ground clear controls. | 145 | 91.1 | 710.31
9911 | TIN-INTERP | Interpolated Ground | 63421.69 | 4.57 | 672.63 | 0 | 43.18 | 0 | OK | Ground clear controls. | 145 | 91.1 | 715.81
9912 | TIN-INTERP | Interpolated Ground | 63421.77 | -5.27 | 673.41 | 0 | 31.4 | 0 | OK | Ground clear controls. | 145 | 91.1 | 704.81
9913 | TIN-INTERP | Interpolated Ground | 63421.83 | 5.07 | 672.63 | 0 | 32.18 | 0 | OK | Ground clear controls. | 145 | 91.1 | 704.81
9914 | TIN-INTERP | Interpolated Ground | 63461.64 | -4.83 | 656.29 | 0 | 44.45 | 0 | OK | Ground clear controls. | 145 | 91.1 | 700.74
9915 | TIN-INTERP | Interpolated Ground | 63461.67 | -6.85 | 655.12 | 0 | 40.13 | 0 | OK | Ground clear controls. | 145 | 91.1 | 695.25
9916 | TIN-INTERP | Interpolated Ground | 63461.68 | 6.65 | 660.94 | 0 | 34.25 | 0 | OK | Ground clear controls. | 145 | 91.1 | 695.19
9917 | TIN-INTERP | Interpolated Ground | 63461.68 | 4.63 | 660.4 | 0 | 40.27 | 0 | OK | Ground clear controls. | 145 | 91.1 | 700.67
9918 | TIN-INTERP | Interpolated Ground | 63461.77 | -5.34 | 655.8 | 0 | 33.87 | 0 | OK | Ground clear controls. | 145 | 91.1 | 689.67
9919 | TIN-INTERP | Interpolated Ground | 63461.83 | 5.15 | 660.41 | 0 | 29.22 | 0 | OK | Ground clear controls. | 145 | 91.1 | 689.63
9920 | TIN-INTERP | Interpolated Ground | 63501.64 | -4.89 | 630.32 | 0 | 56.37 | 0 | OK | Ground clear controls. | 145 | 91.1 | 686.69
9921 | TIN-INTERP | Interpolated Ground | 63501.67 | -6.92 | 629.13 | 0 | 52.08 | 0 | OK | Ground clear controls. | 145 | 91.1 | 681.21
9922 | TIN-INTERP | Interpolated Ground | 63501.68 | 6.72 | 636.68 | 0 | 44.41 | 0 | OK | Ground clear controls. | 145 | 91.1 | 681.09
9923 | TIN-INTERP | Interpolated Ground | 63501.68 | 4.7 | 635.55 | 0 | 51.01 | 0 | OK | Ground clear controls. | 145 | 91.1 | 686.56
9924 | TIN-INTERP | Interpolated Ground | 63501.77 | -5.4 | 629.88 | 0 | 45.68 | 0 | OK | Ground clear controls. | 145 | 91.1 | 675.56
9925 | TIN-INTERP | Interpolated Ground | 63501.83 | 5.22 | 635.79 | 0 | 39.7 | 0 | OK | Ground clear controls. | 145 | 91.1 | 675.49
9926 | TIN-INTERP | Interpolated Ground | 63541.64 | -4.94 | 624.93 | 0 | 48.75 | 0 | OK | Ground clear controls. | 145 | 91.1 | 673.68
9927 | TIN-INTERP | Interpolated Ground | 63541.67 | -6.98 | 623.36 | 0 | 44.83 | 0 | OK | Ground clear controls. | 145 | 91.1 | 668.19
9928 | TIN-INTERP | Interpolated Ground | 63541.68 | 6.8 | 635.65 | 0 | 32.39 | 0 | OK | Ground clear controls. | 145 | 91.1 | 668.04
9929 | TIN-INTERP | Interpolated Ground | 63541.68 | 4.76 | 633.75 | 0 | 39.74 | 0 | OK | Ground clear controls. | 145 | 91.1 | 673.49
9930 | TIN-INTERP | Interpolated Ground | 63541.77 | -5.47 | 624.5 | 0 | 37.98 | 0 | OK | Ground clear controls. | 145 | 91.1 | 662.48
9931 | TIN-INTERP | Interpolated Ground | 63541.83 | 5.3 | 634.27 | 0 | 28.11 | 0 | OK | Ground clear controls. | 145 | 91.1 | 662.38
9932 | TIN-INTERP | Interpolated Ground | 63581.64 | -5 | 623.78 | 0 | 37.92 | 0 | OK | Ground clear controls. | 145 | 91.1 | 661.7
9933 | TIN-INTERP | Interpolated Ground | 63581.67 | -7.05 | 622.28 | 0 | 33.93 | 0 | OK | Ground clear controls. | 145 | 91.1 | 656.21
9934 | TIN-INTERP | Interpolated Ground | 63581.68 | 6.87 | 631.54 | 0 | 24.47 | 0 | OK | Ground clear controls. | 145 | 91.1 | 656.01
9935 | TIN-INTERP | Interpolated Ground | 63581.68 | 4.83 | 630.21 | 0 | 31.28 | 0 | OK | Ground clear controls. | 145 | 91.1 | 661.49
9936 | TIN-INTERP | Interpolated Ground | 63581.77 | -5.53 | 623.36 | 0 | 27.08 | 0 | OK | Ground clear controls. | 145 | 91.1 | 650.44
9937 | TIN-INTERP | Interpolated Ground | 63581.83 | 5.37 | 630.5 | 0 | 19.82 | 0 | OK | Ground clear controls. | 145 | 91.1 | 650.32
9938 | TIN-INTERP | Interpolated Ground | 63621.64 | -5.05 | 597.5 | 0 | 53.23 | 0 | OK | Ground clear controls. | 145 | 91.1 | 650.73
9939 | TIN-INTERP | Interpolated Ground | 63621.67 | -7.12 | 596.52 | 0 | 48.71 | 0 | OK | Ground clear controls. | 145 | 91.1 | 645.23
9940 | TIN-INTERP | Interpolated Ground | 63621.68 | 6.95 | 605.96 | 0 | 39.05 | 0 | OK | Ground clear controls. | 145 | 91.1 | 645.01
9941 | TIN-INTERP | Interpolated Ground | 63621.68 | 4.89 | 604.5 | 0 | 45.98 | 0 | OK | Ground clear controls. | 145 | 91.1 | 650.48
9942 | TIN-INTERP | Interpolated Ground | 63621.77 | -5.59 | 597.16 | 0 | 42.25 | 0 | OK | Ground clear controls. | 145 | 91.1 | 639.41
9943 | TIN-INTERP | Interpolated Ground | 63621.83 | 5.45 | 604.81 | 0 | 34.46 | 0 | OK | Ground clear controls. | 145 | 91.1 | 639.27
9944 | TIN-INTERP | Interpolated Ground | 63661.64 | -5.11 | 576.15 | 0 | 64.63 | 0 | OK | Ground clear controls. | 145 | 91.1 | 640.78
9945 | TIN-INTERP | Interpolated Ground | 63661.67 | -7.19 | 574.67 | 0 | 60.58 | 0 | OK | Ground clear controls. | 145 | 91.1 | 635.25
9946 | TIN-INTERP | Interpolated Ground | 63661.68 | 7.02 | 583.43 | 0 | 51.57 | 0 | OK | Ground clear controls. | 145 | 91.1 | 635
9947 | TIN-INTERP | Interpolated Ground | 63661.68 | 4.96 | 581.68 | 0 | 58.82 | 0 | OK | Ground clear controls. | 145 | 91.1 | 640.5
9948 | TIN-INTERP | Interpolated Ground | 63661.77 | -5.66 | 575.74 | 0 | 53.66 | 0 | OK | Ground clear controls. | 145 | 91.1 | 629.4
9949 | TIN-INTERP | Interpolated Ground | 63661.83 | 5.52 | 582.09 | 0 | 47.15 | 0 | OK | Ground clear controls. | 145 | 91.1 | 629.24
9950 | TIN-INTERP | Interpolated Ground | 63701.64 | -5.17 | 555.75 | 0 | 76.09 | 0 | OK | Ground clear controls. | 145 | 91.1 | 631.84
9951 | TIN-INTERP | Interpolated Ground | 63701.67 | -7.26 | 554.64 | 0 | 71.64 | 0 | OK | Ground clear controls. | 145 | 91.1 | 626.28
9952 | TIN-INTERP | Interpolated Ground | 63701.68 | 7.1 | 559.24 | 0 | 66.78 | 0 | OK | Ground clear controls. | 145 | 91.1 | 626.02
9953 | TIN-INTERP | Interpolated Ground | 63701.68 | 5.02 | 558.57 | 0 | 72.98 | 0 | OK | Ground clear controls. | 145 | 91.1 | 631.55
9954 | TIN-INTERP | Interpolated Ground | 63701.77 | -5.72 | 555.39 | 0 | 65.01 | 0 | OK | Ground clear controls. | 145 | 91.1 | 620.4
9955 | TIN-INTERP | Interpolated Ground | 63701.83 | 5.6 | 558.59 | 0 | 61.64 | 0 | OK | Ground clear controls. | 145 | 91.1 | 620.23
9956 | TIN-INTERP | Interpolated Ground | 63741.64 | -5.22 | 535.21 | 0 | 88.7 | 0 | OK | Ground clear controls. | 145 | 91.1 | 623.91
9957 | TIN-INTERP | Interpolated Ground | 63741.67 | -7.33 | 534.3 | 0 | 84.02 | 0 | OK | Ground clear controls. | 145 | 91.1 | 618.32
9958 | TIN-INTERP | Interpolated Ground | 63741.68 | 7.17 | 542.33 | 0 | 75.71 | 0 | OK | Ground clear controls. | 145 | 91.1 | 618.04
9959 | TIN-INTERP | Interpolated Ground | 63741.68 | 5.09 | 540.64 | 0 | 82.96 | 0 | OK | Ground clear controls. | 145 | 91.1 | 623.6
9960 | TIN-INTERP | Interpolated Ground | 63741.77 | -5.78 | 534.88 | 0 | 77.52 | 0 | OK | Ground clear controls. | 145 | 91.1 | 612.4
9961 | TIN-INTERP | Interpolated Ground | 63741.83 | 5.67 | 541.11 | 0 | 71.12 | 0 | OK | Ground clear controls. | 145 | 91.1 | 612.23
9962 | TIN-INTERP | Interpolated Ground | 63781.64 | -5.28 | 529.24 | 0 | 87.72 | 0 | OK | Ground clear controls. | 145 | 91.1 | 616.96
9963 | TIN-INTERP | Interpolated Ground | 63781.67 | -7.4 | 529.63 | 0 | 81.71 | 0 | OK | Ground clear controls. | 145 | 91.1 | 611.34
9964 | TIN-INTERP | Interpolated Ground | 63781.68 | 7.25 | 525.49 | 0 | 85.57 | 0 | OK | Ground clear controls. | 145 | 91.1 | 611.06
9965 | TIN-INTERP | Interpolated Ground | 63781.68 | 5.15 | 525.55 | 0 | 91.1 | 0 | OK | Ground clear controls. | 145 | 91.1 | 616.65
9966 | TIN-INTERP | Interpolated Ground | 63781.77 | -5.85 | 529.38 | 0 | 76.02 | 0 | OK | Ground clear controls. | 145 | 79.68 | 605.4
9967 | TIN-INTERP | Interpolated Ground | 63781.83 | 5.75 | 525.55 | 0 | 79.68 | 0 | OK | Ground clear controls. | 145 | 79.68 | 605.23
9968 | TIN-INTERP | Interpolated Ground | 63821.64 | -5.34 | 543.6 | 0 | 67.41 | 0 | OK | Ground clear controls. | 145 | 71.63 | 611.01
9969 | TIN-INTERP | Interpolated Ground | 63821.67 | -7.47 | 544.54 | 0 | 60.8 | 0 | OK | Ground clear controls. | 145 | 71.63 | 605.34
9970 | TIN-INTERP | Interpolated Ground | 63821.68 | 7.32 | 538.22 | 0 | 66.83 | 0 | OK | Ground clear controls. | 145 | 71.63 | 605.05
9971 | TIN-INTERP | Interpolated Ground | 63821.68 | 5.22 | 539.07 | 0 | 71.63 | 0 | OK | Ground clear controls. | 145 | 71.63 | 610.7
9972 | TIN-INTERP | Interpolated Ground | 63821.77 | -5.91 | 543.97 | 0 | 55.42 | 0 | OK | Ground clear controls. | 145 | 60.35 | 599.39
9973 | TIN-INTERP | Interpolated Ground | 63821.83 | 5.82 | 538.86 | 0 | 60.35 | 0 | OK | Ground clear controls. | 145 | 60.35 | 599.21
9974 | TIN-INTERP | Interpolated Ground | 63861.64 | -5.39 | 559.94 | 0 | 46.1 | 0 | OK | Ground clear controls. | 145 | 57.98 | 606.04
9975 | TIN-INTERP | Interpolated Ground | 63861.67 | -7.53 | 561.53 | 0 | 38.78 | 0 | OK | Ground clear controls. | 145 | 57.98 | 600.31
9976 | TIN-INTERP | Interpolated Ground | 63861.68 | 7.4 | 552.1 | 0 | 47.94 | 0 | OK | Ground clear controls. | 145 | 57.98 | 600.04
9977 | TIN-INTERP | Interpolated Ground | 63861.68 | 5.28 | 553.61 | 0 | 52.13 | 0 | OK | Ground clear controls. | 145 | 57.98 | 605.74
9978 | TIN-INTERP | Interpolated Ground | 63861.77 | -5.98 | 560.48 | 0 | 33.88 | 0 | OK | Ground clear controls. | 145 | 57.98 | 594.36
9979 | TIN-INTERP | Interpolated Ground | 63861.83 | 5.9 | 553.18 | 0 | 41.01 | 0 | OK | Ground clear controls. | 145 | 57.98 | 594.19
9980 | TIN-INTERP | Interpolated Ground | 63901.64 | -5.45 | 568.69 | 0 | 33.38 | 0 | OK | Ground clear controls. | 145 | 57.98 | 602.07
9981 | TIN-INTERP | Interpolated Ground | 63901.67 | -7.6 | 570.03 | 0 | 26.26 | 0 | OK | Ground clear controls. | 145 | 57.98 | 596.29
9982 | TIN-INTERP | Interpolated Ground | 63901.68 | 7.47 | 561.34 | 0 | 34.7 | 0 | OK | Ground clear controls. | 145 | 57.98 | 596.04
9983 | TIN-INTERP | Interpolated Ground | 63901.68 | 5.35 | 562.63 | 0 | 39.16 | 0 | OK | Ground clear controls. | 145 | 57.98 | 601.79
9984 | TIN-INTERP | Interpolated Ground | 63901.77 | -6.04 | 569.12 | 0 | 21.22 | 0 | OK | Ground clear controls. | 145 | 57.98 | 590.34
9985 | TIN-INTERP | Interpolated Ground | 63901.83 | 5.97 | 562.23 | 0 | 27.94 | 0 | OK | Ground clear controls. | 145 | 57.98 | 590.17
9986 | TIN-INTERP | Interpolated Ground | 63941.64 | -5.5 | 567.72 | 0 | 31.37 | 0 | OK | Ground clear controls. | 145 | 57.98 | 599.09
9987 | TIN-INTERP | Interpolated Ground | 63941.67 | -7.67 | 569.49 | 0 | 23.75 | 0 | OK | Ground clear controls. | 145 | 57.98 | 593.24
9988 | TIN-INTERP | Interpolated Ground | 63941.68 | 7.55 | 560.9 | 0 | 32.1 | 0 | OK | Ground clear controls. | 145 | 57.98 | 593
9989 | TIN-INTERP | Interpolated Ground | 63941.68 | 5.41 | 562.74 | 0 | 36.09 | 0 | OK | Ground clear controls. | 145 | 57.98 | 598.83
9990 | TIN-INTERP | Interpolated Ground | 63941.77 | -6.1 | 568.21 | 0 | 19.08 | 0 | OK | Ground clear controls. | 145 | 57.98 | 587.29
9991 | TIN-INTERP | Interpolated Ground | 63941.83 | 6.05 | 562.31 | 0 | 24.84 | 0 | OK | Ground clear controls. | 145 | 57.98 | 587.15
9992 | TIN-INTERP | Interpolated Ground | 63981.64 | -5.56 | 560.71 | 0 | 36.36 | 0 | OK | Ground clear controls. | 145 | 57.98 | 597.07
9993 | TIN-INTERP | Interpolated Ground | 63981.67 | -7.74 | 562.05 | 0 | 29.11 | 0 | OK | Ground clear controls. | 145 | 57.98 | 591.16
9994 | TIN-INTERP | Interpolated Ground | 63981.68 | 7.62 | 554.13 | 0 | 36.82 | 0 | OK | Ground clear controls. | 145 | 57.98 | 590.95
9995 | TIN-INTERP | Interpolated Ground | 63981.68 | 5.48 | 555.06 | 0 | 41.8 | 0 | OK | Ground clear controls. | 145 | 57.98 | 596.86
9996 | TIN-INTERP | Interpolated Ground | 63981.77 | -6.17 | 561.08 | 0 | 24.14 | 0 | OK | Ground clear controls. | 145 | 57.98 | 585.22
9997 | TIN-INTERP | Interpolated Ground | 63981.83 | 6.12 | 554.75 | 0 | 30.35 | 0 | OK | Ground clear controls. | 145 | 57.98 | 585.1
9998 | TIN-INTERP | Interpolated Ground | 64021.64 | -5.62 | 540.38 | 0 | 55.67 | 0 | OK | Ground clear controls. | 145 | 57.98 | 596.05
9999 | TIN-INTERP | Interpolated Ground | 64021.67 | -7.81 | 540.58 | 0 | 49.47 | 0 | OK | Ground clear controls. | 145 | 57.98 | 590.05
10000 | TIN-INTERP | Interpolated Ground | 64021.68 | 7.7 | 537.48 | 0 | 52.41 | 0 | OK | Ground clear controls. | 145 | 57.98 | 589.89
10001 | TIN-INTERP | Interpolated Ground | 64021.68 | 5.54 | 538.16 | 0 | 57.7 | 0 | OK | Ground clear controls. | 145 | 57.98 | 595.86
10002 | TIN-INTERP | Interpolated Ground | 64021.77 | -6.23 | 540.31 | 0 | 43.83 | 0 | OK | Ground clear controls. | 145 | 57.98 | 584.14
10003 | TIN-INTERP | Interpolated Ground | 64021.83 | 6.2 | 537.87 | 0 | 46.17 | 0 | OK | Ground clear controls. | 145 | 57.98 | 584.04
10004 | TIN-INTERP | Interpolated Ground | 64061.64 | -5.67 | 539.89 | 0 | 56.1 | 0 | OK | Ground clear controls. | 145 | 57.98 | 595.99
10005 | TIN-INTERP | Interpolated Ground | 64061.67 | -7.88 | 540.62 | 0 | 49.3 | 0 | OK | Ground clear controls. | 145 | 57.98 | 589.92
10006 | TIN-INTERP | Interpolated Ground | 64061.67 | 7.77 | 537.08 | 0 | 52.71 | 0 | OK | Ground clear controls. | 145 | 57.98 | 589.79
10007 | TIN-INTERP | Interpolated Ground | 64061.68 | 5.61 | 537.88 | 0 | 57.98 | 0 | OK | Ground clear controls. | 145 | 57.98 | 595.86
10008 | TIN-INTERP | Interpolated Ground | 64061.77 | -6.29 | 540.08 | 0 | 43.96 | 0 | OK | Ground clear controls. | 145 | 47.79 | 584.04
10009 | TIN-INTERP | Interpolated Ground | 64061.83 | 6.27 | 537.56 | 0 | 46.39 | 0 | OK | Ground clear controls. | 145 | 47.79 | 583.95
10010 | TIN-INTERP | Interpolated Ground | 64101.64 | -5.73 | 550.83 | 0 | 46.1 | 0 | OK | Ground clear controls. | 145 | 47.79 | 596.93
10011 | TIN-INTERP | Interpolated Ground | 64101.67 | -7.95 | 551.65 | 0 | 39.1 | 0 | OK | Ground clear controls. | 145 | 47.79 | 590.75
10012 | TIN-INTERP | Interpolated Ground | 64101.67 | 7.85 | 549.12 | 0 | 41.56 | 0 | OK | Ground clear controls. | 145 | 47.79 | 590.68
10013 | TIN-INTERP | Interpolated Ground | 64101.68 | 5.67 | 549.05 | 0 | 47.79 | 0 | OK | Ground clear controls. | 145 | 47.79 | 596.84
10014 | TIN-INTERP | Interpolated Ground | 64101.77 | -6.36 | 551.16 | 0 | 33.74 | 0 | OK | Ground clear controls. | 145 | 35.88 | 584.9
10015 | TIN-INTERP | Interpolated Ground | 64101.83 | 6.35 | 549.17 | 0 | 35.69 | 0 | OK | Ground clear controls. | 145 | 35.88 | 584.86
10016 | TIN-INTERP | Interpolated Ground | 64141.64 | -5.78 | 565.04 | 0 | 33.8 | 0 | OK | Ground clear controls. | 145 | 35.88 | 598.84
10017 | TIN-INTERP | Interpolated Ground | 64141.67 | -8.01 | 565.44 | 0 | 27.14 | 0 | OK | Ground clear controls. | 145 | 35.88 | 592.58
10018 | TIN-INTERP | Interpolated Ground | 64141.67 | 7.92 | 562.58 | 0 | 29.98 | 0 | OK | Ground clear controls. | 145 | 35.88 | 592.56
10019 | TIN-INTERP | Interpolated Ground | 64141.68 | 5.74 | 562.95 | 0 | 35.88 | 0 | OK | Ground clear controls. | 145 | 35.88 | 598.83
10020 | TIN-INTERP | Interpolated Ground | 64141.77 | -6.42 | 565.14 | 0 | 21.63 | 0 | OK | Ground clear controls. | 145 | 23.87 | 586.77
10021 | TIN-INTERP | Interpolated Ground | 64141.83 | 6.42 | 562.89 | 0 | 23.87 | 0 | OK | Ground clear controls. | 145 | 23.87 | 586.76
10022 | TIN-INTERP | Interpolated Ground | 64151.59 | -8.03 | 567.25 | 0 | 25.92 | 0 | OK | Ground clear controls. | 146 | 51.62 | 593.17
10023 | TIN-INTERP | Interpolated Ground | 64151.63 | -5.8 | 567.1 | 0 | 32.37 | 0 | OK | Ground clear controls. | 146 | 51.62 | 599.47
10024 | TIN-INTERP | Interpolated Ground | 64151.64 | -6.44 | 567.28 | 0 | 20.09 | 0 | OK | Ground clear controls. | 146 | 51.62 | 587.37
10025 | TIN-INTERP | Interpolated Ground | 64151.67 | 6.44 | 564.57 | 0 | 22.8 | 0 | OK | Ground clear controls. | 146 | 51.62 | 587.37
10026 | TIN-INTERP | Interpolated Ground | 64151.69 | 7.94 | 564.24 | 0 | 28.93 | 0 | OK | Ground clear controls. | 146 | 51.62 | 593.17
10027 | TIN-INTERP | Interpolated Ground | 64151.69 | 5.75 | 564.73 | 0 | 34.74 | 0 | OK | Ground clear controls. | 146 | 51.62 | 599.47
10028 | TIN-INTERP | Interpolated Ground | 64191.58 | -7.95 | 563.77 | 0 | 24.45 | 0 | OK | Ground clear controls. | 146 | 51.62 | 588.22
10029 | TIN-INTERP | Interpolated Ground | 64191.63 | -5.75 | 562.52 | 0 | 31.92 | 0 | OK | Ground clear controls. | 146 | 51.62 | 594.44
10030 | TIN-INTERP | Interpolated Ground | 64191.63 | -6.37 | 562.87 | 0 | 19.56 | 0 | OK | Ground clear controls. | 146 | 51.62 | 582.43
10031 | TIN-INTERP | Interpolated Ground | 64191.67 | 6.31 | 556.92 | 0 | 25.49 | 0 | OK | Ground clear controls. | 146 | 51.62 | 582.41
10032 | TIN-INTERP | Interpolated Ground | 64191.69 | 7.81 | 556.05 | 0 | 32.16 | 0 | OK | Ground clear controls. | 146 | 51.62 | 588.21
10033 | TIN-INTERP | Interpolated Ground | 64191.69 | 5.65 | 557.18 | 0 | 37.25 | 0 | OK | Ground clear controls. | 146 | 51.62 | 594.43
10034 | TIN-INTERP | Interpolated Ground | 64231.58 | -7.87 | 560.81 | 0 | 23.43 | 0 | OK | Ground clear controls. | 146 | 51.62 | 584.24
10035 | TIN-INTERP | Interpolated Ground | 64231.63 | -5.7 | 559.72 | 0 | 30.69 | 0 | OK | Ground clear controls. | 146 | 51.62 | 590.41
10036 | TIN-INTERP | Interpolated Ground | 64231.63 | -6.3 | 560.05 | 0 | 18.42 | 0 | OK | Ground clear controls. | 146 | 51.62 | 578.47
10037 | TIN-INTERP | Interpolated Ground | 64231.67 | 6.17 | 552.64 | 0 | 25.81 | 0 | OK | Ground clear controls. | 146 | 51.62 | 578.45
10038 | TIN-INTERP | Interpolated Ground | 64231.69 | 7.67 | 552.04 | 0 | 32.19 | 0 | OK | Ground clear controls. | 146 | 51.62 | 584.23
10039 | TIN-INTERP | Interpolated Ground | 64231.69 | 5.54 | 552.96 | 0 | 37.42 | 0 | OK | Ground clear controls. | 146 | 51.62 | 590.38
10040 | TIN-INTERP | Interpolated Ground | 64271.58 | -7.79 | 550.29 | 0 | 30.97 | 0 | OK | Ground clear controls. | 146 | 51.62 | 581.26
10041 | TIN-INTERP | Interpolated Ground | 64271.63 | -5.66 | 549.98 | 0 | 37.39 | 0 | OK | Ground clear controls. | 146 | 51.62 | 587.37
10042 | TIN-INTERP | Interpolated Ground | 64271.63 | -6.22 | 550.04 | 0 | 25.48 | 0 | OK | Ground clear controls. | 146 | 51.62 | 575.52
10043 | TIN-INTERP | Interpolated Ground | 64271.67 | 6.04 | 548.62 | 0 | 26.86 | 0 | OK | Ground clear controls. | 146 | 51.62 | 575.48
10044 | TIN-INTERP | Interpolated Ground | 64271.69 | 7.54 | 548.15 | 0 | 33.11 | 0 | OK | Ground clear controls. | 146 | 51.62 | 581.26
10045 | TIN-INTERP | Interpolated Ground | 64271.69 | 5.44 | 548.66 | 0 | 38.68 | 0 | OK | Ground clear controls. | 146 | 51.62 | 587.34
10046 | TIN-INTERP | Interpolated Ground | 64311.58 | -7.71 | 538.76 | 0 | 40.5 | 0 | OK | Ground clear controls. | 146 | 51.62 | 579.26
10047 | TIN-INTERP | Interpolated Ground | 64311.63 | -5.61 | 537.48 | 0 | 47.83 | 0 | OK | Ground clear controls. | 146 | 51.62 | 585.31
10048 | TIN-INTERP | Interpolated Ground | 64311.63 | -6.15 | 537.89 | 0 | 35.65 | 0 | OK | Ground clear controls. | 146 | 51.62 | 573.54
10049 | TIN-INTERP | Interpolated Ground | 64311.67 | 5.9 | 533.47 | 0 | 40.04 | 0 | OK | Ground clear controls. | 146 | 51.62 | 573.51
10050 | TIN-INTERP | Interpolated Ground | 64311.69 | 7.4 | 532.8 | 0 | 46.46 | 0 | OK | Ground clear controls. | 146 | 51.62 | 579.26
10051 | TIN-INTERP | Interpolated Ground | 64311.69 | 5.33 | 533.66 | 0 | 51.62 | 0 | OK | Ground clear controls. | 146 | 51.62 | 585.28
10052 | TIN-INTERP | Interpolated Ground | 64351.58 | -7.63 | 547.51 | 0 | 30.75 | 0 | OK | Ground clear controls. | 146 | 42.27 | 578.26
10053 | TIN-INTERP | Interpolated Ground | 64351.63 | -5.56 | 546.32 | 0 | 37.93 | 0 | OK | Ground clear controls. | 146 | 42.27 | 584.25
10054 | TIN-INTERP | Interpolated Ground | 64351.63 | -6.08 | 546.77 | 0 | 25.78 | 0 | OK | Ground clear controls. | 146 | 42.27 | 572.55
10055 | TIN-INTERP | Interpolated Ground | 64351.67 | 5.77 | 543.13 | 0 | 29.39 | 0 | OK | Ground clear controls. | 146 | 42.27 | 572.52
10056 | TIN-INTERP | Interpolated Ground | 64351.69 | 7.27 | 542.75 | 0 | 35.5 | 0 | OK | Ground clear controls. | 146 | 42.27 | 578.25
10057 | TIN-INTERP | Interpolated Ground | 64351.69 | 5.22 | 543.25 | 0 | 40.96 | 0 | OK | Ground clear controls. | 146 | 42.27 | 584.21
10058 | TIN-INTERP | Interpolated Ground | 64391.58 | -7.55 | 558.37 | 0 | 19.86 | 0 | OK | Ground clear controls. | 146 | 42.27 | 578.23
10059 | TIN-INTERP | Interpolated Ground | 64391.63 | -5.51 | 557.09 | 0 | 27.08 | 0 | OK | Ground clear controls. | 146 | 42.27 | 584.17
10060 | TIN-INTERP | Interpolated Ground | 64391.63 | -6.01 | 557.46 | 0 | 15.1 | 0 | OK | Ground clear controls. | 146 | 42.27 | 572.56
10061 | TIN-INTERP | Interpolated Ground | 64391.67 | 5.63 | 555.9 | 0 | 16.63 | 0 | OK | Ground clear controls. | 146 | 42.27 | 572.53
10062 | TIN-INTERP | Interpolated Ground | 64391.69 | 7.13 | 555.79 | 0 | 22.42 | 0 | OK | Ground clear controls. | 146 | 42.27 | 578.21
10063 | TIN-INTERP | Interpolated Ground | 64391.69 | 5.12 | 555.95 | 0 | 28.19 | 0 | OK | Ground clear controls. | 146 | 42.27 | 584.14
10064 | TIN-INTERP | Interpolated Ground | 64431.58 | -7.47 | 553.1 | 0 | 26.09 | 0 | OK | Ground clear controls. | 146 | 42.27 | 579.19
10065 | TIN-INTERP | Interpolated Ground | 64431.63 | -5.47 | 552.78 | 0 | 32.31 | 0 | OK | Ground clear controls. | 146 | 42.27 | 585.09
10066 | TIN-INTERP | Interpolated Ground | 64431.63 | -5.94 | 552.82 | 0 | 20.73 | 0 | OK | Ground clear controls. | 146 | 42.27 | 573.55
10067 | TIN-INTERP | Interpolated Ground | 64431.67 | 5.5 | 549.23 | 0 | 24.28 | 0 | OK | Ground clear controls. | 146 | 42.27 | 573.51
10068 | TIN-INTERP | Interpolated Ground | 64431.69 | 7 | 548.81 | 0 | 30.35 | 0 | OK | Ground clear controls. | 146 | 42.27 | 579.16
10069 | TIN-INTERP | Interpolated Ground | 64431.69 | 5.01 | 549.46 | 0 | 35.59 | 0 | OK | Ground clear controls. | 146 | 42.27 | 585.05
10070 | TIN-INTERP | Interpolated Ground | 64471.58 | -7.39 | 553.81 | 0 | 27.31 | 0 | OK | Ground clear controls. | 146 | 42.27 | 581.12
10071 | TIN-INTERP | Interpolated Ground | 64471.63 | -5.42 | 552.74 | 0 | 34.25 | 0 | OK | Ground clear controls. | 146 | 42.27 | 586.99
10072 | TIN-INTERP | Interpolated Ground | 64471.63 | -5.87 | 553 | 0 | 22.54 | 0 | OK | Ground clear controls. | 146 | 42.27 | 575.54
10073 | TIN-INTERP | Interpolated Ground | 64471.67 | 5.36 | 552.12 | 0 | 23.38 | 0 | OK | Ground clear controls. | 146 | 42.27 | 575.5
10074 | TIN-INTERP | Interpolated Ground | 64471.69 | 6.86 | 551.81 | 0 | 29.29 | 0 | OK | Ground clear controls. | 146 | 42.27 | 581.1
10075 | TIN-INTERP | Interpolated Ground | 64471.69 | 4.9 | 552.15 | 0 | 34.81 | 0 | OK | Ground clear controls. | 146 | 42.27 | 586.96
10076 | TIN-INTERP | Interpolated Ground | 64511.58 | -7.31 | 554.51 | 0 | 29.53 | 0 | OK | Ground clear controls. | 146 | 42.27 | 584.04
10077 | TIN-INTERP | Interpolated Ground | 64511.63 | -5.37 | 553.18 | 0 | 36.7 | 0 | OK | Ground clear controls. | 146 | 42.27 | 589.88
10078 | TIN-INTERP | Interpolated Ground | 64511.63 | -5.8 | 553.49 | 0 | 25.01 | 0 | OK | Ground clear controls. | 146 | 42.27 | 578.5
10079 | TIN-INTERP | Interpolated Ground | 64511.67 | 5.23 | 547.42 | 0 | 31.05 | 0 | OK | Ground clear controls. | 146 | 42.27 | 578.47
10080 | TIN-INTERP | Interpolated Ground | 64511.69 | 6.73 | 546.89 | 0 | 37.14 | 0 | OK | Ground clear controls. | 146 | 42.27 | 584.03
10081 | TIN-INTERP | Interpolated Ground | 64511.69 | 4.8 | 547.58 | 0 | 42.27 | 0 | OK | Ground clear controls. | 146 | 42.27 | 589.85
10082 | TIN-INTERP | Interpolated Ground | 64546.46 | -7.24 | 557.89 | 0 | 29.51 | 0 | OK | Ground clear controls. | 147 | 121.71 | 587.4
10083 | TIN-INTERP | Interpolated Ground | 64546.51 | -5.33 | 558.23 | 0 | 34.97 | 0 | OK | Ground clear controls. | 147 | 121.71 | 593.2
10084 | TIN-INTERP | Interpolated Ground | 64546.62 | 4.7 | 559.38 | 0 | 33.81 | 0 | OK | Ground clear controls. | 147 | 121.71 | 593.19
10085 | TIN-INTERP | Interpolated Ground | 64546.62 | 6.61 | 559.28 | 0 | 28.12 | 0 | OK | Ground clear controls. | 147 | 121.71 | 587.4
10086 | TIN-INTERP | Interpolated Ground | 64546.64 | 5.11 | 559.34 | 0 | 22.55 | 0 | OK | Ground clear controls. | 147 | 121.71 | 581.89
10087 | TIN-INTERP | Interpolated Ground | 64546.72 | -5.74 | 558.16 | 0 | 23.74 | 0 | OK | Ground clear controls. | 147 | 121.71 | 581.9
10088 | TIN-INTERP | Interpolated Ground | 64586.53 | 4.72 | 547.58 | 0 | 42.29 | 0 | OK | Ground clear controls. | 147 | 121.71 | 589.87
10089 | TIN-INTERP | Interpolated Ground | 64586.59 | 6.63 | 548.72 | 0 | 35.47 | 0 | OK | Ground clear controls. | 147 | 121.71 | 584.19
10090 | TIN-INTERP | Interpolated Ground | 64586.64 | 5.13 | 547.74 | 0 | 30.93 | 0 | OK | Ground clear controls. | 147 | 121.71 | 578.67
10091 | TIN-INTERP | Interpolated Ground | 64586.66 | -7.18 | 540.75 | 0 | 43.38 | 0 | OK | Ground clear controls. | 147 | 121.71 | 584.13
10092 | TIN-INTERP | Interpolated Ground | 64586.66 | -5.26 | 541.96 | 0 | 47.94 | 0 | OK | Ground clear controls. | 147 | 121.71 | 589.9
10093 | TIN-INTERP | Interpolated Ground | 64586.72 | -5.67 | 541.68 | 0 | 36.97 | 0 | OK | Ground clear controls. | 147 | 121.71 | 578.65
10094 | TIN-INTERP | Interpolated Ground | 64626.53 | 4.74 | 522.49 | 0 | 65.04 | 0 | OK | Ground clear controls. | 147 | 121.71 | 587.53
10095 | TIN-INTERP | Interpolated Ground | 64626.59 | 6.65 | 522.47 | 0 | 59.49 | 0 | OK | Ground clear controls. | 147 | 121.71 | 581.96
10096 | TIN-INTERP | Interpolated Ground | 64626.64 | 5.16 | 522.4 | 0 | 54.02 | 0 | OK | Ground clear controls. | 147 | 121.71 | 576.42
10097 | TIN-INTERP | Interpolated Ground | 64626.66 | -7.11 | 520.25 | 0 | 61.58 | 0 | OK | Ground clear controls. | 147 | 121.71 | 581.83
10098 | TIN-INTERP | Interpolated Ground | 64626.66 | -5.19 | 520.84 | 0 | 66.75 | 0 | OK | Ground clear controls. | 147 | 121.71 | 587.59
10099 | TIN-INTERP | Interpolated Ground | 64626.72 | -5.61 | 520.65 | 0 | 55.74 | 0 | OK | Ground clear controls. | 147 | 121.71 | 576.39
10100 | TIN-INTERP | Interpolated Ground | 64666.53 | 4.75 | 509.68 | 0 | 76.5 | 0 | OK | Ground clear controls. | 147 | 121.71 | 586.18
10101 | TIN-INTERP | Interpolated Ground | 64666.59 | 6.68 | 509.67 | 0 | 71.05 | 0 | OK | Ground clear controls. | 147 | 121.71 | 580.72
10102 | TIN-INTERP | Interpolated Ground | 64666.64 | 5.18 | 509.66 | 0 | 65.5 | 0 | OK | Ground clear controls. | 147 | 121.71 | 575.16
10103 | TIN-INTERP | Interpolated Ground | 64666.66 | -7.05 | 509.83 | 0 | 70.7 | 0 | OK | Ground clear controls. | 147 | 121.71 | 580.53
10104 | TIN-INTERP | Interpolated Ground | 64666.66 | -5.12 | 509.59 | 0 | 76.67 | 0 | OK | Ground clear controls. | 147 | 121.71 | 586.26
10105 | TIN-INTERP | Interpolated Ground | 64666.72 | -5.55 | 509.58 | 0 | 65.52 | 0 | OK | Ground clear controls. | 147 | 121.71 | 575.1
10106 | TIN-INTERP | Interpolated Ground | 64706.53 | 4.77 | 505.06 | 0 | 80.76 | 0 | OK | Ground clear controls. | 147 | 121.71 | 585.82
10107 | TIN-INTERP | Interpolated Ground | 64706.59 | 6.7 | 503.45 | 0 | 76.98 | 0 | OK | Ground clear controls. | 147 | 121.71 | 580.43
10108 | TIN-INTERP | Interpolated Ground | 64706.64 | 5.2 | 504.61 | 0 | 70.25 | 0 | OK | Ground clear controls. | 147 | 121.71 | 574.86
10109 | TIN-INTERP | Interpolated Ground | 64706.66 | -6.98 | 510.34 | 0 | 69.88 | 0 | OK | Ground clear controls. | 147 | 121.71 | 580.22
10110 | TIN-INTERP | Interpolated Ground | 64706.66 | -5.05 | 510.06 | 0 | 75.85 | 0 | OK | Ground clear controls. | 147 | 121.71 | 585.91
10111 | TIN-INTERP | Interpolated Ground | 64706.72 | -5.48 | 510.14 | 0 | 64.66 | 0 | OK | Ground clear controls. | 147 | 121.71 | 574.8
10112 | TIN-INTERP | Interpolated Ground | 64746.53 | 4.79 | 489.41 | 0 | 97.05 | 0 | OK | Ground clear controls. | 147 | 121.71 | 586.46
10113 | TIN-INTERP | Interpolated Ground | 64746.59 | 6.72 | 488.36 | 0 | 92.79 | 0 | OK | Ground clear controls. | 147 | 121.71 | 581.15
10114 | TIN-INTERP | Interpolated Ground | 64746.64 | 5.22 | 489.15 | 0 | 86.43 | 0 | OK | Ground clear controls. | 147 | 121.71 | 575.58
10115 | TIN-INTERP | Interpolated Ground | 64746.66 | -6.92 | 491.47 | 0 | 89.43 | 0 | OK | Ground clear controls. | 147 | 121.71 | 580.9
10116 | TIN-INTERP | Interpolated Ground | 64746.66 | -4.98 | 491.65 | 0 | 94.92 | 0 | OK | Ground clear controls. | 147 | 121.71 | 586.57
10117 | TIN-INTERP | Interpolated Ground | 64746.72 | -5.42 | 491.52 | 0 | 83.98 | 0 | OK | Ground clear controls. | 147 | 121.71 | 575.5
10118 | TIN-INTERP | Interpolated Ground | 64786.53 | 4.8 | 466.4 | 0 | 121.7 | 0 | OK | Ground clear controls. | 147 | 121.71 | 588.1
10119 | TIN-INTERP | Interpolated Ground | 64786.59 | 6.75 | 466.1 | 0 | 116.74 | 0 | OK | Ground clear controls. | 147 | 121.71 | 582.84
10120 | TIN-INTERP | Interpolated Ground | 64786.64 | 5.25 | 466.37 | 0 | 110.89 | 0 | OK | Ground clear controls. | 147 | 121.71 | 577.26
10121 | TIN-INTERP | Interpolated Ground | 64786.66 | -6.85 | 466.88 | 0 | 115.69 | 0 | OK | Ground clear controls. | 147 | 121.71 | 582.57
10122 | TIN-INTERP | Interpolated Ground | 64786.66 | -4.91 | 466.51 | 0 | 121.71 | 0 | OK | Ground clear controls. | 147 | 121.71 | 588.22
10123 | TIN-INTERP | Interpolated Ground | 64786.72 | -5.35 | 466.57 | 0 | 110.61 | 0 | OK | Ground clear controls. | 147 | 120.61 | 577.18
10124 | TIN-INTERP | Interpolated Ground | 64826.53 | 4.82 | 477 | 0 | 113.73 | 0 | OK | Ground clear controls. | 147 | 120.61 | 590.73
10125 | TIN-INTERP | Interpolated Ground | 64826.59 | 6.77 | 477.71 | 0 | 107.8 | 0 | OK | Ground clear controls. | 147 | 120.61 | 585.51
10126 | TIN-INTERP | Interpolated Ground | 64826.64 | 5.27 | 477.28 | 0 | 102.64 | 0 | OK | Ground clear controls. | 147 | 120.61 | 579.92
10127 | TIN-INTERP | Interpolated Ground | 64826.66 | -6.79 | 470.02 | 0 | 115.21 | 0 | OK | Ground clear controls. | 147 | 120.61 | 585.23
10128 | TIN-INTERP | Interpolated Ground | 64826.66 | -4.84 | 470.24 | 0 | 120.61 | 0 | OK | Ground clear controls. | 147 | 120.61 | 590.85
10129 | TIN-INTERP | Interpolated Ground | 64826.72 | -5.29 | 470.19 | 0 | 109.65 | 0 | OK | Ground clear controls. | 147 | 109.65 | 579.84
10130 | TIN-INTERP | Interpolated Ground | 64866.53 | 4.84 | 491.35 | 0 | 103 | 0 | OK | Ground clear controls. | 147 | 107.35 | 594.35
10131 | TIN-INTERP | Interpolated Ground | 64866.59 | 6.79 | 492.6 | 0 | 96.56 | 0 | OK | Ground clear controls. | 147 | 107.35 | 589.16
10132 | TIN-INTERP | Interpolated Ground | 64866.64 | 5.29 | 491.67 | 0 | 91.9 | 0 | OK | Ground clear controls. | 147 | 107.35 | 583.57
10133 | TIN-INTERP | Interpolated Ground | 64866.66 | -6.73 | 486.74 | 0 | 102.13 | 0 | OK | Ground clear controls. | 147 | 107.35 | 588.87
10134 | TIN-INTERP | Interpolated Ground | 64866.66 | -4.77 | 487.14 | 0 | 107.35 | 0 | OK | Ground clear controls. | 147 | 107.35 | 594.49
10135 | TIN-INTERP | Interpolated Ground | 64866.72 | -5.23 | 487.07 | 0 | 96.42 | 0 | OK | Ground clear controls. | 147 | 98.21 | 583.49
10136 | TIN-INTERP | Interpolated Ground | 64906.53 | 4.86 | 508.97 | 0 | 90.01 | 0 | OK | Ground clear controls. | 147 | 98.21 | 598.98
10137 | TIN-INTERP | Interpolated Ground | 64906.59 | 6.82 | 510.06 | 0 | 83.73 | 0 | OK | Ground clear controls. | 147 | 98.21 | 593.79
10138 | TIN-INTERP | Interpolated Ground | 64906.64 | 5.31 | 509.28 | 0 | 78.93 | 0 | OK | Ground clear controls. | 147 | 98.21 | 588.21
10139 | TIN-INTERP | Interpolated Ground | 64906.66 | -6.66 | 499.35 | 0 | 94.17 | 0 | OK | Ground clear controls. | 147 | 98.21 | 593.52
10140 | TIN-INTERP | Interpolated Ground | 64906.66 | -4.7 | 500.9 | 0 | 98.21 | 0 | OK | Ground clear controls. | 147 | 98.21 | 599.11
10141 | TIN-INTERP | Interpolated Ground | 64906.72 | -5.16 | 500.54 | 0 | 87.59 | 0 | OK | Ground clear controls. | 147 | 96.63 | 588.13
10142 | TIN-INTERP | Interpolated Ground | 64946.53 | 4.87 | 515.21 | 0 | 89.39 | 0 | OK | Ground clear controls. | 147 | 96.63 | 604.6
10143 | TIN-INTERP | Interpolated Ground | 64946.59 | 6.84 | 516.64 | 0 | 82.77 | 0 | OK | Ground clear controls. | 147 | 96.63 | 599.41
10144 | TIN-INTERP | Interpolated Ground | 64946.64 | 5.34 | 515.51 | 0 | 78.33 | 0 | OK | Ground clear controls. | 147 | 96.63 | 593.84
10145 | TIN-INTERP | Interpolated Ground | 64946.66 | -6.6 | 505.84 | 0 | 93.32 | 0 | OK | Ground clear controls. | 147 | 96.63 | 599.16
10146 | TIN-INTERP | Interpolated Ground | 64946.66 | -4.63 | 508.11 | 0 | 96.63 | 0 | OK | Ground clear controls. | 147 | 96.63 | 604.74
10147 | TIN-INTERP | Interpolated Ground | 64946.72 | -5.1 | 507.56 | 0 | 86.22 | 0 | OK | Ground clear controls. | 147 | 94.78 | 593.78
10148 | TIN-INTERP | Interpolated Ground | 64986.53 | 4.89 | 516.44 | 0 | 94.78 | 0 | OK | Ground clear controls. | 147 | 94.78 | 611.22
10149 | TIN-INTERP | Interpolated Ground | 64986.59 | 6.86 | 516.27 | 0 | 89.76 | 0 | OK | Ground clear controls. | 147 | 92.36 | 606.03
10150 | TIN-INTERP | Interpolated Ground | 64986.64 | 5.36 | 516.46 | 0 | 84 | 0 | OK | Ground clear controls. | 147 | 92.36 | 600.46
10151 | TIN-INTERP | Interpolated Ground | 64986.66 | -6.53 | 520.06 | 0 | 85.74 | 0 | OK | Ground clear controls. | 147 | 92.36 | 605.8
10152 | TIN-INTERP | Interpolated Ground | 64986.66 | -4.56 | 519.01 | 0 | 92.36 | 0 | OK | Ground clear controls. | 147 | 92.36 | 611.37
10153 | TIN-INTERP | Interpolated Ground | 64986.72 | -5.04 | 519.15 | 0 | 81.26 | 0 | OK | Ground clear controls. | 147 | 81.26 | 600.41
10154 | TIN-INTERP | Interpolated Ground | 65026.53 | 4.91 | 541.13 | 0 | 77.73 | 0 | OK | Ground clear controls. | 147 | 77.73 | 618.86
10155 | TIN-INTERP | Interpolated Ground | 65026.59 | 6.88 | 540.67 | 0 | 72.96 | 0 | OK | Ground clear controls. | 147 | 74.48 | 613.63
10156 | TIN-INTERP | Interpolated Ground | 65026.64 | 5.38 | 540.98 | 0 | 67.09 | 0 | OK | Ground clear controls. | 147 | 74.48 | 608.07
10157 | TIN-INTERP | Interpolated Ground | 65026.66 | -6.47 | 545.43 | 0 | 68.02 | 0 | OK | Ground clear controls. | 147 | 74.48 | 613.45
10158 | TIN-INTERP | Interpolated Ground | 65026.66 | -4.49 | 544.52 | 0 | 74.48 | 0 | OK | Ground clear controls. | 147 | 74.48 | 619
10159 | TIN-INTERP | Interpolated Ground | 65026.72 | -4.97 | 544.69 | 0 | 63.36 | 0 | OK | Ground clear controls. | 147 | 65.23 | 608.05
10160 | TIN-INTERP | Interpolated Ground | 65066.53 | 4.92 | 562.27 | 0 | 65.23 | 0 | OK | Ground clear controls. | 147 | 65.23 | 627.5
10161 | TIN-INTERP | Interpolated Ground | 65066.59 | 6.91 | 561.98 | 0 | 60.25 | 0 | OK | Ground clear controls. | 147 | 63.14 | 622.23
10162 | TIN-INTERP | Interpolated Ground | 65066.64 | 5.4 | 562.22 | 0 | 54.48 | 0 | OK | Ground clear controls. | 147 | 63.14 | 616.7
10163 | TIN-INTERP | Interpolated Ground | 65066.66 | -6.4 | 565.17 | 0 | 56.94 | 0 | OK | Ground clear controls. | 147 | 63.14 | 622.11
10164 | TIN-INTERP | Interpolated Ground | 65066.66 | -4.42 | 564.49 | 0 | 63.14 | 0 | OK | Ground clear controls. | 147 | 63.14 | 627.63
10165 | TIN-INTERP | Interpolated Ground | 65066.72 | -4.91 | 564.72 | 0 | 51.97 | 0 | OK | Ground clear controls. | 147 | 51.97 | 616.69
10166 | TIN-INTERP | Interpolated Ground | 65106.53 | 4.94 | 586.35 | 0 | 50.82 | 0 | OK | Ground clear controls. | 147 | 50.82 | 637.17
10167 | TIN-INTERP | Interpolated Ground | 65106.59 | 6.93 | 585.67 | 0 | 46.17 | 0 | OK | Ground clear controls. | 147 | 48 | 631.84
10168 | TIN-INTERP | Interpolated Ground | 65106.64 | 5.43 | 586.25 | 0 | 40.07 | 0 | OK | Ground clear controls. | 147 | 48 | 626.32
10169 | TIN-INTERP | Interpolated Ground | 65106.65 | -6.34 | 590 | 0 | 41.78 | 0 | OK | Ground clear controls. | 147 | 48 | 631.78
10170 | TIN-INTERP | Interpolated Ground | 65106.66 | -4.35 | 589.3 | 0 | 48 | 0 | OK | Ground clear controls. | 147 | 48 | 637.3
10171 | TIN-INTERP | Interpolated Ground | 65106.72 | -4.84 | 589.51 | 0 | 36.84 | 0 | OK | Ground clear controls. | 147 | 36.84 | 626.35
10172 | TIN-INTERP | Interpolated Ground | 65146.53 | 4.96 | 615.76 | 0 | 32.11 | 0 | OK | Ground clear controls. | 147 | 32.11 | 647.87
10173 | TIN-INTERP | Interpolated Ground | 65146.59 | 6.95 | 615.28 | 0 | 27.18 | 0 | OK | Ground clear controls. | 147 | 28.69 | 642.46
10174 | TIN-INTERP | Interpolated Ground | 65146.64 | 5.45 | 615.54 | 0 | 21.43 | 0 | OK | Ground clear controls. | 147 | 28.69 | 636.97
10175 | TIN-INTERP | Interpolated Ground | 65146.65 | -6.27 | 619.3 | 0 | 23.18 | 0 | OK | Ground clear controls. | 147 | 28.69 | 642.48
10176 | TIN-INTERP | Interpolated Ground | 65146.66 | -4.28 | 619.29 | 0 | 28.69 | 0 | OK | Ground clear controls. | 147 | 28.69 | 647.98
10177 | TIN-INTERP | Interpolated Ground | 65146.72 | -4.78 | 619.3 | 0 | 17.73 | 0 | OK | Ground clear controls. | 147 | 17.73 | 637.03
10178 | TIN-INTERP | Interpolated Ground | 65169.25 | -4.74 | 627.5 | 0 | 15.98 | 0 | OK | Ground clear controls. | 148 | 77.07 | 643.48
10179 | TIN-INTERP | Interpolated Ground | 65169.27 | -6.24 | 627.48 | 0 | 21.51 | 0 | OK | Ground clear controls. | 148 | 77.07 | 648.99
10180 | TIN-INTERP | Interpolated Ground | 65169.27 | -4.24 | 627.54 | 0 | 26.95 | 0 | OK | Ground clear controls. | 148 | 77.07 | 654.49
10181 | TIN-INTERP | Interpolated Ground | 65169.7 | 5.45 | 627.3 | 0 | 16.18 | 0 | OK | Ground clear controls. | 148 | 77.07 | 643.48
10182 | TIN-INTERP | Interpolated Ground | 65169.83 | 4.95 | 627.1 | 0 | 27.4 | 0 | OK | Ground clear controls. | 148 | 77.07 | 654.5
10183 | TIN-INTERP | Interpolated Ground | 65169.84 | 6.95 | 627.07 | 0 | 21.91 | 0 | OK | Ground clear controls. | 148 | 77.07 | 648.98
10184 | TIN-INTERP | Interpolated Ground | 65209.02 | -4.78 | 613.12 | 0 | 29.1 | 0 | OK | Ground clear controls. | 148 | 77.07 | 642.22
10185 | TIN-INTERP | Interpolated Ground | 65209.06 | -6.27 | 613.89 | 0 | 33.94 | 0 | OK | Ground clear controls. | 148 | 77.07 | 647.83
10186 | TIN-INTERP | Interpolated Ground | 65209.14 | -4.28 | 612.86 | 0 | 40.42 | 0 | OK | Ground clear controls. | 148 | 77.07 | 653.28
10187 | TIN-INTERP | Interpolated Ground | 65209.7 | 5.41 | 607.7 | 0 | 34.55 | 0 | OK | Ground clear controls. | 148 | 77.07 | 642.25
10188 | TIN-INTERP | Interpolated Ground | 65209.83 | 4.91 | 607.82 | 0 | 45.51 | 0 | OK | Ground clear controls. | 148 | 77.07 | 653.33
10189 | TIN-INTERP | Interpolated Ground | 65209.84 | 6.91 | 607.19 | 0 | 40.62 | 0 | OK | Ground clear controls. | 148 | 77.07 | 647.81
10190 | TIN-INTERP | Interpolated Ground | 65249.02 | -4.81 | 612.28 | 0 | 29.67 | 0 | OK | Ground clear controls. | 148 | 77.07 | 641.95
10191 | TIN-INTERP | Interpolated Ground | 65249.06 | -6.31 | 613.18 | 0 | 34.44 | 0 | OK | Ground clear controls. | 148 | 77.07 | 647.62
10192 | TIN-INTERP | Interpolated Ground | 65249.14 | -4.32 | 611.99 | 0 | 41.04 | 0 | OK | Ground clear controls. | 148 | 77.07 | 653.03
10193 | TIN-INTERP | Interpolated Ground | 65249.7 | 5.37 | 606.85 | 0 | 35.14 | 0 | OK | Ground clear controls. | 148 | 77.07 | 641.99
10194 | TIN-INTERP | Interpolated Ground | 65249.83 | 4.87 | 607.02 | 0 | 46.09 | 0 | OK | Ground clear controls. | 148 | 77.07 | 653.11
10195 | TIN-INTERP | Interpolated Ground | 65249.84 | 6.87 | 606.02 | 0 | 41.57 | 0 | OK | Ground clear controls. | 148 | 77.07 | 647.59
10196 | TIN-INTERP | Interpolated Ground | 65289.02 | -4.85 | 610.67 | 0 | 31.97 | 0 | OK | Ground clear controls. | 148 | 77.07 | 642.64
10197 | TIN-INTERP | Interpolated Ground | 65289.06 | -6.35 | 611.6 | 0 | 36.77 | 0 | OK | Ground clear controls. | 148 | 77.07 | 648.37
10198 | TIN-INTERP | Interpolated Ground | 65289.14 | -4.35 | 610.5 | 0 | 43.25 | 0 | OK | Ground clear controls. | 148 | 77.07 | 653.75
10199 | TIN-INTERP | Interpolated Ground | 65289.7 | 5.34 | 604.15 | 0 | 38.55 | 0 | OK | Ground clear controls. | 148 | 77.07 | 642.7
10200 | TIN-INTERP | Interpolated Ground | 65289.83 | 4.84 | 604.4 | 0 | 49.47 | 0 | OK | Ground clear controls. | 148 | 77.07 | 653.87
10201 | TIN-INTERP | Interpolated Ground | 65289.84 | 6.84 | 603.31 | 0 | 45.02 | 0 | OK | Ground clear controls. | 148 | 77.07 | 648.33
10202 | TIN-INTERP | Interpolated Ground | 65329.02 | -4.89 | 611.59 | 0 | 32.72 | 0 | OK | Ground clear controls. | 148 | 77.07 | 644.31
10203 | TIN-INTERP | Interpolated Ground | 65329.06 | -6.39 | 612.38 | 0 | 37.71 | 0 | OK | Ground clear controls. | 148 | 77.07 | 650.09
10204 | TIN-INTERP | Interpolated Ground | 65329.14 | -4.39 | 611.42 | 0 | 44.02 | 0 | OK | Ground clear controls. | 148 | 77.07 | 655.44
10205 | TIN-INTERP | Interpolated Ground | 65329.7 | 5.3 | 606.95 | 0 | 37.43 | 0 | OK | Ground clear controls. | 148 | 77.07 | 644.38
10206 | TIN-INTERP | Interpolated Ground | 65329.83 | 4.8 | 607.16 | 0 | 48.43 | 0 | OK | Ground clear controls. | 148 | 77.07 | 655.59
10207 | TIN-INTERP | Interpolated Ground | 65329.84 | 6.8 | 606.4 | 0 | 43.64 | 0 | OK | Ground clear controls. | 148 | 77.07 | 650.04
10208 | TIN-INTERP | Interpolated Ground | 65369.02 | -4.93 | 631.88 | 0 | 15.07 | 0 | OK | Ground clear controls. | 148 | 77.07 | 646.95
10209 | TIN-INTERP | Interpolated Ground | 65369.06 | -6.42 | 632.55 | 0 | 20.2 | 0 | OK | Ground clear controls. | 148 | 77.07 | 652.75
10210 | TIN-INTERP | Interpolated Ground | 65369.14 | -4.43 | 631.5 | 0 | 26.6 | 0 | OK | Ground clear controls. | 148 | 77.07 | 658.1
10211 | TIN-INTERP | Interpolated Ground | 65369.7 | 5.26 | 626.09 | 0 | 20.94 | 0 | OK | Ground clear controls. | 148 | 77.07 | 647.03
10212 | TIN-INTERP | Interpolated Ground | 65369.83 | 4.76 | 626.3 | 0 | 31.96 | 0 | OK | Ground clear controls. | 148 | 77.07 | 658.26
10213 | TIN-INTERP | Interpolated Ground | 65369.84 | 6.76 | 625.12 | 0 | 27.6 | 0 | OK | Ground clear controls. | 148 | 77.07 | 652.72
10214 | TIN-INTERP | Interpolated Ground | 65409.02 | -4.96 | 615.47 | 0 | 35.1 | 0 | OK | Ground clear controls. | 148 | 77.07 | 650.57
10215 | TIN-INTERP | Interpolated Ground | 65409.06 | -6.46 | 615.69 | 0 | 40.7 | 0 | OK | Ground clear controls. | 148 | 77.07 | 656.39
10216 | TIN-INTERP | Interpolated Ground | 65409.14 | -4.46 | 615.21 | 0 | 46.52 | 0 | OK | Ground clear controls. | 148 | 77.07 | 661.73
10217 | TIN-INTERP | Interpolated Ground | 65409.7 | 5.23 | 612.54 | 0 | 38.12 | 0 | OK | Ground clear controls. | 148 | 77.07 | 650.66
10218 | TIN-INTERP | Interpolated Ground | 65409.83 | 4.73 | 612.66 | 0 | 49.25 | 0 | OK | Ground clear controls. | 148 | 77.07 | 661.91
10219 | TIN-INTERP | Interpolated Ground | 65409.84 | 6.73 | 611.5 | 0 | 44.85 | 0 | OK | Ground clear controls. | 148 | 77.07 | 656.35
10220 | TIN-INTERP | Interpolated Ground | 65449.02 | -5 | 589.73 | 0 | 65.45 | 0 | OK | Ground clear controls. | 148 | 77.07 | 655.18
10221 | TIN-INTERP | Interpolated Ground | 65449.06 | -6.5 | 590.97 | 0 | 70.01 | 0 | OK | Ground clear controls. | 148 | 77.07 | 660.98
10222 | TIN-INTERP | Interpolated Ground | 65449.14 | -4.5 | 589.26 | 0 | 77.07 | 0 | OK | Ground clear controls. | 148 | 77.07 | 666.33
10223 | TIN-INTERP | Interpolated Ground | 65449.7 | 5.19 | 589.22 | 0 | 66.06 | 0 | OK | Ground clear controls. | 148 | 77.04 | 655.28
10224 | TIN-INTERP | Interpolated Ground | 65449.83 | 4.69 | 589.47 | 0 | 77.04 | 0 | OK | Ground clear controls. | 148 | 77.04 | 666.51
10225 | TIN-INTERP | Interpolated Ground | 65449.84 | 6.69 | 588.68 | 0 | 72.28 | 0 | OK | Ground clear controls. | 148 | 72.28 | 660.96
10226 | TIN-INTERP | Interpolated Ground | 65489.02 | -5.04 | 605.89 | 0 | 54.87 | 0 | OK | Ground clear controls. | 148 | 66.1 | 660.76
10227 | TIN-INTERP | Interpolated Ground | 65489.06 | -6.54 | 606.95 | 0 | 59.6 | 0 | OK | Ground clear controls. | 148 | 66.1 | 666.55
10228 | TIN-INTERP | Interpolated Ground | 65489.14 | -4.54 | 605.81 | 0 | 66.1 | 0 | OK | Ground clear controls. | 148 | 66.1 | 671.91
10229 | TIN-INTERP | Interpolated Ground | 65489.7 | 5.15 | 610.13 | 0 | 50.74 | 0 | OK | Ground clear controls. | 148 | 62.11 | 660.87
10230 | TIN-INTERP | Interpolated Ground | 65489.83 | 4.65 | 609.99 | 0 | 62.11 | 0 | OK | Ground clear controls. | 148 | 62.11 | 672.1
10231 | TIN-INTERP | Interpolated Ground | 65489.84 | 6.65 | 610.77 | 0 | 55.77 | 0 | OK | Ground clear controls. | 148 | 55.77 | 666.54
10232 | TIN-INTERP | Interpolated Ground | 65529.02 | -5.08 | 632.39 | 0 | 34.94 | 0 | OK | Ground clear controls. | 148 | 45.95 | 667.33
10233 | TIN-INTERP | Interpolated Ground | 65529.06 | -6.57 | 632.25 | 0 | 40.84 | 0 | OK | Ground clear controls. | 148 | 45.95 | 673.09
10234 | TIN-INTERP | Interpolated Ground | 65529.14 | -4.58 | 632.52 | 0 | 45.95 | 0 | OK | Ground clear controls. | 148 | 45.95 | 678.47
10235 | TIN-INTERP | Interpolated Ground | 65529.7 | 5.12 | 633.71 | 0 | 33.74 | 0 | OK | Ground clear controls. | 148 | 44.86 | 667.45
10236 | TIN-INTERP | Interpolated Ground | 65529.83 | 4.62 | 633.79 | 0 | 44.86 | 0 | OK | Ground clear controls. | 148 | 44.86 | 678.65
10237 | TIN-INTERP | Interpolated Ground | 65529.84 | 6.62 | 634.02 | 0 | 39.09 | 0 | OK | Ground clear controls. | 148 | 39.09 | 673.11
10238 | TIN-INTERP | Interpolated Ground | 65569.02 | -5.11 | 655.19 | 0 | 19.7 | 0 | OK | Ground clear controls. | 148 | 32.33 | 674.89
10239 | TIN-INTERP | Interpolated Ground | 65569.06 | -6.61 | 655.17 | 0 | 25.44 | 0 | OK | Ground clear controls. | 148 | 32.33 | 680.61
10240 | TIN-INTERP | Interpolated Ground | 65569.14 | -4.61 | 655.25 | 0 | 30.76 | 0 | OK | Ground clear controls. | 148 | 32.33 | 686.01
10241 | TIN-INTERP | Interpolated Ground | 65569.7 | 5.08 | 656.15 | 0 | 18.87 | 0 | OK | Ground clear controls. | 148 | 32.33 | 675.02
10242 | TIN-INTERP | Interpolated Ground | 65569.83 | 4.58 | 656.22 | 0 | 29.97 | 0 | OK | Ground clear controls. | 148 | 32.33 | 686.19
10243 | TIN-INTERP | Interpolated Ground | 65569.84 | 6.58 | 656.35 | 0 | 24.29 | 0 | OK | Ground clear controls. | 148 | 32.33 | 680.64
10244 | TIN-INTERP | Interpolated Ground | 65609.02 | -5.15 | 673.21 | 0 | 10.24 | 0 | OK | Ground clear controls. | 148 | 32.33 | 683.45
10245 | TIN-INTERP | Interpolated Ground | 65609.06 | -6.65 | 673.03 | 0 | 16.07 | 0 | OK | Ground clear controls. | 148 | 32.33 | 689.1
10246 | TIN-INTERP | Interpolated Ground | 65609.14 | -4.65 | 673.27 | 0 | 21.27 | 0 | OK | Ground clear controls. | 148 | 32.33 | 694.54
10247 | TIN-INTERP | Interpolated Ground | 65609.7 | 5.04 | 672.27 | 0 | 11.31 | 0 | OK | Ground clear controls. | 148 | 32.33 | 683.58
10248 | TIN-INTERP | Interpolated Ground | 65609.83 | 4.54 | 672.33 | 0 | 22.36 | 0 | OK | Ground clear controls. | 148 | 32.33 | 694.69
10249 | TIN-INTERP | Interpolated Ground | 65609.84 | 6.54 | 672.06 | 0 | 17.1 | 0 | OK | Ground clear controls. | 148 | 32.33 | 689.16
10250 | TIN-INTERP | Interpolated Ground | 65649.02 | -5.19 | 671.77 | 0 | 21.24 | 0 | OK | Ground clear controls. | 148 | 32.33 | 693.01
10251 | TIN-INTERP | Interpolated Ground | 65649.06 | -6.69 | 671.95 | 0 | 26.61 | 0 | OK | Ground clear controls. | 148 | 32.33 | 698.56
10252 | TIN-INTERP | Interpolated Ground | 65649.14 | -4.69 | 671.72 | 0 | 32.33 | 0 | OK | Ground clear controls. | 148 | 32.33 | 704.05
10253 | TIN-INTERP | Interpolated Ground | 65649.7 | 5.01 | 672.01 | 0 | 21.13 | 0 | OK | Ground clear controls. | 148 | 32.19 | 693.14
10254 | TIN-INTERP | Interpolated Ground | 65649.83 | 4.51 | 672 | 0 | 32.19 | 0 | OK | Ground clear controls. | 148 | 32.19 | 704.19
10255 | TIN-INTERP | Interpolated Ground | 65649.84 | 6.51 | 672.09 | 0 | 26.59 | 0 | OK | Ground clear controls. | 148 | 26.59 | 698.68
10256 | TIN-INTERP | Interpolated Ground | 65652.74 | -6.69 | 671.71 | 0 | 27.77 | 0 | OK | Ground clear controls. | 149 | 43.8 | 699.48
10257 | TIN-INTERP | Interpolated Ground | 65652.87 | -4.69 | 671.74 | 0 | 33.24 | 0 | OK | Ground clear controls. | 149 | 43.8 | 704.98
10258 | TIN-INTERP | Interpolated Ground | 65652.91 | -5.19 | 671.73 | 0 | 22.26 | 0 | OK | Ground clear controls. | 149 | 43.8 | 693.99
10259 | TIN-INTERP | Interpolated Ground | 65653 | 4.51 | 672.14 | 0 | 32.85 | 0 | OK | Ground clear controls. | 149 | 43.8 | 704.99
10260 | TIN-INTERP | Interpolated Ground | 65653.06 | 5.01 | 672.17 | 0 | 21.81 | 0 | OK | Ground clear controls. | 149 | 43.8 | 693.98
10261 | TIN-INTERP | Interpolated Ground | 65653.08 | 6.5 | 672.26 | 0 | 27.22 | 0 | OK | Ground clear controls. | 149 | 43.8 | 699.48
10262 | TIN-INTERP | Interpolated Ground | 65692.74 | -6.68 | 665.59 | 0 | 28.33 | 0 | OK | Ground clear controls. | 149 | 43.8 | 693.92
10263 | TIN-INTERP | Interpolated Ground | 65692.87 | -4.68 | 665.85 | 0 | 33.58 | 0 | OK | Ground clear controls. | 149 | 43.8 | 699.43
10264 | TIN-INTERP | Interpolated Ground | 65692.91 | -5.18 | 665.8 | 0 | 22.64 | 0 | OK | Ground clear controls. | 149 | 43.8 | 688.44
10265 | TIN-INTERP | Interpolated Ground | 65693 | 4.52 | 668.25 | 0 | 31.14 | 0 | OK | Ground clear controls. | 149 | 43.8 | 699.39
10266 | TIN-INTERP | Interpolated Ground | 65693.06 | 5.02 | 668.34 | 0 | 20.03 | 0 | OK | Ground clear controls. | 149 | 43.8 | 688.37
10267 | TIN-INTERP | Interpolated Ground | 65693.08 | 6.52 | 668.64 | 0 | 25.26 | 0 | OK | Ground clear controls. | 149 | 43.8 | 693.9
10268 | TIN-INTERP | Interpolated Ground | 65732.74 | -6.66 | 652.26 | 0 | 37.04 | 0 | OK | Ground clear controls. | 149 | 43.8 | 689.3
10269 | TIN-INTERP | Interpolated Ground | 65732.87 | -4.66 | 652.63 | 0 | 42.2 | 0 | OK | Ground clear controls. | 149 | 43.8 | 694.83
10270 | TIN-INTERP | Interpolated Ground | 65732.91 | -5.16 | 652.46 | 0 | 31.37 | 0 | OK | Ground clear controls. | 149 | 43.8 | 683.83
10271 | TIN-INTERP | Interpolated Ground | 65733 | 4.54 | 657.56 | 0 | 37.19 | 0 | OK | Ground clear controls. | 149 | 43.8 | 694.75
10272 | TIN-INTERP | Interpolated Ground | 65733.06 | 5.04 | 657.81 | 0 | 25.92 | 0 | OK | Ground clear controls. | 149 | 43.8 | 683.73
10273 | TIN-INTERP | Interpolated Ground | 65733.08 | 6.53 | 658.83 | 0 | 30.43 | 0 | OK | Ground clear controls. | 149 | 43.8 | 689.26
10274 | TIN-INTERP | Interpolated Ground | 65772.74 | -6.65 | 652.45 | 0 | 33.18 | 0 | OK | Ground clear controls. | 149 | 43.8 | 685.63
10275 | TIN-INTERP | Interpolated Ground | 65772.87 | -4.65 | 651.46 | 0 | 39.69 | 0 | OK | Ground clear controls. | 149 | 43.8 | 691.15
10276 | TIN-INTERP | Interpolated Ground | 65772.91 | -5.15 | 651.72 | 0 | 28.45 | 0 | OK | Ground clear controls. | 149 | 43.8 | 680.17
10277 | TIN-INTERP | Interpolated Ground | 65773 | 4.55 | 647.27 | 0 | 43.8 | 0 | OK | Ground clear controls. | 149 | 43.8 | 691.07
10278 | TIN-INTERP | Interpolated Ground | 65773.06 | 5.05 | 646.94 | 0 | 33.1 | 0 | OK | Ground clear controls. | 149 | 38.56 | 680.04
10279 | TIN-INTERP | Interpolated Ground | 65773.08 | 6.55 | 647.02 | 0 | 38.56 | 0 | OK | Ground clear controls. | 149 | 38.56 | 685.58
10280 | TIN-INTERP | Interpolated Ground | 65812.74 | -6.63 | 658.18 | 0 | 24.72 | 0 | OK | Ground clear controls. | 149 | 35.05 | 682.9
10281 | TIN-INTERP | Interpolated Ground | 65812.87 | -4.64 | 657.7 | 0 | 30.73 | 0 | OK | Ground clear controls. | 149 | 35.05 | 688.43
10282 | TIN-INTERP | Interpolated Ground | 65812.91 | -5.13 | 657.83 | 0 | 19.61 | 0 | OK | Ground clear controls. | 149 | 35.05 | 677.44
10283 | TIN-INTERP | Interpolated Ground | 65813 | 4.57 | 653.29 | 0 | 35.05 | 0 | OK | Ground clear controls. | 149 | 35.05 | 688.34
10284 | TIN-INTERP | Interpolated Ground | 65813.06 | 5.07 | 652.81 | 0 | 24.5 | 0 | OK | Ground clear controls. | 149 | 31.22 | 677.31
10285 | TIN-INTERP | Interpolated Ground | 65813.08 | 6.56 | 651.64 | 0 | 31.22 | 0 | OK | Ground clear controls. | 149 | 31.22 | 682.86
10286 | TIN-INTERP | Interpolated Ground | 65852.74 | -6.62 | 657.47 | 0 | 23.66 | 0 | OK | Ground clear controls. | 149 | 29.84 | 681.13
10287 | TIN-INTERP | Interpolated Ground | 65852.87 | -4.62 | 657.29 | 0 | 29.35 | 0 | OK | Ground clear controls. | 149 | 29.84 | 686.64
10288 | TIN-INTERP | Interpolated Ground | 65852.91 | -5.12 | 657.34 | 0 | 18.32 | 0 | OK | Ground clear controls. | 149 | 29.84 | 675.66
10289 | TIN-INTERP | Interpolated Ground | 65853 | 4.59 | 656.73 | 0 | 29.84 | 0 | OK | Ground clear controls. | 149 | 29.84 | 686.57
10290 | TIN-INTERP | Interpolated Ground | 65853.06 | 5.08 | 656.74 | 0 | 18.8 | 0 | OK | Ground clear controls. | 149 | 27.28 | 675.54
10291 | TIN-INTERP | Interpolated Ground | 65853.08 | 6.58 | 656.75 | 0 | 24.33 | 0 | OK | Ground clear controls. | 149 | 27.28 | 681.08
10292 | TIN-INTERP | Interpolated Ground | 65892.74 | -6.6 | 659.82 | 0 | 20.47 | 0 | OK | Ground clear controls. | 149 | 27.28 | 680.29
10293 | TIN-INTERP | Interpolated Ground | 65892.87 | -4.61 | 659.57 | 0 | 26.24 | 0 | OK | Ground clear controls. | 149 | 27.28 | 685.81
10294 | TIN-INTERP | Interpolated Ground | 65892.91 | -5.1 | 659.62 | 0 | 15.2 | 0 | OK | Ground clear controls. | 149 | 27.28 | 674.82
10295 | TIN-INTERP | Interpolated Ground | 65893 | 4.6 | 658.45 | 0 | 27.28 | 0 | OK | Ground clear controls. | 149 | 27.28 | 685.73
10296 | TIN-INTERP | Interpolated Ground | 65893.06 | 5.1 | 658.47 | 0 | 16.25 | 0 | OK | Ground clear controls. | 149 | 24.89 | 674.72
10297 | TIN-INTERP | Interpolated Ground | 65893.08 | 6.59 | 658.43 | 0 | 21.82 | 0 | OK | Ground clear controls. | 149 | 24.89 | 680.25
10298 | TIN-INTERP | Interpolated Ground | 65932.74 | -6.59 | 662.14 | 0 | 18.26 | 0 | OK | Ground clear controls. | 149 | 24.89 | 680.4
10299 | TIN-INTERP | Interpolated Ground | 65932.87 | -4.59 | 662.04 | 0 | 23.86 | 0 | OK | Ground clear controls. | 149 | 24.89 | 685.9
10300 | TIN-INTERP | Interpolated Ground | 65932.91 | -5.09 | 662.06 | 0 | 12.85 | 0 | OK | Ground clear controls. | 149 | 24.89 | 674.91
10301 | TIN-INTERP | Interpolated Ground | 65933 | 4.62 | 660.97 | 0 | 24.89 | 0 | OK | Ground clear controls. | 149 | 24.89 | 685.86
10302 | TIN-INTERP | Interpolated Ground | 65933.06 | 5.11 | 660.92 | 0 | 13.93 | 0 | OK | Ground clear controls. | 149 | 19.66 | 674.85
10303 | TIN-INTERP | Interpolated Ground | 65933.08 | 6.61 | 660.71 | 0 | 19.66 | 0 | OK | Ground clear controls. | 149 | 19.66 | 680.37
10304 | TIN-INTERP | Interpolated Ground | 65960.07 | -6.58 | 661.22 | 0 | 19.79 | 0 | OK | Ground clear controls. | 150 | 38.74 | 681.01
10305 | TIN-INTERP | Interpolated Ground | 65960.15 | -5.08 | 661.12 | 0 | 14.39 | 0 | OK | Ground clear controls. | 150 | 38.74 | 675.51
10306 | TIN-INTERP | Interpolated Ground | 65960.31 | -4.59 | 661.08 | 0 | 25.43 | 0 | OK | Ground clear controls. | 150 | 38.74 | 686.51
10307 | TIN-INTERP | Interpolated Ground | 65960.91 | 5.12 | 661.04 | 0 | 14.47 | 0 | OK | Ground clear controls. | 150 | 38.74 | 675.51
10308 | TIN-INTERP | Interpolated Ground | 65960.94 | 4.63 | 661.03 | 0 | 25.48 | 0 | OK | Ground clear controls. | 150 | 38.74 | 686.51
10309 | TIN-INTERP | Interpolated Ground | 65961.1 | 6.62 | 660.89 | 0 | 20.12 | 0 | OK | Ground clear controls. | 150 | 38.74 | 681.01
10310 | TIN-INTERP | Interpolated Ground | 66000.02 | -6.7 | 657.68 | 0 | 17.64 | 0 | OK | Ground clear controls. | 150 | 38.74 | 675.32
10311 | TIN-INTERP | Interpolated Ground | 66000.11 | -5.21 | 657.56 | 0 | 12.27 | 0 | OK | Ground clear controls. | 150 | 38.74 | 669.83
10312 | TIN-INTERP | Interpolated Ground | 66000.28 | -4.73 | 657.53 | 0 | 23.38 | 0 | OK | Ground clear controls. | 150 | 38.74 | 680.91
10313 | TIN-INTERP | Interpolated Ground | 66000.91 | 5.08 | 657.33 | 0 | 12.47 | 0 | OK | Ground clear controls. | 150 | 38.74 | 669.8
10314 | TIN-INTERP | Interpolated Ground | 66000.94 | 4.6 | 657.33 | 0 | 23.53 | 0 | OK | Ground clear controls. | 150 | 38.74 | 680.86
10315 | TIN-INTERP | Interpolated Ground | 66001.1 | 6.57 | 657.22 | 0 | 18.1 | 0 | OK | Ground clear controls. | 150 | 38.74 | 675.32
10316 | TIN-INTERP | Interpolated Ground | 66040.02 | -6.83 | 652.19 | 0 | 18.41 | 0 | OK | Ground clear controls. | 150 | 38.74 | 670.6
10317 | TIN-INTERP | Interpolated Ground | 66040.11 | -5.33 | 652.31 | 0 | 12.81 | 0 | OK | Ground clear controls. | 150 | 38.74 | 665.12
10318 | TIN-INTERP | Interpolated Ground | 66040.28 | -4.87 | 652.32 | 0 | 23.93 | 0 | OK | Ground clear controls. | 150 | 38.74 | 676.25
10319 | TIN-INTERP | Interpolated Ground | 66040.91 | 5.03 | 652.34 | 0 | 12.7 | 0 | OK | Ground clear controls. | 150 | 38.74 | 665.04
10320 | TIN-INTERP | Interpolated Ground | 66040.94 | 4.57 | 652.39 | 0 | 23.79 | 0 | OK | Ground clear controls. | 150 | 38.74 | 676.18
10321 | TIN-INTERP | Interpolated Ground | 66041.1 | 6.53 | 652.36 | 0 | 18.24 | 0 | OK | Ground clear controls. | 150 | 38.74 | 670.6
10322 | TIN-INTERP | Interpolated Ground | 66080.02 | -6.96 | 650.14 | 0 | 16.68 | 0 | OK | Ground clear controls. | 150 | 38.74 | 666.82
10323 | TIN-INTERP | Interpolated Ground | 66080.11 | -5.46 | 650.05 | 0 | 11.29 | 0 | OK | Ground clear controls. | 150 | 38.74 | 661.34
10324 | TIN-INTERP | Interpolated Ground | 66080.28 | -5.01 | 649.97 | 0 | 22.55 | 0 | OK | Ground clear controls. | 150 | 38.74 | 672.52
10325 | TIN-INTERP | Interpolated Ground | 66080.91 | 4.99 | 649.09 | 0 | 12.16 | 0 | OK | Ground clear controls. | 150 | 38.74 | 661.25
10326 | TIN-INTERP | Interpolated Ground | 66080.94 | 4.53 | 649.14 | 0 | 23.3 | 0 | OK | Ground clear controls. | 150 | 38.74 | 672.44
10327 | TIN-INTERP | Interpolated Ground | 66081.1 | 6.49 | 648.92 | 0 | 17.91 | 0 | OK | Ground clear controls. | 150 | 38.74 | 666.83
10328 | TIN-INTERP | Interpolated Ground | 66120.02 | -7.09 | 644.21 | 0 | 19.78 | 0 | OK | Ground clear controls. | 150 | 38.74 | 663.99
10329 | TIN-INTERP | Interpolated Ground | 66120.11 | -5.59 | 644.27 | 0 | 14.25 | 0 | OK | Ground clear controls. | 150 | 38.74 | 658.52
10330 | TIN-INTERP | Interpolated Ground | 66120.28 | -5.15 | 644.26 | 0 | 25.48 | 0 | OK | Ground clear controls. | 150 | 38.74 | 669.74
10331 | TIN-INTERP | Interpolated Ground | 66120.91 | 4.95 | 644.38 | 0 | 14.05 | 0 | OK | Ground clear controls. | 150 | 38.74 | 658.43
10332 | TIN-INTERP | Interpolated Ground | 66120.94 | 4.5 | 644.45 | 0 | 25.22 | 0 | OK | Ground clear controls. | 150 | 38.74 | 669.67
10333 | TIN-INTERP | Interpolated Ground | 66121.1 | 6.44 | 644.03 | 0 | 19.96 | 0 | OK | Ground clear controls. | 150 | 38.74 | 663.99
10334 | TIN-INTERP | Interpolated Ground | 66160.02 | -7.22 | 635.92 | 0 | 26.2 | 0 | OK | Ground clear controls. | 150 | 38.74 | 662.12
10335 | TIN-INTERP | Interpolated Ground | 66160.11 | -5.71 | 636.3 | 0 | 20.34 | 0 | OK | Ground clear controls. | 150 | 38.74 | 656.64
10336 | TIN-INTERP | Interpolated Ground | 66160.28 | -5.29 | 636.39 | 0 | 31.51 | 0 | OK | Ground clear controls. | 150 | 38.74 | 667.9
10337 | TIN-INTERP | Interpolated Ground | 66160.91 | 4.9 | 637.01 | 0 | 19.56 | 0 | OK | Ground clear controls. | 150 | 38.74 | 656.57
10338 | TIN-INTERP | Interpolated Ground | 66160.94 | 4.47 | 637.08 | 0 | 30.75 | 0 | OK | Ground clear controls. | 150 | 38.74 | 667.83
10339 | TIN-INTERP | Interpolated Ground | 66161.1 | 6.4 | 636.58 | 0 | 25.54 | 0 | OK | Ground clear controls. | 150 | 38.74 | 662.12
10340 | TIN-INTERP | Interpolated Ground | 66200.02 | -7.34 | 628.78 | 0 | 32.4 | 0 | OK | Ground clear controls. | 150 | 38.74 | 661.18
10341 | TIN-INTERP | Interpolated Ground | 66200.11 | -5.84 | 629.01 | 0 | 26.7 | 0 | OK | Ground clear controls. | 150 | 38.74 | 655.71
10342 | TIN-INTERP | Interpolated Ground | 66200.28 | -5.43 | 629.04 | 0 | 37.95 | 0 | OK | Ground clear controls. | 150 | 38.74 | 666.99
10343 | TIN-INTERP | Interpolated Ground | 66200.91 | 4.86 | 628.19 | 0 | 27.48 | 0 | OK | Ground clear controls. | 150 | 38.74 | 655.67
10344 | TIN-INTERP | Interpolated Ground | 66200.94 | 4.44 | 628.22 | 0 | 38.74 | 0 | OK | Ground clear controls. | 150 | 38.74 | 666.96
10345 | TIN-INTERP | Interpolated Ground | 66201.1 | 6.35 | 627.72 | 0 | 33.47 | 0 | OK | Ground clear controls. | 150 | 33.47 | 661.19
10346 | TIN-INTERP | Interpolated Ground | 66225.28 | -5.92 | 622.75 | 0 | 32.85 | 0 | OK | Ground clear controls. | 151 | 66.29 | 655.6
10347 | TIN-INTERP | Interpolated Ground | 66225.33 | -5.52 | 622.92 | 0 | 43.98 | 0 | OK | Ground clear controls. | 151 | 66.29 | 666.9
10348 | TIN-INTERP | Interpolated Ground | 66225.34 | -7.43 | 622.16 | 0 | 38.93 | 0 | OK | Ground clear controls. | 151 | 66.29 | 661.09
10349 | TIN-INTERP | Interpolated Ground | 66225.91 | 4.43 | 623.63 | 0 | 43.26 | 0 | OK | Ground clear controls. | 151 | 66.29 | 666.89
10350 | TIN-INTERP | Interpolated Ground | 66225.91 | 4.83 | 623.49 | 0 | 32.1 | 0 | OK | Ground clear controls. | 151 | 66.29 | 655.59
10351 | TIN-INTERP | Interpolated Ground | 66225.91 | 6.33 | 622.95 | 0 | 38.14 | 0 | OK | Ground clear controls. | 151 | 66.29 | 661.09
10352 | TIN-INTERP | Interpolated Ground | 66265.5 | 6.29 | 616.01 | 0 | 29.28 | 0 | OK | Ground clear controls. | 151 | 66.29 | 645.29
10353 | TIN-INTERP | Interpolated Ground | 66265.58 | 4.8 | 615.63 | 0 | 24.09 | 0 | OK | Ground clear controls. | 151 | 66.29 | 639.72
10354 | TIN-INTERP | Interpolated Ground | 66265.62 | 4.39 | 615.52 | 0 | 35.65 | 0 | OK | Ground clear controls. | 151 | 66.29 | 651.17
10355 | TIN-INTERP | Interpolated Ground | 66265.74 | -5.85 | 612 | 0 | 27.65 | 0 | OK | Ground clear controls. | 151 | 66.29 | 639.65
10356 | TIN-INTERP | Interpolated Ground | 66265.75 | -5.44 | 612.09 | 0 | 39.01 | 0 | OK | Ground clear controls. | 151 | 66.29 | 651.1
10357 | TIN-INTERP | Interpolated Ground | 66265.91 | -7.35 | 611.89 | 0 | 33.4 | 0 | OK | Ground clear controls. | 151 | 66.29 | 645.29
10358 | TIN-INTERP | Interpolated Ground | 66305.5 | 6.27 | 595.98 | 0 | 34.55 | 0 | OK | Ground clear controls. | 151 | 66.29 | 630.53
10359 | TIN-INTERP | Interpolated Ground | 66305.58 | 4.78 | 594.27 | 0 | 30.64 | 0 | OK | Ground clear controls. | 151 | 66.29 | 624.91
10360 | TIN-INTERP | Interpolated Ground | 66305.62 | 4.36 | 593.97 | 0 | 42.52 | 0 | OK | Ground clear controls. | 151 | 66.29 | 636.49
10361 | TIN-INTERP | Interpolated Ground | 66305.74 | -5.75 | 590.01 | 0 | 34.76 | 0 | OK | Ground clear controls. | 151 | 66.29 | 624.77
10362 | TIN-INTERP | Interpolated Ground | 66305.75 | -5.34 | 590.05 | 0 | 46.31 | 0 | OK | Ground clear controls. | 151 | 66.29 | 636.36
10363 | TIN-INTERP | Interpolated Ground | 66305.91 | -7.25 | 589.69 | 0 | 40.85 | 0 | OK | Ground clear controls. | 151 | 66.29 | 630.54
10364 | TIN-INTERP | Interpolated Ground | 66345.5 | 6.25 | 572.55 | 0 | 44.27 | 0 | OK | Ground clear controls. | 151 | 66.29 | 616.82
10365 | TIN-INTERP | Interpolated Ground | 66345.58 | 4.76 | 571.69 | 0 | 39.46 | 0 | OK | Ground clear controls. | 151 | 66.29 | 611.15
10366 | TIN-INTERP | Interpolated Ground | 66345.62 | 4.33 | 571.44 | 0 | 51.42 | 0 | OK | Ground clear controls. | 151 | 66.29 | 622.86
10367 | TIN-INTERP | Interpolated Ground | 66345.74 | -5.66 | 567.06 | 0 | 43.89 | 0 | OK | Ground clear controls. | 151 | 66.29 | 610.95
10368 | TIN-INTERP | Interpolated Ground | 66345.75 | -5.23 | 567.16 | 0 | 55.5 | 0 | OK | Ground clear controls. | 151 | 66.29 | 622.66
10369 | TIN-INTERP | Interpolated Ground | 66345.91 | -7.15 | 566.52 | 0 | 50.32 | 0 | OK | Ground clear controls. | 151 | 66.29 | 616.84
10370 | TIN-INTERP | Interpolated Ground | 66385.5 | 6.23 | 561.42 | 0 | 42.72 | 0 | OK | Ground clear controls. | 151 | 66.29 | 604.14
10371 | TIN-INTERP | Interpolated Ground | 66385.58 | 4.74 | 560.64 | 0 | 37.79 | 0 | OK | Ground clear controls. | 151 | 66.29 | 598.43
10372 | TIN-INTERP | Interpolated Ground | 66385.62 | 4.3 | 560.45 | 0 | 49.8 | 0 | OK | Ground clear controls. | 151 | 66.29 | 610.25
10373 | TIN-INTERP | Interpolated Ground | 66385.74 | -5.56 | 556.78 | 0 | 41.4 | 0 | OK | Ground clear controls. | 151 | 66.29 | 598.18
10374 | TIN-INTERP | Interpolated Ground | 66385.75 | -5.13 | 556.95 | 0 | 53.05 | 0 | OK | Ground clear controls. | 151 | 66.29 | 610
10375 | TIN-INTERP | Interpolated Ground | 66385.91 | -7.05 | 556.65 | 0 | 47.52 | 0 | OK | Ground clear controls. | 151 | 66.29 | 604.17
10376 | TIN-INTERP | Interpolated Ground | 66425.5 | 6.21 | 560.03 | 0 | 32.46 | 0 | OK | Ground clear controls. | 151 | 66.29 | 592.49
10377 | TIN-INTERP | Interpolated Ground | 66425.58 | 4.72 | 559.91 | 0 | 26.83 | 0 | OK | Ground clear controls. | 151 | 66.29 | 586.74
10378 | TIN-INTERP | Interpolated Ground | 66425.62 | 4.27 | 559.9 | 0 | 38.76 | 0 | OK | Ground clear controls. | 151 | 66.29 | 598.66
10379 | TIN-INTERP | Interpolated Ground | 66425.74 | -5.46 | 556.89 | 0 | 29.57 | 0 | OK | Ground clear controls. | 151 | 66.29 | 586.46
10380 | TIN-INTERP | Interpolated Ground | 66425.75 | -5.02 | 556.96 | 0 | 41.42 | 0 | OK | Ground clear controls. | 151 | 66.29 | 598.38
10381 | TIN-INTERP | Interpolated Ground | 66425.91 | -6.95 | 556.72 | 0 | 35.8 | 0 | OK | Ground clear controls. | 151 | 66.29 | 592.52
10382 | TIN-INTERP | Interpolated Ground | 66465.5 | 6.18 | 549.21 | 0 | 32.66 | 0 | OK | Ground clear controls. | 151 | 66.29 | 581.87
10383 | TIN-INTERP | Interpolated Ground | 66465.58 | 4.7 | 548.43 | 0 | 27.65 | 0 | OK | Ground clear controls. | 151 | 66.29 | 576.08
10384 | TIN-INTERP | Interpolated Ground | 66465.62 | 4.25 | 548.28 | 0 | 39.79 | 0 | OK | Ground clear controls. | 151 | 66.29 | 588.07
10385 | TIN-INTERP | Interpolated Ground | 66465.74 | -5.36 | 545.56 | 0 | 30.22 | 0 | OK | Ground clear controls. | 151 | 66.29 | 575.78
10386 | TIN-INTERP | Interpolated Ground | 66465.75 | -4.91 | 545.58 | 0 | 42.19 | 0 | OK | Ground clear controls. | 151 | 66.29 | 587.77
10387 | TIN-INTERP | Interpolated Ground | 66465.91 | -6.85 | 545.29 | 0 | 36.61 | 0 | OK | Ground clear controls. | 151 | 66.29 | 581.9
10388 | TIN-INTERP | Interpolated Ground | 66505.5 | 6.16 | 542.79 | 0 | 29.47 | 0 | OK | Ground clear controls. | 151 | 66.29 | 572.26
10389 | TIN-INTERP | Interpolated Ground | 66505.58 | 4.67 | 541.84 | 0 | 24.61 | 0 | OK | Ground clear controls. | 151 | 66.29 | 566.45
10390 | TIN-INTERP | Interpolated Ground | 66505.62 | 4.22 | 541.55 | 0 | 36.96 | 0 | OK | Ground clear controls. | 151 | 66.29 | 578.51
10391 | TIN-INTERP | Interpolated Ground | 66505.74 | -5.26 | 536.62 | 0 | 29.51 | 0 | OK | Ground clear controls. | 151 | 66.29 | 566.13
10392 | TIN-INTERP | Interpolated Ground | 66505.75 | -4.81 | 536.79 | 0 | 41.4 | 0 | OK | Ground clear controls. | 151 | 66.29 | 578.19
10393 | TIN-INTERP | Interpolated Ground | 66505.91 | -6.75 | 536.28 | 0 | 36.01 | 0 | OK | Ground clear controls. | 151 | 66.29 | 572.29
10394 | TIN-INTERP | Interpolated Ground | 66545.5 | 6.14 | 527.97 | 0 | 35.68 | 0 | OK | Ground clear controls. | 151 | 66.29 | 563.65
10395 | TIN-INTERP | Interpolated Ground | 66545.58 | 4.65 | 527.08 | 0 | 30.73 | 0 | OK | Ground clear controls. | 151 | 66.29 | 557.81
10396 | TIN-INTERP | Interpolated Ground | 66545.62 | 4.19 | 526.85 | 0 | 43.08 | 0 | OK | Ground clear controls. | 151 | 66.29 | 569.93
10397 | TIN-INTERP | Interpolated Ground | 66545.74 | -5.17 | 522.2 | 0 | 35.3 | 0 | OK | Ground clear controls. | 151 | 66.29 | 557.5
10398 | TIN-INTERP | Interpolated Ground | 66545.75 | -4.7 | 522.3 | 0 | 47.32 | 0 | OK | Ground clear controls. | 151 | 66.29 | 569.62
10399 | TIN-INTERP | Interpolated Ground | 66545.91 | -6.65 | 521.51 | 0 | 42.17 | 0 | OK | Ground clear controls. | 151 | 66.29 | 563.68
10400 | TIN-INTERP | Interpolated Ground | 66585.5 | 6.12 | 509.34 | 0 | 46.7 | 0 | OK | Ground clear controls. | 151 | 66.29 | 556.04
10401 | TIN-INTERP | Interpolated Ground | 66585.58 | 4.63 | 508.59 | 0 | 41.61 | 0 | OK | Ground clear controls. | 151 | 66.29 | 550.2
10402 | TIN-INTERP | Interpolated Ground | 66585.62 | 4.16 | 508.35 | 0 | 53.99 | 0 | OK | Ground clear controls. | 151 | 66.29 | 562.34
10403 | TIN-INTERP | Interpolated Ground | 66585.74 | -5.07 | 504.47 | 0 | 45.41 | 0 | OK | Ground clear controls. | 151 | 66.29 | 549.88
10404 | TIN-INTERP | Interpolated Ground | 66585.75 | -4.6 | 504.6 | 0 | 57.44 | 0 | OK | Ground clear controls. | 151 | 66.29 | 562.04
10405 | TIN-INTERP | Interpolated Ground | 66585.91 | -6.55 | 504.18 | 0 | 51.89 | 0 | OK | Ground clear controls. | 151 | 66.29 | 556.07
10406 | TIN-INTERP | Interpolated Ground | 66625.5 | 6.1 | 493.89 | 0 | 55.54 | 0 | OK | Ground clear controls. | 151 | 66.29 | 549.43
10407 | TIN-INTERP | Interpolated Ground | 66625.58 | 4.61 | 493.22 | 0 | 50.36 | 0 | OK | Ground clear controls. | 151 | 66.29 | 543.58
10408 | TIN-INTERP | Interpolated Ground | 66625.62 | 4.13 | 492.55 | 0 | 63.21 | 0 | OK | Ground clear controls. | 151 | 66.29 | 555.76
10409 | TIN-INTERP | Interpolated Ground | 66625.74 | -4.97 | 489.11 | 0 | 54.17 | 0 | OK | Ground clear controls. | 151 | 66.29 | 543.28
10410 | TIN-INTERP | Interpolated Ground | 66625.75 | -4.49 | 489.18 | 0 | 66.29 | 0 | OK | Ground clear controls. | 151 | 66.29 | 555.47
10411 | TIN-INTERP | Interpolated Ground | 66625.91 | -6.45 | 489.46 | 0 | 60 | 0 | OK | Ground clear controls. | 151 | 60 | 549.46
10412 | TIN-INTERP | Interpolated Ground | 66665.5 | 6.08 | 493.1 | 0 | 50.72 | 0 | OK | Ground clear controls. | 151 | 58.73 | 543.82
10413 | TIN-INTERP | Interpolated Ground | 66665.58 | 4.59 | 493.02 | 0 | 44.95 | 0 | OK | Ground clear controls. | 151 | 58.73 | 537.97
10414 | TIN-INTERP | Interpolated Ground | 66665.62 | 4.1 | 493 | 0 | 57.16 | 0 | OK | Ground clear controls. | 151 | 58.73 | 550.16
10415 | TIN-INTERP | Interpolated Ground | 66665.74 | -4.87 | 492.25 | 0 | 45.45 | 0 | OK | Ground clear controls. | 151 | 58.73 | 537.7
10416 | TIN-INTERP | Interpolated Ground | 66665.75 | -4.38 | 492.31 | 0 | 57.59 | 0 | OK | Ground clear controls. | 151 | 58.73 | 549.9
10417 | TIN-INTERP | Interpolated Ground | 66665.91 | -6.35 | 492.03 | 0 | 51.81 | 0 | OK | Ground clear controls. | 151 | 58.73 | 543.84
10418 | TIN-INTERP | Interpolated Ground | 66705.5 | 6.05 | 487.03 | 0 | 52.18 | 0 | OK | Ground clear controls. | 151 | 58.73 | 539.21
10419 | TIN-INTERP | Interpolated Ground | 66705.58 | 4.57 | 487.05 | 0 | 46.31 | 0 | OK | Ground clear controls. | 151 | 58.73 | 533.36
10420 | TIN-INTERP | Interpolated Ground | 66705.62 | 4.08 | 487.07 | 0 | 58.48 | 0 | OK | Ground clear controls. | 151 | 58.73 | 545.55
10421 | TIN-INTERP | Interpolated Ground | 66705.74 | -4.77 | 486.52 | 0 | 46.62 | 0 | OK | Ground clear controls. | 151 | 58.73 | 533.14
10422 | TIN-INTERP | Interpolated Ground | 66705.75 | -4.28 | 486.6 | 0 | 58.73 | 0 | OK | Ground clear controls. | 151 | 58.73 | 545.33
10423 | TIN-INTERP | Interpolated Ground | 66705.91 | -6.25 | 486.08 | 0 | 53.15 | 0 | OK | Ground clear controls. | 151 | 56.07 | 539.23
10424 | TIN-INTERP | Interpolated Ground | 66745.5 | 6.03 | 486.35 | 0 | 49.22 | 0 | OK | Ground clear controls. | 151 | 56.07 | 535.57
10425 | TIN-INTERP | Interpolated Ground | 66745.58 | 4.55 | 486.21 | 0 | 43.52 | 0 | OK | Ground clear controls. | 151 | 56.07 | 529.73
10426 | TIN-INTERP | Interpolated Ground | 66745.62 | 4.05 | 486.16 | 0 | 55.75 | 0 | OK | Ground clear controls. | 151 | 56.07 | 541.91
10427 | TIN-INTERP | Interpolated Ground | 66745.74 | -4.67 | 485.47 | 0 | 44.09 | 0 | OK | Ground clear controls. | 151 | 56.07 | 529.56
10428 | TIN-INTERP | Interpolated Ground | 66745.75 | -4.17 | 485.67 | 0 | 56.07 | 0 | OK | Ground clear controls. | 151 | 56.07 | 541.74
10429 | TIN-INTERP | Interpolated Ground | 66745.91 | -6.16 | 484.1 | 0 | 51.49 | 0 | OK | Ground clear controls. | 151 | 51.49 | 535.59
10430 | TIN-INTERP | Interpolated Ground | 66785.5 | 6.01 | 487.94 | 0 | 44.98 | 0 | OK | Ground clear controls. | 151 | 51.2 | 532.92
10431 | TIN-INTERP | Interpolated Ground | 66785.58 | 4.53 | 488.04 | 0 | 39.04 | 0 | OK | Ground clear controls. | 151 | 51.2 | 527.08
10432 | TIN-INTERP | Interpolated Ground | 66785.62 | 4.02 | 488.05 | 0 | 51.2 | 0 | OK | Ground clear controls. | 151 | 51.2 | 539.25
10433 | TIN-INTERP | Interpolated Ground | 66785.74 | -4.58 | 488.04 | 0 | 38.95 | 0 | OK | Ground clear controls. | 151 | 51.07 | 526.99
10434 | TIN-INTERP | Interpolated Ground | 66785.75 | -4.07 | 488.07 | 0 | 51.07 | 0 | OK | Ground clear controls. | 151 | 51.07 | 539.14
10435 | TIN-INTERP | Interpolated Ground | 66785.91 | -6.06 | 487.82 | 0 | 45.1 | 0 | OK | Ground clear controls. | 151 | 49.76 | 532.92
10436 | TIN-INTERP | Interpolated Ground | 66825.5 | 5.99 | 488.36 | 0 | 42.9 | 0 | OK | Ground clear controls. | 151 | 49.76 | 531.26
10437 | TIN-INTERP | Interpolated Ground | 66825.58 | 4.51 | 488.3 | 0 | 37.15 | 0 | OK | Ground clear controls. | 151 | 49.76 | 525.45
10438 | TIN-INTERP | Interpolated Ground | 66825.62 | 3.99 | 488.29 | 0 | 49.28 | 0 | OK | Ground clear controls. | 151 | 49.76 | 537.57
10439 | TIN-INTERP | Interpolated Ground | 66825.74 | -4.48 | 487.29 | 0 | 38.13 | 0 | OK | Ground clear controls. | 151 | 49.76 | 525.42
10440 | TIN-INTERP | Interpolated Ground | 66825.75 | -3.96 | 487.77 | 0 | 49.76 | 0 | OK | Ground clear controls. | 151 | 49.76 | 537.53
10441 | TIN-INTERP | Interpolated Ground | 66825.91 | -5.96 | 485.97 | 0 | 45.28 | 0 | OK | Ground clear controls. | 151 | 45.28 | 531.25
10442 | TIN-INTERP | Interpolated Ground | 66843.33 | -5.92 | 488.78 | 0 | 41.66 | 0 | OK | Ground clear controls. | 152 | 97.46 | 530.44
10443 | TIN-INTERP | Interpolated Ground | 66843.35 | -4.44 | 488.86 | 0 | 35.78 | 0 | OK | Ground clear controls. | 152 | 97.46 | 524.64
10444 | TIN-INTERP | Interpolated Ground | 66843.35 | -3.92 | 488.77 | 0 | 47.96 | 0 | OK | Ground clear controls. | 152 | 97.46 | 536.73
10445 | TIN-INTERP | Interpolated Ground | 66843.45 | 3.99 | 488.05 | 0 | 48.68 | 0 | OK | Ground clear controls. | 152 | 97.46 | 536.73
10446 | TIN-INTERP | Interpolated Ground | 66843.46 | 4.51 | 488.02 | 0 | 36.63 | 0 | OK | Ground clear controls. | 152 | 97.46 | 524.65
10447 | TIN-INTERP | Interpolated Ground | 66843.48 | 5.99 | 487.92 | 0 | 42.51 | 0 | OK | Ground clear controls. | 152 | 97.46 | 530.43
10448 | TIN-INTERP | Interpolated Ground | 66883.33 | -5.93 | 479.48 | 0 | 44.59 | 0 | OK | Ground clear controls. | 152 | 97.46 | 524.07
10449 | TIN-INTERP | Interpolated Ground | 66883.35 | -4.45 | 479.51 | 0 | 38.77 | 0 | OK | Ground clear controls. | 152 | 97.46 | 518.28
10450 | TIN-INTERP | Interpolated Ground | 66883.35 | -3.93 | 479.52 | 0 | 50.63 | 0 | OK | Ground clear controls. | 152 | 97.46 | 530.15
10451 | TIN-INTERP | Interpolated Ground | 66883.45 | 4.11 | 479.57 | 0 | 50.65 | 0 | OK | Ground clear controls. | 152 | 97.46 | 530.22
10452 | TIN-INTERP | Interpolated Ground | 66883.46 | 4.63 | 479.56 | 0 | 38.89 | 0 | OK | Ground clear controls. | 152 | 97.46 | 518.45
10453 | TIN-INTERP | Interpolated Ground | 66883.48 | 6.1 | 479.53 | 0 | 44.37 | 0 | OK | Ground clear controls. | 152 | 97.46 | 523.9
10454 | TIN-INTERP | Interpolated Ground | 66923.33 | -5.94 | 455.25 | 0 | 63.43 | 0 | OK | Ground clear controls. | 152 | 97.46 | 518.68
10455 | TIN-INTERP | Interpolated Ground | 66923.35 | -4.46 | 456.03 | 0 | 56.89 | 0 | OK | Ground clear controls. | 152 | 97.46 | 512.92
10456 | TIN-INTERP | Interpolated Ground | 66923.35 | -3.94 | 456.46 | 0 | 68.13 | 0 | OK | Ground clear controls. | 152 | 97.46 | 524.59
10457 | TIN-INTERP | Interpolated Ground | 66923.45 | 4.22 | 462.62 | 0 | 62.08 | 0 | OK | Ground clear controls. | 152 | 97.46 | 524.7
10458 | TIN-INTERP | Interpolated Ground | 66923.46 | 4.74 | 463.06 | 0 | 50.15 | 0 | OK | Ground clear controls. | 152 | 97.46 | 513.21
10459 | TIN-INTERP | Interpolated Ground | 66923.48 | 6.22 | 464.47 | 0 | 53.92 | 0 | OK | Ground clear controls. | 152 | 97.46 | 518.39
10460 | TIN-INTERP | Interpolated Ground | 66963.33 | -5.95 | 437.7 | 0 | 76.58 | 0 | OK | Ground clear controls. | 152 | 97.46 | 514.28
10461 | TIN-INTERP | Interpolated Ground | 66963.35 | -4.46 | 438.18 | 0 | 70.36 | 0 | OK | Ground clear controls. | 152 | 97.46 | 508.54
10462 | TIN-INTERP | Interpolated Ground | 66963.35 | -3.95 | 438.35 | 0 | 81.7 | 0 | OK | Ground clear controls. | 152 | 97.46 | 520.05
10463 | TIN-INTERP | Interpolated Ground | 66963.45 | 4.34 | 441.2 | 0 | 78.98 | 0 | OK | Ground clear controls. | 152 | 97.46 | 520.18
10464 | TIN-INTERP | Interpolated Ground | 66963.46 | 4.86 | 441.6 | 0 | 67.31 | 0 | OK | Ground clear controls. | 152 | 97.46 | 508.91
10465 | TIN-INTERP | Interpolated Ground | 66963.47 | 6.34 | 441.36 | 0 | 72.55 | 0 | OK | Ground clear controls. | 152 | 97.46 | 513.91
10466 | TIN-INTERP | Interpolated Ground | 67003.33 | -5.96 | 436.82 | 0 | 74.05 | 0 | OK | Ground clear controls. | 152 | 97.46 | 510.87
10467 | TIN-INTERP | Interpolated Ground | 67003.35 | -4.47 | 436.83 | 0 | 68.33 | 0 | OK | Ground clear controls. | 152 | 97.46 | 505.16
10468 | TIN-INTERP | Interpolated Ground | 67003.35 | -3.96 | 436.84 | 0 | 79.67 | 0 | OK | Ground clear controls. | 152 | 97.46 | 516.51
10469 | TIN-INTERP | Interpolated Ground | 67003.45 | 4.46 | 436.95 | 0 | 79.71 | 0 | OK | Ground clear controls. | 152 | 97.46 | 516.66
10470 | TIN-INTERP | Interpolated Ground | 67003.46 | 4.98 | 436.93 | 0 | 68.64 | 0 | OK | Ground clear controls. | 152 | 97.46 | 505.57
10471 | TIN-INTERP | Interpolated Ground | 67003.47 | 6.46 | 436.96 | 0 | 73.48 | 0 | OK | Ground clear controls. | 152 | 97.46 | 510.44
10472 | TIN-INTERP | Interpolated Ground | 67043.33 | -5.97 | 433.94 | 0 | 74.48 | 0 | OK | Ground clear controls. | 152 | 97.46 | 508.42
10473 | TIN-INTERP | Interpolated Ground | 67043.35 | -4.48 | 433.99 | 0 | 68.75 | 0 | OK | Ground clear controls. | 152 | 97.46 | 502.74
10474 | TIN-INTERP | Interpolated Ground | 67043.35 | -3.97 | 434.01 | 0 | 79.98 | 0 | OK | Ground clear controls. | 152 | 97.46 | 513.99
10475 | TIN-INTERP | Interpolated Ground | 67043.45 | 4.58 | 434.39 | 0 | 79.76 | 0 | OK | Ground clear controls. | 152 | 97.46 | 514.15
10476 | TIN-INTERP | Interpolated Ground | 67043.46 | 5.1 | 434.41 | 0 | 68.76 | 0 | OK | Ground clear controls. | 152 | 97.46 | 503.17
10477 | TIN-INTERP | Interpolated Ground | 67043.47 | 6.57 | 434.62 | 0 | 73.37 | 0 | OK | Ground clear controls. | 152 | 97.46 | 507.99
10478 | TIN-INTERP | Interpolated Ground | 67083.33 | -5.98 | 414.98 | 0 | 91.99 | 0 | OK | Ground clear controls. | 152 | 97.46 | 506.97
10479 | TIN-INTERP | Interpolated Ground | 67083.35 | -4.49 | 414.97 | 0 | 86.34 | 0 | OK | Ground clear controls. | 152 | 97.46 | 501.31
10480 | TIN-INTERP | Interpolated Ground | 67083.35 | -3.98 | 415 | 0 | 97.46 | 0 | OK | Ground clear controls. | 152 | 97.46 | 512.46
10481 | TIN-INTERP | Interpolated Ground | 67083.45 | 4.7 | 415.51 | 0 | 97.1 | 0 | OK | Ground clear controls. | 152 | 97.1 | 512.61
10482 | TIN-INTERP | Interpolated Ground | 67083.46 | 5.22 | 415.58 | 0 | 86.15 | 0 | OK | Ground clear controls. | 152 | 91.08 | 501.73
10483 | TIN-INTERP | Interpolated Ground | 67083.47 | 6.69 | 415.47 | 0 | 91.08 | 0 | OK | Ground clear controls. | 152 | 91.08 | 506.55
10484 | TIN-INTERP | Interpolated Ground | 67123.33 | -5.99 | 427.77 | 0 | 78.71 | 0 | OK | Ground clear controls. | 152 | 85.36 | 506.48
10485 | TIN-INTERP | Interpolated Ground | 67123.35 | -4.49 | 427.7 | 0 | 73.17 | 0 | OK | Ground clear controls. | 152 | 85.36 | 500.87
10486 | TIN-INTERP | Interpolated Ground | 67123.35 | -3.99 | 427.67 | 0 | 84.27 | 0 | OK | Ground clear controls. | 152 | 85.36 | 511.94
10487 | TIN-INTERP | Interpolated Ground | 67123.45 | 4.82 | 426.71 | 0 | 85.36 | 0 | OK | Ground clear controls. | 152 | 85.36 | 512.07
10488 | TIN-INTERP | Interpolated Ground | 67123.46 | 5.33 | 426.61 | 0 | 74.61 | 0 | OK | Ground clear controls. | 152 | 79.8 | 501.22
10489 | TIN-INTERP | Interpolated Ground | 67123.47 | 6.81 | 426.33 | 0 | 79.8 | 0 | OK | Ground clear controls. | 152 | 79.8 | 506.13
10490 | TIN-INTERP | Interpolated Ground | 67163.33 | -6 | 440.07 | 0 | 66.91 | 0 | OK | Ground clear controls. | 152 | 72.47 | 506.98
10491 | TIN-INTERP | Interpolated Ground | 67163.35 | -4.5 | 439.96 | 0 | 61.44 | 0 | OK | Ground clear controls. | 152 | 72.47 | 501.4
10492 | TIN-INTERP | Interpolated Ground | 67163.35 | -4 | 439.96 | 0 | 72.47 | 0 | OK | Ground clear controls. | 152 | 72.47 | 512.43
10493 | TIN-INTERP | Interpolated Ground | 67163.45 | 4.93 | 440.69 | 0 | 71.84 | 0 | OK | Ground clear controls. | 152 | 71.84 | 512.53
10494 | TIN-INTERP | Interpolated Ground | 67163.46 | 5.45 | 440.85 | 0 | 60.81 | 0 | OK | Ground clear controls. | 152 | 65.6 | 501.66
10495 | TIN-INTERP | Interpolated Ground | 67163.47 | 6.92 | 441.12 | 0 | 65.6 | 0 | OK | Ground clear controls. | 152 | 65.6 | 506.72
10496 | TIN-INTERP | Interpolated Ground | 67203.33 | -6.01 | 481.29 | 0 | 27.16 | 0 | OK | Ground clear controls. | 152 | 33.18 | 508.45
10497 | TIN-INTERP | Interpolated Ground | 67203.35 | -4.51 | 480.81 | 0 | 22.1 | 0 | OK | Ground clear controls. | 152 | 33.18 | 502.91
10498 | TIN-INTERP | Interpolated Ground | 67203.35 | -4.02 | 480.74 | 0 | 33.18 | 0 | OK | Ground clear controls. | 152 | 33.18 | 513.92
10499 | TIN-INTERP | Interpolated Ground | 67203.45 | 5.05 | 481.32 | 0 | 32.66 | 0 | OK | Ground clear controls. | 152 | 32.66 | 513.98
10500 | TIN-INTERP | Interpolated Ground | 67203.46 | 5.57 | 481.37 | 0 | 21.68 | 0 | OK | Ground clear controls. | 152 | 26.81 | 503.05
10501 | TIN-INTERP | Interpolated Ground | 67203.47 | 7.04 | 481.52 | 0 | 26.81 | 0 | OK | Ground clear controls. | 152 | 26.81 | 508.33
10502 | TIN-INTERP | Interpolated Ground | 67234.56 | -6.02 | 482.02 | 0 | 28.26 | 0 | OK | Ground clear controls. | 153 | 34.28 | 510.28
10503 | TIN-INTERP | Interpolated Ground | 67234.57 | -4.03 | 481.9 | 0 | 33.89 | 0 | OK | Ground clear controls. | 153 | 34.28 | 515.79
10504 | TIN-INTERP | Interpolated Ground | 67234.6 | -4.52 | 481.92 | 0 | 22.87 | 0 | OK | Ground clear controls. | 153 | 34.28 | 504.79
10505 | TIN-INTERP | Interpolated Ground | 67234.74 | 5.14 | 481.5 | 0 | 34.28 | 0 | OK | Ground clear controls. | 153 | 34.28 | 515.78
10506 | TIN-INTERP | Interpolated Ground | 67234.76 | 5.66 | 481.47 | 0 | 23.31 | 0 | OK | Ground clear controls. | 153 | 29.68 | 504.78
10507 | TIN-INTERP | Interpolated Ground | 67234.95 | 7.12 | 481.43 | 0 | 28.85 | 0 | OK | Ground clear controls. | 153 | 29.68 | 510.28
10508 | TIN-INTERP | Interpolated Ground | 67274.45 | -6.05 | 484.11 | 0 | 20.93 | 0 | OK | Ground clear controls. | 153 | 29.68 | 505.04
10509 | TIN-INTERP | Interpolated Ground | 67274.57 | -4.06 | 484.74 | 0 | 25.73 | 0 | OK | Ground clear controls. | 153 | 29.68 | 510.47
10510 | TIN-INTERP | Interpolated Ground | 67274.6 | -4.55 | 484.6 | 0 | 14.96 | 0 | OK | Ground clear controls. | 153 | 29.68 | 499.56
10511 | TIN-INTERP | Interpolated Ground | 67274.74 | 5.12 | 485.98 | 0 | 24.49 | 0 | OK | Ground clear controls. | 153 | 29.68 | 510.47
10512 | TIN-INTERP | Interpolated Ground | 67274.76 | 5.64 | 485.99 | 0 | 13.64 | 0 | OK | Ground clear controls. | 153 | 29.68 | 499.63
10513 | TIN-INTERP | Interpolated Ground | 67274.95 | 7.1 | 486 | 0 | 18.93 | 0 | OK | Ground clear controls. | 153 | 29.68 | 504.93
10514 | TIN-INTERP | Interpolated Ground | 67314.45 | -6.07 | 482.94 | 0 | 17.83 | 0 | OK | Ground clear controls. | 153 | 29.68 | 500.77
10515 | TIN-INTERP | Interpolated Ground | 67314.57 | -4.09 | 483.07 | 0 | 23.07 | 0 | OK | Ground clear controls. | 153 | 29.68 | 506.14
10516 | TIN-INTERP | Interpolated Ground | 67314.6 | -4.58 | 483.03 | 0 | 12.28 | 0 | OK | Ground clear controls. | 153 | 29.68 | 495.31
10517 | TIN-INTERP | Interpolated Ground | 67314.74 | 5.09 | 482.99 | 0 | 23.16 | 0 | OK | Ground clear controls. | 153 | 29.68 | 506.15
10518 | TIN-INTERP | Interpolated Ground | 67314.76 | 5.61 | 483 | 0 | 12.44 | 0 | OK | Ground clear controls. | 153 | 29.68 | 495.44
10519 | TIN-INTERP | Interpolated Ground | 67314.95 | 7.08 | 482.95 | 0 | 17.65 | 0 | OK | Ground clear controls. | 153 | 29.68 | 500.6
10520 | TIN-INTERP | Interpolated Ground | 67354.45 | -6.1 | 480.73 | 0 | 16.75 | 0 | OK | Ground clear controls. | 153 | 29.68 | 497.48
10521 | TIN-INTERP | Interpolated Ground | 67354.57 | -4.11 | 480.84 | 0 | 21.97 | 0 | OK | Ground clear controls. | 153 | 29.68 | 502.81
10522 | TIN-INTERP | Interpolated Ground | 67354.6 | -4.61 | 480.8 | 0 | 11.23 | 0 | OK | Ground clear controls. | 153 | 29.68 | 492.03
10523 | TIN-INTERP | Interpolated Ground | 67354.74 | 5.07 | 481.18 | 0 | 21.65 | 0 | OK | Ground clear controls. | 153 | 29.68 | 502.83
10524 | TIN-INTERP | Interpolated Ground | 67354.76 | 5.59 | 481.2 | 0 | 10.98 | 0 | OK | Ground clear controls. | 153 | 29.68 | 492.18
10525 | TIN-INTERP | Interpolated Ground | 67354.95 | 7.05 | 481.16 | 0 | 16.1 | 0 | OK | Ground clear controls. | 153 | 29.68 | 497.26
10526 | TIN-INTERP | Interpolated Ground | 67394.45 | -6.13 | 478.46 | 0 | 16.69 | 0 | OK | Ground clear controls. | 153 | 29.68 | 495.15
10527 | TIN-INTERP | Interpolated Ground | 67394.57 | -4.14 | 478.5 | 0 | 21.97 | 0 | OK | Ground clear controls. | 153 | 29.68 | 500.47
10528 | TIN-INTERP | Interpolated Ground | 67394.6 | -4.63 | 478.47 | 0 | 11.24 | 0 | OK | Ground clear controls. | 153 | 29.68 | 489.71
10529 | TIN-INTERP | Interpolated Ground | 67394.74 | 5.04 | 478.76 | 0 | 21.74 | 0 | OK | Ground clear controls. | 153 | 29.68 | 500.5
10530 | TIN-INTERP | Interpolated Ground | 67394.76 | 5.56 | 478.78 | 0 | 11.1 | 0 | OK | Ground clear controls. | 153 | 29.68 | 489.88
10531 | TIN-INTERP | Interpolated Ground | 67394.95 | 7.03 | 478.83 | 0 | 16.09 | 0 | OK | Ground clear controls. | 153 | 29.68 | 494.92
10532 | TIN-INTERP | Interpolated Ground | 67434.45 | -6.16 | 476.3 | 0 | 17.5 | 0 | OK | Ground clear controls. | 153 | 29.68 | 493.8
10533 | TIN-INTERP | Interpolated Ground | 67434.57 | -4.17 | 476.41 | 0 | 22.72 | 0 | OK | Ground clear controls. | 153 | 29.68 | 499.13
10534 | TIN-INTERP | Interpolated Ground | 67434.6 | -4.66 | 476.38 | 0 | 11.97 | 0 | OK | Ground clear controls. | 153 | 29.68 | 488.35
10535 | TIN-INTERP | Interpolated Ground | 67434.74 | 5.02 | 476.29 | 0 | 22.86 | 0 | OK | Ground clear controls. | 153 | 29.68 | 499.15
10536 | TIN-INTERP | Interpolated Ground | 67434.76 | 5.54 | 476.28 | 0 | 12.24 | 0 | OK | Ground clear controls. | 153 | 29.68 | 488.52
10537 | TIN-INTERP | Interpolated Ground | 67434.95 | 7.01 | 476.31 | 0 | 17.28 | 0 | OK | Ground clear controls. | 153 | 29.68 | 493.59
10538 | TIN-INTERP | Interpolated Ground | 67474.45 | -6.19 | 474.54 | 0 | 18.88 | 0 | OK | Ground clear controls. | 153 | 29.68 | 493.42
10539 | TIN-INTERP | Interpolated Ground | 67474.57 | -4.2 | 474.4 | 0 | 24.38 | 0 | OK | Ground clear controls. | 153 | 29.68 | 498.78
10540 | TIN-INTERP | Interpolated Ground | 67474.6 | -4.69 | 474.42 | 0 | 13.54 | 0 | OK | Ground clear controls. | 153 | 29.68 | 487.96
10541 | TIN-INTERP | Interpolated Ground | 67474.74 | 4.99 | 474.15 | 0 | 24.65 | 0 | OK | Ground clear controls. | 153 | 29.68 | 498.8
10542 | TIN-INTERP | Interpolated Ground | 67474.76 | 5.52 | 474.1 | 0 | 14.01 | 0 | OK | Ground clear controls. | 153 | 29.68 | 488.11
10543 | TIN-INTERP | Interpolated Ground | 67474.95 | 6.98 | 474.11 | 0 | 19.15 | 0 | OK | Ground clear controls. | 153 | 29.68 | 493.26
10544 | TIN-INTERP | Interpolated Ground | 67514.45 | -6.21 | 473.68 | 0 | 20.33 | 0 | OK | Ground clear controls. | 153 | 29.68 | 494.01
10545 | TIN-INTERP | Interpolated Ground | 67514.57 | -4.22 | 473.66 | 0 | 25.77 | 0 | OK | Ground clear controls. | 153 | 29.68 | 499.43
10546 | TIN-INTERP | Interpolated Ground | 67514.6 | -4.71 | 473.66 | 0 | 14.88 | 0 | OK | Ground clear controls. | 153 | 29.68 | 488.54
10547 | TIN-INTERP | Interpolated Ground | 67514.74 | 4.97 | 473.43 | 0 | 26.01 | 0 | OK | Ground clear controls. | 153 | 29.68 | 499.44
10548 | TIN-INTERP | Interpolated Ground | 67514.76 | 5.49 | 473.42 | 0 | 15.22 | 0 | OK | Ground clear controls. | 153 | 29.68 | 488.64
10549 | TIN-INTERP | Interpolated Ground | 67514.95 | 6.96 | 473.46 | 0 | 20.46 | 0 | OK | Ground clear controls. | 153 | 29.68 | 493.92
10550 | TIN-INTERP | Interpolated Ground | 67554.45 | -6.24 | 472.22 | 0 | 23.34 | 0 | OK | Ground clear controls. | 153 | 29.68 | 495.56
10551 | TIN-INTERP | Interpolated Ground | 67554.57 | -4.25 | 472.09 | 0 | 28.97 | 0 | OK | Ground clear controls. | 153 | 29.68 | 501.06
10552 | TIN-INTERP | Interpolated Ground | 67554.6 | -4.74 | 472.13 | 0 | 17.95 | 0 | OK | Ground clear controls. | 153 | 29.68 | 490.08
10553 | TIN-INTERP | Interpolated Ground | 67554.74 | 4.94 | 471.4 | 0 | 29.68 | 0 | OK | Ground clear controls. | 153 | 29.68 | 501.08
10554 | TIN-INTERP | Interpolated Ground | 67554.76 | 5.47 | 471.4 | 0 | 18.72 | 0 | OK | Ground clear controls. | 153 | 24.16 | 490.12
10555 | TIN-INTERP | Interpolated Ground | 67554.95 | 6.94 | 471.42 | 0 | 24.16 | 0 | OK | Ground clear controls. | 153 | 24.16 | 495.58
10556 | TIN-INTERP | Interpolated Ground | 67561.67 | 4.94 | 471.13 | 0 | 30.33 | 0 | OK | Ground clear controls. | 154 | 37.8 | 501.46
10557 | TIN-INTERP | Interpolated Ground | 67561.74 | -4.75 | 472 | 0 | 18.46 | 0 | OK | Ground clear controls. | 154 | 37.8 | 490.46
10558 | TIN-INTERP | Interpolated Ground | 67561.77 | -6.25 | 472.08 | 0 | 23.88 | 0 | OK | Ground clear controls. | 154 | 37.8 | 495.96
10559 | TIN-INTERP | Interpolated Ground | 67561.82 | -4.26 | 471.98 | 0 | 29.48 | 0 | OK | Ground clear controls. | 154 | 37.8 | 501.46
10560 | TIN-INTERP | Interpolated Ground | 67561.88 | 5.46 | 471.09 | 0 | 19.37 | 0 | OK | Ground clear controls. | 154 | 37.8 | 490.46
10561 | TIN-INTERP | Interpolated Ground | 67561.88 | 6.93 | 470.93 | 0 | 25.03 | 0 | OK | Ground clear controls. | 154 | 37.8 | 495.96
10562 | TIN-INTERP | Interpolated Ground | 67601.74 | -4.79 | 470.36 | 0 | 16.58 | 0 | OK | Ground clear controls. | 154 | 37.8 | 486.94
10563 | TIN-INTERP | Interpolated Ground | 67601.77 | -6.29 | 470.56 | 0 | 21.87 | 0 | OK | Ground clear controls. | 154 | 37.8 | 492.43
10564 | TIN-INTERP | Interpolated Ground | 67601.79 | 4.9 | 470.16 | 0 | 27.69 | 0 | OK | Ground clear controls. | 154 | 37.8 | 497.85
10565 | TIN-INTERP | Interpolated Ground | 67601.82 | -4.3 | 470.37 | 0 | 27.49 | 0 | OK | Ground clear controls. | 154 | 37.8 | 497.86
10566 | TIN-INTERP | Interpolated Ground | 67601.88 | 5.42 | 470.15 | 0 | 16.89 | 0 | OK | Ground clear controls. | 154 | 37.8 | 487.04
10567 | TIN-INTERP | Interpolated Ground | 67601.88 | 6.89 | 470.04 | 0 | 22.3 | 0 | OK | Ground clear controls. | 154 | 37.8 | 492.34
10568 | TIN-INTERP | Interpolated Ground | 67641.74 | -4.83 | 458.83 | 0 | 25.56 | 0 | OK | Ground clear controls. | 154 | 37.8 | 484.39
10569 | TIN-INTERP | Interpolated Ground | 67641.77 | -6.33 | 459.43 | 0 | 30.44 | 0 | OK | Ground clear controls. | 154 | 37.8 | 489.87
10570 | TIN-INTERP | Interpolated Ground | 67641.79 | 4.86 | 457.43 | 0 | 37.8 | 0 | OK | Ground clear controls. | 154 | 37.8 | 495.23
10571 | TIN-INTERP | Interpolated Ground | 67641.82 | -4.34 | 458.71 | 0 | 36.55 | 0 | OK | Ground clear controls. | 154 | 36.55 | 495.26
10572 | TIN-INTERP | Interpolated Ground | 67641.88 | 5.38 | 457.2 | 0 | 27.36 | 0 | OK | Ground clear controls. | 154 | 33.37 | 484.56
10573 | TIN-INTERP | Interpolated Ground | 67641.88 | 6.86 | 457.12 | 0 | 32.59 | 0 | OK | Ground clear controls. | 154 | 33.37 | 489.71
10574 | TIN-INTERP | Interpolated Ground | 67681.74 | -4.87 | 466.57 | 0 | 16.22 | 0 | OK | Ground clear controls. | 154 | 33.37 | 482.79
10575 | TIN-INTERP | Interpolated Ground | 67681.77 | -6.37 | 467.12 | 0 | 21.16 | 0 | OK | Ground clear controls. | 154 | 33.37 | 488.28
10576 | TIN-INTERP | Interpolated Ground | 67681.79 | 4.82 | 462.66 | 0 | 30.94 | 0 | OK | Ground clear controls. | 154 | 33.37 | 493.6
10577 | TIN-INTERP | Interpolated Ground | 67681.82 | -4.38 | 466.37 | 0 | 27.26 | 0 | OK | Ground clear controls. | 154 | 33.37 | 493.63
10578 | TIN-INTERP | Interpolated Ground | 67681.88 | 5.33 | 462.47 | 0 | 20.53 | 0 | OK | Ground clear controls. | 154 | 33.37 | 483
10579 | TIN-INTERP | Interpolated Ground | 67681.88 | 6.82 | 462.07 | 0 | 26.01 | 0 | OK | Ground clear controls. | 154 | 33.37 | 488.08
10580 | TIN-INTERP | Interpolated Ground | 67721.74 | -4.91 | 470.67 | 0 | 11.5 | 0 | OK | Ground clear controls. | 154 | 33.37 | 482.17
10581 | TIN-INTERP | Interpolated Ground | 67721.77 | -6.41 | 470.81 | 0 | 16.84 | 0 | OK | Ground clear controls. | 154 | 33.37 | 487.65
10582 | TIN-INTERP | Interpolated Ground | 67721.79 | 4.78 | 470.01 | 0 | 22.95 | 0 | OK | Ground clear controls. | 154 | 33.37 | 492.96
10583 | TIN-INTERP | Interpolated Ground | 67721.82 | -4.42 | 470.6 | 0 | 22.39 | 0 | OK | Ground clear controls. | 154 | 33.37 | 492.99
10584 | TIN-INTERP | Interpolated Ground | 67721.88 | 5.29 | 469.97 | 0 | 12.43 | 0 | OK | Ground clear controls. | 154 | 33.37 | 482.4
10585 | TIN-INTERP | Interpolated Ground | 67721.88 | 6.78 | 469.88 | 0 | 17.55 | 0 | OK | Ground clear controls. | 154 | 33.37 | 487.43
10586 | TIN-INTERP | Interpolated Ground | 67761.74 | -4.95 | 470.16 | 0 | 12.34 | 0 | OK | Ground clear controls. | 154 | 33.37 | 482.5
10587 | TIN-INTERP | Interpolated Ground | 67761.77 | -6.45 | 470.38 | 0 | 17.61 | 0 | OK | Ground clear controls. | 154 | 33.37 | 487.99
10588 | TIN-INTERP | Interpolated Ground | 67761.79 | 4.74 | 468.7 | 0 | 24.61 | 0 | OK | Ground clear controls. | 154 | 33.37 | 493.31
10589 | TIN-INTERP | Interpolated Ground | 67761.82 | -4.46 | 470.09 | 0 | 23.25 | 0 | OK | Ground clear controls. | 154 | 33.37 | 493.34
10590 | TIN-INTERP | Interpolated Ground | 67761.88 | 5.25 | 468.67 | 0 | 14.05 | 0 | OK | Ground clear controls. | 154 | 33.37 | 482.72
10591 | TIN-INTERP | Interpolated Ground | 67761.88 | 6.74 | 468.62 | 0 | 19.16 | 0 | OK | Ground clear controls. | 154 | 33.37 | 487.78
10592 | TIN-INTERP | Interpolated Ground | 67801.74 | -4.99 | 468.42 | 0 | 15.38 | 0 | OK | Ground clear controls. | 154 | 33.37 | 483.8
10593 | TIN-INTERP | Interpolated Ground | 67801.77 | -6.49 | 468.34 | 0 | 20.95 | 0 | OK | Ground clear controls. | 154 | 33.37 | 489.29
10594 | TIN-INTERP | Interpolated Ground | 67801.79 | 4.7 | 467.37 | 0 | 27.27 | 0 | OK | Ground clear controls. | 154 | 33.37 | 494.64
10595 | TIN-INTERP | Interpolated Ground | 67801.82 | -4.5 | 468.43 | 0 | 26.24 | 0 | OK | Ground clear controls. | 154 | 33.37 | 494.67
10596 | TIN-INTERP | Interpolated Ground | 67801.88 | 5.21 | 467.28 | 0 | 16.71 | 0 | OK | Ground clear controls. | 154 | 33.37 | 483.99
10597 | TIN-INTERP | Interpolated Ground | 67801.88 | 6.7 | 467.11 | 0 | 22 | 0 | OK | Ground clear controls. | 154 | 33.37 | 489.11
10598 | TIN-INTERP | Interpolated Ground | 67841.74 | -5.04 | 466.99 | 0 | 19.08 | 0 | OK | Ground clear controls. | 154 | 33.37 | 486.07
10599 | TIN-INTERP | Interpolated Ground | 67841.77 | -6.54 | 466.94 | 0 | 24.63 | 0 | OK | Ground clear controls. | 154 | 33.37 | 491.57
10600 | TIN-INTERP | Interpolated Ground | 67841.79 | 4.66 | 466.86 | 0 | 30.1 | 0 | OK | Ground clear controls. | 154 | 33.37 | 496.96
10601 | TIN-INTERP | Interpolated Ground | 67841.82 | -4.54 | 466.98 | 0 | 30.01 | 0 | OK | Ground clear controls. | 154 | 33.37 | 496.99
10602 | TIN-INTERP | Interpolated Ground | 67841.88 | 5.17 | 466.87 | 0 | 19.33 | 0 | OK | Ground clear controls. | 154 | 33.37 | 486.2
10603 | TIN-INTERP | Interpolated Ground | 67841.88 | 6.66 | 466.82 | 0 | 24.63 | 0 | OK | Ground clear controls. | 154 | 33.37 | 491.45
10604 | TIN-INTERP | Interpolated Ground | 67881.74 | -5.08 | 466.93 | 0 | 22.38 | 0 | OK | Ground clear controls. | 154 | 33.37 | 489.31
10605 | TIN-INTERP | Interpolated Ground | 67881.77 | -6.58 | 466.86 | 0 | 27.95 | 0 | OK | Ground clear controls. | 154 | 33.37 | 494.81
10606 | TIN-INTERP | Interpolated Ground | 67881.79 | 4.62 | 467.2 | 0 | 33.08 | 0 | OK | Ground clear controls. | 154 | 33.37 | 500.28
10607 | TIN-INTERP | Interpolated Ground | 67881.82 | -4.58 | 466.93 | 0 | 33.37 | 0 | OK | Ground clear controls. | 154 | 33.37 | 500.3
10608 | TIN-INTERP | Interpolated Ground | 67881.88 | 5.12 | 467.19 | 0 | 22.15 | 0 | OK | Ground clear controls. | 154 | 27.56 | 489.34
10609 | TIN-INTERP | Interpolated Ground | 67881.88 | 6.62 | 467.21 | 0 | 27.56 | 0 | OK | Ground clear controls. | 154 | 27.56 | 494.77
10610 | TIN-INTERP | Interpolated Ground | 67890.9 | -6.59 | 466.77 | 0 | 28.92 | 0 | OK | Ground clear controls. | 155 | 34.4 | 495.69
10611 | TIN-INTERP | Interpolated Ground | 67890.97 | -4.59 | 466.79 | 0 | 34.4 | 0 | OK | Ground clear controls. | 155 | 34.4 | 501.19
10612 | TIN-INTERP | Interpolated Ground | 67891.03 | 5.11 | 467.16 | 0 | 23.04 | 0 | OK | Ground clear controls. | 155 | 34.11 | 490.2
10613 | TIN-INTERP | Interpolated Ground | 67891.07 | -5.09 | 466.79 | 0 | 23.4 | 0 | OK | Ground clear controls. | 155 | 34.11 | 490.19
10614 | TIN-INTERP | Interpolated Ground | 67891.13 | 4.61 | 467.08 | 0 | 34.11 | 0 | OK | Ground clear controls. | 155 | 34.11 | 501.19
10615 | TIN-INTERP | Interpolated Ground | 67891.25 | 6.61 | 467.16 | 0 | 28.53 | 0 | OK | Ground clear controls. | 155 | 31.24 | 495.69
10616 | TIN-INTERP | Interpolated Ground | 67930.9 | -6.59 | 467.01 | 0 | 24.45 | 0 | OK | Ground clear controls. | 155 | 31.24 | 491.46
10617 | TIN-INTERP | Interpolated Ground | 67930.96 | -4.59 | 466.49 | 0 | 30.41 | 0 | OK | Ground clear controls. | 155 | 31.24 | 496.9
10618 | TIN-INTERP | Interpolated Ground | 67931.03 | 5.11 | 465.65 | 0 | 20.4 | 0 | OK | Ground clear controls. | 155 | 31.24 | 486.05
10619 | TIN-INTERP | Interpolated Ground | 67931.07 | -5.09 | 466.65 | 0 | 19.38 | 0 | OK | Ground clear controls. | 155 | 31.24 | 486.03
10620 | TIN-INTERP | Interpolated Ground | 67931.13 | 4.61 | 465.65 | 0 | 31.24 | 0 | OK | Ground clear controls. | 155 | 31.24 | 496.89
10621 | TIN-INTERP | Interpolated Ground | 67931.25 | 6.61 | 465.65 | 0 | 25.75 | 0 | OK | Ground clear controls. | 155 | 28.44 | 491.4
10622 | TIN-INTERP | Interpolated Ground | 67970.9 | -6.59 | 466.57 | 0 | 21.62 | 0 | OK | Ground clear controls. | 155 | 28.44 | 488.19
10623 | TIN-INTERP | Interpolated Ground | 67970.96 | -4.59 | 466.63 | 0 | 26.96 | 0 | OK | Ground clear controls. | 155 | 28.44 | 493.59
10624 | TIN-INTERP | Interpolated Ground | 67971.03 | 5.11 | 466.49 | 0 | 16.37 | 0 | OK | Ground clear controls. | 155 | 28.44 | 482.86
10625 | TIN-INTERP | Interpolated Ground | 67971.07 | -5.09 | 466.63 | 0 | 16.18 | 0 | OK | Ground clear controls. | 155 | 28.44 | 482.81
10626 | TIN-INTERP | Interpolated Ground | 67971.13 | 4.61 | 466.51 | 0 | 27.08 | 0 | OK | Ground clear controls. | 155 | 28.44 | 493.59
10627 | TIN-INTERP | Interpolated Ground | 67971.25 | 6.61 | 466.51 | 0 | 21.6 | 0 | OK | Ground clear controls. | 155 | 28.44 | 488.11
10628 | TIN-INTERP | Interpolated Ground | 68010.9 | -6.59 | 466.48 | 0 | 19.43 | 0 | OK | Ground clear controls. | 155 | 28.44 | 485.91
10629 | TIN-INTERP | Interpolated Ground | 68010.96 | -4.59 | 466.16 | 0 | 25.11 | 0 | OK | Ground clear controls. | 155 | 28.44 | 491.27
10630 | TIN-INTERP | Interpolated Ground | 68011.03 | 5.11 | 465.14 | 0 | 15.48 | 0 | OK | Ground clear controls. | 155 | 28.44 | 480.62
10631 | TIN-INTERP | Interpolated Ground | 68011.07 | -5.09 | 466.25 | 0 | 14.3 | 0 | OK | Ground clear controls. | 155 | 28.44 | 480.55
10632 | TIN-INTERP | Interpolated Ground | 68011.13 | 4.61 | 465.1 | 0 | 26.16 | 0 | OK | Ground clear controls. | 155 | 28.44 | 491.26
10633 | TIN-INTERP | Interpolated Ground | 68011.25 | 6.61 | 465.07 | 0 | 20.72 | 0 | OK | Ground clear controls. | 155 | 28.44 | 485.79
10634 | TIN-INTERP | Interpolated Ground | 68050.9 | -6.59 | 467.99 | 0 | 16.6 | 0 | OK | Ground clear controls. | 155 | 28.44 | 484.59
10635 | TIN-INTERP | Interpolated Ground | 68050.96 | -4.59 | 467.92 | 0 | 22.02 | 0 | OK | Ground clear controls. | 155 | 28.44 | 489.94
10636 | TIN-INTERP | Interpolated Ground | 68051.03 | 5.11 | 467.09 | 0 | 12.23 | 0 | OK | Ground clear controls. | 155 | 28.44 | 479.32
10637 | TIN-INTERP | Interpolated Ground | 68051.07 | -5.09 | 467.97 | 0 | 11.28 | 0 | OK | Ground clear controls. | 155 | 28.44 | 479.25
10638 | TIN-INTERP | Interpolated Ground | 68051.13 | 4.61 | 467.16 | 0 | 22.76 | 0 | OK | Ground clear controls. | 155 | 28.44 | 489.92
10639 | TIN-INTERP | Interpolated Ground | 68051.25 | 6.61 | 467.01 | 0 | 17.45 | 0 | OK | Ground clear controls. | 155 | 28.44 | 484.46
10640 | TIN-INTERP | Interpolated Ground | 68090.9 | -6.6 | 467.3 | 0 | 16.93 | 0 | OK | Ground clear controls. | 155 | 28.44 | 484.23
10641 | TIN-INTERP | Interpolated Ground | 68090.96 | -4.6 | 467.28 | 0 | 22.31 | 0 | OK | Ground clear controls. | 155 | 28.44 | 489.59
10642 | TIN-INTERP | Interpolated Ground | 68091.03 | 5.11 | 467.09 | 0 | 11.87 | 0 | OK | Ground clear controls. | 155 | 28.44 | 478.96
10643 | TIN-INTERP | Interpolated Ground | 68091.07 | -5.1 | 467.29 | 0 | 11.61 | 0 | OK | Ground clear controls. | 155 | 28.44 | 478.9
10644 | TIN-INTERP | Interpolated Ground | 68091.13 | 4.6 | 467.07 | 0 | 22.5 | 0 | OK | Ground clear controls. | 155 | 28.44 | 489.57
10645 | TIN-INTERP | Interpolated Ground | 68091.25 | 6.6 | 467.06 | 0 | 17.05 | 0 | OK | Ground clear controls. | 155 | 28.44 | 484.11
10646 | TIN-INTERP | Interpolated Ground | 68130.9 | -6.6 | 467.24 | 0 | 17.61 | 0 | OK | Ground clear controls. | 155 | 28.44 | 484.85
10647 | TIN-INTERP | Interpolated Ground | 68130.96 | -4.6 | 467.23 | 0 | 22.99 | 0 | OK | Ground clear controls. | 155 | 28.44 | 490.22
10648 | TIN-INTERP | Interpolated Ground | 68131.03 | 5.1 | 467.32 | 0 | 12.24 | 0 | OK | Ground clear controls. | 155 | 28.44 | 479.56
10649 | TIN-INTERP | Interpolated Ground | 68131.07 | -5.1 | 467.2 | 0 | 12.29 | 0 | OK | Ground clear controls. | 155 | 28.44 | 479.49
10650 | TIN-INTERP | Interpolated Ground | 68131.13 | 4.6 | 467.31 | 0 | 22.9 | 0 | OK | Ground clear controls. | 155 | 28.44 | 490.21
10651 | TIN-INTERP | Interpolated Ground | 68131.25 | 6.6 | 467.33 | 0 | 17.42 | 0 | OK | Ground clear controls. | 155 | 28.44 | 484.75
10652 | TIN-INTERP | Interpolated Ground | 68170.9 | -6.6 | 466.67 | 0 | 19.76 | 0 | OK | Ground clear controls. | 155 | 28.44 | 486.43
10653 | TIN-INTERP | Interpolated Ground | 68170.96 | -4.6 | 466.72 | 0 | 25.11 | 0 | OK | Ground clear controls. | 155 | 28.44 | 491.83
10654 | TIN-INTERP | Interpolated Ground | 68171.03 | 5.1 | 467.11 | 0 | 13.98 | 0 | OK | Ground clear controls. | 155 | 28.44 | 481.09
10655 | TIN-INTERP | Interpolated Ground | 68171.07 | -5.1 | 466.7 | 0 | 14.35 | 0 | OK | Ground clear controls. | 155 | 28.44 | 481.05
10656 | TIN-INTERP | Interpolated Ground | 68171.13 | 4.6 | 467.09 | 0 | 24.74 | 0 | OK | Ground clear controls. | 155 | 28.44 | 491.83
10657 | TIN-INTERP | Interpolated Ground | 68171.25 | 6.6 | 467.22 | 0 | 19.14 | 0 | OK | Ground clear controls. | 155 | 28.44 | 486.36
10658 | TIN-INTERP | Interpolated Ground | 68210.9 | -6.6 | 466.05 | 0 | 22.93 | 0 | OK | Ground clear controls. | 155 | 28.44 | 488.98
10659 | TIN-INTERP | Interpolated Ground | 68210.96 | -4.6 | 466 | 0 | 28.44 | 0 | OK | Ground clear controls. | 155 | 28.44 | 494.44
10660 | TIN-INTERP | Interpolated Ground | 68211.03 | 5.1 | 466.48 | 0 | 17.09 | 0 | OK | Ground clear controls. | 155 | 27.95 | 483.57
10661 | TIN-INTERP | Interpolated Ground | 68211.07 | -5.1 | 466 | 0 | 17.55 | 0 | OK | Ground clear controls. | 155 | 27.95 | 483.55
10662 | TIN-INTERP | Interpolated Ground | 68211.13 | 4.6 | 466.5 | 0 | 27.95 | 0 | OK | Ground clear controls. | 155 | 27.95 | 494.45
10663 | TIN-INTERP | Interpolated Ground | 68211.25 | 6.6 | 466.48 | 0 | 22.49 | 0 | OK | Ground clear controls. | 155 | 22.49 | 488.97
10664 | TIN-INTERP | Interpolated Ground | 68244.23 | 4.6 | 464.24 | 0 | 33.11 | 0 | OK | Ground clear controls. | 156 | 39.61 | 497.35
10665 | TIN-INTERP | Interpolated Ground | 68244.24 | -4.6 | 464.13 | 0 | 33.22 | 0 | OK | Ground clear controls. | 156 | 39.61 | 497.35
10666 | TIN-INTERP | Interpolated Ground | 68244.24 | -6.6 | 464.12 | 0 | 27.73 | 0 | OK | Ground clear controls. | 156 | 39.61 | 491.85
10667 | TIN-INTERP | Interpolated Ground | 68244.26 | 6.6 | 464.3 | 0 | 27.55 | 0 | OK | Ground clear controls. | 156 | 39.61 | 491.85
10668 | TIN-INTERP | Interpolated Ground | 68244.28 | -5.1 | 464.14 | 0 | 22.21 | 0 | OK | Ground clear controls. | 156 | 39.61 | 486.35
10669 | TIN-INTERP | Interpolated Ground | 68244.29 | 5.1 | 464.24 | 0 | 22.11 | 0 | OK | Ground clear controls. | 156 | 39.61 | 486.35
10670 | TIN-INTERP | Interpolated Ground | 68284.23 | 4.58 | 463.79 | 0 | 29.21 | 0 | OK | Ground clear controls. | 156 | 39.61 | 493
10671 | TIN-INTERP | Interpolated Ground | 68284.24 | -4.63 | 463.75 | 0 | 29.27 | 0 | OK | Ground clear controls. | 156 | 39.61 | 493.02
10672 | TIN-INTERP | Interpolated Ground | 68284.24 | -6.63 | 463.6 | 0 | 23.98 | 0 | OK | Ground clear controls. | 156 | 39.61 | 487.58
10673 | TIN-INTERP | Interpolated Ground | 68284.26 | 6.58 | 463.79 | 0 | 23.74 | 0 | OK | Ground clear controls. | 156 | 39.61 | 487.53
10674 | TIN-INTERP | Interpolated Ground | 68284.28 | -5.13 | 463.73 | 0 | 18.43 | 0 | OK | Ground clear controls. | 156 | 39.61 | 482.16
10675 | TIN-INTERP | Interpolated Ground | 68284.29 | 5.08 | 463.82 | 0 | 18.37 | 0 | OK | Ground clear controls. | 156 | 39.61 | 482.19
10676 | TIN-INTERP | Interpolated Ground | 68324.23 | 4.56 | 462.46 | 0 | 27.19 | 0 | OK | Ground clear controls. | 156 | 39.61 | 489.65
10677 | TIN-INTERP | Interpolated Ground | 68324.24 | -4.66 | 463.35 | 0 | 26.33 | 0 | OK | Ground clear controls. | 156 | 39.61 | 489.68
10678 | TIN-INTERP | Interpolated Ground | 68324.24 | -6.66 | 463.34 | 0 | 20.94 | 0 | OK | Ground clear controls. | 156 | 39.61 | 484.28
10679 | TIN-INTERP | Interpolated Ground | 68324.26 | 6.56 | 462.11 | 0 | 22.08 | 0 | OK | Ground clear controls. | 156 | 39.61 | 484.19
10680 | TIN-INTERP | Interpolated Ground | 68324.28 | -5.16 | 463.33 | 0 | 15.59 | 0 | OK | Ground clear controls. | 156 | 39.61 | 478.92
10681 | TIN-INTERP | Interpolated Ground | 68324.29 | 5.06 | 462.35 | 0 | 16.63 | 0 | OK | Ground clear controls. | 156 | 39.61 | 478.98
10682 | TIN-INTERP | Interpolated Ground | 68364.23 | 4.54 | 462.23 | 0 | 25.06 | 0 | OK | Ground clear controls. | 156 | 39.61 | 487.29
10683 | TIN-INTERP | Interpolated Ground | 68364.24 | -4.68 | 462.76 | 0 | 24.55 | 0 | OK | Ground clear controls. | 156 | 39.61 | 487.31
10684 | TIN-INTERP | Interpolated Ground | 68364.24 | -6.69 | 462.9 | 0 | 19.06 | 0 | OK | Ground clear controls. | 156 | 39.61 | 481.96
10685 | TIN-INTERP | Interpolated Ground | 68364.26 | 6.55 | 462.29 | 0 | 19.55 | 0 | OK | Ground clear controls. | 156 | 39.61 | 481.84
10686 | TIN-INTERP | Interpolated Ground | 68364.28 | -5.19 | 462.81 | 0 | 13.82 | 0 | OK | Ground clear controls. | 156 | 39.61 | 476.63
10687 | TIN-INTERP | Interpolated Ground | 68364.29 | 5.04 | 462.24 | 0 | 14.46 | 0 | OK | Ground clear controls. | 156 | 39.61 | 476.7
10688 | TIN-INTERP | Interpolated Ground | 68404.23 | 4.52 | 461.77 | 0 | 24.14 | 0 | OK | Ground clear controls. | 156 | 39.61 | 485.91
10689 | TIN-INTERP | Interpolated Ground | 68404.24 | -4.71 | 462.44 | 0 | 23.49 | 0 | OK | Ground clear controls. | 156 | 39.61 | 485.93
10690 | TIN-INTERP | Interpolated Ground | 68404.24 | -6.72 | 462.63 | 0 | 17.97 | 0 | OK | Ground clear controls. | 156 | 39.61 | 480.6
10691 | TIN-INTERP | Interpolated Ground | 68404.26 | 6.53 | 461.59 | 0 | 18.87 | 0 | OK | Ground clear controls. | 156 | 39.61 | 480.46
10692 | TIN-INTERP | Interpolated Ground | 68404.28 | -5.22 | 462.49 | 0 | 12.79 | 0 | OK | Ground clear controls. | 156 | 39.61 | 475.28
10693 | TIN-INTERP | Interpolated Ground | 68404.29 | 5.03 | 461.72 | 0 | 13.64 | 0 | OK | Ground clear controls. | 156 | 39.61 | 475.36
10694 | TIN-INTERP | Interpolated Ground | 68444.23 | 4.51 | 461.55 | 0 | 23.96 | 0 | OK | Ground clear controls. | 156 | 39.61 | 485.51
10695 | TIN-INTERP | Interpolated Ground | 68444.24 | -4.74 | 461.95 | 0 | 23.59 | 0 | OK | Ground clear controls. | 156 | 39.61 | 485.54
10696 | TIN-INTERP | Interpolated Ground | 68444.24 | -6.74 | 462 | 0 | 18.2 | 0 | OK | Ground clear controls. | 156 | 39.61 | 480.2
10697 | TIN-INTERP | Interpolated Ground | 68444.26 | 6.51 | 461.49 | 0 | 18.58 | 0 | OK | Ground clear controls. | 156 | 39.61 | 480.07
10698 | TIN-INTERP | Interpolated Ground | 68444.28 | -5.24 | 461.94 | 0 | 12.95 | 0 | OK | Ground clear controls. | 156 | 39.61 | 474.89
10699 | TIN-INTERP | Interpolated Ground | 68444.29 | 5.01 | 461.59 | 0 | 13.38 | 0 | OK | Ground clear controls. | 156 | 39.61 | 474.97
10700 | TIN-INTERP | Interpolated Ground | 68484.23 | 4.49 | 461.7 | 0 | 24.4 | 0 | OK | Ground clear controls. | 156 | 39.61 | 486.1
10701 | TIN-INTERP | Interpolated Ground | 68484.24 | -4.77 | 461.5 | 0 | 24.63 | 0 | OK | Ground clear controls. | 156 | 39.61 | 486.13
10702 | TIN-INTERP | Interpolated Ground | 68484.24 | -6.77 | 461.63 | 0 | 19.14 | 0 | OK | Ground clear controls. | 156 | 39.61 | 480.77
10703 | TIN-INTERP | Interpolated Ground | 68484.26 | 6.49 | 461.65 | 0 | 19.01 | 0 | OK | Ground clear controls. | 156 | 39.61 | 480.66
10704 | TIN-INTERP | Interpolated Ground | 68484.28 | -5.27 | 461.51 | 0 | 13.94 | 0 | OK | Ground clear controls. | 156 | 39.61 | 475.45
10705 | TIN-INTERP | Interpolated Ground | 68484.29 | 4.99 | 461.71 | 0 | 13.81 | 0 | OK | Ground clear controls. | 156 | 39.61 | 475.52
10706 | TIN-INTERP | Interpolated Ground | 68524.23 | 4.47 | 458.16 | 0 | 29.52 | 0 | OK | Ground clear controls. | 156 | 39.61 | 487.68
10707 | TIN-INTERP | Interpolated Ground | 68524.24 | -4.79 | 458.75 | 0 | 28.95 | 0 | OK | Ground clear controls. | 156 | 39.61 | 487.7
10708 | TIN-INTERP | Interpolated Ground | 68524.24 | -6.8 | 459.03 | 0 | 23.29 | 0 | OK | Ground clear controls. | 156 | 39.61 | 482.32
10709 | TIN-INTERP | Interpolated Ground | 68524.26 | 6.48 | 458.09 | 0 | 24.13 | 0 | OK | Ground clear controls. | 156 | 39.61 | 482.22
10710 | TIN-INTERP | Interpolated Ground | 68524.28 | -5.3 | 458.85 | 0 | 18.1 | 0 | OK | Ground clear controls. | 156 | 39.61 | 476.95
10711 | TIN-INTERP | Interpolated Ground | 68524.29 | 4.97 | 458.17 | 0 | 18.84 | 0 | OK | Ground clear controls. | 156 | 39.61 | 477.01
10712 | TIN-INTERP | Interpolated Ground | 68564.23 | 4.45 | 451.31 | 0 | 38.93 | 0 | OK | Ground clear controls. | 156 | 39.61 | 490.24
10713 | TIN-INTERP | Interpolated Ground | 68564.24 | -4.82 | 450.64 | 0 | 39.61 | 0 | OK | Ground clear controls. | 156 | 39.61 | 490.25
10714 | TIN-INTERP | Interpolated Ground | 68564.24 | -6.83 | 451.17 | 0 | 33.65 | 0 | OK | Ground clear controls. | 156 | 33.65 | 484.82
10715 | TIN-INTERP | Interpolated Ground | 68564.26 | 6.46 | 451.32 | 0 | 33.44 | 0 | OK | Ground clear controls. | 156 | 33.44 | 484.76
10716 | TIN-INTERP | Interpolated Ground | 68564.28 | -5.33 | 450.8 | 0 | 28.6 | 0 | OK | Ground clear controls. | 156 | 28.6 | 479.4
10717 | TIN-INTERP | Interpolated Ground | 68564.29 | 4.95 | 451.41 | 0 | 28.02 | 0 | OK | Ground clear controls. | 156 | 28.02 | 479.43
10718 | TIN-INTERP | Interpolated Ground | 68600.72 | 4.94 | 459.23 | 0 | 23.23 | 0 | OK | Ground clear controls. | 157 | 51.89 | 482.46
10719 | TIN-INTERP | Interpolated Ground | 68600.76 | -5.35 | 459.27 | 0 | 23.19 | 0 | OK | Ground clear controls. | 157 | 51.89 | 482.46
10720 | TIN-INTERP | Interpolated Ground | 68600.82 | -6.85 | 459.4 | 0 | 28.57 | 0 | OK | Ground clear controls. | 157 | 51.89 | 487.97
10721 | TIN-INTERP | Interpolated Ground | 68600.86 | 6.44 | 459.18 | 0 | 28.78 | 0 | OK | Ground clear controls. | 157 | 51.89 | 487.96
10722 | TIN-INTERP | Interpolated Ground | 68600.92 | -4.85 | 459.22 | 0 | 34.24 | 0 | OK | Ground clear controls. | 157 | 51.89 | 493.46
10723 | TIN-INTERP | Interpolated Ground | 68600.96 | 4.43 | 459.24 | 0 | 34.22 | 0 | OK | Ground clear controls. | 157 | 51.89 | 493.46
10724 | TIN-INTERP | Interpolated Ground | 68640.72 | 4.9 | 458.31 | 0 | 21.77 | 0 | OK | Ground clear controls. | 157 | 51.89 | 480.08
10725 | TIN-INTERP | Interpolated Ground | 68640.76 | -5.64 | 459.4 | 0 | 20.66 | 0 | OK | Ground clear controls. | 157 | 51.89 | 480.06
10726 | TIN-INTERP | Interpolated Ground | 68640.82 | -7.14 | 460 | 0 | 25.52 | 0 | OK | Ground clear controls. | 157 | 51.89 | 485.52
10727 | TIN-INTERP | Interpolated Ground | 68640.86 | 6.42 | 458.08 | 0 | 27.37 | 0 | OK | Ground clear controls. | 157 | 51.89 | 485.45
10728 | TIN-INTERP | Interpolated Ground | 68640.92 | -5.11 | 459.3 | 0 | 31.75 | 0 | OK | Ground clear controls. | 157 | 51.89 | 491.05
10729 | TIN-INTERP | Interpolated Ground | 68640.96 | 4.39 | 458.42 | 0 | 32.63 | 0 | OK | Ground clear controls. | 157 | 51.89 | 491.05
10730 | TIN-INTERP | Interpolated Ground | 68680.72 | 4.86 | 458.02 | 0 | 20.63 | 0 | OK | Ground clear controls. | 157 | 51.89 | 478.65
10731 | TIN-INTERP | Interpolated Ground | 68680.76 | -5.93 | 460.6 | 0 | 18.02 | 0 | OK | Ground clear controls. | 157 | 51.89 | 478.62
10732 | TIN-INTERP | Interpolated Ground | 68680.82 | -7.43 | 460.69 | 0 | 23.36 | 0 | OK | Ground clear controls. | 157 | 51.89 | 484.05
10733 | TIN-INTERP | Interpolated Ground | 68680.86 | 6.39 | 457.14 | 0 | 26.79 | 0 | OK | Ground clear controls. | 157 | 51.89 | 483.93
10734 | TIN-INTERP | Interpolated Ground | 68680.92 | -5.38 | 460.49 | 0 | 29.13 | 0 | OK | Ground clear controls. | 157 | 51.89 | 489.62
10735 | TIN-INTERP | Interpolated Ground | 68680.96 | 4.34 | 458.41 | 0 | 31.2 | 0 | OK | Ground clear controls. | 157 | 51.89 | 489.61
10736 | TIN-INTERP | Interpolated Ground | 68720.72 | 4.82 | 455.2 | 0 | 22.97 | 0 | OK | Ground clear controls. | 157 | 51.89 | 478.17
10737 | TIN-INTERP | Interpolated Ground | 68720.76 | -6.21 | 454.04 | 0 | 24.08 | 0 | OK | Ground clear controls. | 157 | 51.89 | 478.12
10738 | TIN-INTERP | Interpolated Ground | 68720.82 | -7.72 | 453.29 | 0 | 30.26 | 0 | OK | Ground clear controls. | 157 | 51.89 | 483.55
10739 | TIN-INTERP | Interpolated Ground | 68720.86 | 6.36 | 454.47 | 0 | 28.92 | 0 | OK | Ground clear controls. | 157 | 51.89 | 483.39
10740 | TIN-INTERP | Interpolated Ground | 68720.92 | -5.65 | 454.21 | 0 | 34.96 | 0 | OK | Ground clear controls. | 157 | 51.89 | 489.17
10741 | TIN-INTERP | Interpolated Ground | 68720.96 | 4.29 | 455.49 | 0 | 33.66 | 0 | OK | Ground clear controls. | 157 | 51.89 | 489.15
10742 | TIN-INTERP | Interpolated Ground | 68760.72 | 4.79 | 437.7 | 0 | 40.94 | 0 | OK | Ground clear controls. | 157 | 51.89 | 478.64
10743 | TIN-INTERP | Interpolated Ground | 68760.76 | -6.5 | 439.46 | 0 | 39.13 | 0 | OK | Ground clear controls. | 157 | 51.89 | 478.59
10744 | TIN-INTERP | Interpolated Ground | 68760.82 | -8.01 | 439.68 | 0 | 44.34 | 0 | OK | Ground clear controls. | 157 | 51.89 | 484.02
10745 | TIN-INTERP | Interpolated Ground | 68760.86 | 6.34 | 437.47 | 0 | 46.36 | 0 | OK | Ground clear controls. | 157 | 51.89 | 483.83
10746 | TIN-INTERP | Interpolated Ground | 68760.91 | -5.92 | 439.37 | 0 | 50.32 | 0 | OK | Ground clear controls. | 157 | 51.89 | 489.69
10747 | TIN-INTERP | Interpolated Ground | 68760.96 | 4.24 | 437.79 | 0 | 51.89 | 0 | OK | Ground clear controls. | 157 | 51.89 | 489.68
10748 | TIN-INTERP | Interpolated Ground | 68800.72 | 4.75 | 451.54 | 0 | 28.51 | 0 | OK | Ground clear controls. | 157 | 43.22 | 480.05
10749 | TIN-INTERP | Interpolated Ground | 68800.76 | -6.78 | 449.29 | 0 | 30.72 | 0 | OK | Ground clear controls. | 157 | 43.22 | 480.01
10750 | TIN-INTERP | Interpolated Ground | 68800.82 | -8.3 | 449.33 | 0 | 36.13 | 0 | OK | Ground clear controls. | 157 | 43.22 | 485.46
10751 | TIN-INTERP | Interpolated Ground | 68800.86 | 6.31 | 452.11 | 0 | 33.13 | 0 | OK | Ground clear controls. | 157 | 43.22 | 485.24
10752 | TIN-INTERP | Interpolated Ground | 68800.91 | -6.19 | 449.38 | 0 | 41.82 | 0 | OK | Ground clear controls. | 157 | 43.22 | 491.2
10753 | TIN-INTERP | Interpolated Ground | 68800.96 | 4.19 | 451.42 | 0 | 39.75 | 0 | OK | Ground clear controls. | 157 | 43.22 | 491.17
10754 | TIN-INTERP | Interpolated Ground | 68840.72 | 4.71 | 457.22 | 0 | 25.19 | 0 | OK | Ground clear controls. | 157 | 43.22 | 482.41
10755 | TIN-INTERP | Interpolated Ground | 68840.76 | -7.07 | 459 | 0 | 23.39 | 0 | OK | Ground clear controls. | 157 | 43.22 | 482.39
10756 | TIN-INTERP | Interpolated Ground | 68840.82 | -8.59 | 459.4 | 0 | 28.47 | 0 | OK | Ground clear controls. | 157 | 43.22 | 487.87
10757 | TIN-INTERP | Interpolated Ground | 68840.86 | 6.29 | 457.02 | 0 | 30.63 | 0 | OK | Ground clear controls. | 157 | 43.22 | 487.65
10758 | TIN-INTERP | Interpolated Ground | 68840.91 | -6.46 | 458.88 | 0 | 34.8 | 0 | OK | Ground clear controls. | 157 | 43.22 | 493.68
10759 | TIN-INTERP | Interpolated Ground | 68840.96 | 4.15 | 457.35 | 0 | 36.31 | 0 | OK | Ground clear controls. | 157 | 43.22 | 493.66
10760 | TIN-INTERP | Interpolated Ground | 68880.72 | 4.67 | 459.23 | 0 | 26.5 | 0 | OK | Ground clear controls. | 157 | 43.22 | 485.73
10761 | TIN-INTERP | Interpolated Ground | 68880.76 | -7.36 | 460.71 | 0 | 25.01 | 0 | OK | Ground clear controls. | 157 | 43.22 | 485.72
10762 | TIN-INTERP | Interpolated Ground | 68880.82 | -8.88 | 460.98 | 0 | 30.27 | 0 | OK | Ground clear controls. | 157 | 43.22 | 491.25
10763 | TIN-INTERP | Interpolated Ground | 68880.86 | 6.26 | 459.19 | 0 | 31.86 | 0 | OK | Ground clear controls. | 157 | 43.22 | 491.05
10764 | TIN-INTERP | Interpolated Ground | 68880.91 | -6.72 | 460.63 | 0 | 36.53 | 0 | OK | Ground clear controls. | 157 | 43.22 | 497.16
10765 | TIN-INTERP | Interpolated Ground | 68880.96 | 4.1 | 459.25 | 0 | 37.87 | 0 | OK | Ground clear controls. | 157 | 43.22 | 497.12
10766 | TIN-INTERP | Interpolated Ground | 68920.72 | 4.64 | 470.1 | 0 | 19.91 | 0 | OK | Ground clear controls. | 157 | 43.22 | 490.01
10767 | TIN-INTERP | Interpolated Ground | 68920.76 | -7.64 | 475.56 | 0 | 14.44 | 0 | OK | Ground clear controls. | 157 | 43.22 | 490
10768 | TIN-INTERP | Interpolated Ground | 68920.81 | -9.17 | 476.18 | 0 | 19.44 | 0 | OK | Ground clear controls. | 157 | 43.22 | 495.62
10769 | TIN-INTERP | Interpolated Ground | 68920.86 | 6.23 | 470 | 0 | 25.42 | 0 | OK | Ground clear controls. | 157 | 43.22 | 495.42
10770 | TIN-INTERP | Interpolated Ground | 68920.91 | -6.99 | 475.29 | 0 | 26.32 | 0 | OK | Ground clear controls. | 157 | 43.22 | 501.61
10771 | TIN-INTERP | Interpolated Ground | 68920.96 | 4.05 | 470.25 | 0 | 31.32 | 0 | OK | Ground clear controls. | 157 | 43.22 | 501.57
10772 | TIN-INTERP | Interpolated Ground | 68960.72 | 4.6 | 463.73 | 0 | 31.5 | 0 | OK | Ground clear controls. | 157 | 43.22 | 495.23
10773 | TIN-INTERP | Interpolated Ground | 68960.76 | -7.93 | 476.41 | 0 | 18.85 | 0 | OK | Ground clear controls. | 157 | 43.22 | 495.26
10774 | TIN-INTERP | Interpolated Ground | 68960.81 | -9.46 | 477.97 | 0 | 22.98 | 0 | OK | Ground clear controls. | 157 | 43.22 | 500.95
10775 | TIN-INTERP | Interpolated Ground | 68960.86 | 6.21 | 464.42 | 0 | 36.36 | 0 | OK | Ground clear controls. | 157 | 43.22 | 500.78
10776 | TIN-INTERP | Interpolated Ground | 68960.91 | -7.26 | 475.74 | 0 | 31.32 | 0 | OK | Ground clear controls. | 157 | 43.22 | 507.06
10777 | TIN-INTERP | Interpolated Ground | 68960.96 | 4 | 463.79 | 0 | 43.22 | 0 | OK | Ground clear controls. | 157 | 43.22 | 507.01
10778 | TIN-INTERP | Interpolated Ground | 69000.72 | 4.56 | 481.55 | 0 | 19.88 | 0 | OK | Ground clear controls. | 157 | 31.74 | 501.43
10779 | TIN-INTERP | Interpolated Ground | 69000.75 | -8.21 | 483.74 | 0 | 17.74 | 0 | OK | Ground clear controls. | 157 | 31.74 | 501.48
10780 | TIN-INTERP | Interpolated Ground | 69000.81 | -9.76 | 483.82 | 0 | 23.45 | 0 | OK | Ground clear controls. | 157 | 31.74 | 507.27
10781 | TIN-INTERP | Interpolated Ground | 69000.86 | 6.18 | 481.25 | 0 | 25.88 | 0 | OK | Ground clear controls. | 157 | 31.74 | 507.13
10782 | TIN-INTERP | Interpolated Ground | 69000.91 | -7.53 | 483.71 | 0 | 29.78 | 0 | OK | Ground clear controls. | 157 | 31.74 | 513.49
10783 | TIN-INTERP | Interpolated Ground | 69000.96 | 3.95 | 481.69 | 0 | 31.74 | 0 | OK | Ground clear controls. | 157 | 31.74 | 513.43
10784 | TIN-INTERP | Interpolated Ground | 69004.23 | -9.78 | 483.67 | 0 | 24.18 | 0 | OK | Ground clear controls. | 158 | 36.99 | 507.85
10785 | TIN-INTERP | Interpolated Ground | 69004.43 | -8.24 | 483.51 | 0 | 18.58 | 0 | OK | Ground clear controls. | 158 | 36.99 | 502.09
10786 | TIN-INTERP | Interpolated Ground | 69005.12 | 3.96 | 482.06 | 0 | 32.15 | 0 | OK | Ground clear controls. | 158 | 36.99 | 514.21
10787 | TIN-INTERP | Interpolated Ground | 69005.12 | 4.56 | 481.95 | 0 | 20.24 | 0 | OK | Ground clear controls. | 158 | 36.99 | 502.19
10788 | TIN-INTERP | Interpolated Ground | 69005.12 | 6.19 | 481.69 | 0 | 26.24 | 0 | OK | Ground clear controls. | 158 | 36.99 | 507.93
10789 | TIN-INTERP | Interpolated Ground | 69005.7 | -7.55 | 483.45 | 0 | 30.69 | 0 | OK | Ground clear controls. | 158 | 36.99 | 514.14
10790 | TIN-INTERP | Interpolated Ground | 69044.63 | 4.47 | 483.39 | 0 | 21.45 | 0 | OK | Ground clear controls. | 158 | 36.99 | 504.84
10791 | TIN-INTERP | Interpolated Ground | 69044.67 | 6.1 | 483.76 | 0 | 26.72 | 0 | OK | Ground clear controls. | 158 | 36.99 | 510.48
10792 | TIN-INTERP | Interpolated Ground | 69044.91 | 3.91 | 483.33 | 0 | 33.4 | 0 | OK | Ground clear controls. | 158 | 36.99 | 516.73
10793 | TIN-INTERP | Interpolated Ground | 69045.57 | -8.04 | 485.85 | 0 | 18.94 | 0 | OK | Ground clear controls. | 158 | 36.99 | 504.79
10794 | TIN-INTERP | Interpolated Ground | 69045.59 | -9.59 | 485.66 | 0 | 24.79 | 0 | OK | Ground clear controls. | 158 | 36.99 | 510.45
10795 | TIN-INTERP | Interpolated Ground | 69045.7 | -7.37 | 485.95 | 0 | 30.74 | 0 | OK | Ground clear controls. | 158 | 36.99 | 516.69
10796 | TIN-INTERP | Interpolated Ground | 69084.63 | 4.41 | 483.1 | 0 | 25.36 | 0 | OK | Ground clear controls. | 158 | 36.99 | 508.46
10797 | TIN-INTERP | Interpolated Ground | 69084.67 | 6.02 | 483.75 | 0 | 30.25 | 0 | OK | Ground clear controls. | 158 | 36.99 | 514
10798 | TIN-INTERP | Interpolated Ground | 69084.91 | 3.87 | 483.24 | 0 | 36.99 | 0 | OK | Ground clear controls. | 158 | 36.99 | 520.23
10799 | TIN-INTERP | Interpolated Ground | 69085.57 | -7.83 | 487.92 | 0 | 20.53 | 0 | OK | Ground clear controls. | 158 | 34.79 | 508.45
10800 | TIN-INTERP | Interpolated Ground | 69085.59 | -9.37 | 488.06 | 0 | 25.98 | 0 | OK | Ground clear controls. | 158 | 34.79 | 514.04
10801 | TIN-INTERP | Interpolated Ground | 69085.7 | -7.19 | 487.85 | 0 | 32.37 | 0 | OK | Ground clear controls. | 158 | 34.79 | 520.22
10802 | TIN-INTERP | Interpolated Ground | 69124.63 | 4.35 | 490.97 | 0 | 22.08 | 0 | OK | Ground clear controls. | 158 | 34.79 | 513.05
10803 | TIN-INTERP | Interpolated Ground | 69124.67 | 5.94 | 491.71 | 0 | 26.81 | 0 | OK | Ground clear controls. | 158 | 34.79 | 518.52
10804 | TIN-INTERP | Interpolated Ground | 69124.91 | 3.83 | 490.76 | 0 | 33.95 | 0 | OK | Ground clear controls. | 158 | 34.79 | 524.71
10805 | TIN-INTERP | Interpolated Ground | 69125.57 | -7.62 | 490.17 | 0 | 22.91 | 0 | OK | Ground clear controls. | 158 | 34.79 | 513.08
10806 | TIN-INTERP | Interpolated Ground | 69125.59 | -9.15 | 490.89 | 0 | 27.72 | 0 | OK | Ground clear controls. | 158 | 34.79 | 518.61
10807 | TIN-INTERP | Interpolated Ground | 69125.7 | -7.02 | 489.93 | 0 | 34.79 | 0 | OK | Ground clear controls. | 158 | 34.79 | 524.72
10808 | TIN-INTERP | Interpolated Ground | 69164.63 | 4.29 | 495.7 | 0 | 22.9 | 0 | OK | Ground clear controls. | 158 | 34.02 | 518.6
10809 | TIN-INTERP | Interpolated Ground | 69164.67 | 5.86 | 494.66 | 0 | 29.36 | 0 | OK | Ground clear controls. | 158 | 34.02 | 524.02
10810 | TIN-INTERP | Interpolated Ground | 69164.91 | 3.78 | 496.15 | 0 | 34.02 | 0 | OK | Ground clear controls. | 158 | 34.02 | 530.17
10811 | TIN-INTERP | Interpolated Ground | 69165.57 | -7.4 | 499.62 | 0 | 19.05 | 0 | OK | Ground clear controls. | 158 | 30.68 | 518.67
10812 | TIN-INTERP | Interpolated Ground | 69165.59 | -8.94 | 499.99 | 0 | 24.19 | 0 | OK | Ground clear controls. | 158 | 30.68 | 524.18
10813 | TIN-INTERP | Interpolated Ground | 69165.69 | -6.84 | 499.53 | 0 | 30.68 | 0 | OK | Ground clear controls. | 158 | 30.68 | 530.21
10814 | TIN-INTERP | Interpolated Ground | 69204.63 | 4.23 | 505.93 | 0 | 19.21 | 0 | OK | Ground clear controls. | 158 | 30.56 | 525.14
10815 | TIN-INTERP | Interpolated Ground | 69204.67 | 5.78 | 505.71 | 0 | 24.81 | 0 | OK | Ground clear controls. | 158 | 30.56 | 530.52
10816 | TIN-INTERP | Interpolated Ground | 69204.91 | 3.74 | 506.05 | 0 | 30.56 | 0 | OK | Ground clear controls. | 158 | 30.56 | 536.61
10817 | TIN-INTERP | Interpolated Ground | 69205.57 | -7.19 | 508.23 | 0 | 17.02 | 0 | OK | Ground clear controls. | 158 | 28.92 | 525.25
10818 | TIN-INTERP | Interpolated Ground | 69205.59 | -8.72 | 508.41 | 0 | 22.33 | 0 | OK | Ground clear controls. | 158 | 28.92 | 530.74
10819 | TIN-INTERP | Interpolated Ground | 69205.69 | -6.66 | 508.12 | 0 | 28.56 | 0 | OK | Ground clear controls. | 158 | 28.92 | 536.68
10820 | TIN-INTERP | Interpolated Ground | 69244.63 | 4.17 | 514.89 | 0 | 17.75 | 0 | OK | Ground clear controls. | 158 | 28.92 | 532.64
10821 | TIN-INTERP | Interpolated Ground | 69244.67 | 5.71 | 514.46 | 0 | 23.56 | 0 | OK | Ground clear controls. | 158 | 28.92 | 538.02
10822 | TIN-INTERP | Interpolated Ground | 69244.91 | 3.69 | 515.11 | 0 | 28.92 | 0 | OK | Ground clear controls. | 158 | 28.92 | 544.03
10823 | TIN-INTERP | Interpolated Ground | 69245.57 | -6.98 | 517.89 | 0 | 14.9 | 0 | OK | Ground clear controls. | 158 | 28.73 | 532.79
10824 | TIN-INTERP | Interpolated Ground | 69245.58 | -8.5 | 518.22 | 0 | 20.08 | 0 | OK | Ground clear controls. | 158 | 28.73 | 538.3
10825 | TIN-INTERP | Interpolated Ground | 69245.69 | -6.49 | 517.83 | 0 | 26.32 | 0 | OK | Ground clear controls. | 158 | 28.73 | 544.15
10826 | TIN-INTERP | Interpolated Ground | 69284.63 | 4.11 | 523.59 | 0 | 17.53 | 0 | OK | Ground clear controls. | 158 | 28.73 | 541.12
10827 | TIN-INTERP | Interpolated Ground | 69284.67 | 5.63 | 523.39 | 0 | 23.13 | 0 | OK | Ground clear controls. | 158 | 28.73 | 546.52
10828 | TIN-INTERP | Interpolated Ground | 69284.91 | 3.65 | 523.73 | 0 | 28.73 | 0 | OK | Ground clear controls. | 158 | 28.73 | 552.46
10829 | TIN-INTERP | Interpolated Ground | 69285.57 | -6.76 | 526.57 | 0 | 14.75 | 0 | OK | Ground clear controls. | 158 | 26.13 | 541.32
10830 | TIN-INTERP | Interpolated Ground | 69285.58 | -8.28 | 527.09 | 0 | 19.78 | 0 | OK | Ground clear controls. | 158 | 26.13 | 546.87
10831 | TIN-INTERP | Interpolated Ground | 69285.69 | -6.31 | 526.49 | 0 | 26.13 | 0 | OK | Ground clear controls. | 158 | 26.13 | 552.62
10832 | TIN-INTERP | Interpolated Ground | 69310.02 | -8.15 | 530.87 | 0 | 21.72 | 0 | OK | Ground clear controls. | 159 | 29.87 | 552.59
10833 | TIN-INTERP | Interpolated Ground | 69310.39 | 3.63 | 529.46 | 0 | 28.93 | 0 | OK | Ground clear controls. | 159 | 29.87 | 558.39
10834 | TIN-INTERP | Interpolated Ground | 69310.39 | 4.07 | 529.33 | 0 | 17.8 | 0 | OK | Ground clear controls. | 159 | 29.87 | 547.13
10835 | TIN-INTERP | Interpolated Ground | 69310.39 | 5.58 | 528.93 | 0 | 23.65 | 0 | OK | Ground clear controls. | 159 | 29.87 | 552.58
10836 | TIN-INTERP | Interpolated Ground | 69310.68 | -6.2 | 530.61 | 0 | 27.67 | 0 | OK | Ground clear controls. | 159 | 29.87 | 558.28
10837 | TIN-INTERP | Interpolated Ground | 69310.74 | -6.63 | 530.61 | 0 | 16.46 | 0 | OK | Ground clear controls. | 159 | 29.87 | 547.07
10838 | TIN-INTERP | Interpolated Ground | 69350.16 | 4.21 | 534.91 | 0 | 16.88 | 0 | OK | Ground clear controls. | 159 | 29.87 | 551.79
10839 | TIN-INTERP | Interpolated Ground | 69350.22 | 5.73 | 534.57 | 0 | 22.66 | 0 | OK | Ground clear controls. | 159 | 29.87 | 557.23
10840 | TIN-INTERP | Interpolated Ground | 69350.28 | 3.76 | 534.91 | 0 | 28.09 | 0 | OK | Ground clear controls. | 159 | 29.87 | 563
10841 | TIN-INTERP | Interpolated Ground | 69350.68 | -5.98 | 538.05 | 0 | 24.88 | 0 | OK | Ground clear controls. | 159 | 29.87 | 562.93
10842 | TIN-INTERP | Interpolated Ground | 69350.71 | -7.93 | 538.59 | 0 | 18.66 | 0 | OK | Ground clear controls. | 159 | 29.87 | 557.25
10843 | TIN-INTERP | Interpolated Ground | 69350.74 | -6.41 | 538.25 | 0 | 13.55 | 0 | OK | Ground clear controls. | 159 | 29.87 | 551.8
10844 | TIN-INTERP | Interpolated Ground | 69390.16 | 4.36 | 538.86 | 0 | 18.57 | 0 | OK | Ground clear controls. | 159 | 29.87 | 557.43
10845 | TIN-INTERP | Interpolated Ground | 69390.22 | 5.87 | 539.05 | 0 | 23.8 | 0 | OK | Ground clear controls. | 159 | 29.87 | 562.85
10846 | TIN-INTERP | Interpolated Ground | 69390.28 | 3.9 | 538.9 | 0 | 29.69 | 0 | OK | Ground clear controls. | 159 | 29.87 | 568.59
10847 | TIN-INTERP | Interpolated Ground | 69390.68 | -5.75 | 541.42 | 0 | 27.15 | 0 | OK | Ground clear controls. | 159 | 29.87 | 568.57
10848 | TIN-INTERP | Interpolated Ground | 69390.71 | -7.72 | 541.97 | 0 | 20.93 | 0 | OK | Ground clear controls. | 159 | 29.87 | 562.9
10849 | TIN-INTERP | Interpolated Ground | 69390.74 | -6.2 | 541.55 | 0 | 15.95 | 0 | OK | Ground clear controls. | 159 | 29.87 | 557.5
10850 | TIN-INTERP | Interpolated Ground | 69430.16 | 4.51 | 545.2 | 0 | 18.83 | 0 | OK | Ground clear controls. | 159 | 29.87 | 564.03
10851 | TIN-INTERP | Interpolated Ground | 69430.21 | 6.02 | 544.94 | 0 | 24.53 | 0 | OK | Ground clear controls. | 159 | 29.87 | 569.47
10852 | TIN-INTERP | Interpolated Ground | 69430.28 | 4.04 | 545.29 | 0 | 29.87 | 0 | OK | Ground clear controls. | 159 | 29.87 | 575.16
10853 | TIN-INTERP | Interpolated Ground | 69430.68 | -5.52 | 547.18 | 0 | 28.01 | 0 | OK | Ground clear controls. | 159 | 29.37 | 575.19
10854 | TIN-INTERP | Interpolated Ground | 69430.71 | -7.5 | 547.6 | 0 | 21.94 | 0 | OK | Ground clear controls. | 159 | 29.37 | 569.54
10855 | TIN-INTERP | Interpolated Ground | 69430.74 | -5.99 | 547.27 | 0 | 16.9 | 0 | OK | Ground clear controls. | 159 | 29.37 | 564.17
10856 | TIN-INTERP | Interpolated Ground | 69470.16 | 4.66 | 553.23 | 0 | 18.39 | 0 | OK | Ground clear controls. | 159 | 29.37 | 571.62
10857 | TIN-INTERP | Interpolated Ground | 69470.21 | 6.17 | 552.94 | 0 | 24.14 | 0 | OK | Ground clear controls. | 159 | 29.37 | 577.08
10858 | TIN-INTERP | Interpolated Ground | 69470.28 | 4.18 | 553.35 | 0 | 29.37 | 0 | OK | Ground clear controls. | 159 | 29.37 | 582.72
10859 | TIN-INTERP | Interpolated Ground | 69470.68 | -5.3 | 556.1 | 0 | 26.71 | 0 | OK | Ground clear controls. | 159 | 26.92 | 582.81
10860 | TIN-INTERP | Interpolated Ground | 69470.71 | -7.29 | 556.57 | 0 | 20.63 | 0 | OK | Ground clear controls. | 159 | 26.92 | 577.2
10861 | TIN-INTERP | Interpolated Ground | 69470.74 | -5.78 | 556.22 | 0 | 15.59 | 0 | OK | Ground clear controls. | 159 | 26.92 | 571.81
10862 | TIN-INTERP | Interpolated Ground | 69510.16 | 4.81 | 564.02 | 0 | 16.17 | 0 | OK | Ground clear controls. | 159 | 26.92 | 580.19
10863 | TIN-INTERP | Interpolated Ground | 69510.21 | 6.31 | 563.15 | 0 | 22.55 | 0 | OK | Ground clear controls. | 159 | 26.92 | 585.7
10864 | TIN-INTERP | Interpolated Ground | 69510.27 | 4.31 | 564.35 | 0 | 26.92 | 0 | OK | Ground clear controls. | 159 | 26.92 | 591.27
10865 | TIN-INTERP | Interpolated Ground | 69510.68 | -5.07 | 568.22 | 0 | 23.19 | 0 | OK | Ground clear controls. | 159 | 23.19 | 591.41
10866 | TIN-INTERP | Interpolated Ground | 69510.71 | -7.07 | 568.14 | 0 | 17.71 | 0 | OK | Ground clear controls. | 159 | 17.71 | 585.85
10867 | TIN-INTERP | Interpolated Ground | 69510.74 | -5.56 | 568.23 | 0 | 12.21 | 0 | OK | Ground clear controls. | 159 | 12.21 | 580.44
10868 | TIN-INTERP | Interpolated Ground | 69537.37 | -5.42 | 571.15 | 0 | 15.56 | 0 | OK | Ground clear controls. | 160 | 29.05 | 586.71
10869 | TIN-INTERP | Interpolated Ground | 69537.4 | -4.92 | 570.94 | 0 | 26.77 | 0 | OK | Ground clear controls. | 160 | 29.05 | 597.71
10870 | TIN-INTERP | Interpolated Ground | 69537.55 | -6.93 | 571.84 | 0 | 20.39 | 0 | OK | Ground clear controls. | 160 | 29.05 | 592.23
10871 | TIN-INTERP | Interpolated Ground | 69537.72 | 4.41 | 568.87 | 0 | 28.84 | 0 | OK | Ground clear controls. | 160 | 29.05 | 597.71
10872 | TIN-INTERP | Interpolated Ground | 69537.76 | 6.41 | 568.49 | 0 | 23.72 | 0 | OK | Ground clear controls. | 160 | 29.05 | 592.21
10873 | TIN-INTERP | Interpolated Ground | 69537.87 | 4.91 | 568.8 | 0 | 17.92 | 0 | OK | Ground clear controls. | 160 | 29.05 | 586.72
10874 | TIN-INTERP | Interpolated Ground | 69577.37 | -5.59 | 579.38 | 0 | 11.65 | 0 | OK | Ground clear controls. | 160 | 29.05 | 591.03
10875 | TIN-INTERP | Interpolated Ground | 69577.4 | -5.08 | 579.11 | 0 | 22.97 | 0 | OK | Ground clear controls. | 160 | 29.05 | 602.08
10876 | TIN-INTERP | Interpolated Ground | 69577.55 | -7.11 | 580.18 | 0 | 16.32 | 0 | OK | Ground clear controls. | 160 | 29.05 | 596.5
10877 | TIN-INTERP | Interpolated Ground | 69577.72 | 4.49 | 574.52 | 0 | 27.56 | 0 | OK | Ground clear controls. | 160 | 29.05 | 602.08
10878 | TIN-INTERP | Interpolated Ground | 69577.76 | 6.51 | 573.53 | 0 | 22.94 | 0 | OK | Ground clear controls. | 160 | 29.05 | 596.47
10879 | TIN-INTERP | Interpolated Ground | 69577.87 | 5.01 | 574.29 | 0 | 16.76 | 0 | OK | Ground clear controls. | 160 | 29.05 | 591.05
10880 | TIN-INTERP | Interpolated Ground | 69617.37 | -5.76 | 583.36 | 0 | 12.96 | 0 | OK | Ground clear controls. | 160 | 29.05 | 596.32
10881 | TIN-INTERP | Interpolated Ground | 69617.4 | -5.23 | 583.14 | 0 | 24.28 | 0 | OK | Ground clear controls. | 160 | 29.05 | 607.42
10882 | TIN-INTERP | Interpolated Ground | 69617.55 | -7.28 | 583.87 | 0 | 17.91 | 0 | OK | Ground clear controls. | 160 | 29.05 | 601.78
10883 | TIN-INTERP | Interpolated Ground | 69617.72 | 4.57 | 579.87 | 0 | 27.56 | 0 | OK | Ground clear controls. | 160 | 29.05 | 607.43
10884 | TIN-INTERP | Interpolated Ground | 69617.76 | 6.61 | 579.48 | 0 | 22.23 | 0 | OK | Ground clear controls. | 160 | 29.05 | 601.71
10885 | TIN-INTERP | Interpolated Ground | 69617.87 | 5.11 | 579.82 | 0 | 16.53 | 0 | OK | Ground clear controls. | 160 | 29.05 | 596.35
10886 | TIN-INTERP | Interpolated Ground | 69657.37 | -5.93 | 590.26 | 0 | 12.32 | 0 | OK | Ground clear controls. | 160 | 29.05 | 602.58
10887 | TIN-INTERP | Interpolated Ground | 69657.4 | -5.38 | 590.09 | 0 | 23.66 | 0 | OK | Ground clear controls. | 160 | 29.05 | 613.75
10888 | TIN-INTERP | Interpolated Ground | 69657.55 | -7.46 | 590.76 | 0 | 17.27 | 0 | OK | Ground clear controls. | 160 | 29.05 | 608.03
10889 | TIN-INTERP | Interpolated Ground | 69657.72 | 4.65 | 587.46 | 0 | 26.3 | 0 | OK | Ground clear controls. | 160 | 29.05 | 613.76
10890 | TIN-INTERP | Interpolated Ground | 69657.76 | 6.71 | 586.89 | 0 | 21.05 | 0 | OK | Ground clear controls. | 160 | 29.05 | 607.94
10891 | TIN-INTERP | Interpolated Ground | 69657.87 | 5.21 | 587.34 | 0 | 15.27 | 0 | OK | Ground clear controls. | 160 | 29.05 | 602.61
10892 | TIN-INTERP | Interpolated Ground | 69697.37 | -6.1 | 596.99 | 0 | 12.83 | 0 | OK | Ground clear controls. | 160 | 29.05 | 609.82
10893 | TIN-INTERP | Interpolated Ground | 69697.4 | -5.54 | 596.73 | 0 | 24.34 | 0 | OK | Ground clear controls. | 160 | 29.05 | 621.07
10894 | TIN-INTERP | Interpolated Ground | 69697.55 | -7.64 | 597.58 | 0 | 17.7 | 0 | OK | Ground clear controls. | 160 | 29.05 | 615.28
10895 | TIN-INTERP | Interpolated Ground | 69697.72 | 4.73 | 592.37 | 0 | 28.71 | 0 | OK | Ground clear controls. | 160 | 29.05 | 621.08
10896 | TIN-INTERP | Interpolated Ground | 69697.76 | 6.81 | 591.43 | 0 | 23.73 | 0 | OK | Ground clear controls. | 160 | 29.05 | 615.16
10897 | TIN-INTERP | Interpolated Ground | 69697.87 | 5.31 | 592.09 | 0 | 17.74 | 0 | OK | Ground clear controls. | 160 | 29.05 | 609.83
10898 | TIN-INTERP | Interpolated Ground | 69737.37 | -6.27 | 601.65 | 0 | 16.39 | 0 | OK | Ground clear controls. | 160 | 29.05 | 618.04
10899 | TIN-INTERP | Interpolated Ground | 69737.4 | -5.69 | 601.59 | 0 | 27.81 | 0 | OK | Ground clear controls. | 160 | 29.05 | 629.4
10900 | TIN-INTERP | Interpolated Ground | 69737.55 | -7.82 | 602.05 | 0 | 21.48 | 0 | OK | Ground clear controls. | 160 | 29.05 | 623.53
10901 | TIN-INTERP | Interpolated Ground | 69737.72 | 4.81 | 600.33 | 0 | 29.05 | 0 | OK | Ground clear controls. | 160 | 29.05 | 629.38
10902 | TIN-INTERP | Interpolated Ground | 69737.76 | 6.91 | 600.45 | 0 | 22.92 | 0 | OK | Ground clear controls. | 160 | 26.47 | 623.37
10903 | TIN-INTERP | Interpolated Ground | 69737.87 | 5.41 | 600.37 | 0 | 17.67 | 0 | OK | Ground clear controls. | 160 | 26.47 | 618.04
10904 | TIN-INTERP | Interpolated Ground | 69777.37 | -6.44 | 613.86 | 0 | 13.37 | 0 | OK | Ground clear controls. | 160 | 26.47 | 627.23
10905 | TIN-INTERP | Interpolated Ground | 69777.4 | -5.84 | 613.66 | 0 | 25.05 | 0 | OK | Ground clear controls. | 160 | 26.47 | 638.71
10906 | TIN-INTERP | Interpolated Ground | 69777.55 | -8 | 614.32 | 0 | 18.46 | 0 | OK | Ground clear controls. | 160 | 26.47 | 632.78
10907 | TIN-INTERP | Interpolated Ground | 69777.72 | 4.89 | 612.22 | 0 | 26.47 | 0 | OK | Ground clear controls. | 160 | 26.47 | 638.69
10908 | TIN-INTERP | Interpolated Ground | 69777.76 | 7.01 | 612.33 | 0 | 20.26 | 0 | OK | Ground clear controls. | 160 | 26.32 | 632.59
10909 | TIN-INTERP | Interpolated Ground | 69777.87 | 5.51 | 612.3 | 0 | 14.92 | 0 | OK | Ground clear controls. | 160 | 26.32 | 627.22
10910 | TIN-INTERP | Interpolated Ground | 69817.37 | -6.6 | 624.33 | 0 | 13.08 | 0 | OK | Ground clear controls. | 160 | 26.32 | 637.41
10911 | TIN-INTERP | Interpolated Ground | 69817.4 | -6 | 624.44 | 0 | 24.6 | 0 | OK | Ground clear controls. | 160 | 26.32 | 649.04
10912 | TIN-INTERP | Interpolated Ground | 69817.55 | -8.18 | 623.99 | 0 | 19.04 | 0 | OK | Ground clear controls. | 160 | 26.32 | 643.03
10913 | TIN-INTERP | Interpolated Ground | 69817.72 | 4.97 | 622.87 | 0 | 26.11 | 0 | OK | Ground clear controls. | 160 | 26.32 | 648.98
10914 | TIN-INTERP | Interpolated Ground | 69817.76 | 7.11 | 623.07 | 0 | 19.74 | 0 | OK | Ground clear controls. | 160 | 26.32 | 642.81
10915 | TIN-INTERP | Interpolated Ground | 69817.87 | 5.61 | 622.91 | 0 | 14.47 | 0 | OK | Ground clear controls. | 160 | 26.32 | 637.38
10916 | TIN-INTERP | Interpolated Ground | 69857.37 | -6.77 | 634.85 | 0 | 13.75 | 0 | OK | Ground clear controls. | 160 | 26.32 | 648.6
10917 | TIN-INTERP | Interpolated Ground | 69857.4 | -6.15 | 634.87 | 0 | 25.51 | 0 | OK | Ground clear controls. | 160 | 26.32 | 660.38
10918 | TIN-INTERP | Interpolated Ground | 69857.55 | -8.36 | 634.86 | 0 | 19.43 | 0 | OK | Ground clear controls. | 160 | 26.32 | 654.29
10919 | TIN-INTERP | Interpolated Ground | 69857.72 | 5.05 | 633.96 | 0 | 26.32 | 0 | OK | Ground clear controls. | 160 | 26.32 | 660.28
10920 | TIN-INTERP | Interpolated Ground | 69857.76 | 7.21 | 634.11 | 0 | 19.93 | 0 | OK | Ground clear controls. | 160 | 25.7 | 654.04
10921 | TIN-INTERP | Interpolated Ground | 69857.87 | 5.71 | 634.05 | 0 | 14.48 | 0 | OK | Ground clear controls. | 160 | 25.7 | 648.53
10922 | TIN-INTERP | Interpolated Ground | 69897.37 | -6.94 | 647.48 | 0 | 13.3 | 0 | OK | Ground clear controls. | 160 | 25.7 | 660.78
10923 | TIN-INTERP | Interpolated Ground | 69897.4 | -6.3 | 647.34 | 0 | 25.39 | 0 | OK | Ground clear controls. | 160 | 25.7 | 672.73
10924 | TIN-INTERP | Interpolated Ground | 69897.55 | -8.53 | 647.72 | 0 | 18.85 | 0 | OK | Ground clear controls. | 160 | 25.7 | 666.57
10925 | TIN-INTERP | Interpolated Ground | 69897.72 | 5.13 | 646.9 | 0 | 25.7 | 0 | OK | Ground clear controls. | 160 | 25.7 | 672.6
10926 | TIN-INTERP | Interpolated Ground | 69897.75 | 7.31 | 647.25 | 0 | 19.05 | 0 | OK | Ground clear controls. | 160 | 19.05 | 666.3
10927 | TIN-INTERP | Interpolated Ground | 69897.87 | 5.81 | 646.99 | 0 | 13.69 | 0 | OK | Ground clear controls. | 160 | 13.69 | 660.68
10928 | TIN-INTERP | Interpolated Ground | 69924.85 | -7.06 | 651.97 | 0 | 17.77 | 0 | OK | Ground clear controls. | 161 | 99.56 | 669.74
10929 | TIN-INTERP | Interpolated Ground | 69924.95 | -6.41 | 652.03 | 0 | 29.81 | 0 | OK | Ground clear controls. | 161 | 99.56 | 681.84
10930 | TIN-INTERP | Interpolated Ground | 69925.37 | 5.2 | 652.37 | 0 | 29.47 | 0 | OK | Ground clear controls. | 161 | 99.56 | 681.84
10931 | TIN-INTERP | Interpolated Ground | 69925.37 | 5.89 | 652.31 | 0 | 17.43 | 0 | OK | Ground clear controls. | 161 | 99.56 | 669.74
10932 | TIN-INTERP | Interpolated Ground | 69925.37 | 7.4 | 652.08 | 0 | 23.46 | 0 | OK | Ground clear controls. | 161 | 99.56 | 675.54
10933 | TIN-INTERP | Interpolated Ground | 69925.94 | -8.65 | 651.87 | 0 | 23.67 | 0 | OK | Ground clear controls. | 161 | 99.56 | 675.54
10934 | TIN-INTERP | Interpolated Ground | 69964.99 | 7.42 | 640 | 0 | 26.54 | 0 | OK | Ground clear controls. | 161 | 99.56 | 666.54
10935 | TIN-INTERP | Interpolated Ground | 69965.01 | 5.91 | 639.88 | 0 | 20.95 | 0 | OK | Ground clear controls. | 161 | 99.56 | 660.83
10936 | TIN-INTERP | Interpolated Ground | 69965.1 | 5.22 | 639.86 | 0 | 33.02 | 0 | OK | Ground clear controls. | 161 | 99.56 | 672.88
10937 | TIN-INTERP | Interpolated Ground | 69965.77 | -7.06 | 641.68 | 0 | 19.15 | 0 | OK | Ground clear controls. | 161 | 99.56 | 660.83
10938 | TIN-INTERP | Interpolated Ground | 69965.78 | -6.4 | 641.58 | 0 | 31.31 | 0 | OK | Ground clear controls. | 161 | 99.56 | 672.89
10939 | TIN-INTERP | Interpolated Ground | 69965.94 | -8.64 | 641.67 | 0 | 24.97 | 0 | OK | Ground clear controls. | 161 | 99.56 | 666.64
10940 | TIN-INTERP | Interpolated Ground | 70004.99 | 7.44 | 621.94 | 0 | 36.57 | 0 | OK | Ground clear controls. | 161 | 99.56 | 658.51
10941 | TIN-INTERP | Interpolated Ground | 70005.01 | 5.94 | 622.09 | 0 | 30.79 | 0 | OK | Ground clear controls. | 161 | 99.56 | 652.88
10942 | TIN-INTERP | Interpolated Ground | 70005.1 | 5.25 | 622.12 | 0 | 42.76 | 0 | OK | Ground clear controls. | 161 | 99.56 | 664.88
10943 | TIN-INTERP | Interpolated Ground | 70005.77 | -7.05 | 626.69 | 0 | 26.2 | 0 | OK | Ground clear controls. | 161 | 99.56 | 652.89
10944 | TIN-INTERP | Interpolated Ground | 70005.78 | -6.39 | 626.29 | 0 | 38.62 | 0 | OK | Ground clear controls. | 161 | 99.56 | 664.91
10945 | TIN-INTERP | Interpolated Ground | 70005.94 | -8.63 | 627.58 | 0 | 31.13 | 0 | OK | Ground clear controls. | 161 | 99.56 | 658.71
10946 | TIN-INTERP | Interpolated Ground | 70044.99 | 7.47 | 609.21 | 0 | 42.26 | 0 | OK | Ground clear controls. | 161 | 99.56 | 651.47
10947 | TIN-INTERP | Interpolated Ground | 70045.01 | 5.96 | 609.48 | 0 | 36.44 | 0 | OK | Ground clear controls. | 161 | 99.56 | 645.92
10948 | TIN-INTERP | Interpolated Ground | 70045.1 | 5.27 | 609.64 | 0 | 48.24 | 0 | OK | Ground clear controls. | 161 | 99.56 | 657.88
10949 | TIN-INTERP | Interpolated Ground | 70045.77 | -7.04 | 616.1 | 0 | 29.85 | 0 | OK | Ground clear controls. | 161 | 99.56 | 645.95
10950 | TIN-INTERP | Interpolated Ground | 70045.78 | -6.38 | 615.68 | 0 | 42.24 | 0 | OK | Ground clear controls. | 161 | 99.56 | 657.92
10951 | TIN-INTERP | Interpolated Ground | 70045.94 | -8.62 | 616.95 | 0 | 34.81 | 0 | OK | Ground clear controls. | 161 | 99.56 | 651.76
10952 | TIN-INTERP | Interpolated Ground | 70084.99 | 7.49 | 595.51 | 0 | 49.92 | 0 | OK | Ground clear controls. | 161 | 99.56 | 645.43
10953 | TIN-INTERP | Interpolated Ground | 70085.01 | 5.99 | 596.4 | 0 | 43.54 | 0 | OK | Ground clear controls. | 161 | 99.56 | 639.94
10954 | TIN-INTERP | Interpolated Ground | 70085.1 | 5.3 | 596.78 | 0 | 55.1 | 0 | OK | Ground clear controls. | 161 | 99.56 | 651.88
10955 | TIN-INTERP | Interpolated Ground | 70085.77 | -7.04 | 602.84 | 0 | 37.13 | 0 | OK | Ground clear controls. | 161 | 99.56 | 639.97
10956 | TIN-INTERP | Interpolated Ground | 70085.78 | -6.37 | 602.39 | 0 | 49.53 | 0 | OK | Ground clear controls. | 161 | 99.56 | 651.92
10957 | TIN-INTERP | Interpolated Ground | 70085.94 | -8.61 | 603.8 | 0 | 41.99 | 0 | OK | Ground clear controls. | 161 | 99.56 | 645.79
10958 | TIN-INTERP | Interpolated Ground | 70124.99 | 7.52 | 582.73 | 0 | 57.63 | 0 | OK | Ground clear controls. | 161 | 99.56 | 640.36
10959 | TIN-INTERP | Interpolated Ground | 70125.01 | 6.02 | 583.02 | 0 | 51.88 | 0 | OK | Ground clear controls. | 161 | 99.56 | 634.9
10960 | TIN-INTERP | Interpolated Ground | 70125.1 | 5.33 | 583.37 | 0 | 63.45 | 0 | OK | Ground clear controls. | 161 | 99.56 | 646.82
10961 | TIN-INTERP | Interpolated Ground | 70125.77 | -7.03 | 589.37 | 0 | 45.58 | 0 | OK | Ground clear controls. | 161 | 99.56 | 634.95
10962 | TIN-INTERP | Interpolated Ground | 70125.78 | -6.36 | 588.93 | 0 | 57.95 | 0 | OK | Ground clear controls. | 161 | 99.56 | 646.88
10963 | TIN-INTERP | Interpolated Ground | 70125.94 | -8.59 | 590.02 | 0 | 50.77 | 0 | OK | Ground clear controls. | 161 | 99.56 | 640.79
10964 | TIN-INTERP | Interpolated Ground | 70164.99 | 7.55 | 566.21 | 0 | 70.06 | 0 | OK | Ground clear controls. | 161 | 99.56 | 636.27
10965 | TIN-INTERP | Interpolated Ground | 70165.01 | 6.04 | 565.59 | 0 | 65.27 | 0 | OK | Ground clear controls. | 161 | 99.56 | 630.86
10966 | TIN-INTERP | Interpolated Ground | 70165.1 | 5.35 | 565.56 | 0 | 77.2 | 0 | OK | Ground clear controls. | 161 | 99.56 | 642.76
10967 | TIN-INTERP | Interpolated Ground | 70165.77 | -7.02 | 570.2 | 0 | 60.72 | 0 | OK | Ground clear controls. | 161 | 99.56 | 630.92
10968 | TIN-INTERP | Interpolated Ground | 70165.78 | -6.35 | 569.96 | 0 | 72.87 | 0 | OK | Ground clear controls. | 161 | 99.56 | 642.83
10969 | TIN-INTERP | Interpolated Ground | 70165.94 | -8.58 | 570.65 | 0 | 66.12 | 0 | OK | Ground clear controls. | 161 | 99.56 | 636.77
10970 | TIN-INTERP | Interpolated Ground | 70204.99 | 7.57 | 555.16 | 0 | 78.01 | 0 | OK | Ground clear controls. | 161 | 99.56 | 633.17
10971 | TIN-INTERP | Interpolated Ground | 70205.01 | 6.07 | 554.62 | 0 | 73.16 | 0 | OK | Ground clear controls. | 161 | 99.56 | 627.78
10972 | TIN-INTERP | Interpolated Ground | 70205.1 | 5.38 | 554.21 | 0 | 85.45 | 0 | OK | Ground clear controls. | 161 | 99.56 | 639.66
10973 | TIN-INTERP | Interpolated Ground | 70205.77 | -7.02 | 556.7 | 0 | 71.15 | 0 | OK | Ground clear controls. | 161 | 99.56 | 627.85
10974 | TIN-INTERP | Interpolated Ground | 70205.78 | -6.34 | 555.98 | 0 | 83.76 | 0 | OK | Ground clear controls. | 161 | 99.56 | 639.74
10975 | TIN-INTERP | Interpolated Ground | 70205.94 | -8.57 | 558.33 | 0 | 75.37 | 0 | OK | Ground clear controls. | 161 | 99.56 | 633.7
10976 | TIN-INTERP | Interpolated Ground | 70244.99 | 7.6 | 543.86 | 0 | 87.17 | 0 | OK | Ground clear controls. | 161 | 99.56 | 631.03
10977 | TIN-INTERP | Interpolated Ground | 70245.01 | 6.1 | 542.99 | 0 | 82.66 | 0 | OK | Ground clear controls. | 161 | 99.56 | 625.65
10978 | TIN-INTERP | Interpolated Ground | 70245.1 | 5.4 | 542.57 | 0 | 94.96 | 0 | OK | Ground clear controls. | 161 | 99.56 | 637.53
10979 | TIN-INTERP | Interpolated Ground | 70245.77 | -7.01 | 541.88 | 0 | 83.85 | 0 | OK | Ground clear controls. | 161 | 99.56 | 625.73
10980 | TIN-INTERP | Interpolated Ground | 70245.78 | -6.33 | 541.22 | 0 | 96.4 | 0 | OK | Ground clear controls. | 161 | 99.56 | 637.62
10981 | TIN-INTERP | Interpolated Ground | 70245.94 | -8.56 | 542.43 | 0 | 89.15 | 0 | OK | Ground clear controls. | 161 | 99.56 | 631.58
10982 | TIN-INTERP | Interpolated Ground | 70284.99 | 7.63 | 535.76 | 0 | 94.11 | 0 | OK | Ground clear controls. | 161 | 99.56 | 629.87
10983 | TIN-INTERP | Interpolated Ground | 70285.01 | 6.12 | 536.47 | 0 | 88.03 | 0 | OK | Ground clear controls. | 161 | 99.56 | 624.5
10984 | TIN-INTERP | Interpolated Ground | 70285.1 | 5.43 | 536.82 | 0 | 99.56 | 0 | OK | Ground clear controls. | 161 | 99.56 | 636.38
10985 | TIN-INTERP | Interpolated Ground | 70285.77 | -7 | 545.25 | 0 | 79.34 | 0 | OK | Ground clear controls. | 161 | 91.61 | 624.59
10986 | TIN-INTERP | Interpolated Ground | 70285.78 | -6.32 | 544.87 | 0 | 91.61 | 0 | OK | Ground clear controls. | 161 | 91.61 | 636.48
10987 | TIN-INTERP | Interpolated Ground | 70285.94 | -8.55 | 546.32 | 0 | 84.12 | 0 | OK | Ground clear controls. | 161 | 90.17 | 630.44
10988 | TIN-INTERP | Interpolated Ground | 70324.99 | 7.65 | 544.75 | 0 | 84.93 | 0 | OK | Ground clear controls. | 161 | 90.17 | 629.68
10989 | TIN-INTERP | Interpolated Ground | 70325.01 | 6.15 | 545.61 | 0 | 78.7 | 0 | OK | Ground clear controls. | 161 | 90.17 | 624.31
10990 | TIN-INTERP | Interpolated Ground | 70325.1 | 5.46 | 546.02 | 0 | 90.17 | 0 | OK | Ground clear controls. | 161 | 90.17 | 636.19
10991 | TIN-INTERP | Interpolated Ground | 70325.77 | -7 | 553.49 | 0 | 70.92 | 0 | OK | Ground clear controls. | 161 | 83.14 | 624.41
10992 | TIN-INTERP | Interpolated Ground | 70325.78 | -6.31 | 553.16 | 0 | 83.14 | 0 | OK | Ground clear controls. | 161 | 83.14 | 636.3
10993 | TIN-INTERP | Interpolated Ground | 70325.94 | -8.53 | 554.34 | 0 | 75.93 | 0 | OK | Ground clear controls. | 161 | 82.05 | 630.27
10994 | TIN-INTERP | Interpolated Ground | 70364.99 | 7.68 | 553.48 | 0 | 76.98 | 0 | OK | Ground clear controls. | 161 | 82.05 | 630.46
10995 | TIN-INTERP | Interpolated Ground | 70365.01 | 6.18 | 554.53 | 0 | 70.53 | 0 | OK | Ground clear controls. | 161 | 82.05 | 625.06
10996 | TIN-INTERP | Interpolated Ground | 70365.1 | 5.48 | 554.92 | 0 | 82.05 | 0 | OK | Ground clear controls. | 161 | 82.05 | 636.97
10997 | TIN-INTERP | Interpolated Ground | 70365.77 | -6.99 | 563.65 | 0 | 61.53 | 0 | OK | Ground clear controls. | 161 | 78.94 | 625.18
10998 | TIN-INTERP | Interpolated Ground | 70365.78 | -6.3 | 563.01 | 0 | 74.07 | 0 | OK | Ground clear controls. | 161 | 78.94 | 637.08
10999 | TIN-INTERP | Interpolated Ground | 70365.94 | -8.52 | 564.56 | 0 | 66.48 | 0 | OK | Ground clear controls. | 161 | 78.94 | 631.04
11000 | TIN-INTERP | Interpolated Ground | 70404.99 | 7.71 | 558.37 | 0 | 73.86 | 0 | OK | Ground clear controls. | 161 | 78.94 | 632.23
11001 | TIN-INTERP | Interpolated Ground | 70405.01 | 6.2 | 559.38 | 0 | 67.42 | 0 | OK | Ground clear controls. | 161 | 78.94 | 626.8
11002 | TIN-INTERP | Interpolated Ground | 70405.1 | 5.51 | 559.78 | 0 | 78.94 | 0 | OK | Ground clear controls. | 161 | 78.94 | 638.72
11003 | TIN-INTERP | Interpolated Ground | 70405.77 | -6.98 | 568.4 | 0 | 58.53 | 0 | OK | Ground clear controls. | 161 | 72.68 | 626.93
11004 | TIN-INTERP | Interpolated Ground | 70405.78 | -6.29 | 567.97 | 0 | 70.88 | 0 | OK | Ground clear controls. | 161 | 72.68 | 638.85
11005 | TIN-INTERP | Interpolated Ground | 70405.94 | -8.51 | 569.32 | 0 | 63.47 | 0 | OK | Ground clear controls. | 161 | 72.68 | 632.79
11006 | TIN-INTERP | Interpolated Ground | 70444.99 | 7.73 | 567.92 | 0 | 67.05 | 0 | OK | Ground clear controls. | 161 | 72.68 | 634.97
11007 | TIN-INTERP | Interpolated Ground | 70445.01 | 6.23 | 568.37 | 0 | 61.13 | 0 | OK | Ground clear controls. | 161 | 72.68 | 629.5
11008 | TIN-INTERP | Interpolated Ground | 70445.1 | 5.53 | 568.76 | 0 | 72.68 | 0 | OK | Ground clear controls. | 161 | 72.68 | 641.44
11009 | TIN-INTERP | Interpolated Ground | 70445.77 | -6.97 | 575.72 | 0 | 53.92 | 0 | OK | Ground clear controls. | 161 | 66.19 | 629.64
11010 | TIN-INTERP | Interpolated Ground | 70445.78 | -6.29 | 575.38 | 0 | 66.19 | 0 | OK | Ground clear controls. | 161 | 66.19 | 641.57
11011 | TIN-INTERP | Interpolated Ground | 70445.94 | -8.5 | 576.86 | 0 | 58.63 | 0 | OK | Ground clear controls. | 161 | 58.63 | 635.49
11012 | TIN-INTERP | Interpolated Ground | 70484.99 | 7.76 | 587.38 | 0 | 51.28 | 0 | OK | Ground clear controls. | 161 | 56.52 | 638.66
11013 | TIN-INTERP | Interpolated Ground | 70485.01 | 6.26 | 588.17 | 0 | 44.99 | 0 | OK | Ground clear controls. | 161 | 56.52 | 633.16
11014 | TIN-INTERP | Interpolated Ground | 70485.1 | 5.56 | 588.6 | 0 | 56.52 | 0 | OK | Ground clear controls. | 161 | 56.52 | 645.12
11015 | TIN-INTERP | Interpolated Ground | 70485.77 | -6.97 | 599.31 | 0 | 33.99 | 0 | OK | Ground clear controls. | 161 | 46.83 | 633.3
11016 | TIN-INTERP | Interpolated Ground | 70485.78 | -6.28 | 598.56 | 0 | 46.7 | 0 | OK | Ground clear controls. | 161 | 46.83 | 645.26
11017 | TIN-INTERP | Interpolated Ground | 70485.94 | -8.49 | 601.65 | 0 | 37.5 | 0 | OK | Ground clear controls. | 161 | 46.83 | 639.15
11018 | TIN-INTERP | Interpolated Ground | 70524.99 | 7.78 | 601.38 | 0 | 41.97 | 0 | OK | Ground clear controls. | 161 | 46.83 | 643.35
11019 | TIN-INTERP | Interpolated Ground | 70525.01 | 6.28 | 602.43 | 0 | 35.35 | 0 | OK | Ground clear controls. | 161 | 46.83 | 637.78
11020 | TIN-INTERP | Interpolated Ground | 70525.1 | 5.59 | 602.95 | 0 | 46.83 | 0 | OK | Ground clear controls. | 161 | 46.83 | 649.78
11021 | TIN-INTERP | Interpolated Ground | 70525.77 | -6.96 | 612.88 | 0 | 25.07 | 0 | OK | Ground clear controls. | 161 | 37.53 | 637.95
11022 | TIN-INTERP | Interpolated Ground | 70525.78 | -6.27 | 612.41 | 0 | 37.53 | 0 | OK | Ground clear controls. | 161 | 37.53 | 649.94
11023 | TIN-INTERP | Interpolated Ground | 70525.94 | -8.47 | 614.88 | 0 | 28.91 | 0 | OK | Ground clear controls. | 161 | 33.37 | 643.79
11024 | TIN-INTERP | Interpolated Ground | 70564.99 | 7.81 | 619.01 | 0 | 30.01 | 0 | OK | Ground clear controls. | 161 | 33.37 | 649.02
11025 | TIN-INTERP | Interpolated Ground | 70565.01 | 6.31 | 621.03 | 0 | 22.35 | 0 | OK | Ground clear controls. | 161 | 33.37 | 643.38
11026 | TIN-INTERP | Interpolated Ground | 70565.1 | 5.61 | 622.06 | 0 | 33.37 | 0 | OK | Ground clear controls. | 161 | 33.37 | 655.43
11027 | TIN-INTERP | Interpolated Ground | 70565.77 | -6.95 | 634.09 | 0 | 9.47 | 0 | OK | Ground clear controls. | 161 | 26.24 | 643.56
11028 | TIN-INTERP | Interpolated Ground | 70565.78 | -6.26 | 633.88 | 0 | 21.7 | 0 | OK | Ground clear controls. | 161 | 26.24 | 655.58
11029 | TIN-INTERP | Interpolated Ground | 70565.94 | -8.46 | 634.73 | 0 | 14.68 | 0 | OK | Ground clear controls. | 161 | 26.24 | 649.41
11030 | TIN-INTERP | Interpolated Ground | 70604.99 | 7.84 | 634.83 | 0 | 20.84 | 0 | OK | Ground clear controls. | 161 | 26.24 | 655.67
11031 | TIN-INTERP | Interpolated Ground | 70605.01 | 6.34 | 635.41 | 0 | 14.53 | 0 | OK | Ground clear controls. | 161 | 26.24 | 649.94
11032 | TIN-INTERP | Interpolated Ground | 70605.1 | 5.64 | 635.79 | 0 | 26.24 | 0 | OK | Ground clear controls. | 161 | 26.24 | 662.03
11033 | TIN-INTERP | Interpolated Ground | 70605.77 | -6.95 | 636.47 | 0 | 13.65 | 0 | OK | Ground clear controls. | 161 | 25.63 | 650.12
11034 | TIN-INTERP | Interpolated Ground | 70605.78 | -6.25 | 636.57 | 0 | 25.63 | 0 | OK | Ground clear controls. | 161 | 25.63 | 662.2
11035 | TIN-INTERP | Interpolated Ground | 70605.94 | -8.45 | 636.07 | 0 | 19.9 | 0 | OK | Ground clear controls. | 161 | 19.9 | 655.97
11036 | TIN-INTERP | Interpolated Ground | 70628.31 | -8.44 | 636.87 | 0 | 23.21 | 0 | OK | Ground clear controls. | 162 | 223.6 | 660.08
11037 | TIN-INTERP | Interpolated Ground | 70628.48 | 5.65 | 634.62 | 0 | 31.76 | 0 | OK | Ground clear controls. | 162 | 223.6 | 666.38
11038 | TIN-INTERP | Interpolated Ground | 70628.48 | 6.35 | 634.5 | 0 | 19.78 | 0 | OK | Ground clear controls. | 162 | 223.6 | 654.28
11039 | TIN-INTERP | Interpolated Ground | 70628.48 | 7.86 | 634.19 | 0 | 25.88 | 0 | OK | Ground clear controls. | 162 | 223.6 | 660.07
11040 | TIN-INTERP | Interpolated Ground | 70628.62 | -6.24 | 636.82 | 0 | 29.56 | 0 | OK | Ground clear controls. | 162 | 223.6 | 666.38
11041 | TIN-INTERP | Interpolated Ground | 70628.65 | -6.94 | 636.76 | 0 | 17.51 | 0 | OK | Ground clear controls. | 162 | 223.6 | 654.27
11042 | TIN-INTERP | Interpolated Ground | 70668.37 | 5.69 | 611.61 | 0 | 42.45 | 0 | OK | Ground clear controls. | 162 | 223.6 | 654.06
11043 | TIN-INTERP | Interpolated Ground | 70668.38 | 7.89 | 611.34 | 0 | 36.48 | 0 | OK | Ground clear controls. | 162 | 223.6 | 647.82
11044 | TIN-INTERP | Interpolated Ground | 70668.38 | 6.38 | 611.64 | 0 | 30.43 | 0 | OK | Ground clear controls. | 162 | 223.6 | 642.07
11045 | TIN-INTERP | Interpolated Ground | 70668.62 | -6.2 | 612.3 | 0 | 41.79 | 0 | OK | Ground clear controls. | 162 | 223.6 | 654.09
11046 | TIN-INTERP | Interpolated Ground | 70668.64 | -8.4 | 612.29 | 0 | 35.52 | 0 | OK | Ground clear controls. | 162 | 223.6 | 647.81
11047 | TIN-INTERP | Interpolated Ground | 70668.65 | -6.9 | 612.33 | 0 | 29.75 | 0 | OK | Ground clear controls. | 162 | 223.6 | 642.08
11048 | TIN-INTERP | Interpolated Ground | 70708.37 | 5.72 | 582.39 | 0 | 60.36 | 0 | OK | Ground clear controls. | 162 | 223.6 | 642.75
11049 | TIN-INTERP | Interpolated Ground | 70708.38 | 7.92 | 582.84 | 0 | 53.71 | 0 | OK | Ground clear controls. | 162 | 223.6 | 636.55
11050 | TIN-INTERP | Interpolated Ground | 70708.38 | 6.42 | 582.47 | 0 | 48.39 | 0 | OK | Ground clear controls. | 162 | 223.6 | 630.86
11051 | TIN-INTERP | Interpolated Ground | 70708.62 | -6.16 | 582.25 | 0 | 60.55 | 0 | OK | Ground clear controls. | 162 | 223.6 | 642.8
11052 | TIN-INTERP | Interpolated Ground | 70708.64 | -8.36 | 582.32 | 0 | 54.22 | 0 | OK | Ground clear controls. | 162 | 223.6 | 636.54
11053 | TIN-INTERP | Interpolated Ground | 70708.65 | -6.86 | 582.24 | 0 | 48.62 | 0 | OK | Ground clear controls. | 162 | 223.6 | 630.86
11054 | TIN-INTERP | Interpolated Ground | 70748.37 | 5.76 | 555.49 | 0 | 76.96 | 0 | OK | Ground clear controls. | 162 | 223.6 | 632.45
11055 | TIN-INTERP | Interpolated Ground | 70748.38 | 7.96 | 556.22 | 0 | 70.06 | 0 | OK | Ground clear controls. | 162 | 223.6 | 626.28
11056 | TIN-INTERP | Interpolated Ground | 70748.38 | 6.45 | 555.72 | 0 | 64.91 | 0 | OK | Ground clear controls. | 162 | 223.6 | 620.63
11057 | TIN-INTERP | Interpolated Ground | 70748.62 | -6.11 | 554.19 | 0 | 78.32 | 0 | OK | Ground clear controls. | 162 | 223.6 | 632.51
11058 | TIN-INTERP | Interpolated Ground | 70748.64 | -8.32 | 554.6 | 0 | 71.67 | 0 | OK | Ground clear controls. | 162 | 223.6 | 626.27
11059 | TIN-INTERP | Interpolated Ground | 70748.65 | -6.81 | 554.27 | 0 | 66.37 | 0 | OK | Ground clear controls. | 162 | 223.6 | 620.64
11060 | TIN-INTERP | Interpolated Ground | 70788.37 | 5.79 | 526.92 | 0 | 96.21 | 0 | OK | Ground clear controls. | 162 | 223.6 | 623.13
11061 | TIN-INTERP | Interpolated Ground | 70788.38 | 7.99 | 527.63 | 0 | 89.37 | 0 | OK | Ground clear controls. | 162 | 223.6 | 617
11062 | TIN-INTERP | Interpolated Ground | 70788.38 | 6.48 | 527.08 | 0 | 84.31 | 0 | OK | Ground clear controls. | 162 | 223.6 | 611.39
11063 | TIN-INTERP | Interpolated Ground | 70788.62 | -6.07 | 524.87 | 0 | 98.34 | 0 | OK | Ground clear controls. | 162 | 223.6 | 623.21
11064 | TIN-INTERP | Interpolated Ground | 70788.64 | -8.27 | 524.43 | 0 | 92.56 | 0 | OK | Ground clear controls. | 162 | 223.6 | 616.99
11065 | TIN-INTERP | Interpolated Ground | 70788.65 | -6.77 | 524.73 | 0 | 86.67 | 0 | OK | Ground clear controls. | 162 | 223.6 | 611.4
11066 | TIN-INTERP | Interpolated Ground | 70828.37 | 5.83 | 496.4 | 0 | 118.42 | 0 | OK | Ground clear controls. | 162 | 223.6 | 614.82
11067 | TIN-INTERP | Interpolated Ground | 70828.38 | 8.03 | 497.14 | 0 | 111.57 | 0 | OK | Ground clear controls. | 162 | 223.6 | 608.71
11068 | TIN-INTERP | Interpolated Ground | 70828.38 | 6.51 | 496.64 | 0 | 106.48 | 0 | OK | Ground clear controls. | 162 | 223.6 | 603.12
11069 | TIN-INTERP | Interpolated Ground | 70828.62 | -6.03 | 491.41 | 0 | 123.5 | 0 | OK | Ground clear controls. | 162 | 223.6 | 614.91
11070 | TIN-INTERP | Interpolated Ground | 70828.64 | -8.23 | 490.9 | 0 | 117.8 | 0 | OK | Ground clear controls. | 162 | 223.6 | 608.7
11071 | TIN-INTERP | Interpolated Ground | 70828.65 | -6.73 | 491.23 | 0 | 111.91 | 0 | OK | Ground clear controls. | 162 | 223.6 | 603.14
11072 | TIN-INTERP | Interpolated Ground | 70868.37 | 5.86 | 469.31 | 0 | 138.16 | 0 | OK | Ground clear controls. | 162 | 223.6 | 607.47
11073 | TIN-INTERP | Interpolated Ground | 70868.38 | 8.06 | 469.85 | 0 | 131.55 | 0 | OK | Ground clear controls. | 162 | 223.6 | 601.4
11074 | TIN-INTERP | Interpolated Ground | 70868.38 | 6.55 | 469.49 | 0 | 126.34 | 0 | OK | Ground clear controls. | 162 | 223.6 | 595.83
11075 | TIN-INTERP | Interpolated Ground | 70868.62 | -5.99 | 462.41 | 0 | 145.17 | 0 | OK | Ground clear controls. | 162 | 223.6 | 607.58
11076 | TIN-INTERP | Interpolated Ground | 70868.64 | -8.19 | 460.91 | 0 | 140.47 | 0 | OK | Ground clear controls. | 162 | 223.6 | 601.38
11077 | TIN-INTERP | Interpolated Ground | 70868.65 | -6.69 | 461.92 | 0 | 133.92 | 0 | OK | Ground clear controls. | 162 | 223.6 | 595.84
11078 | TIN-INTERP | Interpolated Ground | 70908.37 | 5.9 | 444.02 | 0 | 157.09 | 0 | OK | Ground clear controls. | 162 | 223.6 | 601.11
11079 | TIN-INTERP | Interpolated Ground | 70908.38 | 8.1 | 441.06 | 0 | 153.99 | 0 | OK | Ground clear controls. | 162 | 223.6 | 595.05
11080 | TIN-INTERP | Interpolated Ground | 70908.38 | 6.58 | 443.4 | 0 | 146.11 | 0 | OK | Ground clear controls. | 162 | 223.6 | 589.51
11081 | TIN-INTERP | Interpolated Ground | 70908.62 | -5.95 | 451.8 | 0 | 149.43 | 0 | OK | Ground clear controls. | 162 | 223.6 | 601.23
11082 | TIN-INTERP | Interpolated Ground | 70908.64 | -8.15 | 453.55 | 0 | 141.49 | 0 | OK | Ground clear controls. | 162 | 223.6 | 595.04
11083 | TIN-INTERP | Interpolated Ground | 70908.65 | -6.64 | 452.41 | 0 | 137.12 | 0 | OK | Ground clear controls. | 162 | 223.6 | 589.53
11084 | TIN-INTERP | Interpolated Ground | 70948.37 | 5.93 | 450.32 | 0 | 145.41 | 0 | OK | Ground clear controls. | 162 | 223.6 | 595.73
11085 | TIN-INTERP | Interpolated Ground | 70948.38 | 8.13 | 448.34 | 0 | 141.35 | 0 | OK | Ground clear controls. | 162 | 223.6 | 589.69
11086 | TIN-INTERP | Interpolated Ground | 70948.38 | 6.61 | 449.72 | 0 | 134.43 | 0 | OK | Ground clear controls. | 162 | 223.6 | 584.15
11087 | TIN-INTERP | Interpolated Ground | 70948.61 | -5.9 | 463.49 | 0 | 132.37 | 0 | OK | Ground clear controls. | 162 | 223.6 | 595.86
11088 | TIN-INTERP | Interpolated Ground | 70948.64 | -8.1 | 465.02 | 0 | 124.65 | 0 | OK | Ground clear controls. | 162 | 223.6 | 589.67
11089 | TIN-INTERP | Interpolated Ground | 70948.65 | -6.6 | 464.03 | 0 | 120.14 | 0 | OK | Ground clear controls. | 162 | 223.6 | 584.17
11090 | TIN-INTERP | Interpolated Ground | 70988.37 | 5.97 | 418.69 | 0 | 172.65 | 0 | OK | Ground clear controls. | 162 | 223.6 | 591.34
11091 | TIN-INTERP | Interpolated Ground | 70988.38 | 8.17 | 418.28 | 0 | 167.01 | 0 | OK | Ground clear controls. | 162 | 223.6 | 585.29
11092 | TIN-INTERP | Interpolated Ground | 70988.38 | 6.64 | 418.51 | 0 | 161.25 | 0 | OK | Ground clear controls. | 162 | 223.6 | 579.76
11093 | TIN-INTERP | Interpolated Ground | 70988.61 | -5.86 | 418.5 | 0 | 172.95 | 0 | OK | Ground clear controls. | 162 | 223.6 | 591.45
11094 | TIN-INTERP | Interpolated Ground | 70988.64 | -8.06 | 418.67 | 0 | 166.6 | 0 | OK | Ground clear controls. | 162 | 223.6 | 585.27
11095 | TIN-INTERP | Interpolated Ground | 70988.65 | -6.56 | 418.48 | 0 | 161.3 | 0 | OK | Ground clear controls. | 162 | 223.6 | 579.78
11096 | TIN-INTERP | Interpolated Ground | 71028.37 | 6 | 377.93 | 0 | 209.97 | 0 | OK | Ground clear controls. | 162 | 223.6 | 587.9
11097 | TIN-INTERP | Interpolated Ground | 71028.38 | 8.2 | 377.64 | 0 | 204.22 | 0 | OK | Ground clear controls. | 162 | 223.6 | 581.86
11098 | TIN-INTERP | Interpolated Ground | 71028.38 | 6.68 | 377.9 | 0 | 198.44 | 0 | OK | Ground clear controls. | 162 | 223.6 | 576.34
11099 | TIN-INTERP | Interpolated Ground | 71028.61 | -5.82 | 381.69 | 0 | 206.33 | 0 | OK | Ground clear controls. | 162 | 223.6 | 588.02
11100 | TIN-INTERP | Interpolated Ground | 71028.64 | -8.02 | 382.33 | 0 | 199.51 | 0 | OK | Ground clear controls. | 162 | 223.6 | 581.84
11101 | TIN-INTERP | Interpolated Ground | 71028.65 | -6.52 | 381.87 | 0 | 194.48 | 0 | OK | Ground clear controls. | 162 | 223.6 | 576.35
11102 | TIN-INTERP | Interpolated Ground | 71068.37 | 6.04 | 364.3 | 0 | 221.15 | 0 | OK | Ground clear controls. | 162 | 223.6 | 585.45
11103 | TIN-INTERP | Interpolated Ground | 71068.38 | 8.23 | 364.61 | 0 | 214.79 | 0 | OK | Ground clear controls. | 162 | 223.6 | 579.4
11104 | TIN-INTERP | Interpolated Ground | 71068.38 | 6.71 | 364.48 | 0 | 209.39 | 0 | OK | Ground clear controls. | 162 | 223.6 | 573.87
11105 | TIN-INTERP | Interpolated Ground | 71068.61 | -5.78 | 361.96 | 0 | 223.6 | 0 | OK | Ground clear controls. | 162 | 223.6 | 585.56
11106 | TIN-INTERP | Interpolated Ground | 71068.64 | -7.98 | 361.55 | 0 | 217.83 | 0 | OK | Ground clear controls. | 162 | 217.83 | 579.38
11107 | TIN-INTERP | Interpolated Ground | 71068.65 | -6.47 | 361.73 | 0 | 212.15 | 0 | OK | Ground clear controls. | 162 | 212.15 | 573.88
11108 | TIN-INTERP | Interpolated Ground | 71108.37 | 6.07 | 395.24 | 0 | 188.71 | 0 | OK | Ground clear controls. | 162 | 188.98 | 583.95
11109 | TIN-INTERP | Interpolated Ground | 71108.38 | 8.27 | 396.07 | 0 | 181.83 | 0 | OK | Ground clear controls. | 162 | 188.98 | 577.9
11110 | TIN-INTERP | Interpolated Ground | 71108.38 | 6.74 | 395.69 | 0 | 176.66 | 0 | OK | Ground clear controls. | 162 | 188.98 | 572.35
11111 | TIN-INTERP | Interpolated Ground | 71108.61 | -5.73 | 395.09 | 0 | 188.98 | 0 | OK | Ground clear controls. | 162 | 188.98 | 584.07
11112 | TIN-INTERP | Interpolated Ground | 71108.64 | -7.93 | 394.62 | 0 | 183.25 | 0 | OK | Ground clear controls. | 162 | 183.25 | 577.87
11113 | TIN-INTERP | Interpolated Ground | 71108.65 | -6.43 | 394.96 | 0 | 177.4 | 0 | OK | Ground clear controls. | 162 | 177.4 | 572.36
11114 | TIN-INTERP | Interpolated Ground | 71148.37 | 6.1 | 437.32 | 0 | 146.11 | 0 | OK | Ground clear controls. | 162 | 148.17 | 583.43
11115 | TIN-INTERP | Interpolated Ground | 71148.38 | 8.3 | 437.35 | 0 | 140.01 | 0 | OK | Ground clear controls. | 162 | 148.17 | 577.36
11116 | TIN-INTERP | Interpolated Ground | 71148.38 | 6.77 | 437.17 | 0 | 134.63 | 0 | OK | Ground clear controls. | 162 | 148.17 | 571.8
11117 | TIN-INTERP | Interpolated Ground | 71148.61 | -5.69 | 435.36 | 0 | 148.17 | 0 | OK | Ground clear controls. | 162 | 148.17 | 583.53
11118 | TIN-INTERP | Interpolated Ground | 71148.64 | -7.89 | 435.25 | 0 | 142.09 | 0 | OK | Ground clear controls. | 162 | 142.09 | 577.34
11119 | TIN-INTERP | Interpolated Ground | 71148.65 | -6.39 | 435.37 | 0 | 136.44 | 0 | OK | Ground clear controls. | 162 | 136.44 | 571.81
11120 | TIN-INTERP | Interpolated Ground | 71188.37 | 6.14 | 457.62 | 0 | 126.26 | 0 | OK | Ground clear controls. | 162 | 132.46 | 583.88
11121 | TIN-INTERP | Interpolated Ground | 71188.38 | 8.34 | 459.02 | 0 | 118.77 | 0 | OK | Ground clear controls. | 162 | 132.46 | 577.79
11122 | TIN-INTERP | Interpolated Ground | 71188.38 | 6.81 | 458.03 | 0 | 114.18 | 0 | OK | Ground clear controls. | 162 | 132.46 | 572.21
11123 | TIN-INTERP | Interpolated Ground | 71188.61 | -5.65 | 451.51 | 0 | 132.46 | 0 | OK | Ground clear controls. | 162 | 132.46 | 583.97
11124 | TIN-INTERP | Interpolated Ground | 71188.64 | -7.85 | 450.7 | 0 | 127.06 | 0 | OK | Ground clear controls. | 162 | 127.06 | 577.76
11125 | TIN-INTERP | Interpolated Ground | 71188.65 | -6.35 | 451.22 | 0 | 120.98 | 0 | OK | Ground clear controls. | 162 | 125.93 | 572.2
11126 | TIN-INTERP | Interpolated Ground | 71228.37 | 6.17 | 462.7 | 0 | 122.59 | 0 | OK | Ground clear controls. | 162 | 125.93 | 585.29
11127 | TIN-INTERP | Interpolated Ground | 71228.38 | 8.37 | 463.27 | 0 | 115.9 | 0 | OK | Ground clear controls. | 162 | 125.93 | 579.17
11128 | TIN-INTERP | Interpolated Ground | 71228.38 | 6.84 | 462.92 | 0 | 110.64 | 0 | OK | Ground clear controls. | 162 | 125.93 | 573.56
11129 | TIN-INTERP | Interpolated Ground | 71228.61 | -5.61 | 459.44 | 0 | 125.93 | 0 | OK | Ground clear controls. | 162 | 125.93 | 585.37
11130 | TIN-INTERP | Interpolated Ground | 71228.64 | -7.81 | 458.52 | 0 | 120.62 | 0 | OK | Ground clear controls. | 162 | 120.62 | 579.14
11131 | TIN-INTERP | Interpolated Ground | 71228.65 | -6.3 | 459.24 | 0 | 114.33 | 0 | OK | Ground clear controls. | 162 | 114.33 | 573.57
11132 | TIN-INTERP | Interpolated Ground | 71268.37 | 6.21 | 477.54 | 0 | 110.13 | 0 | OK | Ground clear controls. | 162 | 112.26 | 587.67
11133 | TIN-INTERP | Interpolated Ground | 71268.38 | 8.41 | 477.97 | 0 | 103.55 | 0 | OK | Ground clear controls. | 162 | 112.26 | 581.52
11134 | TIN-INTERP | Interpolated Ground | 71268.38 | 6.87 | 477.67 | 0 | 98.21 | 0 | OK | Ground clear controls. | 162 | 112.26 | 575.88
11135 | TIN-INTERP | Interpolated Ground | 71268.61 | -5.57 | 475.47 | 0 | 112.26 | 0 | OK | Ground clear controls. | 162 | 112.26 | 587.73
11136 | TIN-INTERP | Interpolated Ground | 71268.64 | -7.76 | 474.92 | 0 | 106.57 | 0 | OK | Ground clear controls. | 162 | 106.57 | 581.49
11137 | TIN-INTERP | Interpolated Ground | 71268.65 | -6.26 | 475.23 | 0 | 100.65 | 0 | OK | Ground clear controls. | 162 | 100.65 | 575.88
11138 | TIN-INTERP | Interpolated Ground | 71308.37 | 6.24 | 502.63 | 0 | 88.39 | 0 | OK | Ground clear controls. | 162 | 89.66 | 591.02
11139 | TIN-INTERP | Interpolated Ground | 71308.38 | 8.44 | 502.59 | 0 | 82.25 | 0 | OK | Ground clear controls. | 162 | 89.66 | 584.84
11140 | TIN-INTERP | Interpolated Ground | 71308.38 | 6.9 | 502.56 | 0 | 76.59 | 0 | OK | Ground clear controls. | 162 | 89.66 | 579.15
11141 | TIN-INTERP | Interpolated Ground | 71308.61 | -5.52 | 501.4 | 0 | 89.66 | 0 | OK | Ground clear controls. | 162 | 89.66 | 591.06
11142 | TIN-INTERP | Interpolated Ground | 71308.64 | -7.72 | 501.43 | 0 | 83.38 | 0 | OK | Ground clear controls. | 162 | 83.38 | 584.81
11143 | TIN-INTERP | Interpolated Ground | 71308.65 | -6.22 | 501.42 | 0 | 77.73 | 0 | OK | Ground clear controls. | 162 | 77.73 | 579.15
11144 | TIN-INTERP | Interpolated Ground | 71348.37 | 6.28 | 527.32 | 0 | 68.02 | 0 | OK | Ground clear controls. | 162 | 68.02 | 595.34
11145 | TIN-INTERP | Interpolated Ground | 71348.38 | 8.48 | 527.39 | 0 | 61.74 | 0 | OK | Ground clear controls. | 162 | 67.09 | 589.13
11146 | TIN-INTERP | Interpolated Ground | 71348.38 | 6.93 | 527.29 | 0 | 56.1 | 0 | OK | Ground clear controls. | 162 | 67.09 | 583.39
11147 | TIN-INTERP | Interpolated Ground | 71348.61 | -5.48 | 528.28 | 0 | 67.09 | 0 | OK | Ground clear controls. | 162 | 67.09 | 595.37
11148 | TIN-INTERP | Interpolated Ground | 71348.64 | -7.68 | 528.58 | 0 | 60.51 | 0 | OK | Ground clear controls. | 162 | 60.51 | 589.09
11149 | TIN-INTERP | Interpolated Ground | 71348.65 | -6.18 | 528.32 | 0 | 55.06 | 0 | OK | Ground clear controls. | 162 | 55.06 | 583.38
11150 | TIN-INTERP | Interpolated Ground | 71388.37 | 6.31 | 560.86 | 0 | 39.78 | 0 | OK | Ground clear controls. | 162 | 40.32 | 600.64
11151 | TIN-INTERP | Interpolated Ground | 71388.38 | 8.51 | 560.85 | 0 | 33.53 | 0 | OK | Ground clear controls. | 162 | 40.32 | 594.38
11152 | TIN-INTERP | Interpolated Ground | 71388.38 | 6.97 | 560.87 | 0 | 27.72 | 0 | OK | Ground clear controls. | 162 | 40.32 | 588.59
11153 | TIN-INTERP | Interpolated Ground | 71388.61 | -5.44 | 560.33 | 0 | 40.32 | 0 | OK | Ground clear controls. | 162 | 40.32 | 600.65
11154 | TIN-INTERP | Interpolated Ground | 71388.64 | -7.64 | 560.94 | 0 | 33.41 | 0 | OK | Ground clear controls. | 162 | 33.41 | 594.35
11155 | TIN-INTERP | Interpolated Ground | 71388.65 | -6.13 | 560.49 | 0 | 28.09 | 0 | OK | Ground clear controls. | 162 | 28.09 | 588.58
11156 | TIN-INTERP | Interpolated Ground | 71399.17 | 8.52 | 564.96 | 0 | 31 | 0 | OK | Ground clear controls. | 163 | 75.73 | 595.96
11157 | TIN-INTERP | Interpolated Ground | 71399.2 | 6.98 | 564.98 | 0 | 25.18 | 0 | OK | Ground clear controls. | 163 | 75.73 | 590.16
11158 | TIN-INTERP | Interpolated Ground | 71399.43 | -7.63 | 562.8 | 0 | 33.15 | 0 | OK | Ground clear controls. | 163 | 75.73 | 595.95
11159 | TIN-INTERP | Interpolated Ground | 71399.43 | -6.12 | 563.02 | 0 | 27.14 | 0 | OK | Ground clear controls. | 163 | 75.73 | 590.16
11160 | TIN-INTERP | Interpolated Ground | 71399.43 | -5.43 | 563.13 | 0 | 39.13 | 0 | OK | Ground clear controls. | 163 | 75.73 | 602.26
11161 | TIN-INTERP | Interpolated Ground | 71399.61 | 6.32 | 565.02 | 0 | 37.23 | 0 | OK | Ground clear controls. | 163 | 75.73 | 602.25
11162 | TIN-INTERP | Interpolated Ground | 71439.26 | -6.08 | 549.68 | 0 | 35.23 | 0 | OK | Ground clear controls. | 163 | 75.73 | 584.91
11163 | TIN-INTERP | Interpolated Ground | 71439.26 | -7.58 | 549 | 0 | 41.68 | 0 | OK | Ground clear controls. | 163 | 75.73 | 590.68
11164 | TIN-INTERP | Interpolated Ground | 71439.32 | -5.38 | 549.83 | 0 | 47.14 | 0 | OK | Ground clear controls. | 163 | 75.73 | 596.97
11165 | TIN-INTERP | Interpolated Ground | 71439.54 | 7.03 | 553.41 | 0 | 31.49 | 0 | OK | Ground clear controls. | 163 | 75.73 | 584.9
11166 | TIN-INTERP | Interpolated Ground | 71439.58 | 8.57 | 553.52 | 0 | 37.15 | 0 | OK | Ground clear controls. | 163 | 75.73 | 590.67
11167 | TIN-INTERP | Interpolated Ground | 71439.61 | 6.37 | 553.31 | 0 | 43.68 | 0 | OK | Ground clear controls. | 163 | 75.73 | 596.99
11168 | TIN-INTERP | Interpolated Ground | 71479.26 | -6.03 | 524.46 | 0 | 56.14 | 0 | OK | Ground clear controls. | 163 | 75.73 | 580.6
11169 | TIN-INTERP | Interpolated Ground | 71479.26 | -7.54 | 524.07 | 0 | 62.29 | 0 | OK | Ground clear controls. | 163 | 75.73 | 586.36
11170 | TIN-INTERP | Interpolated Ground | 71479.32 | -5.34 | 524.6 | 0 | 68.04 | 0 | OK | Ground clear controls. | 163 | 75.73 | 592.64
11171 | TIN-INTERP | Interpolated Ground | 71479.54 | 7.08 | 528.1 | 0 | 52.51 | 0 | OK | Ground clear controls. | 163 | 75.73 | 580.61
11172 | TIN-INTERP | Interpolated Ground | 71479.58 | 8.62 | 528.34 | 0 | 58 | 0 | OK | Ground clear controls. | 163 | 75.73 | 586.34
11173 | TIN-INTERP | Interpolated Ground | 71479.61 | 6.42 | 527.97 | 0 | 64.7 | 0 | OK | Ground clear controls. | 163 | 75.73 | 592.67
11174 | TIN-INTERP | Interpolated Ground | 71519.26 | -5.99 | 538.4 | 0 | 38.88 | 0 | OK | Ground clear controls. | 163 | 75.73 | 577.28
11175 | TIN-INTERP | Interpolated Ground | 71519.26 | -7.49 | 538.68 | 0 | 44.34 | 0 | OK | Ground clear controls. | 163 | 75.73 | 583.02
11176 | TIN-INTERP | Interpolated Ground | 71519.32 | -5.3 | 538.37 | 0 | 50.92 | 0 | OK | Ground clear controls. | 163 | 75.73 | 589.29
11177 | TIN-INTERP | Interpolated Ground | 71519.54 | 7.13 | 537.39 | 0 | 39.9 | 0 | OK | Ground clear controls. | 163 | 75.73 | 577.29
11178 | TIN-INTERP | Interpolated Ground | 71519.58 | 8.66 | 537.37 | 0 | 45.62 | 0 | OK | Ground clear controls. | 163 | 75.73 | 582.99
11179 | TIN-INTERP | Interpolated Ground | 71519.61 | 6.47 | 537.45 | 0 | 51.88 | 0 | OK | Ground clear controls. | 163 | 75.73 | 589.33
11180 | TIN-INTERP | Interpolated Ground | 71559.26 | -5.95 | 537.68 | 0 | 37.22 | 0 | OK | Ground clear controls. | 163 | 75.73 | 574.9
11181 | TIN-INTERP | Interpolated Ground | 71559.26 | -7.45 | 536.93 | 0 | 43.69 | 0 | OK | Ground clear controls. | 163 | 75.73 | 580.62
11182 | TIN-INTERP | Interpolated Ground | 71559.32 | -5.25 | 538.27 | 0 | 48.63 | 0 | OK | Ground clear controls. | 163 | 75.73 | 586.9
11183 | TIN-INTERP | Interpolated Ground | 71559.54 | 7.18 | 546.03 | 0 | 28.9 | 0 | OK | Ground clear controls. | 163 | 75.73 | 574.93
11184 | TIN-INTERP | Interpolated Ground | 71559.58 | 8.71 | 547.56 | 0 | 33.04 | 0 | OK | Ground clear controls. | 163 | 75.73 | 580.6
11185 | TIN-INTERP | Interpolated Ground | 71559.61 | 6.51 | 545.65 | 0 | 41.31 | 0 | OK | Ground clear controls. | 163 | 75.73 | 586.96
11186 | TIN-INTERP | Interpolated Ground | 71599.26 | -5.9 | 539.1 | 0 | 34.4 | 0 | OK | Ground clear controls. | 163 | 75.73 | 573.5
11187 | TIN-INTERP | Interpolated Ground | 71599.26 | -7.4 | 538.4 | 0 | 40.81 | 0 | OK | Ground clear controls. | 163 | 75.73 | 579.21
11188 | TIN-INTERP | Interpolated Ground | 71599.32 | -5.21 | 539.42 | 0 | 46.05 | 0 | OK | Ground clear controls. | 163 | 75.73 | 585.47
11189 | TIN-INTERP | Interpolated Ground | 71599.54 | 7.23 | 544 | 0 | 29.53 | 0 | OK | Ground clear controls. | 163 | 75.73 | 573.53
11190 | TIN-INTERP | Interpolated Ground | 71599.58 | 8.76 | 544.41 | 0 | 34.78 | 0 | OK | Ground clear controls. | 163 | 75.73 | 579.19
11191 | TIN-INTERP | Interpolated Ground | 71599.61 | 6.56 | 543.75 | 0 | 41.8 | 0 | OK | Ground clear controls. | 163 | 75.73 | 585.55
11192 | TIN-INTERP | Interpolated Ground | 71639.26 | -5.86 | 518.62 | 0 | 54.42 | 0 | OK | Ground clear controls. | 163 | 75.73 | 573.04
11193 | TIN-INTERP | Interpolated Ground | 71639.26 | -7.36 | 518.41 | 0 | 60.33 | 0 | OK | Ground clear controls. | 163 | 75.73 | 578.74
11194 | TIN-INTERP | Interpolated Ground | 71639.32 | -5.16 | 518.71 | 0 | 66.3 | 0 | OK | Ground clear controls. | 163 | 75.73 | 585.01
11195 | TIN-INTERP | Interpolated Ground | 71639.54 | 7.28 | 522.97 | 0 | 50.12 | 0 | OK | Ground clear controls. | 163 | 75.73 | 573.09
11196 | TIN-INTERP | Interpolated Ground | 71639.58 | 8.81 | 523.56 | 0 | 55.18 | 0 | OK | Ground clear controls. | 163 | 75.73 | 578.74
11197 | TIN-INTERP | Interpolated Ground | 71639.61 | 6.61 | 522.69 | 0 | 62.42 | 0 | OK | Ground clear controls. | 163 | 75.73 | 585.11
11198 | TIN-INTERP | Interpolated Ground | 71679.26 | -5.82 | 511.61 | 0 | 61.95 | 0 | OK | Ground clear controls. | 163 | 75.73 | 573.56
11199 | TIN-INTERP | Interpolated Ground | 71679.26 | -7.31 | 510.93 | 0 | 68.32 | 0 | OK | Ground clear controls. | 163 | 75.73 | 579.25
11200 | TIN-INTERP | Interpolated Ground | 71679.32 | -5.12 | 511.86 | 0 | 73.66 | 0 | OK | Ground clear controls. | 163 | 75.73 | 585.52
11201 | TIN-INTERP | Interpolated Ground | 71679.54 | 7.33 | 516.69 | 0 | 56.93 | 0 | OK | Ground clear controls. | 163 | 75.73 | 573.62
11202 | TIN-INTERP | Interpolated Ground | 71679.58 | 8.85 | 517.23 | 0 | 62.03 | 0 | OK | Ground clear controls. | 163 | 75.73 | 579.26
11203 | TIN-INTERP | Interpolated Ground | 71679.61 | 6.66 | 516.43 | 0 | 69.21 | 0 | OK | Ground clear controls. | 163 | 75.73 | 585.64
11204 | TIN-INTERP | Interpolated Ground | 71719.26 | -5.77 | 514.46 | 0 | 60.57 | 0 | OK | Ground clear controls. | 163 | 75.73 | 575.03
11205 | TIN-INTERP | Interpolated Ground | 71719.26 | -7.27 | 513.92 | 0 | 66.78 | 0 | OK | Ground clear controls. | 163 | 75.73 | 580.7
11206 | TIN-INTERP | Interpolated Ground | 71719.32 | -5.08 | 514.58 | 0 | 72.4 | 0 | OK | Ground clear controls. | 163 | 75.73 | 586.98
11207 | TIN-INTERP | Interpolated Ground | 71719.54 | 7.38 | 516.26 | 0 | 58.86 | 0 | OK | Ground clear controls. | 163 | 75.73 | 575.12
11208 | TIN-INTERP | Interpolated Ground | 71719.58 | 8.9 | 516.62 | 0 | 64.14 | 0 | OK | Ground clear controls. | 163 | 75.73 | 580.76
11209 | TIN-INTERP | Interpolated Ground | 71719.61 | 6.71 | 516.21 | 0 | 70.92 | 0 | OK | Ground clear controls. | 163 | 75.73 | 587.13
11210 | TIN-INTERP | Interpolated Ground | 71759.26 | -5.73 | 526.21 | 0 | 51.25 | 0 | OK | Ground clear controls. | 163 | 75.73 | 577.46
11211 | TIN-INTERP | Interpolated Ground | 71759.26 | -7.23 | 525.98 | 0 | 57.15 | 0 | OK | Ground clear controls. | 163 | 75.73 | 583.13
11212 | TIN-INTERP | Interpolated Ground | 71759.32 | -5.03 | 526.35 | 0 | 63.06 | 0 | OK | Ground clear controls. | 163 | 75.73 | 589.41
11213 | TIN-INTERP | Interpolated Ground | 71759.54 | 7.43 | 529.11 | 0 | 48.47 | 0 | OK | Ground clear controls. | 163 | 75.73 | 577.58
11214 | TIN-INTERP | Interpolated Ground | 71759.58 | 8.95 | 529.33 | 0 | 53.88 | 0 | OK | Ground clear controls. | 163 | 75.73 | 583.21
11215 | TIN-INTERP | Interpolated Ground | 71759.61 | 6.75 | 529 | 0 | 60.58 | 0 | OK | Ground clear controls. | 163 | 75.73 | 589.58
11216 | TIN-INTERP | Interpolated Ground | 71799.26 | -5.68 | 535.67 | 0 | 45.17 | 0 | OK | Ground clear controls. | 163 | 75.73 | 580.84
11217 | TIN-INTERP | Interpolated Ground | 71799.26 | -7.18 | 534.98 | 0 | 51.54 | 0 | OK | Ground clear controls. | 163 | 75.73 | 586.52
11218 | TIN-INTERP | Interpolated Ground | 71799.32 | -4.99 | 536.12 | 0 | 56.69 | 0 | OK | Ground clear controls. | 163 | 75.73 | 592.81
11219 | TIN-INTERP | Interpolated Ground | 71799.54 | 7.48 | 543.22 | 0 | 37.77 | 0 | OK | Ground clear controls. | 163 | 75.73 | 580.99
11220 | TIN-INTERP | Interpolated Ground | 71799.58 | 8.99 | 543.75 | 0 | 42.9 | 0 | OK | Ground clear controls. | 163 | 75.73 | 586.65
11221 | TIN-INTERP | Interpolated Ground | 71799.61 | 6.8 | 543.02 | 0 | 49.99 | 0 | OK | Ground clear controls. | 163 | 75.73 | 593.01
11222 | TIN-INTERP | Interpolated Ground | 71839.26 | -5.64 | 546.38 | 0 | 38.81 | 0 | OK | Ground clear controls. | 163 | 75.73 | 585.19
11223 | TIN-INTERP | Interpolated Ground | 71839.26 | -7.14 | 546.07 | 0 | 44.81 | 0 | OK | Ground clear controls. | 163 | 75.73 | 590.88
11224 | TIN-INTERP | Interpolated Ground | 71839.32 | -4.94 | 546.61 | 0 | 50.56 | 0 | OK | Ground clear controls. | 163 | 75.73 | 597.17
11225 | TIN-INTERP | Interpolated Ground | 71839.54 | 7.53 | 554.37 | 0 | 31.02 | 0 | OK | Ground clear controls. | 163 | 75.73 | 585.39
11226 | TIN-INTERP | Interpolated Ground | 71839.58 | 9.04 | 555.04 | 0 | 36.01 | 0 | OK | Ground clear controls. | 163 | 75.73 | 591.05
11227 | TIN-INTERP | Interpolated Ground | 71839.61 | 6.85 | 554.13 | 0 | 43.27 | 0 | OK | Ground clear controls. | 163 | 75.73 | 597.4
11228 | TIN-INTERP | Interpolated Ground | 71879.26 | -5.6 | 565.53 | 0 | 24.99 | 0 | OK | Ground clear controls. | 163 | 75.73 | 590.52
11229 | TIN-INTERP | Interpolated Ground | 71879.26 | -7.09 | 565.3 | 0 | 30.9 | 0 | OK | Ground clear controls. | 163 | 75.73 | 596.2
11230 | TIN-INTERP | Interpolated Ground | 71879.32 | -4.9 | 565.65 | 0 | 36.86 | 0 | OK | Ground clear controls. | 163 | 75.73 | 602.51
11231 | TIN-INTERP | Interpolated Ground | 71879.54 | 7.58 | 567.7 | 0 | 23.05 | 0 | OK | Ground clear controls. | 163 | 75.73 | 590.75
11232 | TIN-INTERP | Interpolated Ground | 71879.58 | 9.09 | 568.09 | 0 | 28.35 | 0 | OK | Ground clear controls. | 163 | 75.73 | 596.44
11233 | TIN-INTERP | Interpolated Ground | 71879.61 | 6.9 | 567.56 | 0 | 35.21 | 0 | OK | Ground clear controls. | 163 | 75.73 | 602.77
11234 | TIN-INTERP | Interpolated Ground | 71919.26 | -5.55 | 579.85 | 0 | 16.95 | 0 | OK | Ground clear controls. | 163 | 75.73 | 596.8
11235 | TIN-INTERP | Interpolated Ground | 71919.26 | -7.05 | 579.05 | 0 | 23.45 | 0 | OK | Ground clear controls. | 163 | 75.73 | 602.5
11236 | TIN-INTERP | Interpolated Ground | 71919.32 | -4.86 | 580.29 | 0 | 28.52 | 0 | OK | Ground clear controls. | 163 | 75.73 | 608.81
11237 | TIN-INTERP | Interpolated Ground | 71919.54 | 7.63 | 584.46 | 0 | 12.62 | 0 | OK | Ground clear controls. | 163 | 75.73 | 597.08
11238 | TIN-INTERP | Interpolated Ground | 71919.58 | 9.13 | 584.44 | 0 | 18.35 | 0 | OK | Ground clear controls. | 163 | 75.73 | 602.79
11239 | TIN-INTERP | Interpolated Ground | 71919.61 | 6.95 | 584.23 | 0 | 24.88 | 0 | OK | Ground clear controls. | 163 | 75.73 | 609.11
11240 | TIN-INTERP | Interpolated Ground | 71959.26 | -5.51 | 554.26 | 0 | 49.8 | 0 | OK | Ground clear controls. | 163 | 75.73 | 604.06
11241 | TIN-INTERP | Interpolated Ground | 71959.26 | -7 | 553.81 | 0 | 55.97 | 0 | OK | Ground clear controls. | 163 | 75.73 | 609.78
11242 | TIN-INTERP | Interpolated Ground | 71959.32 | -4.81 | 554.51 | 0 | 61.6 | 0 | OK | Ground clear controls. | 163 | 75.73 | 616.11
11243 | TIN-INTERP | Interpolated Ground | 71959.54 | 7.68 | 559.98 | 0 | 44.41 | 0 | OK | Ground clear controls. | 163 | 75.73 | 604.39
11244 | TIN-INTERP | Interpolated Ground | 71959.58 | 9.18 | 560.53 | 0 | 49.61 | 0 | OK | Ground clear controls. | 163 | 75.73 | 610.14
11245 | TIN-INTERP | Interpolated Ground | 71959.61 | 6.99 | 559.68 | 0 | 56.76 | 0 | OK | Ground clear controls. | 163 | 75.73 | 616.44
11246 | TIN-INTERP | Interpolated Ground | 71999.26 | -5.47 | 551.33 | 0 | 60.96 | 0 | OK | Ground clear controls. | 163 | 75.73 | 612.29
11247 | TIN-INTERP | Interpolated Ground | 71999.26 | -6.96 | 551.48 | 0 | 66.53 | 0 | OK | Ground clear controls. | 163 | 75.73 | 618.01
11248 | TIN-INTERP | Interpolated Ground | 71999.32 | -4.77 | 551.24 | 0 | 73.12 | 0 | OK | Ground clear controls. | 163 | 75.73 | 624.36
11249 | TIN-INTERP | Interpolated Ground | 71999.54 | 7.73 | 548.7 | 0 | 63.97 | 0 | OK | Ground clear controls. | 163 | 75.73 | 612.67
11250 | TIN-INTERP | Interpolated Ground | 71999.58 | 9.23 | 548.18 | 0 | 70.27 | 0 | OK | Ground clear controls. | 163 | 75.73 | 618.45
11251 | TIN-INTERP | Interpolated Ground | 71999.61 | 7.04 | 549 | 0 | 75.73 | 0 | OK | Ground clear controls. | 163 | 75.73 | 624.73
11252 | TIN-INTERP | Interpolated Ground | 72039.26 | -5.42 | 581.24 | 0 | 40.28 | 0 | OK | Ground clear controls. | 163 | 53.9 | 621.52
11253 | TIN-INTERP | Interpolated Ground | 72039.26 | -6.91 | 581.45 | 0 | 45.81 | 0 | OK | Ground clear controls. | 163 | 53.9 | 627.26
11254 | TIN-INTERP | Interpolated Ground | 72039.32 | -4.72 | 581.2 | 0 | 52.42 | 0 | OK | Ground clear controls. | 163 | 53.9 | 633.62
11255 | TIN-INTERP | Interpolated Ground | 72039.54 | 7.78 | 580.1 | 0 | 41.86 | 0 | OK | Ground clear controls. | 163 | 53.9 | 621.96
11256 | TIN-INTERP | Interpolated Ground | 72039.58 | 9.28 | 579.83 | 0 | 47.95 | 0 | OK | Ground clear controls. | 163 | 53.9 | 627.78
11257 | TIN-INTERP | Interpolated Ground | 72039.61 | 7.09 | 580.13 | 0 | 53.9 | 0 | OK | Ground clear controls. | 163 | 53.9 | 634.03
11258 | TIN-INTERP | Interpolated Ground | 72064.49 | 9.3 | 595.07 | 0 | 39.01 | 0 | OK | Ground clear controls. | 164 | 92.9 | 634.08
11259 | TIN-INTERP | Interpolated Ground | 72064.65 | 7.82 | 595.5 | 0 | 32.78 | 0 | OK | Ground clear controls. | 164 | 92.9 | 628.28
11260 | TIN-INTERP | Interpolated Ground | 72064.75 | 7.12 | 595.7 | 0 | 44.67 | 0 | OK | Ground clear controls. | 164 | 92.9 | 640.37
11261 | TIN-INTERP | Interpolated Ground | 72065.63 | -6.93 | 594.8 | 0 | 39.27 | 0 | OK | Ground clear controls. | 164 | 92.9 | 634.07
11262 | TIN-INTERP | Interpolated Ground | 72065.63 | -5.42 | 594.82 | 0 | 33.45 | 0 | OK | Ground clear controls. | 164 | 92.9 | 628.27
11263 | TIN-INTERP | Interpolated Ground | 72065.63 | -4.72 | 594.82 | 0 | 45.56 | 0 | OK | Ground clear controls. | 164 | 92.9 | 640.38
11264 | TIN-INTERP | Interpolated Ground | 72104.75 | -6.88 | 576.46 | 0 | 48.66 | 0 | OK | Ground clear controls. | 164 | 92.9 | 625.12
11265 | TIN-INTERP | Interpolated Ground | 72104.92 | -5.38 | 577.33 | 0 | 42.01 | 0 | OK | Ground clear controls. | 164 | 92.9 | 619.34
11266 | TIN-INTERP | Interpolated Ground | 72105.03 | -4.69 | 577.61 | 0 | 53.84 | 0 | OK | Ground clear controls. | 164 | 92.9 | 631.45
11267 | TIN-INTERP | Interpolated Ground | 72106.45 | 7.11 | 586.51 | 0 | 44.96 | 0 | OK | Ground clear controls. | 164 | 92.9 | 631.47
11268 | TIN-INTERP | Interpolated Ground | 72106.52 | 7.81 | 587.36 | 0 | 32.01 | 0 | OK | Ground clear controls. | 164 | 92.9 | 619.37
11269 | TIN-INTERP | Interpolated Ground | 72106.71 | 9.3 | 588.27 | 0 | 36.88 | 0 | OK | Ground clear controls. | 164 | 92.9 | 625.15
11270 | TIN-INTERP | Interpolated Ground | 72144.75 | -6.89 | 566.08 | 0 | 51.07 | 0 | OK | Ground clear controls. | 164 | 92.9 | 617.15
11271 | TIN-INTERP | Interpolated Ground | 72144.92 | -5.39 | 567 | 0 | 44.39 | 0 | OK | Ground clear controls. | 164 | 92.9 | 611.39
11272 | TIN-INTERP | Interpolated Ground | 72145.03 | -4.7 | 567.4 | 0 | 56.12 | 0 | OK | Ground clear controls. | 164 | 92.9 | 623.52
11273 | TIN-INTERP | Interpolated Ground | 72146.45 | 7.1 | 575.72 | 0 | 47.83 | 0 | OK | Ground clear controls. | 164 | 92.9 | 623.55
11274 | TIN-INTERP | Interpolated Ground | 72146.52 | 7.79 | 576.25 | 0 | 35.21 | 0 | OK | Ground clear controls. | 164 | 92.9 | 611.46
11275 | TIN-INTERP | Interpolated Ground | 72146.71 | 9.28 | 577.36 | 0 | 39.86 | 0 | OK | Ground clear controls. | 164 | 92.9 | 617.22
11276 | TIN-INTERP | Interpolated Ground | 72184.75 | -6.9 | 552.24 | 0 | 57.94 | 0 | OK | Ground clear controls. | 164 | 92.9 | 610.18
11277 | TIN-INTERP | Interpolated Ground | 72184.92 | -5.39 | 552.3 | 0 | 52.13 | 0 | OK | Ground clear controls. | 164 | 92.9 | 604.43
11278 | TIN-INTERP | Interpolated Ground | 72185.03 | -4.71 | 552.43 | 0 | 64.15 | 0 | OK | Ground clear controls. | 164 | 92.9 | 616.58
11279 | TIN-INTERP | Interpolated Ground | 72186.45 | 7.08 | 556.53 | 0 | 60.11 | 0 | OK | Ground clear controls. | 164 | 92.9 | 616.64
11280 | TIN-INTERP | Interpolated Ground | 72186.52 | 7.78 | 556.91 | 0 | 47.63 | 0 | OK | Ground clear controls. | 164 | 92.9 | 604.54
11281 | TIN-INTERP | Interpolated Ground | 72186.71 | 9.26 | 558.21 | 0 | 52.08 | 0 | OK | Ground clear controls. | 164 | 92.9 | 610.29
11282 | TIN-INTERP | Interpolated Ground | 72224.75 | -6.91 | 521.27 | 0 | 82.92 | 0 | OK | Ground clear controls. | 164 | 92.9 | 604.19
11283 | TIN-INTERP | Interpolated Ground | 72224.92 | -5.4 | 521.71 | 0 | 76.75 | 0 | OK | Ground clear controls. | 164 | 92.9 | 598.46
11284 | TIN-INTERP | Interpolated Ground | 72225.03 | -4.72 | 521.9 | 0 | 88.72 | 0 | OK | Ground clear controls. | 164 | 92.9 | 610.62
11285 | TIN-INTERP | Interpolated Ground | 72226.45 | 7.06 | 528.99 | 0 | 81.71 | 0 | OK | Ground clear controls. | 164 | 92.9 | 610.7
11286 | TIN-INTERP | Interpolated Ground | 72226.52 | 7.76 | 529.49 | 0 | 69.12 | 0 | OK | Ground clear controls. | 164 | 92.9 | 598.61
11287 | TIN-INTERP | Interpolated Ground | 72226.71 | 9.25 | 530.52 | 0 | 73.83 | 0 | OK | Ground clear controls. | 164 | 92.9 | 604.35
11288 | TIN-INTERP | Interpolated Ground | 72264.75 | -6.92 | 530.45 | 0 | 68.74 | 0 | OK | Ground clear controls. | 164 | 92.9 | 599.19
11289 | TIN-INTERP | Interpolated Ground | 72264.92 | -5.41 | 531.1 | 0 | 62.37 | 0 | OK | Ground clear controls. | 164 | 92.9 | 593.47
11290 | TIN-INTERP | Interpolated Ground | 72265.03 | -4.72 | 531.19 | 0 | 74.46 | 0 | OK | Ground clear controls. | 164 | 92.9 | 605.65
11291 | TIN-INTERP | Interpolated Ground | 72266.45 | 7.04 | 532.94 | 0 | 72.81 | 0 | OK | Ground clear controls. | 164 | 92.9 | 605.75
11292 | TIN-INTERP | Interpolated Ground | 72266.52 | 7.74 | 533.19 | 0 | 60.47 | 0 | OK | Ground clear controls. | 164 | 92.9 | 593.66
11293 | TIN-INTERP | Interpolated Ground | 72266.71 | 9.23 | 533.97 | 0 | 65.42 | 0 | OK | Ground clear controls. | 164 | 92.9 | 599.39
11294 | TIN-INTERP | Interpolated Ground | 72304.75 | -6.94 | 540.91 | 0 | 54.27 | 0 | OK | Ground clear controls. | 164 | 92.9 | 595.18
11295 | TIN-INTERP | Interpolated Ground | 72304.92 | -5.41 | 540.78 | 0 | 48.68 | 0 | OK | Ground clear controls. | 164 | 92.9 | 589.46
11296 | TIN-INTERP | Interpolated Ground | 72305.03 | -4.73 | 540.82 | 0 | 60.83 | 0 | OK | Ground clear controls. | 164 | 92.9 | 601.65
11297 | TIN-INTERP | Interpolated Ground | 72306.45 | 7.02 | 547.71 | 0 | 54.06 | 0 | OK | Ground clear controls. | 164 | 92.9 | 601.77
11298 | TIN-INTERP | Interpolated Ground | 72306.52 | 7.73 | 547.97 | 0 | 41.71 | 0 | OK | Ground clear controls. | 164 | 92.9 | 589.68
11299 | TIN-INTERP | Interpolated Ground | 72306.71 | 9.21 | 548.4 | 0 | 47.01 | 0 | OK | Ground clear controls. | 164 | 92.9 | 595.41
11300 | TIN-INTERP | Interpolated Ground | 72344.75 | -6.95 | 561.53 | 0 | 30.61 | 0 | OK | Ground clear controls. | 164 | 92.9 | 592.14
11301 | TIN-INTERP | Interpolated Ground | 72344.92 | -5.42 | 561.63 | 0 | 24.8 | 0 | OK | Ground clear controls. | 164 | 92.9 | 586.43
11302 | TIN-INTERP | Interpolated Ground | 72345.03 | -4.74 | 561.67 | 0 | 36.96 | 0 | OK | Ground clear controls. | 164 | 92.9 | 598.63
11303 | TIN-INTERP | Interpolated Ground | 72346.45 | 7.01 | 562.52 | 0 | 36.26 | 0 | OK | Ground clear controls. | 164 | 92.9 | 598.78
11304 | TIN-INTERP | Interpolated Ground | 72346.52 | 7.71 | 562.57 | 0 | 24.12 | 0 | OK | Ground clear controls. | 164 | 92.9 | 586.69
11305 | TIN-INTERP | Interpolated Ground | 72346.71 | 9.19 | 562.64 | 0 | 29.77 | 0 | OK | Ground clear controls. | 164 | 92.9 | 592.41
11306 | TIN-INTERP | Interpolated Ground | 72384.75 | -6.96 | 549.21 | 0 | 40.86 | 0 | OK | Ground clear controls. | 164 | 92.9 | 590.07
11307 | TIN-INTERP | Interpolated Ground | 72384.92 | -5.42 | 549.87 | 0 | 34.5 | 0 | OK | Ground clear controls. | 164 | 92.9 | 584.37
11308 | TIN-INTERP | Interpolated Ground | 72385.03 | -4.75 | 549.99 | 0 | 46.59 | 0 | OK | Ground clear controls. | 164 | 92.9 | 596.58
11309 | TIN-INTERP | Interpolated Ground | 72386.45 | 6.99 | 550.71 | 0 | 46.05 | 0 | OK | Ground clear controls. | 164 | 92.9 | 596.76
11310 | TIN-INTERP | Interpolated Ground | 72386.52 | 7.69 | 550.62 | 0 | 34.04 | 0 | OK | Ground clear controls. | 164 | 92.9 | 584.66
11311 | TIN-INTERP | Interpolated Ground | 72386.71 | 9.18 | 550.42 | 0 | 39.96 | 0 | OK | Ground clear controls. | 164 | 92.9 | 590.38
11312 | TIN-INTERP | Interpolated Ground | 72424.75 | -6.97 | 525.18 | 0 | 63.81 | 0 | OK | Ground clear controls. | 164 | 92.9 | 588.99
11313 | TIN-INTERP | Interpolated Ground | 72424.92 | -5.43 | 525.38 | 0 | 57.91 | 0 | OK | Ground clear controls. | 164 | 92.9 | 583.29
11314 | TIN-INTERP | Interpolated Ground | 72425.03 | -4.76 | 525.58 | 0 | 69.92 | 0 | OK | Ground clear controls. | 164 | 92.9 | 595.5
11315 | TIN-INTERP | Interpolated Ground | 72426.45 | 6.97 | 528.42 | 0 | 67.29 | 0 | OK | Ground clear controls. | 164 | 92.9 | 595.71
11316 | TIN-INTERP | Interpolated Ground | 72426.52 | 7.67 | 528.85 | 0 | 54.76 | 0 | OK | Ground clear controls. | 164 | 92.9 | 583.61
11317 | TIN-INTERP | Interpolated Ground | 72426.71 | 9.16 | 529.93 | 0 | 59.4 | 0 | OK | Ground clear controls. | 164 | 92.9 | 589.33
11318 | TIN-INTERP | Interpolated Ground | 72464.75 | -6.98 | 501.66 | 0 | 87.2 | 0 | OK | Ground clear controls. | 164 | 92.9 | 588.86
11319 | TIN-INTERP | Interpolated Ground | 72464.92 | -5.44 | 502.2 | 0 | 80.98 | 0 | OK | Ground clear controls. | 164 | 92.9 | 583.18
11320 | TIN-INTERP | Interpolated Ground | 72465.03 | -4.76 | 502.5 | 0 | 92.9 | 0 | OK | Ground clear controls. | 164 | 92.9 | 595.4
11321 | TIN-INTERP | Interpolated Ground | 72466.45 | 6.95 | 504.62 | 0 | 91 | 0 | OK | Ground clear controls. | 164 | 91 | 595.62
11322 | TIN-INTERP | Interpolated Ground | 72466.52 | 7.66 | 504.64 | 0 | 78.89 | 0 | OK | Ground clear controls. | 164 | 85.86 | 583.53
11323 | TIN-INTERP | Interpolated Ground | 72466.71 | 9.14 | 505.2 | 0 | 84.06 | 0 | OK | Ground clear controls. | 164 | 85.86 | 589.26
11324 | TIN-INTERP | Interpolated Ground | 72504.75 | -6.99 | 515.88 | 0 | 73.84 | 0 | OK | Ground clear controls. | 164 | 85.86 | 589.72
11325 | TIN-INTERP | Interpolated Ground | 72504.92 | -5.44 | 517.04 | 0 | 67.01 | 0 | OK | Ground clear controls. | 164 | 85.86 | 584.05
11326 | TIN-INTERP | Interpolated Ground | 72505.03 | -4.77 | 517.51 | 0 | 78.74 | 0 | OK | Ground clear controls. | 164 | 85.86 | 596.25
11327 | TIN-INTERP | Interpolated Ground | 72506.45 | 6.94 | 525.22 | 0 | 71.29 | 0 | OK | Ground clear controls. | 164 | 85.86 | 596.51
11328 | TIN-INTERP | Interpolated Ground | 72506.52 | 7.64 | 525.36 | 0 | 59.06 | 0 | OK | Ground clear controls. | 164 | 85.86 | 584.42
11329 | TIN-INTERP | Interpolated Ground | 72506.71 | 9.13 | 525.64 | 0 | 64.52 | 0 | OK | Ground clear controls. | 164 | 85.86 | 590.16
11330 | TIN-INTERP | Interpolated Ground | 72544.75 | -7 | 511.01 | 0 | 80.55 | 0 | OK | Ground clear controls. | 164 | 85.86 | 591.56
11331 | TIN-INTERP | Interpolated Ground | 72544.92 | -5.45 | 511.85 | 0 | 74.02 | 0 | OK | Ground clear controls. | 164 | 85.86 | 585.87
11332 | TIN-INTERP | Interpolated Ground | 72545.03 | -4.78 | 512.22 | 0 | 85.86 | 0 | OK | Ground clear controls. | 164 | 85.86 | 598.08
11333 | TIN-INTERP | Interpolated Ground | 72546.45 | 6.92 | 518.85 | 0 | 79.54 | 0 | OK | Ground clear controls. | 164 | 79.54 | 598.39
11334 | TIN-INTERP | Interpolated Ground | 72546.52 | 7.62 | 519.25 | 0 | 67.05 | 0 | OK | Ground clear controls. | 164 | 78.27 | 586.3
11335 | TIN-INTERP | Interpolated Ground | 72546.71 | 9.11 | 519.83 | 0 | 72.2 | 0 | OK | Ground clear controls. | 164 | 78.27 | 592.03
11336 | TIN-INTERP | Interpolated Ground | 72584.75 | -7.01 | 529.19 | 0 | 65.18 | 0 | OK | Ground clear controls. | 164 | 78.27 | 594.37
11337 | TIN-INTERP | Interpolated Ground | 72584.92 | -5.45 | 529.68 | 0 | 59.01 | 0 | OK | Ground clear controls. | 164 | 78.27 | 588.69
11338 | TIN-INTERP | Interpolated Ground | 72585.03 | -4.79 | 529.88 | 0 | 71.02 | 0 | OK | Ground clear controls. | 164 | 78.27 | 600.9
11339 | TIN-INTERP | Interpolated Ground | 72586.45 | 6.9 | 530.86 | 0 | 70.36 | 0 | OK | Ground clear controls. | 164 | 78.27 | 601.22
11340 | TIN-INTERP | Interpolated Ground | 72586.52 | 7.61 | 530.87 | 0 | 58.27 | 0 | OK | Ground clear controls. | 164 | 78.27 | 589.14
11341 | TIN-INTERP | Interpolated Ground | 72586.71 | 9.09 | 530.91 | 0 | 63.97 | 0 | OK | Ground clear controls. | 164 | 78.27 | 594.88
11342 | TIN-INTERP | Interpolated Ground | 72624.75 | -7.03 | 538.29 | 0 | 59.88 | 0 | OK | Ground clear controls. | 164 | 78.27 | 598.17
11343 | TIN-INTERP | Interpolated Ground | 72624.92 | -5.46 | 538.97 | 0 | 53.51 | 0 | OK | Ground clear controls. | 164 | 78.27 | 592.48
11344 | TIN-INTERP | Interpolated Ground | 72625.03 | -4.8 | 539.24 | 0 | 65.45 | 0 | OK | Ground clear controls. | 164 | 78.27 | 604.69
11345 | TIN-INTERP | Interpolated Ground | 72626.45 | 6.88 | 543.42 | 0 | 61.62 | 0 | OK | Ground clear controls. | 164 | 78.27 | 605.04
11346 | TIN-INTERP | Interpolated Ground | 72626.52 | 7.59 | 543.63 | 0 | 49.32 | 0 | OK | Ground clear controls. | 164 | 78.27 | 592.95
11347 | TIN-INTERP | Interpolated Ground | 72626.71 | 9.08 | 544.18 | 0 | 54.53 | 0 | OK | Ground clear controls. | 164 | 78.27 | 598.71
11348 | TIN-INTERP | Interpolated Ground | 72664.75 | -7.04 | 530.21 | 0 | 72.73 | 0 | OK | Ground clear controls. | 164 | 78.27 | 602.94
11349 | TIN-INTERP | Interpolated Ground | 72664.92 | -5.46 | 530.91 | 0 | 66.35 | 0 | OK | Ground clear controls. | 164 | 78.27 | 597.26
11350 | TIN-INTERP | Interpolated Ground | 72665.03 | -4.8 | 531.19 | 0 | 78.27 | 0 | OK | Ground clear controls. | 164 | 78.27 | 609.46
11351 | TIN-INTERP | Interpolated Ground | 72666.45 | 6.87 | 535.99 | 0 | 73.85 | 0 | OK | Ground clear controls. | 164 | 74.47 | 609.84
11352 | TIN-INTERP | Interpolated Ground | 72666.52 | 7.57 | 536.35 | 0 | 61.4 | 0 | OK | Ground clear controls. | 164 | 74.47 | 597.75
11353 | TIN-INTERP | Interpolated Ground | 72666.71 | 9.06 | 537.11 | 0 | 66.42 | 0 | OK | Ground clear controls. | 164 | 74.47 | 603.53
11354 | TIN-INTERP | Interpolated Ground | 72704.75 | -7.05 | 541.28 | 0 | 67.43 | 0 | OK | Ground clear controls. | 164 | 74.47 | 608.71
11355 | TIN-INTERP | Interpolated Ground | 72704.92 | -5.47 | 541.41 | 0 | 61.6 | 0 | OK | Ground clear controls. | 164 | 74.47 | 603.01
11356 | TIN-INTERP | Interpolated Ground | 72705.03 | -4.81 | 541.43 | 0 | 73.77 | 0 | OK | Ground clear controls. | 164 | 74.47 | 615.2
11357 | TIN-INTERP | Interpolated Ground | 72706.45 | 6.85 | 541.16 | 0 | 74.47 | 0 | OK | Ground clear controls. | 164 | 74.47 | 615.63
11358 | TIN-INTERP | Interpolated Ground | 72706.52 | 7.55 | 541.17 | 0 | 62.37 | 0 | OK | Ground clear controls. | 164 | 67.91 | 603.54
11359 | TIN-INTERP | Interpolated Ground | 72706.71 | 9.04 | 541.42 | 0 | 67.91 | 0 | OK | Ground clear controls. | 164 | 67.91 | 609.33
11360 | TIN-INTERP | Interpolated Ground | 72744.75 | -7.06 | 557.56 | 0 | 57.89 | 0 | OK | Ground clear controls. | 164 | 66.31 | 615.45
11361 | TIN-INTERP | Interpolated Ground | 72744.92 | -5.48 | 557.37 | 0 | 52.38 | 0 | OK | Ground clear controls. | 164 | 66.31 | 609.75
11362 | TIN-INTERP | Interpolated Ground | 72745.03 | -4.82 | 557.34 | 0 | 64.6 | 0 | OK | Ground clear controls. | 164 | 66.31 | 621.94
11363 | TIN-INTERP | Interpolated Ground | 72746.45 | 6.83 | 556.08 | 0 | 66.31 | 0 | OK | Ground clear controls. | 164 | 66.31 | 622.39
11364 | TIN-INTERP | Interpolated Ground | 72746.52 | 7.54 | 556.1 | 0 | 54.21 | 0 | OK | Ground clear controls. | 164 | 60.13 | 610.31
11365 | TIN-INTERP | Interpolated Ground | 72746.71 | 9.03 | 555.99 | 0 | 60.13 | 0 | OK | Ground clear controls. | 164 | 60.13 | 616.12
11366 | TIN-INTERP | Interpolated Ground | 72784.75 | -7.07 | 574.29 | 0 | 48.89 | 0 | OK | Ground clear controls. | 164 | 56.61 | 623.18
11367 | TIN-INTERP | Interpolated Ground | 72784.92 | -5.48 | 574.18 | 0 | 43.3 | 0 | OK | Ground clear controls. | 164 | 56.61 | 617.48
11368 | TIN-INTERP | Interpolated Ground | 72785.03 | -4.83 | 574.18 | 0 | 55.47 | 0 | OK | Ground clear controls. | 164 | 56.61 | 629.65
11369 | TIN-INTERP | Interpolated Ground | 72786.45 | 6.81 | 573.54 | 0 | 56.61 | 0 | OK | Ground clear controls. | 164 | 56.61 | 630.15
11370 | TIN-INTERP | Interpolated Ground | 72786.52 | 7.52 | 573.48 | 0 | 44.59 | 0 | OK | Ground clear controls. | 164 | 50.49 | 618.07
11371 | TIN-INTERP | Interpolated Ground | 72786.71 | 9.01 | 573.41 | 0 | 50.49 | 0 | OK | Ground clear controls. | 164 | 50.49 | 623.9
11372 | TIN-INTERP | Interpolated Ground | 72824.75 | -7.08 | 598.75 | 0 | 33.16 | 0 | OK | Ground clear controls. | 164 | 40.95 | 631.91
11373 | TIN-INTERP | Interpolated Ground | 72824.92 | -5.49 | 598.58 | 0 | 27.62 | 0 | OK | Ground clear controls. | 164 | 40.95 | 626.2
11374 | TIN-INTERP | Interpolated Ground | 72825.03 | -4.83 | 598.65 | 0 | 39.71 | 0 | OK | Ground clear controls. | 164 | 40.95 | 638.36
11375 | TIN-INTERP | Interpolated Ground | 72826.45 | 6.8 | 597.94 | 0 | 40.95 | 0 | OK | Ground clear controls. | 164 | 40.95 | 638.89
11376 | TIN-INTERP | Interpolated Ground | 72826.52 | 7.5 | 597.89 | 0 | 28.92 | 0 | OK | Ground clear controls. | 164 | 34.86 | 626.81
11377 | TIN-INTERP | Interpolated Ground | 72826.71 | 8.99 | 597.81 | 0 | 34.86 | 0 | OK | Ground clear controls. | 164 | 34.86 | 632.67
11378 | TIN-INTERP | Interpolated Ground | 72864.75 | -7.09 | 623.3 | 0 | 18.34 | 0 | OK | Ground clear controls. | 164 | 27.76 | 641.64
11379 | TIN-INTERP | Interpolated Ground | 72864.92 | -5.49 | 623.28 | 0 | 12.63 | 0 | OK | Ground clear controls. | 164 | 27.76 | 635.91
11380 | TIN-INTERP | Interpolated Ground | 72865.03 | -4.84 | 623.27 | 0 | 24.79 | 0 | OK | Ground clear controls. | 164 | 27.76 | 648.06
11381 | TIN-INTERP | Interpolated Ground | 72866.45 | 6.78 | 620.88 | 0 | 27.76 | 0 | OK | Ground clear controls. | 164 | 27.76 | 648.64
11382 | TIN-INTERP | Interpolated Ground | 72866.52 | 7.49 | 620.49 | 0 | 16.07 | 0 | OK | Ground clear controls. | 164 | 22.59 | 636.56
11383 | TIN-INTERP | Interpolated Ground | 72866.71 | 8.97 | 619.85 | 0 | 22.59 | 0 | OK | Ground clear controls. | 164 | 22.59 | 642.44
11384 | TIN-INTERP | Interpolated Ground | 72870.59 | -7.12 | 623.33 | 0 | 19.96 | 0 | OK | Ground clear controls. | 165 | 140.29 | 643.29
11385 | TIN-INTERP | Interpolated Ground | 72870.59 | -5.52 | 623.34 | 0 | 14.14 | 0 | OK | Ground clear controls. | 165 | 140.29 | 637.48
11386 | TIN-INTERP | Interpolated Ground | 72870.59 | -4.86 | 623.36 | 0 | 26.22 | 0 | OK | Ground clear controls. | 165 | 140.29 | 649.58
11387 | TIN-INTERP | Interpolated Ground | 72871.33 | 6.75 | 621.56 | 0 | 28.03 | 0 | OK | Ground clear controls. | 165 | 140.29 | 649.59
11388 | TIN-INTERP | Interpolated Ground | 72871.45 | 7.45 | 621.26 | 0 | 16.23 | 0 | OK | Ground clear controls. | 165 | 140.29 | 637.49
11389 | TIN-INTERP | Interpolated Ground | 72871.57 | 8.94 | 620.19 | 0 | 23.1 | 0 | OK | Ground clear controls. | 165 | 140.29 | 643.29
11390 | TIN-INTERP | Interpolated Ground | 72909.96 | -7.15 | 593.57 | 0 | 43.66 | 0 | OK | Ground clear controls. | 165 | 140.29 | 637.23
11391 | TIN-INTERP | Interpolated Ground | 72910.13 | -5.56 | 594.17 | 0 | 37.3 | 0 | OK | Ground clear controls. | 165 | 140.29 | 631.47
11392 | TIN-INTERP | Interpolated Ground | 72910.2 | -4.91 | 594.42 | 0 | 49.17 | 0 | OK | Ground clear controls. | 165 | 140.29 | 643.59
11393 | TIN-INTERP | Interpolated Ground | 72911.33 | 6.7 | 600.51 | 0 | 43.05 | 0 | OK | Ground clear controls. | 165 | 140.29 | 643.56
11394 | TIN-INTERP | Interpolated Ground | 72911.45 | 7.39 | 600.67 | 0 | 30.89 | 0 | OK | Ground clear controls. | 165 | 140.29 | 631.56
11395 | TIN-INTERP | Interpolated Ground | 72911.57 | 8.88 | 601.98 | 0 | 35.3 | 0 | OK | Ground clear controls. | 165 | 140.29 | 637.28
11396 | TIN-INTERP | Interpolated Ground | 72949.96 | -7.21 | 568.46 | 0 | 63.68 | 0 | OK | Ground clear controls. | 165 | 140.29 | 632.14
11397 | TIN-INTERP | Interpolated Ground | 72950.13 | -5.62 | 569.1 | 0 | 57.32 | 0 | OK | Ground clear controls. | 165 | 140.29 | 626.42
11398 | TIN-INTERP | Interpolated Ground | 72950.2 | -4.97 | 569.41 | 0 | 69.15 | 0 | OK | Ground clear controls. | 165 | 140.29 | 638.56
11399 | TIN-INTERP | Interpolated Ground | 72951.33 | 6.65 | 574.32 | 0 | 64.17 | 0 | OK | Ground clear controls. | 165 | 140.29 | 638.49
11400 | TIN-INTERP | Interpolated Ground | 72951.45 | 7.34 | 574.57 | 0 | 52.01 | 0 | OK | Ground clear controls. | 165 | 140.29 | 626.58
11401 | TIN-INTERP | Interpolated Ground | 72951.57 | 8.83 | 575.23 | 0 | 57 | 0 | OK | Ground clear controls. | 165 | 140.29 | 632.23
11402 | TIN-INTERP | Interpolated Ground | 72989.96 | -7.26 | 547.21 | 0 | 80.79 | 0 | OK | Ground clear controls. | 165 | 140.29 | 628
11403 | TIN-INTERP | Interpolated Ground | 72990.13 | -5.68 | 547.73 | 0 | 74.59 | 0 | OK | Ground clear controls. | 165 | 140.29 | 622.32
11404 | TIN-INTERP | Interpolated Ground | 72990.2 | -5.03 | 547.88 | 0 | 86.6 | 0 | OK | Ground clear controls. | 165 | 140.29 | 634.48
11405 | TIN-INTERP | Interpolated Ground | 72991.33 | 6.59 | 547.3 | 0 | 87.08 | 0 | OK | Ground clear controls. | 165 | 140.29 | 634.38
11406 | TIN-INTERP | Interpolated Ground | 72991.45 | 7.29 | 546.94 | 0 | 75.61 | 0 | OK | Ground clear controls. | 165 | 140.29 | 622.55
11407 | TIN-INTERP | Interpolated Ground | 72991.57 | 8.78 | 546.52 | 0 | 81.62 | 0 | OK | Ground clear controls. | 165 | 140.29 | 628.14
11408 | TIN-INTERP | Interpolated Ground | 73029.96 | -7.32 | 527.84 | 0 | 96.99 | 0 | OK | Ground clear controls. | 165 | 140.29 | 624.83
11409 | TIN-INTERP | Interpolated Ground | 73030.13 | -5.74 | 527.48 | 0 | 91.7 | 0 | OK | Ground clear controls. | 165 | 140.29 | 619.18
11410 | TIN-INTERP | Interpolated Ground | 73030.19 | -5.09 | 527.16 | 0 | 104.2 | 0 | OK | Ground clear controls. | 165 | 140.29 | 631.36
11411 | TIN-INTERP | Interpolated Ground | 73031.33 | 6.54 | 524.36 | 0 | 106.87 | 0 | OK | Ground clear controls. | 165 | 140.29 | 631.23
11412 | TIN-INTERP | Interpolated Ground | 73031.45 | 7.24 | 524.28 | 0 | 95.2 | 0 | OK | Ground clear controls. | 165 | 140.29 | 619.48
11413 | TIN-INTERP | Interpolated Ground | 73031.57 | 8.73 | 524.01 | 0 | 100.99 | 0 | OK | Ground clear controls. | 165 | 140.29 | 625
11414 | TIN-INTERP | Interpolated Ground | 73069.96 | -7.38 | 510.46 | 0 | 112.16 | 0 | OK | Ground clear controls. | 165 | 140.29 | 622.62
11415 | TIN-INTERP | Interpolated Ground | 73070.13 | -5.81 | 509.33 | 0 | 107.67 | 0 | OK | Ground clear controls. | 165 | 140.29 | 617
11416 | TIN-INTERP | Interpolated Ground | 73070.19 | -5.15 | 508.81 | 0 | 120.37 | 0 | OK | Ground clear controls. | 165 | 140.29 | 629.18
11417 | TIN-INTERP | Interpolated Ground | 73071.33 | 6.49 | 501.22 | 0 | 127.81 | 0 | OK | Ground clear controls. | 165 | 140.29 | 629.03
11418 | TIN-INTERP | Interpolated Ground | 73071.45 | 7.19 | 500.94 | 0 | 116.42 | 0 | OK | Ground clear controls. | 165 | 140.29 | 617.36
11419 | TIN-INTERP | Interpolated Ground | 73071.57 | 8.68 | 500.41 | 0 | 122.42 | 0 | OK | Ground clear controls. | 165 | 140.29 | 622.83
11420 | TIN-INTERP | Interpolated Ground | 73109.96 | -7.44 | 487.93 | 0 | 133.46 | 0 | OK | Ground clear controls. | 165 | 140.29 | 621.39
11421 | TIN-INTERP | Interpolated Ground | 73110.13 | -5.87 | 487.51 | 0 | 128.29 | 0 | OK | Ground clear controls. | 165 | 140.29 | 615.8
11422 | TIN-INTERP | Interpolated Ground | 73110.19 | -5.21 | 487.7 | 0 | 140.29 | 0 | OK | Ground clear controls. | 165 | 140.29 | 627.99
11423 | TIN-INTERP | Interpolated Ground | 73111.33 | 6.44 | 495.42 | 0 | 132.41 | 0 | OK | Ground clear controls. | 165 | 135.82 | 627.83
11424 | TIN-INTERP | Interpolated Ground | 73111.45 | 7.13 | 495.85 | 0 | 120.37 | 0 | OK | Ground clear controls. | 165 | 135.82 | 616.22
11425 | TIN-INTERP | Interpolated Ground | 73111.57 | 8.62 | 496.76 | 0 | 124.88 | 0 | OK | Ground clear controls. | 165 | 135.82 | 621.64
11426 | TIN-INTERP | Interpolated Ground | 73149.96 | -7.5 | 490.89 | 0 | 130.24 | 0 | OK | Ground clear controls. | 165 | 135.82 | 621.13
11427 | TIN-INTERP | Interpolated Ground | 73150.13 | -5.93 | 491.7 | 0 | 123.86 | 0 | OK | Ground clear controls. | 165 | 135.82 | 615.56
11428 | TIN-INTERP | Interpolated Ground | 73150.19 | -5.27 | 492.23 | 0 | 135.54 | 0 | OK | Ground clear controls. | 165 | 135.82 | 627.77
11429 | TIN-INTERP | Interpolated Ground | 73151.33 | 6.38 | 500.24 | 0 | 127.35 | 0 | OK | Ground clear controls. | 165 | 135.82 | 627.59
11430 | TIN-INTERP | Interpolated Ground | 73151.45 | 7.08 | 500.59 | 0 | 115.43 | 0 | OK | Ground clear controls. | 165 | 135.82 | 616.02
11431 | TIN-INTERP | Interpolated Ground | 73151.57 | 8.57 | 501.31 | 0 | 120.1 | 0 | OK | Ground clear controls. | 165 | 135.82 | 621.41
11432 | TIN-INTERP | Interpolated Ground | 73189.96 | -7.56 | 509.61 | 0 | 112.21 | 0 | OK | Ground clear controls. | 165 | 135.82 | 621.82
11433 | TIN-INTERP | Interpolated Ground | 73190.13 | -5.99 | 510.3 | 0 | 105.97 | 0 | OK | Ground clear controls. | 165 | 135.82 | 616.27
11434 | TIN-INTERP | Interpolated Ground | 73190.19 | -5.33 | 510.59 | 0 | 117.9 | 0 | OK | Ground clear controls. | 165 | 135.82 | 628.49
11435 | TIN-INTERP | Interpolated Ground | 73191.33 | 6.33 | 513.27 | 0 | 115.03 | 0 | OK | Ground clear controls. | 165 | 135.82 | 628.3
11436 | TIN-INTERP | Interpolated Ground | 73191.45 | 7.03 | 513.34 | 0 | 103.43 | 0 | OK | Ground clear controls. | 165 | 135.82 | 616.77
11437 | TIN-INTERP | Interpolated Ground | 73191.57 | 8.52 | 513.96 | 0 | 108.17 | 0 | OK | Ground clear controls. | 165 | 135.82 | 622.13
11438 | TIN-INTERP | Interpolated Ground | 73229.96 | -7.61 | 508.19 | 0 | 115.29 | 0 | OK | Ground clear controls. | 165 | 135.82 | 623.48
11439 | TIN-INTERP | Interpolated Ground | 73230.13 | -6.05 | 508.65 | 0 | 109.29 | 0 | OK | Ground clear controls. | 165 | 135.82 | 617.94
11440 | TIN-INTERP | Interpolated Ground | 73230.19 | -5.39 | 508.77 | 0 | 121.39 | 0 | OK | Ground clear controls. | 165 | 135.82 | 630.16
11441 | TIN-INTERP | Interpolated Ground | 73231.33 | 6.28 | 510.56 | 0 | 119.4 | 0 | OK | Ground clear controls. | 165 | 135.82 | 629.96
11442 | TIN-INTERP | Interpolated Ground | 73231.45 | 6.98 | 510.47 | 0 | 108.01 | 0 | OK | Ground clear controls. | 165 | 135.82 | 618.48
11443 | TIN-INTERP | Interpolated Ground | 73231.57 | 8.47 | 510.51 | 0 | 113.3 | 0 | OK | Ground clear controls. | 165 | 135.82 | 623.81
11444 | TIN-INTERP | Interpolated Ground | 73269.96 | -7.67 | 498.49 | 0 | 127.59 | 0 | OK | Ground clear controls. | 165 | 135.82 | 626.08
11445 | TIN-INTERP | Interpolated Ground | 73270.13 | -6.11 | 498.58 | 0 | 121.99 | 0 | OK | Ground clear controls. | 165 | 135.82 | 620.57
11446 | TIN-INTERP | Interpolated Ground | 73270.19 | -5.45 | 498.95 | 0 | 133.84 | 0 | OK | Ground clear controls. | 165 | 135.82 | 632.79
11447 | TIN-INTERP | Interpolated Ground | 73271.33 | 6.23 | 503.97 | 0 | 128.62 | 0 | OK | Ground clear controls. | 165 | 135.82 | 632.59
11448 | TIN-INTERP | Interpolated Ground | 73271.45 | 6.92 | 504.11 | 0 | 117.03 | 0 | OK | Ground clear controls. | 165 | 135.82 | 621.14
11449 | TIN-INTERP | Interpolated Ground | 73271.57 | 8.42 | 504.44 | 0 | 122 | 0 | OK | Ground clear controls. | 165 | 135.82 | 626.44
11450 | TIN-INTERP | Interpolated Ground | 73309.96 | -7.73 | 508.48 | 0 | 121.17 | 0 | OK | Ground clear controls. | 165 | 135.82 | 629.65
11451 | TIN-INTERP | Interpolated Ground | 73310.13 | -6.18 | 507.53 | 0 | 116.61 | 0 | OK | Ground clear controls. | 165 | 135.82 | 624.14
11452 | TIN-INTERP | Interpolated Ground | 73310.19 | -5.51 | 507.1 | 0 | 129.28 | 0 | OK | Ground clear controls. | 165 | 135.82 | 636.38
11453 | TIN-INTERP | Interpolated Ground | 73311.33 | 6.18 | 503.96 | 0 | 132.22 | 0 | OK | Ground clear controls. | 165 | 135.82 | 636.18
11454 | TIN-INTERP | Interpolated Ground | 73311.45 | 6.87 | 504.56 | 0 | 120.19 | 0 | OK | Ground clear controls. | 165 | 135.82 | 624.75
11455 | TIN-INTERP | Interpolated Ground | 73311.57 | 8.36 | 506.03 | 0 | 123.99 | 0 | OK | Ground clear controls. | 165 | 135.82 | 630.02
11456 | TIN-INTERP | Interpolated Ground | 73349.96 | -7.79 | 517.45 | 0 | 116.76 | 0 | OK | Ground clear controls. | 165 | 135.82 | 634.21
11457 | TIN-INTERP | Interpolated Ground | 73350.13 | -6.24 | 516.09 | 0 | 112.62 | 0 | OK | Ground clear controls. | 165 | 135.82 | 628.71
11458 | TIN-INTERP | Interpolated Ground | 73350.19 | -5.57 | 515.45 | 0 | 125.5 | 0 | OK | Ground clear controls. | 165 | 135.82 | 640.95
11459 | TIN-INTERP | Interpolated Ground | 73351.33 | 6.12 | 504.93 | 0 | 135.82 | 0 | OK | Ground clear controls. | 165 | 135.82 | 640.75
11460 | TIN-INTERP | Interpolated Ground | 73351.45 | 6.82 | 505.17 | 0 | 124.18 | 0 | OK | Ground clear controls. | 165 | 128.79 | 629.35
11461 | TIN-INTERP | Interpolated Ground | 73351.57 | 8.31 | 505.82 | 0 | 128.79 | 0 | OK | Ground clear controls. | 165 | 128.79 | 634.61
11462 | TIN-INTERP | Interpolated Ground | 73389.96 | -7.85 | 535.51 | 0 | 104.23 | 0 | OK | Ground clear controls. | 165 | 117.97 | 639.74
11463 | TIN-INTERP | Interpolated Ground | 73390.13 | -6.3 | 534.72 | 0 | 99.53 | 0 | OK | Ground clear controls. | 165 | 117.97 | 634.25
11464 | TIN-INTERP | Interpolated Ground | 73390.19 | -5.63 | 534.36 | 0 | 112.12 | 0 | OK | Ground clear controls. | 165 | 117.97 | 646.48
11465 | TIN-INTERP | Interpolated Ground | 73391.33 | 6.07 | 528.32 | 0 | 117.97 | 0 | OK | Ground clear controls. | 165 | 117.97 | 646.29
11466 | TIN-INTERP | Interpolated Ground | 73391.45 | 6.77 | 528.02 | 0 | 106.87 | 0 | OK | Ground clear controls. | 165 | 112.89 | 634.89
11467 | TIN-INTERP | Interpolated Ground | 73391.57 | 8.26 | 527.27 | 0 | 112.89 | 0 | OK | Ground clear controls. | 165 | 112.89 | 640.16
11468 | TIN-INTERP | Interpolated Ground | 73429.96 | -7.9 | 554.01 | 0 | 92.22 | 0 | OK | Ground clear controls. | 165 | 106.15 | 646.23
11469 | TIN-INTERP | Interpolated Ground | 73430.13 | -6.36 | 553.38 | 0 | 87.37 | 0 | OK | Ground clear controls. | 165 | 106.15 | 640.75
11470 | TIN-INTERP | Interpolated Ground | 73430.19 | -5.69 | 552.9 | 0 | 100.08 | 0 | OK | Ground clear controls. | 165 | 106.15 | 652.98
11471 | TIN-INTERP | Interpolated Ground | 73431.33 | 6.02 | 546.65 | 0 | 106.15 | 0 | OK | Ground clear controls. | 165 | 106.15 | 652.8
11472 | TIN-INTERP | Interpolated Ground | 73431.45 | 6.71 | 546.35 | 0 | 95.05 | 0 | OK | Ground clear controls. | 165 | 101.69 | 641.4
11473 | TIN-INTERP | Interpolated Ground | 73431.57 | 8.21 | 545.53 | 0 | 101.14 | 0 | OK | Ground clear controls. | 165 | 101.69 | 646.67
11474 | TIN-INTERP | Interpolated Ground | 73469.96 | -7.96 | 567.48 | 0 | 86.22 | 0 | OK | Ground clear controls. | 165 | 101.69 | 653.7
11475 | TIN-INTERP | Interpolated Ground | 73470.13 | -6.42 | 566.54 | 0 | 81.66 | 0 | OK | Ground clear controls. | 165 | 101.69 | 648.2
11476 | TIN-INTERP | Interpolated Ground | 73470.19 | -5.75 | 566.15 | 0 | 94.29 | 0 | OK | Ground clear controls. | 165 | 101.69 | 660.44
11477 | TIN-INTERP | Interpolated Ground | 73471.33 | 5.97 | 560.1 | 0 | 100.18 | 0 | OK | Ground clear controls. | 165 | 101.69 | 660.28
11478 | TIN-INTERP | Interpolated Ground | 73471.45 | 6.66 | 559.84 | 0 | 89.03 | 0 | OK | Ground clear controls. | 165 | 101.69 | 648.87
11479 | TIN-INTERP | Interpolated Ground | 73471.57 | 8.16 | 558.95 | 0 | 95.19 | 0 | OK | Ground clear controls. | 165 | 101.69 | 654.14
11480 | TIN-INTERP | Interpolated Ground | 73509.96 | -8.02 | 575.55 | 0 | 86.58 | 0 | OK | Ground clear controls. | 165 | 101.69 | 662.13
11481 | TIN-INTERP | Interpolated Ground | 73510.13 | -6.49 | 574.65 | 0 | 81.99 | 0 | OK | Ground clear controls. | 165 | 101.69 | 656.64
11482 | TIN-INTERP | Interpolated Ground | 73510.19 | -5.81 | 574.33 | 0 | 94.54 | 0 | OK | Ground clear controls. | 165 | 101.69 | 668.87
11483 | TIN-INTERP | Interpolated Ground | 73511.33 | 5.92 | 567.03 | 0 | 101.69 | 0 | OK | Ground clear controls. | 165 | 101.69 | 668.72
11484 | TIN-INTERP | Interpolated Ground | 73511.45 | 6.61 | 566.63 | 0 | 90.67 | 0 | OK | Ground clear controls. | 165 | 96.64 | 657.3
11485 | TIN-INTERP | Interpolated Ground | 73511.57 | 8.1 | 565.94 | 0 | 96.64 | 0 | OK | Ground clear controls. | 165 | 96.64 | 662.58
11486 | TIN-INTERP | Interpolated Ground | 73549.96 | -8.08 | 590.86 | 0 | 80.73 | 0 | OK | Ground clear controls. | 165 | 94.83 | 671.59
11487 | TIN-INTERP | Interpolated Ground | 73550.13 | -6.55 | 589.65 | 0 | 76.44 | 0 | OK | Ground clear controls. | 165 | 94.83 | 666.09
11488 | TIN-INTERP | Interpolated Ground | 73550.19 | -5.87 | 589.21 | 0 | 89.1 | 0 | OK | Ground clear controls. | 165 | 94.83 | 678.31
11489 | TIN-INTERP | Interpolated Ground | 73551.33 | 5.86 | 583.36 | 0 | 94.83 | 0 | OK | Ground clear controls. | 165 | 94.83 | 678.19
11490 | TIN-INTERP | Interpolated Ground | 73551.45 | 6.56 | 583.08 | 0 | 83.67 | 0 | OK | Ground clear controls. | 165 | 91.09 | 666.75
11491 | TIN-INTERP | Interpolated Ground | 73551.57 | 8.05 | 582.43 | 0 | 89.62 | 0 | OK | Ground clear controls. | 165 | 91.09 | 672.05
11492 | TIN-INTERP | Interpolated Ground | 73589.96 | -8.14 | 606.04 | 0 | 75.99 | 0 | OK | Ground clear controls. | 165 | 91.09 | 682.03
11493 | TIN-INTERP | Interpolated Ground | 73590.13 | -6.61 | 605.27 | 0 | 71.24 | 0 | OK | Ground clear controls. | 165 | 91.09 | 676.51
11494 | TIN-INTERP | Interpolated Ground | 73590.19 | -5.93 | 604.73 | 0 | 84 | 0 | OK | Ground clear controls. | 165 | 91.09 | 688.73
11495 | TIN-INTERP | Interpolated Ground | 73591.33 | 5.81 | 597.55 | 0 | 91.09 | 0 | OK | Ground clear controls. | 165 | 91.09 | 688.64
11496 | TIN-INTERP | Interpolated Ground | 73591.45 | 6.51 | 597.24 | 0 | 79.93 | 0 | OK | Ground clear controls. | 165 | 85.93 | 677.17
11497 | TIN-INTERP | Interpolated Ground | 73591.57 | 8 | 596.56 | 0 | 85.93 | 0 | OK | Ground clear controls. | 165 | 85.93 | 682.49
11498 | TIN-INTERP | Interpolated Ground | 73629.96 | -8.2 | 626.28 | 0 | 67.17 | 0 | OK | Ground clear controls. | 165 | 78.62 | 693.45
11499 | TIN-INTERP | Interpolated Ground | 73630.13 | -6.67 | 625.86 | 0 | 62.07 | 0 | OK | Ground clear controls. | 165 | 78.62 | 687.93
11500 | TIN-INTERP | Interpolated Ground | 73630.19 | -5.99 | 625.58 | 0 | 74.56 | 0 | OK | Ground clear controls. | 165 | 78.62 | 700.14
11501 | TIN-INTERP | Interpolated Ground | 73631.33 | 5.76 | 621.45 | 0 | 78.61 | 0 | OK | Ground clear controls. | 165 | 78.62 | 700.06
11502 | TIN-INTERP | Interpolated Ground | 73631.45 | 6.45 | 621.31 | 0 | 67.26 | 0 | OK | Ground clear controls. | 165 | 78.62 | 688.57
11503 | TIN-INTERP | Interpolated Ground | 73631.57 | 7.95 | 620.86 | 0 | 73.05 | 0 | OK | Ground clear controls. | 165 | 78.62 | 693.91
11504 | TIN-INTERP | Interpolated Ground | 73669.96 | -8.25 | 644.95 | 0 | 60.92 | 0 | OK | Ground clear controls. | 165 | 78.62 | 705.87
11505 | TIN-INTERP | Interpolated Ground | 73670.13 | -6.73 | 643.87 | 0 | 56.45 | 0 | OK | Ground clear controls. | 165 | 78.62 | 700.32
11506 | TIN-INTERP | Interpolated Ground | 73670.19 | -6.05 | 643.38 | 0 | 69.14 | 0 | OK | Ground clear controls. | 165 | 78.62 | 712.52
11507 | TIN-INTERP | Interpolated Ground | 73671.33 | 5.71 | 633.87 | 0 | 78.62 | 0 | OK | Ground clear controls. | 165 | 78.62 | 712.49
11508 | TIN-INTERP | Interpolated Ground | 73671.45 | 6.4 | 633.26 | 0 | 67.69 | 0 | OK | Ground clear controls. | 165 | 74.09 | 700.95
11509 | TIN-INTERP | Interpolated Ground | 73671.57 | 7.9 | 632.24 | 0 | 74.09 | 0 | OK | Ground clear controls. | 165 | 74.09 | 706.33
11510 | TIN-INTERP | Interpolated Ground | 73709.96 | -8.31 | 662.18 | 0 | 57.15 | 0 | OK | Ground clear controls. | 165 | 67.05 | 719.33
11511 | TIN-INTERP | Interpolated Ground | 73710.13 | -6.79 | 661.78 | 0 | 51.98 | 0 | OK | Ground clear controls. | 165 | 67.05 | 713.76
11512 | TIN-INTERP | Interpolated Ground | 73710.19 | -6.11 | 661.6 | 0 | 64.35 | 0 | OK | Ground clear controls. | 165 | 67.05 | 725.95
11513 | TIN-INTERP | Interpolated Ground | 73711.33 | 5.66 | 658.91 | 0 | 67.05 | 0 | OK | Ground clear controls. | 165 | 67.05 | 725.96
11514 | TIN-INTERP | Interpolated Ground | 73711.45 | 6.35 | 658.92 | 0 | 55.44 | 0 | OK | Ground clear controls. | 165 | 66.32 | 714.36
11515 | TIN-INTERP | Interpolated Ground | 73711.57 | 7.84 | 658.78 | 0 | 61.02 | 0 | OK | Ground clear controls. | 165 | 66.32 | 719.8
11516 | TIN-INTERP | Interpolated Ground | 73749.96 | -8.37 | 682.95 | 0 | 50.85 | 0 | OK | Ground clear controls. | 165 | 66.32 | 733.8
11517 | TIN-INTERP | Interpolated Ground | 73750.13 | -6.86 | 682 | 0 | 46.21 | 0 | OK | Ground clear controls. | 165 | 66.32 | 728.21
11518 | TIN-INTERP | Interpolated Ground | 73750.19 | -6.17 | 681.53 | 0 | 58.85 | 0 | OK | Ground clear controls. | 165 | 66.32 | 740.38
11519 | TIN-INTERP | Interpolated Ground | 73751.33 | 5.6 | 674.1 | 0 | 66.32 | 0 | OK | Ground clear controls. | 165 | 66.32 | 740.42
11520 | TIN-INTERP | Interpolated Ground | 73751.45 | 6.3 | 673.78 | 0 | 54.99 | 0 | OK | Ground clear controls. | 165 | 61.07 | 728.77
11521 | TIN-INTERP | Interpolated Ground | 73751.57 | 7.79 | 673.19 | 0 | 61.07 | 0 | OK | Ground clear controls. | 165 | 61.07 | 734.26
11522 | TIN-INTERP | Interpolated Ground | 73789.96 | -8.43 | 705.72 | 0 | 43.55 | 0 | OK | Ground clear controls. | 165 | 54.27 | 749.27
11523 | TIN-INTERP | Interpolated Ground | 73790.13 | -6.92 | 704.78 | 0 | 38.87 | 0 | OK | Ground clear controls. | 165 | 54.27 | 743.65
11524 | TIN-INTERP | Interpolated Ground | 73790.19 | -6.23 | 704.4 | 0 | 51.41 | 0 | OK | Ground clear controls. | 165 | 54.27 | 755.81
11525 | TIN-INTERP | Interpolated Ground | 73791.33 | 5.55 | 701.63 | 0 | 54.27 | 0 | OK | Ground clear controls. | 165 | 54.27 | 755.9
11526 | TIN-INTERP | Interpolated Ground | 73791.45 | 6.24 | 701.67 | 0 | 42.5 | 0 | OK | Ground clear controls. | 165 | 50.34 | 744.17
11527 | TIN-INTERP | Interpolated Ground | 73791.57 | 7.74 | 701.42 | 0 | 48.3 | 0 | OK | Ground clear controls. | 165 | 50.34 | 749.72
11528 | TIN-INTERP | Interpolated Ground | 73829.96 | -8.49 | 731.26 | 0 | 34.55 | 0 | OK | Ground clear controls. | 165 | 50.34 | 765.81
11529 | TIN-INTERP | Interpolated Ground | 73830.13 | -6.98 | 730.14 | 0 | 30.02 | 0 | OK | Ground clear controls. | 165 | 50.34 | 760.16
11530 | TIN-INTERP | Interpolated Ground | 73830.19 | -6.29 | 729.54 | 0 | 42.76 | 0 | OK | Ground clear controls. | 165 | 50.34 | 772.3
11531 | TIN-INTERP | Interpolated Ground | 73831.33 | 5.5 | 722.12 | 0 | 50.34 | 0 | OK | Ground clear controls. | 165 | 50.34 | 772.46
11532 | TIN-INTERP | Interpolated Ground | 73831.45 | 6.19 | 721.79 | 0 | 38.85 | 0 | OK | Ground clear controls. | 165 | 45.72 | 760.64
11533 | TIN-INTERP | Interpolated Ground | 73831.57 | 7.69 | 720.87 | 0 | 45.39 | 0 | OK | Ground clear controls. | 165 | 45.72 | 766.26
11534 | TIN-INTERP | Interpolated Ground | 73869.96 | -8.55 | 747.98 | 0 | 35.41 | 0 | OK | Ground clear controls. | 165 | 45.72 | 783.39
11535 | TIN-INTERP | Interpolated Ground | 73870.13 | -7.04 | 747.38 | 0 | 30.33 | 0 | OK | Ground clear controls. | 165 | 45.72 | 777.71
11536 | TIN-INTERP | Interpolated Ground | 73870.19 | -6.35 | 747.06 | 0 | 42.77 | 0 | OK | Ground clear controls. | 165 | 45.72 | 789.83
11537 | TIN-INTERP | Interpolated Ground | 73871.33 | 5.45 | 744.31 | 0 | 45.72 | 0 | OK | Ground clear controls. | 165 | 45.72 | 790.03
11538 | TIN-INTERP | Interpolated Ground | 73871.45 | 6.14 | 744.4 | 0 | 33.74 | 0 | OK | Ground clear controls. | 165 | 39.46 | 778.14
11539 | TIN-INTERP | Interpolated Ground | 73871.57 | 7.63 | 744.35 | 0 | 39.46 | 0 | OK | Ground clear controls. | 165 | 39.46 | 783.81
11540 | TIN-INTERP | Interpolated Ground | 73909.96 | -8.6 | 772.73 | 0 | 29.27 | 0 | OK | Ground clear controls. | 165 | 35.89 | 802
11541 | TIN-INTERP | Interpolated Ground | 73910.13 | -7.1 | 773.07 | 0 | 23.21 | 0 | OK | Ground clear controls. | 165 | 35.89 | 796.28
11542 | TIN-INTERP | Interpolated Ground | 73910.19 | -6.41 | 773.05 | 0 | 35.34 | 0 | OK | Ground clear controls. | 165 | 35.89 | 808.39
11543 | TIN-INTERP | Interpolated Ground | 73911.33 | 5.4 | 772.76 | 0 | 35.89 | 0 | OK | Ground clear controls. | 165 | 35.89 | 808.65
11544 | TIN-INTERP | Interpolated Ground | 73911.45 | 6.09 | 772.69 | 0 | 23.97 | 0 | OK | Ground clear controls. | 165 | 29.89 | 796.66
11545 | TIN-INTERP | Interpolated Ground | 73911.57 | 7.58 | 772.53 | 0 | 29.89 | 0 | OK | Ground clear controls. | 165 | 29.89 | 802.42
11546 | TIN-INTERP | Interpolated Ground | 73925.99 | 6.09 | 778.23 | 0 | 25.68 | 0 | OK | Ground clear controls. | 166 | 40.29 | 803.91
11547 | TIN-INTERP | Interpolated Ground | 73925.99 | 7.59 | 778.27 | 0 | 31.45 | 0 | OK | Ground clear controls. | 166 | 40.29 | 809.72
11548 | TIN-INTERP | Interpolated Ground | 73926.05 | 5.41 | 778.19 | 0 | 37.83 | 0 | OK | Ground clear controls. | 166 | 40.29 | 816.02
11549 | TIN-INTERP | Interpolated Ground | 73926.58 | -7.1 | 775.43 | 0 | 28.46 | 0 | OK | Ground clear controls. | 166 | 40.29 | 803.89
11550 | TIN-INTERP | Interpolated Ground | 73926.61 | -6.4 | 775.72 | 0 | 40.29 | 0 | OK | Ground clear controls. | 166 | 40.29 | 816.01
11551 | TIN-INTERP | Interpolated Ground | 73926.68 | -8.6 | 774.77 | 0 | 34.93 | 0 | OK | Ground clear controls. | 166 | 34.93 | 809.7
11552 | TIN-INTERP | Interpolated Ground | 73965.93 | 5.81 | 786.23 | 0 | 14.96 | 0 | OK | Ground clear controls. | 166 | 33.08 | 801.19
11553 | TIN-INTERP | Interpolated Ground | 73965.95 | 7.31 | 786.86 | 0 | 20.06 | 0 | OK | Ground clear controls. | 166 | 33.08 | 806.92
11554 | TIN-INTERP | Interpolated Ground | 73966.04 | 5.17 | 785.77 | 0 | 27.22 | 0 | OK | Ground clear controls. | 166 | 33.08 | 812.99
11555 | TIN-INTERP | Interpolated Ground | 73966.57 | -6.62 | 779.68 | 0 | 21.5 | 0 | OK | Ground clear controls. | 166 | 33.08 | 801.18
11556 | TIN-INTERP | Interpolated Ground | 73966.61 | -5.98 | 779.91 | 0 | 33.08 | 0 | OK | Ground clear controls. | 166 | 33.08 | 812.99
11557 | TIN-INTERP | Interpolated Ground | 73966.68 | -8.12 | 779.09 | 0 | 27.8 | 0 | OK | Ground clear controls. | 166 | 27.8 | 806.89
11558 | TIN-INTERP | Interpolated Ground | 74005.93 | 5.53 | 788.29 | 0 | 11.09 | 0 | OK | Ground clear controls. | 166 | 24.82 | 799.38
11559 | TIN-INTERP | Interpolated Ground | 74005.94 | 7.03 | 788.23 | 0 | 16.79 | 0 | OK | Ground clear controls. | 166 | 24.82 | 805.02
11560 | TIN-INTERP | Interpolated Ground | 74006.04 | 4.94 | 788.32 | 0 | 22.53 | 0 | OK | Ground clear controls. | 166 | 24.82 | 810.85
11561 | TIN-INTERP | Interpolated Ground | 74006.57 | -6.14 | 787.97 | 0 | 11.41 | 0 | OK | Ground clear controls. | 166 | 24.82 | 799.38
11562 | TIN-INTERP | Interpolated Ground | 74006.61 | -5.55 | 788.03 | 0 | 22.83 | 0 | OK | Ground clear controls. | 166 | 24.82 | 810.86
11563 | TIN-INTERP | Interpolated Ground | 74006.68 | -7.64 | 787.8 | 0 | 17.2 | 0 | OK | Ground clear controls. | 166 | 24.82 | 805
11564 | TIN-INTERP | Interpolated Ground | 74045.93 | 5.25 | 784.85 | 0 | 13.63 | 0 | OK | Ground clear controls. | 166 | 24.82 | 798.48
11565 | TIN-INTERP | Interpolated Ground | 74045.94 | 6.75 | 784.83 | 0 | 19.18 | 0 | OK | Ground clear controls. | 166 | 24.82 | 804.01
11566 | TIN-INTERP | Interpolated Ground | 74046.04 | 4.71 | 784.84 | 0 | 24.78 | 0 | OK | Ground clear controls. | 166 | 24.82 | 809.62
11567 | TIN-INTERP | Interpolated Ground | 74046.57 | -5.65 | 784.76 | 0 | 13.73 | 0 | OK | Ground clear controls. | 166 | 24.82 | 798.49
11568 | TIN-INTERP | Interpolated Ground | 74046.6 | -5.12 | 784.81 | 0 | 24.82 | 0 | OK | Ground clear controls. | 166 | 24.82 | 809.63
11569 | TIN-INTERP | Interpolated Ground | 74046.68 | -7.15 | 784.6 | 0 | 19.4 | 0 | OK | Ground clear controls. | 166 | 19.4 | 804
11570 | TIN-INTERP | Interpolated Ground | 74066.12 | -6.92 | 781.91 | 0 | 21.95 | 0 | OK | Ground clear controls. | 167 | 32.33 | 803.86
11571 | TIN-INTERP | Interpolated Ground | 74066.13 | -4.91 | 781.73 | 0 | 27.62 | 0 | OK | Ground clear controls. | 167 | 32.33 | 809.35
11572 | TIN-INTERP | Interpolated Ground | 74066.2 | 4.59 | 781.76 | 0 | 27.58 | 0 | OK | Ground clear controls. | 167 | 32.33 | 809.34
11573 | TIN-INTERP | Interpolated Ground | 74066.23 | 6.61 | 781.61 | 0 | 22.23 | 0 | OK | Ground clear controls. | 167 | 32.33 | 803.84
11574 | TIN-INTERP | Interpolated Ground | 74066.34 | -5.41 | 781.74 | 0 | 16.64 | 0 | OK | Ground clear controls. | 167 | 32.33 | 798.38
11575 | TIN-INTERP | Interpolated Ground | 74066.36 | 5.11 | 781.73 | 0 | 16.63 | 0 | OK | Ground clear controls. | 167 | 32.33 | 798.36
11576 | TIN-INTERP | Interpolated Ground | 74106.12 | -6.95 | 774.38 | 0 | 24.46 | 0 | OK | Ground clear controls. | 167 | 32.33 | 798.84
11577 | TIN-INTERP | Interpolated Ground | 74106.13 | -4.95 | 774.58 | 0 | 29.79 | 0 | OK | Ground clear controls. | 167 | 32.33 | 804.37
11578 | TIN-INTERP | Interpolated Ground | 74106.2 | 4.52 | 775.72 | 0 | 28.64 | 0 | OK | Ground clear controls. | 167 | 32.33 | 804.36
11579 | TIN-INTERP | Interpolated Ground | 74106.23 | 6.53 | 775.95 | 0 | 22.92 | 0 | OK | Ground clear controls. | 167 | 32.33 | 798.87
11580 | TIN-INTERP | Interpolated Ground | 74106.34 | -5.45 | 774.49 | 0 | 18.89 | 0 | OK | Ground clear controls. | 167 | 32.33 | 793.38
11581 | TIN-INTERP | Interpolated Ground | 74106.36 | 5.03 | 775.75 | 0 | 17.62 | 0 | OK | Ground clear controls. | 167 | 32.33 | 793.37
11582 | TIN-INTERP | Interpolated Ground | 74146.12 | -6.99 | 769.57 | 0 | 25.16 | 0 | OK | Ground clear controls. | 167 | 32.33 | 794.73
11583 | TIN-INTERP | Interpolated Ground | 74146.13 | -4.98 | 769.7 | 0 | 30.58 | 0 | OK | Ground clear controls. | 167 | 32.33 | 800.28
11584 | TIN-INTERP | Interpolated Ground | 74146.2 | 4.44 | 771.5 | 0 | 28.76 | 0 | OK | Ground clear controls. | 167 | 32.33 | 800.26
11585 | TIN-INTERP | Interpolated Ground | 74146.23 | 6.45 | 771.93 | 0 | 22.85 | 0 | OK | Ground clear controls. | 167 | 32.33 | 794.78
11586 | TIN-INTERP | Interpolated Ground | 74146.34 | -5.48 | 769.68 | 0 | 19.61 | 0 | OK | Ground clear controls. | 167 | 32.33 | 789.29
11587 | TIN-INTERP | Interpolated Ground | 74146.36 | 4.95 | 771.62 | 0 | 17.65 | 0 | OK | Ground clear controls. | 167 | 32.33 | 789.27
11588 | TIN-INTERP | Interpolated Ground | 74186.12 | -7.02 | 772.67 | 0 | 18.84 | 0 | OK | Ground clear controls. | 167 | 32.33 | 791.51
11589 | TIN-INTERP | Interpolated Ground | 74186.13 | -5.02 | 772.43 | 0 | 24.64 | 0 | OK | Ground clear controls. | 167 | 32.33 | 797.07
11590 | TIN-INTERP | Interpolated Ground | 74186.2 | 4.36 | 772.55 | 0 | 24.51 | 0 | OK | Ground clear controls. | 167 | 32.33 | 797.06
11591 | TIN-INTERP | Interpolated Ground | 74186.23 | 6.37 | 772.33 | 0 | 19.25 | 0 | OK | Ground clear controls. | 167 | 32.33 | 791.58
11592 | TIN-INTERP | Interpolated Ground | 74186.34 | -5.52 | 772.49 | 0 | 13.59 | 0 | OK | Ground clear controls. | 167 | 32.33 | 786.08
11593 | TIN-INTERP | Interpolated Ground | 74186.36 | 4.87 | 772.5 | 0 | 13.56 | 0 | OK | Ground clear controls. | 167 | 32.33 | 786.06
11594 | TIN-INTERP | Interpolated Ground | 74226.12 | -7.06 | 772.7 | 0 | 16.5 | 0 | OK | Ground clear controls. | 167 | 32.33 | 789.2
11595 | TIN-INTERP | Interpolated Ground | 74226.13 | -5.05 | 772.59 | 0 | 22.17 | 0 | OK | Ground clear controls. | 167 | 32.33 | 794.76
11596 | TIN-INTERP | Interpolated Ground | 74226.2 | 4.29 | 772.27 | 0 | 22.47 | 0 | OK | Ground clear controls. | 167 | 32.33 | 794.74
11597 | TIN-INTERP | Interpolated Ground | 74226.23 | 6.3 | 772.08 | 0 | 17.17 | 0 | OK | Ground clear controls. | 167 | 32.33 | 789.25
11598 | TIN-INTERP | Interpolated Ground | 74226.34 | -5.56 | 772.62 | 0 | 11.14 | 0 | OK | Ground clear controls. | 167 | 32.33 | 783.76
11599 | TIN-INTERP | Interpolated Ground | 74226.36 | 4.79 | 772.2 | 0 | 11.54 | 0 | OK | Ground clear controls. | 167 | 32.33 | 783.74
11600 | TIN-INTERP | Interpolated Ground | 74266.12 | -7.09 | 767.81 | 0 | 19.96 | 0 | OK | Ground clear controls. | 167 | 32.33 | 787.77
11601 | TIN-INTERP | Interpolated Ground | 74266.13 | -5.09 | 767.42 | 0 | 25.9 | 0 | OK | Ground clear controls. | 167 | 32.33 | 793.32
11602 | TIN-INTERP | Interpolated Ground | 74266.2 | 4.21 | 766.16 | 0 | 27.14 | 0 | OK | Ground clear controls. | 167 | 32.33 | 793.3
11603 | TIN-INTERP | Interpolated Ground | 74266.23 | 6.22 | 765.97 | 0 | 21.85 | 0 | OK | Ground clear controls. | 167 | 32.33 | 787.82
11604 | TIN-INTERP | Interpolated Ground | 74266.34 | -5.59 | 767.52 | 0 | 14.81 | 0 | OK | Ground clear controls. | 167 | 32.33 | 782.33
11605 | TIN-INTERP | Interpolated Ground | 74266.36 | 4.72 | 766.13 | 0 | 16.18 | 0 | OK | Ground clear controls. | 167 | 32.33 | 782.31
11606 | TIN-INTERP | Interpolated Ground | 74306.12 | -7.13 | 766.07 | 0 | 21.16 | 0 | OK | Ground clear controls. | 167 | 32.33 | 787.23
11607 | TIN-INTERP | Interpolated Ground | 74306.13 | -5.13 | 765.03 | 0 | 27.74 | 0 | OK | Ground clear controls. | 167 | 32.33 | 792.77
11608 | TIN-INTERP | Interpolated Ground | 74306.2 | 4.14 | 761.88 | 0 | 30.87 | 0 | OK | Ground clear controls. | 167 | 32.33 | 792.75
11609 | TIN-INTERP | Interpolated Ground | 74306.23 | 6.14 | 761.3 | 0 | 25.97 | 0 | OK | Ground clear controls. | 167 | 32.33 | 787.27
11610 | TIN-INTERP | Interpolated Ground | 74306.34 | -5.63 | 765.01 | 0 | 16.76 | 0 | OK | Ground clear controls. | 167 | 32.33 | 781.77
11611 | TIN-INTERP | Interpolated Ground | 74306.36 | 4.64 | 761.67 | 0 | 20.09 | 0 | OK | Ground clear controls. | 167 | 32.33 | 781.76
11612 | TIN-INTERP | Interpolated Ground | 74346.12 | -7.16 | 760.95 | 0 | 26.64 | 0 | OK | Ground clear controls. | 167 | 32.33 | 787.59
11613 | TIN-INTERP | Interpolated Ground | 74346.13 | -5.16 | 760.77 | 0 | 32.33 | 0 | OK | Ground clear controls. | 167 | 32.33 | 793.1
11614 | TIN-INTERP | Interpolated Ground | 74346.2 | 4.06 | 760.94 | 0 | 32.15 | 0 | OK | Ground clear controls. | 167 | 32.15 | 793.09
11615 | TIN-INTERP | Interpolated Ground | 74346.23 | 6.06 | 760.69 | 0 | 26.9 | 0 | OK | Ground clear controls. | 167 | 26.9 | 787.59
11616 | TIN-INTERP | Interpolated Ground | 74346.34 | -5.66 | 760.79 | 0 | 21.32 | 0 | OK | Ground clear controls. | 167 | 21.32 | 782.11
11617 | TIN-INTERP | Interpolated Ground | 74346.36 | 4.56 | 760.95 | 0 | 21.14 | 0 | OK | Ground clear controls. | 167 | 21.14 | 782.09
11618 | TIN-INTERP | Interpolated Ground | 74360 | 6.04 | 758.65 | 0 | 29.27 | 0 | OK | Ground clear controls. | 168 | 53.1 | 787.92
11619 | TIN-INTERP | Interpolated Ground | 74360.01 | 4.04 | 759.02 | 0 | 34.4 | 0 | OK | Ground clear controls. | 168 | 53.1 | 793.42
11620 | TIN-INTERP | Interpolated Ground | 74360.06 | 4.54 | 758.93 | 0 | 23.49 | 0 | OK | Ground clear controls. | 168 | 53.1 | 782.42
11621 | TIN-INTERP | Interpolated Ground | 74360.19 | -5.17 | 759.69 | 0 | 33.73 | 0 | OK | Ground clear controls. | 168 | 53.1 | 793.42
11622 | TIN-INTERP | Interpolated Ground | 74360.25 | -7.16 | 759.83 | 0 | 28.09 | 0 | OK | Ground clear controls. | 168 | 53.1 | 787.92
11623 | TIN-INTERP | Interpolated Ground | 74360.31 | -5.66 | 759.76 | 0 | 22.67 | 0 | OK | Ground clear controls. | 168 | 53.1 | 782.43
11624 | TIN-INTERP | Interpolated Ground | 74400 | 6.11 | 749.58 | 0 | 31.43 | 0 | OK | Ground clear controls. | 168 | 53.1 | 781.01
11625 | TIN-INTERP | Interpolated Ground | 74400.01 | 4.11 | 749.36 | 0 | 37.13 | 0 | OK | Ground clear controls. | 168 | 53.1 | 786.49
11626 | TIN-INTERP | Interpolated Ground | 74400.06 | 4.61 | 749.42 | 0 | 26.08 | 0 | OK | Ground clear controls. | 168 | 53.1 | 775.5
11627 | TIN-INTERP | Interpolated Ground | 74400.19 | -5.1 | 749.17 | 0 | 37.34 | 0 | OK | Ground clear controls. | 168 | 53.1 | 786.51
11628 | TIN-INTERP | Interpolated Ground | 74400.25 | -7.09 | 749.17 | 0 | 31.82 | 0 | OK | Ground clear controls. | 168 | 53.1 | 780.99
11629 | TIN-INTERP | Interpolated Ground | 74400.31 | -5.59 | 749.16 | 0 | 26.38 | 0 | OK | Ground clear controls. | 168 | 53.1 | 775.54
11630 | TIN-INTERP | Interpolated Ground | 74440 | 6.18 | 741.6 | 0 | 33.39 | 0 | OK | Ground clear controls. | 168 | 53.1 | 774.99
11631 | TIN-INTERP | Interpolated Ground | 74440.01 | 4.18 | 741.39 | 0 | 39.07 | 0 | OK | Ground clear controls. | 168 | 53.1 | 780.46
11632 | TIN-INTERP | Interpolated Ground | 74440.06 | 4.68 | 741.46 | 0 | 28.02 | 0 | OK | Ground clear controls. | 168 | 53.1 | 769.48
11633 | TIN-INTERP | Interpolated Ground | 74440.19 | -5.03 | 741.67 | 0 | 38.81 | 0 | OK | Ground clear controls. | 168 | 53.1 | 780.48
11634 | TIN-INTERP | Interpolated Ground | 74440.25 | -7.03 | 741.76 | 0 | 33.19 | 0 | OK | Ground clear controls. | 168 | 53.1 | 774.95
11635 | TIN-INTERP | Interpolated Ground | 74440.31 | -5.53 | 741.68 | 0 | 27.84 | 0 | OK | Ground clear controls. | 168 | 53.1 | 769.52
11636 | TIN-INTERP | Interpolated Ground | 74480 | 6.24 | 736.83 | 0 | 33.01 | 0 | OK | Ground clear controls. | 168 | 53.1 | 769.84
11637 | TIN-INTERP | Interpolated Ground | 74480.01 | 4.24 | 736.05 | 0 | 39.26 | 0 | OK | Ground clear controls. | 168 | 53.1 | 775.31
11638 | TIN-INTERP | Interpolated Ground | 74480.06 | 4.75 | 736.2 | 0 | 28.13 | 0 | OK | Ground clear controls. | 168 | 53.1 | 764.33
11639 | TIN-INTERP | Interpolated Ground | 74480.19 | -4.96 | 733.02 | 0 | 42.31 | 0 | OK | Ground clear controls. | 168 | 53.1 | 775.33
11640 | TIN-INTERP | Interpolated Ground | 74480.25 | -6.96 | 732.8 | 0 | 36.99 | 0 | OK | Ground clear controls. | 168 | 53.1 | 769.79
11641 | TIN-INTERP | Interpolated Ground | 74480.31 | -5.46 | 733.02 | 0 | 31.35 | 0 | OK | Ground clear controls. | 168 | 53.1 | 764.37
11642 | TIN-INTERP | Interpolated Ground | 74520 | 6.31 | 717.81 | 0 | 47.75 | 0 | OK | Ground clear controls. | 168 | 53.1 | 765.56
11643 | TIN-INTERP | Interpolated Ground | 74520.01 | 4.31 | 717.94 | 0 | 53.1 | 0 | OK | Ground clear controls. | 168 | 53.1 | 771.04
11644 | TIN-INTERP | Interpolated Ground | 74520.06 | 4.81 | 717.9 | 0 | 42.15 | 0 | OK | Ground clear controls. | 168 | 49.57 | 760.05
11645 | TIN-INTERP | Interpolated Ground | 74520.19 | -4.89 | 721.49 | 0 | 49.57 | 0 | OK | Ground clear controls. | 168 | 49.57 | 771.06
11646 | TIN-INTERP | Interpolated Ground | 74520.25 | -6.89 | 722.79 | 0 | 42.72 | 0 | OK | Ground clear controls. | 168 | 43.24 | 765.51
11647 | TIN-INTERP | Interpolated Ground | 74520.31 | -5.39 | 721.84 | 0 | 38.25 | 0 | OK | Ground clear controls. | 168 | 43.24 | 760.09
11648 | TIN-INTERP | Interpolated Ground | 74560 | 6.38 | 723.6 | 0 | 38.55 | 0 | OK | Ground clear controls. | 168 | 43.24 | 762.15
11649 | TIN-INTERP | Interpolated Ground | 74560.01 | 4.38 | 724.4 | 0 | 43.24 | 0 | OK | Ground clear controls. | 168 | 43.24 | 767.64
11650 | TIN-INTERP | Interpolated Ground | 74560.06 | 4.88 | 724.2 | 0 | 32.45 | 0 | OK | Ground clear controls. | 168 | 39.34 | 756.65
11651 | TIN-INTERP | Interpolated Ground | 74560.19 | -4.82 | 728.31 | 0 | 39.34 | 0 | OK | Ground clear controls. | 168 | 39.34 | 767.65
11652 | TIN-INTERP | Interpolated Ground | 74560.25 | -6.82 | 729.39 | 0 | 32.73 | 0 | OK | Ground clear controls. | 168 | 35.04 | 762.12
11653 | TIN-INTERP | Interpolated Ground | 74560.31 | -5.32 | 728.56 | 0 | 28.12 | 0 | OK | Ground clear controls. | 168 | 35.04 | 756.68
11654 | TIN-INTERP | Interpolated Ground | 74600 | 6.45 | 729.32 | 0 | 30.31 | 0 | OK | Ground clear controls. | 168 | 35.04 | 759.63
11655 | TIN-INTERP | Interpolated Ground | 74600.01 | 4.45 | 730.08 | 0 | 35.04 | 0 | OK | Ground clear controls. | 168 | 35.04 | 765.12
11656 | TIN-INTERP | Interpolated Ground | 74600.06 | 4.95 | 730.02 | 0 | 24.1 | 0 | OK | Ground clear controls. | 168 | 33.36 | 754.12
11657 | TIN-INTERP | Interpolated Ground | 74600.19 | -4.75 | 731.76 | 0 | 33.36 | 0 | OK | Ground clear controls. | 168 | 33.36 | 765.12
11658 | TIN-INTERP | Interpolated Ground | 74600.25 | -6.75 | 732.15 | 0 | 27.45 | 0 | OK | Ground clear controls. | 168 | 31.66 | 759.6
11659 | TIN-INTERP | Interpolated Ground | 74600.31 | -5.25 | 731.88 | 0 | 22.26 | 0 | OK | Ground clear controls. | 168 | 31.66 | 754.14
11660 | TIN-INTERP | Interpolated Ground | 74640 | 6.52 | 731.46 | 0 | 26.5 | 0 | OK | Ground clear controls. | 168 | 31.66 | 757.96
11661 | TIN-INTERP | Interpolated Ground | 74640.01 | 4.52 | 731.81 | 0 | 31.66 | 0 | OK | Ground clear controls. | 168 | 31.66 | 763.47
11662 | TIN-INTERP | Interpolated Ground | 74640.06 | 5.02 | 731.73 | 0 | 20.73 | 0 | OK | Ground clear controls. | 168 | 29.89 | 752.46
11663 | TIN-INTERP | Interpolated Ground | 74640.19 | -4.69 | 733.58 | 0 | 29.89 | 0 | OK | Ground clear controls. | 168 | 29.89 | 763.47
11664 | TIN-INTERP | Interpolated Ground | 74640.25 | -6.69 | 733.75 | 0 | 24.21 | 0 | OK | Ground clear controls. | 168 | 24.21 | 757.96
11665 | TIN-INTERP | Interpolated Ground | 74640.31 | -5.19 | 733.63 | 0 | 18.83 | 0 | OK | Ground clear controls. | 168 | 18.83 | 752.46
11666 | TIN-INTERP | Interpolated Ground | 74647.45 | 5.03 | 731.94 | 0 | 20.31 | 0 | OK | Ground clear controls. | 169 | 32.19 | 752.25
11667 | TIN-INTERP | Interpolated Ground | 74647.49 | 6.53 | 731.85 | 0 | 25.9 | 0 | OK | Ground clear controls. | 169 | 32.19 | 757.75
11668 | TIN-INTERP | Interpolated Ground | 74647.5 | -5.17 | 733.9 | 0 | 18.35 | 0 | OK | Ground clear controls. | 169 | 32.19 | 752.25
11669 | TIN-INTERP | Interpolated Ground | 74647.51 | -4.67 | 733.95 | 0 | 29.3 | 0 | OK | Ground clear controls. | 169 | 32.19 | 763.25
11670 | TIN-INTERP | Interpolated Ground | 74647.52 | -6.67 | 733.81 | 0 | 23.94 | 0 | OK | Ground clear controls. | 169 | 32.19 | 757.75
11671 | TIN-INTERP | Interpolated Ground | 74647.57 | 4.53 | 731.99 | 0 | 31.27 | 0 | OK | Ground clear controls. | 169 | 32.19 | 763.26
11672 | TIN-INTERP | Interpolated Ground | 74687.45 | 5.04 | 723.95 | 0 | 21.01 | 0 | OK | Ground clear controls. | 169 | 32.19 | 744.96
11673 | TIN-INTERP | Interpolated Ground | 74687.49 | 6.54 | 723.77 | 0 | 26.7 | 0 | OK | Ground clear controls. | 169 | 32.19 | 750.47
11674 | TIN-INTERP | Interpolated Ground | 74687.5 | -5.16 | 726.55 | 0 | 18.43 | 0 | OK | Ground clear controls. | 169 | 32.19 | 744.98
11675 | TIN-INTERP | Interpolated Ground | 74687.51 | -4.66 | 726.44 | 0 | 29.53 | 0 | OK | Ground clear controls. | 169 | 32.19 | 755.97
11676 | TIN-INTERP | Interpolated Ground | 74687.52 | -6.66 | 727.08 | 0 | 23.38 | 0 | OK | Ground clear controls. | 169 | 32.19 | 750.46
11677 | TIN-INTERP | Interpolated Ground | 74687.57 | 4.54 | 723.98 | 0 | 32 | 0 | OK | Ground clear controls. | 169 | 32.19 | 755.98
11678 | TIN-INTERP | Interpolated Ground | 74727.45 | 5.06 | 722.65 | 0 | 15.9 | 0 | OK | Ground clear controls. | 169 | 32.19 | 738.55
11679 | TIN-INTERP | Interpolated Ground | 74727.49 | 6.56 | 722.21 | 0 | 21.85 | 0 | OK | Ground clear controls. | 169 | 32.19 | 744.06
11680 | TIN-INTERP | Interpolated Ground | 74727.5 | -5.14 | 723.95 | 0 | 14.63 | 0 | OK | Ground clear controls. | 169 | 32.19 | 738.58
11681 | TIN-INTERP | Interpolated Ground | 74727.51 | -4.64 | 724.03 | 0 | 25.53 | 0 | OK | Ground clear controls. | 169 | 32.19 | 749.56
11682 | TIN-INTERP | Interpolated Ground | 74727.52 | -6.64 | 723.9 | 0 | 20.15 | 0 | OK | Ground clear controls. | 169 | 32.19 | 744.05
11683 | TIN-INTERP | Interpolated Ground | 74727.57 | 4.56 | 722.77 | 0 | 26.79 | 0 | OK | Ground clear controls. | 169 | 32.19 | 749.56
11684 | TIN-INTERP | Interpolated Ground | 74767.45 | 5.08 | 714.71 | 0 | 18.31 | 0 | OK | Ground clear controls. | 169 | 32.19 | 733.02
11685 | TIN-INTERP | Interpolated Ground | 74767.49 | 6.58 | 714.93 | 0 | 23.59 | 0 | OK | Ground clear controls. | 169 | 32.19 | 738.52
11686 | TIN-INTERP | Interpolated Ground | 74767.5 | -5.13 | 714.82 | 0 | 18.21 | 0 | OK | Ground clear controls. | 169 | 32.19 | 733.03
11687 | TIN-INTERP | Interpolated Ground | 74767.51 | -4.63 | 714.88 | 0 | 29.14 | 0 | OK | Ground clear controls. | 169 | 32.19 | 744.02
11688 | TIN-INTERP | Interpolated Ground | 74767.52 | -6.63 | 714.61 | 0 | 23.9 | 0 | OK | Ground clear controls. | 169 | 32.19 | 738.51
11689 | TIN-INTERP | Interpolated Ground | 74767.57 | 4.58 | 714.74 | 0 | 29.29 | 0 | OK | Ground clear controls. | 169 | 32.19 | 744.03
11690 | TIN-INTERP | Interpolated Ground | 74807.45 | 5.09 | 707.18 | 0 | 21.18 | 0 | OK | Ground clear controls. | 169 | 32.19 | 728.36
11691 | TIN-INTERP | Interpolated Ground | 74807.49 | 6.59 | 707.24 | 0 | 26.61 | 0 | OK | Ground clear controls. | 169 | 32.19 | 733.85
11692 | TIN-INTERP | Interpolated Ground | 74807.5 | -5.12 | 707.4 | 0 | 20.97 | 0 | OK | Ground clear controls. | 169 | 32.19 | 728.37
11693 | TIN-INTERP | Interpolated Ground | 74807.51 | -4.62 | 707.41 | 0 | 31.94 | 0 | OK | Ground clear controls. | 169 | 32.19 | 739.35
11694 | TIN-INTERP | Interpolated Ground | 74807.52 | -6.62 | 707.34 | 0 | 26.51 | 0 | OK | Ground clear controls. | 169 | 32.19 | 733.85
11695 | TIN-INTERP | Interpolated Ground | 74807.57 | 4.59 | 707.18 | 0 | 32.19 | 0 | OK | Ground clear controls. | 169 | 32.19 | 739.37
11696 | TIN-INTERP | Interpolated Ground | 74839.32 | 6.6 | 703.05 | 0 | 27.71 | 0 | OK | Ground clear controls. | 170 | 72.38 | 730.76
11697 | TIN-INTERP | Interpolated Ground | 74839.33 | -5.1 | 703.08 | 0 | 22.18 | 0 | OK | Ground clear controls. | 170 | 72.38 | 725.26
11698 | TIN-INTERP | Interpolated Ground | 74839.36 | -4.61 | 703.04 | 0 | 33.22 | 0 | OK | Ground clear controls. | 170 | 72.38 | 736.26
11699 | TIN-INTERP | Interpolated Ground | 74839.38 | -6.6 | 703 | 0 | 27.76 | 0 | OK | Ground clear controls. | 170 | 72.38 | 730.76
11700 | TIN-INTERP | Interpolated Ground | 74839.44 | 5.1 | 703.21 | 0 | 22.05 | 0 | OK | Ground clear controls. | 170 | 72.38 | 725.26
11701 | TIN-INTERP | Interpolated Ground | 74839.45 | 4.61 | 703.26 | 0 | 33.01 | 0 | OK | Ground clear controls. | 170 | 72.38 | 736.27
11702 | TIN-INTERP | Interpolated Ground | 74879.32 | 6.62 | 694.36 | 0 | 22.39 | 0 | OK | Ground clear controls. | 170 | 72.38 | 716.75
11703 | TIN-INTERP | Interpolated Ground | 74879.33 | -5.12 | 693.01 | 0 | 18.28 | 0 | OK | Ground clear controls. | 170 | 72.38 | 711.29
11704 | TIN-INTERP | Interpolated Ground | 74879.36 | -4.63 | 692.92 | 0 | 29.38 | 0 | OK | Ground clear controls. | 170 | 72.38 | 722.3
11705 | TIN-INTERP | Interpolated Ground | 74879.38 | -6.62 | 692.95 | 0 | 23.8 | 0 | OK | Ground clear controls. | 170 | 72.38 | 716.75
11706 | TIN-INTERP | Interpolated Ground | 74879.44 | 5.12 | 694.23 | 0 | 17.08 | 0 | OK | Ground clear controls. | 170 | 72.38 | 711.31
11707 | TIN-INTERP | Interpolated Ground | 74879.45 | 4.63 | 694.19 | 0 | 28.17 | 0 | OK | Ground clear controls. | 170 | 72.38 | 722.36
11708 | TIN-INTERP | Interpolated Ground | 74919.32 | 6.64 | 681.83 | 0 | 21.81 | 0 | OK | Ground clear controls. | 170 | 72.38 | 703.64
11709 | TIN-INTERP | Interpolated Ground | 74919.33 | -5.14 | 677.07 | 0 | 21.16 | 0 | OK | Ground clear controls. | 170 | 72.38 | 698.23
11710 | TIN-INTERP | Interpolated Ground | 74919.36 | -4.65 | 677.25 | 0 | 32 | 0 | OK | Ground clear controls. | 170 | 72.38 | 709.25
11711 | TIN-INTERP | Interpolated Ground | 74919.38 | -6.64 | 676.45 | 0 | 27.19 | 0 | OK | Ground clear controls. | 170 | 72.38 | 703.64
11712 | TIN-INTERP | Interpolated Ground | 74919.44 | 5.14 | 681.35 | 0 | 16.9 | 0 | OK | Ground clear controls. | 170 | 72.38 | 698.25
11713 | TIN-INTERP | Interpolated Ground | 74919.45 | 4.66 | 681.12 | 0 | 28.24 | 0 | OK | Ground clear controls. | 170 | 72.38 | 709.36
11714 | TIN-INTERP | Interpolated Ground | 74959.32 | 6.67 | 660.6 | 0 | 30.84 | 0 | OK | Ground clear controls. | 170 | 72.38 | 691.44
11715 | TIN-INTERP | Interpolated Ground | 74959.33 | -5.15 | 657.37 | 0 | 28.69 | 0 | OK | Ground clear controls. | 170 | 72.38 | 686.06
11716 | TIN-INTERP | Interpolated Ground | 74959.36 | -4.67 | 657.26 | 0 | 39.83 | 0 | OK | Ground clear controls. | 170 | 72.38 | 697.09
11717 | TIN-INTERP | Interpolated Ground | 74959.38 | -6.65 | 658.07 | 0 | 33.37 | 0 | OK | Ground clear controls. | 170 | 72.38 | 691.44
11718 | TIN-INTERP | Interpolated Ground | 74959.44 | 5.17 | 659.96 | 0 | 26.13 | 0 | OK | Ground clear controls. | 170 | 72.38 | 686.09
11719 | TIN-INTERP | Interpolated Ground | 74959.45 | 4.69 | 659.82 | 0 | 37.42 | 0 | OK | Ground clear controls. | 170 | 72.38 | 697.24
11720 | TIN-INTERP | Interpolated Ground | 74999.32 | 6.69 | 648.29 | 0 | 31.85 | 0 | OK | Ground clear controls. | 170 | 72.38 | 680.14
11721 | TIN-INTERP | Interpolated Ground | 74999.33 | -5.17 | 640.28 | 0 | 34.5 | 0 | OK | Ground clear controls. | 170 | 72.38 | 674.78
11722 | TIN-INTERP | Interpolated Ground | 74999.36 | -4.7 | 640.64 | 0 | 45.18 | 0 | OK | Ground clear controls. | 170 | 72.38 | 685.82
11723 | TIN-INTERP | Interpolated Ground | 74999.38 | -6.67 | 639.18 | 0 | 40.96 | 0 | OK | Ground clear controls. | 170 | 72.38 | 680.14
11724 | TIN-INTERP | Interpolated Ground | 74999.44 | 5.19 | 647.2 | 0 | 27.62 | 0 | OK | Ground clear controls. | 170 | 72.38 | 674.82
11725 | TIN-INTERP | Interpolated Ground | 74999.45 | 4.71 | 646.82 | 0 | 39.19 | 0 | OK | Ground clear controls. | 170 | 72.38 | 686.01
11726 | TIN-INTERP | Interpolated Ground | 75039.32 | 6.71 | 640.44 | 0 | 29.28 | 0 | OK | Ground clear controls. | 170 | 72.38 | 669.72
11727 | TIN-INTERP | Interpolated Ground | 75039.33 | -5.19 | 635.27 | 0 | 29.12 | 0 | OK | Ground clear controls. | 170 | 72.38 | 664.39
11728 | TIN-INTERP | Interpolated Ground | 75039.36 | -4.72 | 635.37 | 0 | 40.07 | 0 | OK | Ground clear controls. | 170 | 72.38 | 675.44
11729 | TIN-INTERP | Interpolated Ground | 75039.38 | -6.69 | 634.67 | 0 | 35.05 | 0 | OK | Ground clear controls. | 170 | 72.38 | 669.72
11730 | TIN-INTERP | Interpolated Ground | 75039.44 | 5.21 | 639.79 | 0 | 24.64 | 0 | OK | Ground clear controls. | 170 | 72.38 | 664.43
11731 | TIN-INTERP | Interpolated Ground | 75039.45 | 4.74 | 639.58 | 0 | 36.08 | 0 | OK | Ground clear controls. | 170 | 72.38 | 675.66
11732 | TIN-INTERP | Interpolated Ground | 75079.32 | 6.73 | 623.73 | 0 | 36.46 | 0 | OK | Ground clear controls. | 170 | 72.38 | 660.19
11733 | TIN-INTERP | Interpolated Ground | 75079.33 | -5.2 | 617.61 | 0 | 37.26 | 0 | OK | Ground clear controls. | 170 | 72.38 | 654.87
11734 | TIN-INTERP | Interpolated Ground | 75079.36 | -4.74 | 617.9 | 0 | 48.04 | 0 | OK | Ground clear controls. | 170 | 72.38 | 665.94
11735 | TIN-INTERP | Interpolated Ground | 75079.38 | -6.7 | 616.56 | 0 | 43.63 | 0 | OK | Ground clear controls. | 170 | 72.38 | 660.19
11736 | TIN-INTERP | Interpolated Ground | 75079.44 | 5.23 | 622.85 | 0 | 32.07 | 0 | OK | Ground clear controls. | 170 | 72.38 | 654.92
11737 | TIN-INTERP | Interpolated Ground | 75079.45 | 4.76 | 622.64 | 0 | 43.54 | 0 | OK | Ground clear controls. | 170 | 72.38 | 666.18
11738 | TIN-INTERP | Interpolated Ground | 75119.32 | 6.75 | 617.92 | 0 | 33.62 | 0 | OK | Ground clear controls. | 170 | 72.38 | 651.54
11739 | TIN-INTERP | Interpolated Ground | 75119.33 | -5.22 | 612.33 | 0 | 33.91 | 0 | OK | Ground clear controls. | 170 | 72.38 | 646.24
11740 | TIN-INTERP | Interpolated Ground | 75119.36 | -4.76 | 612.58 | 0 | 44.74 | 0 | OK | Ground clear controls. | 170 | 72.38 | 657.32
11741 | TIN-INTERP | Interpolated Ground | 75119.38 | -6.72 | 611.4 | 0 | 40.15 | 0 | OK | Ground clear controls. | 170 | 72.38 | 651.55
11742 | TIN-INTERP | Interpolated Ground | 75119.44 | 5.25 | 617.53 | 0 | 28.75 | 0 | OK | Ground clear controls. | 170 | 72.38 | 646.28
11743 | TIN-INTERP | Interpolated Ground | 75119.45 | 4.79 | 617.34 | 0 | 40.23 | 0 | OK | Ground clear controls. | 170 | 72.38 | 657.57
11744 | TIN-INTERP | Interpolated Ground | 75159.32 | 6.77 | 603.81 | 0 | 39.97 | 0 | OK | Ground clear controls. | 170 | 72.38 | 643.78
11745 | TIN-INTERP | Interpolated Ground | 75159.33 | -5.24 | 600.25 | 0 | 38.21 | 0 | OK | Ground clear controls. | 170 | 72.38 | 638.46
11746 | TIN-INTERP | Interpolated Ground | 75159.36 | -4.79 | 600.36 | 0 | 49.21 | 0 | OK | Ground clear controls. | 170 | 72.38 | 649.57
11747 | TIN-INTERP | Interpolated Ground | 75159.38 | -6.74 | 599.82 | 0 | 43.95 | 0 | OK | Ground clear controls. | 170 | 72.38 | 643.77
11748 | TIN-INTERP | Interpolated Ground | 75159.44 | 5.27 | 603.22 | 0 | 35.29 | 0 | OK | Ground clear controls. | 170 | 72.38 | 638.51
11749 | TIN-INTERP | Interpolated Ground | 75159.45 | 4.82 | 603.03 | 0 | 46.78 | 0 | OK | Ground clear controls. | 170 | 72.38 | 649.81
11750 | TIN-INTERP | Interpolated Ground | 75199.32 | 6.79 | 593.77 | 0 | 43.11 | 0 | OK | Ground clear controls. | 170 | 72.38 | 636.88
11751 | TIN-INTERP | Interpolated Ground | 75199.33 | -5.25 | 589.27 | 0 | 42.29 | 0 | OK | Ground clear controls. | 170 | 72.38 | 631.56
11752 | TIN-INTERP | Interpolated Ground | 75199.36 | -4.81 | 589.39 | 0 | 53.3 | 0 | OK | Ground clear controls. | 170 | 72.38 | 642.69
11753 | TIN-INTERP | Interpolated Ground | 75199.38 | -6.75 | 588.9 | 0 | 47.99 | 0 | OK | Ground clear controls. | 170 | 72.38 | 636.89
11754 | TIN-INTERP | Interpolated Ground | 75199.44 | 5.29 | 593.19 | 0 | 38.42 | 0 | OK | Ground clear controls. | 170 | 72.38 | 631.61
11755 | TIN-INTERP | Interpolated Ground | 75199.45 | 4.84 | 592.98 | 0 | 49.94 | 0 | OK | Ground clear controls. | 170 | 72.38 | 642.92
11756 | TIN-INTERP | Interpolated Ground | 75239.32 | 6.81 | 582.32 | 0 | 48.54 | 0 | OK | Ground clear controls. | 170 | 72.38 | 630.86
11757 | TIN-INTERP | Interpolated Ground | 75239.33 | -5.27 | 578.25 | 0 | 47.28 | 0 | OK | Ground clear controls. | 170 | 72.38 | 625.53
11758 | TIN-INTERP | Interpolated Ground | 75239.36 | -4.83 | 578.4 | 0 | 58.28 | 0 | OK | Ground clear controls. | 170 | 72.38 | 636.68
11759 | TIN-INTERP | Interpolated Ground | 75239.38 | -6.77 | 578.18 | 0 | 52.68 | 0 | OK | Ground clear controls. | 170 | 72.38 | 630.86
11760 | TIN-INTERP | Interpolated Ground | 75239.44 | 5.31 | 581.9 | 0 | 43.67 | 0 | OK | Ground clear controls. | 170 | 72.38 | 625.57
11761 | TIN-INTERP | Interpolated Ground | 75239.45 | 4.87 | 581.91 | 0 | 54.99 | 0 | OK | Ground clear controls. | 170 | 72.38 | 636.9
11762 | TIN-INTERP | Interpolated Ground | 75279.32 | 6.83 | 570.87 | 0 | 54.84 | 0 | OK | Ground clear controls. | 170 | 72.38 | 625.71
11763 | TIN-INTERP | Interpolated Ground | 75279.33 | -5.29 | 568.41 | 0 | 51.96 | 0 | OK | Ground clear controls. | 170 | 72.38 | 620.37
11764 | TIN-INTERP | Interpolated Ground | 75279.36 | -4.86 | 568.51 | 0 | 63.03 | 0 | OK | Ground clear controls. | 170 | 72.38 | 631.54
11765 | TIN-INTERP | Interpolated Ground | 75279.38 | -6.79 | 567.95 | 0 | 57.76 | 0 | OK | Ground clear controls. | 170 | 72.38 | 625.71
11766 | TIN-INTERP | Interpolated Ground | 75279.44 | 5.33 | 570.58 | 0 | 49.82 | 0 | OK | Ground clear controls. | 170 | 72.38 | 620.4
11767 | TIN-INTERP | Interpolated Ground | 75279.45 | 4.9 | 570.48 | 0 | 61.25 | 0 | OK | Ground clear controls. | 170 | 72.38 | 631.73
11768 | TIN-INTERP | Interpolated Ground | 75319.32 | 6.85 | 557.52 | 0 | 63.9 | 0 | OK | Ground clear controls. | 170 | 72.38 | 621.42
11769 | TIN-INTERP | Interpolated Ground | 75319.33 | -5.3 | 554.7 | 0 | 61.35 | 0 | OK | Ground clear controls. | 170 | 72.38 | 616.05
11770 | TIN-INTERP | Interpolated Ground | 75319.36 | -4.88 | 554.88 | 0 | 72.38 | 0 | OK | Ground clear controls. | 170 | 72.38 | 627.26
11771 | TIN-INTERP | Interpolated Ground | 75319.38 | -6.8 | 554.07 | 0 | 67.36 | 0 | OK | Ground clear controls. | 170 | 71.82 | 621.43
11772 | TIN-INTERP | Interpolated Ground | 75319.44 | 5.35 | 557.34 | 0 | 58.74 | 0 | OK | Ground clear controls. | 170 | 71.82 | 616.08
11773 | TIN-INTERP | Interpolated Ground | 75319.45 | 4.92 | 557.29 | 0 | 70.12 | 0 | OK | Ground clear controls. | 170 | 71.82 | 627.41
11774 | TIN-INTERP | Interpolated Ground | 75359.32 | 6.87 | 557.28 | 0 | 60.72 | 0 | OK | Ground clear controls. | 170 | 71.82 | 618
11775 | TIN-INTERP | Interpolated Ground | 75359.33 | -5.32 | 551.82 | 0 | 60.77 | 0 | OK | Ground clear controls. | 170 | 71.82 | 612.59
11776 | TIN-INTERP | Interpolated Ground | 75359.36 | -4.9 | 552 | 0 | 71.82 | 0 | OK | Ground clear controls. | 170 | 71.82 | 623.82
11777 | TIN-INTERP | Interpolated Ground | 75359.38 | -6.82 | 551.47 | 0 | 66.53 | 0 | OK | Ground clear controls. | 170 | 67.47 | 618
11778 | TIN-INTERP | Interpolated Ground | 75359.44 | 5.37 | 556.76 | 0 | 55.86 | 0 | OK | Ground clear controls. | 170 | 67.47 | 612.62
11779 | TIN-INTERP | Interpolated Ground | 75359.45 | 4.95 | 556.48 | 0 | 67.47 | 0 | OK | Ground clear controls. | 170 | 67.47 | 623.95
11780 | TIN-INTERP | Interpolated Ground | 75399.32 | 6.89 | 577.73 | 0 | 37.7 | 0 | OK | Ground clear controls. | 170 | 44.66 | 615.43
11781 | TIN-INTERP | Interpolated Ground | 75399.33 | -5.34 | 576.55 | 0 | 33.44 | 0 | OK | Ground clear controls. | 170 | 44.66 | 609.99
11782 | TIN-INTERP | Interpolated Ground | 75399.36 | -4.92 | 576.59 | 0 | 44.66 | 0 | OK | Ground clear controls. | 170 | 44.66 | 621.25
11783 | TIN-INTERP | Interpolated Ground | 75399.38 | -6.84 | 576.42 | 0 | 39.01 | 0 | OK | Ground clear controls. | 170 | 43.81 | 615.43
11784 | TIN-INTERP | Interpolated Ground | 75399.44 | 5.39 | 577.61 | 0 | 32.39 | 0 | OK | Ground clear controls. | 170 | 43.81 | 610
11785 | TIN-INTERP | Interpolated Ground | 75399.45 | 4.98 | 577.51 | 0 | 43.81 | 0 | OK | Ground clear controls. | 170 | 43.81 | 621.32
11786 | TIN-INTERP | Interpolated Ground | 75439.32 | 6.91 | 587.19 | 0 | 26.55 | 0 | OK | Ground clear controls. | 170 | 31.7 | 613.74
11787 | TIN-INTERP | Interpolated Ground | 75439.33 | -5.35 | 591.77 | 0 | 16.49 | 0 | OK | Ground clear controls. | 170 | 31.7 | 608.26
11788 | TIN-INTERP | Interpolated Ground | 75439.36 | -4.95 | 591.67 | 0 | 27.88 | 0 | OK | Ground clear controls. | 170 | 31.7 | 619.55
11789 | TIN-INTERP | Interpolated Ground | 75439.38 | -6.85 | 592.11 | 0 | 21.63 | 0 | OK | Ground clear controls. | 170 | 31.7 | 613.74
11790 | TIN-INTERP | Interpolated Ground | 75439.44 | 5.41 | 587.72 | 0 | 20.54 | 0 | OK | Ground clear controls. | 170 | 31.7 | 608.26
11791 | TIN-INTERP | Interpolated Ground | 75439.45 | 5 | 587.86 | 0 | 31.7 | 0 | OK | Ground clear controls. | 170 | 31.7 | 619.56
11792 | TIN-INTERP | Interpolated Ground | 75451.85 | 5.01 | 592.21 | 0 | 26.97 | 0 | OK | Ground clear controls. | 171 | 65.43 | 619.18
11793 | TIN-INTERP | Interpolated Ground | 75451.87 | -6.86 | 592.65 | 0 | 20.73 | 0 | OK | Ground clear controls. | 171 | 65.43 | 613.38
11794 | TIN-INTERP | Interpolated Ground | 75451.87 | 6.91 | 591.44 | 0 | 21.94 | 0 | OK | Ground clear controls. | 171 | 65.43 | 613.38
11795 | TIN-INTERP | Interpolated Ground | 75451.87 | 5.41 | 592.1 | 0 | 15.78 | 0 | OK | Ground clear controls. | 171 | 65.43 | 607.88
11796 | TIN-INTERP | Interpolated Ground | 75451.89 | -5.36 | 592.51 | 0 | 15.37 | 0 | OK | Ground clear controls. | 171 | 65.43 | 607.88
11797 | TIN-INTERP | Interpolated Ground | 75451.89 | -4.95 | 592.54 | 0 | 26.64 | 0 | OK | Ground clear controls. | 171 | 65.43 | 619.18
11798 | TIN-INTERP | Interpolated Ground | 75491.85 | 4.99 | 572.88 | 0 | 39.13 | 0 | OK | Ground clear controls. | 171 | 65.43 | 612.01
11799 | TIN-INTERP | Interpolated Ground | 75491.87 | -6.84 | 570.77 | 0 | 35.38 | 0 | OK | Ground clear controls. | 171 | 65.43 | 606.15
11800 | TIN-INTERP | Interpolated Ground | 75491.87 | 6.9 | 573.41 | 0 | 32.73 | 0 | OK | Ground clear controls. | 171 | 65.43 | 606.14
11801 | TIN-INTERP | Interpolated Ground | 75491.87 | 5.4 | 573.02 | 0 | 27.68 | 0 | OK | Ground clear controls. | 171 | 65.43 | 600.7
11802 | TIN-INTERP | Interpolated Ground | 75491.89 | -5.34 | 570.98 | 0 | 29.72 | 0 | OK | Ground clear controls. | 171 | 65.43 | 600.7
11803 | TIN-INTERP | Interpolated Ground | 75491.89 | -4.93 | 570.98 | 0 | 40.99 | 0 | OK | Ground clear controls. | 171 | 65.43 | 611.97
11804 | TIN-INTERP | Interpolated Ground | 75531.85 | 4.96 | 555.45 | 0 | 50.23 | 0 | OK | Ground clear controls. | 171 | 65.43 | 605.68
11805 | TIN-INTERP | Interpolated Ground | 75531.87 | -6.82 | 554.07 | 0 | 45.71 | 0 | OK | Ground clear controls. | 171 | 65.43 | 599.78
11806 | TIN-INTERP | Interpolated Ground | 75531.87 | 6.88 | 556.07 | 0 | 43.71 | 0 | OK | Ground clear controls. | 171 | 65.43 | 599.78
11807 | TIN-INTERP | Interpolated Ground | 75531.87 | 5.38 | 555.56 | 0 | 38.82 | 0 | OK | Ground clear controls. | 171 | 65.43 | 594.38
11808 | TIN-INTERP | Interpolated Ground | 75531.89 | -5.32 | 554.25 | 0 | 40.12 | 0 | OK | Ground clear controls. | 171 | 65.43 | 594.37
11809 | TIN-INTERP | Interpolated Ground | 75531.89 | -4.9 | 554.3 | 0 | 51.31 | 0 | OK | Ground clear controls. | 171 | 65.43 | 605.61
11810 | TIN-INTERP | Interpolated Ground | 75571.85 | 4.94 | 538.08 | 0 | 62.14 | 0 | OK | Ground clear controls. | 171 | 65.43 | 600.22
11811 | TIN-INTERP | Interpolated Ground | 75571.87 | -6.8 | 535.76 | 0 | 58.52 | 0 | OK | Ground clear controls. | 171 | 65.43 | 594.28
11812 | TIN-INTERP | Interpolated Ground | 75571.87 | 6.86 | 539.1 | 0 | 55.18 | 0 | OK | Ground clear controls. | 171 | 65.43 | 594.28
11813 | TIN-INTERP | Interpolated Ground | 75571.87 | 5.36 | 538.33 | 0 | 50.59 | 0 | OK | Ground clear controls. | 171 | 65.43 | 588.92
11814 | TIN-INTERP | Interpolated Ground | 75571.89 | -5.3 | 535.89 | 0 | 53.02 | 0 | OK | Ground clear controls. | 171 | 65.43 | 588.91
11815 | TIN-INTERP | Interpolated Ground | 75571.89 | -4.88 | 535.92 | 0 | 64.2 | 0 | OK | Ground clear controls. | 171 | 65.43 | 600.12
11816 | TIN-INTERP | Interpolated Ground | 75611.85 | 4.91 | 541.59 | 0 | 54.01 | 0 | OK | Ground clear controls. | 171 | 65.43 | 595.6
11817 | TIN-INTERP | Interpolated Ground | 75611.87 | -6.78 | 533.94 | 0 | 55.71 | 0 | OK | Ground clear controls. | 171 | 65.43 | 589.65
11818 | TIN-INTERP | Interpolated Ground | 75611.87 | 6.84 | 542.57 | 0 | 47.08 | 0 | OK | Ground clear controls. | 171 | 65.43 | 589.65
11819 | TIN-INTERP | Interpolated Ground | 75611.87 | 5.34 | 541.8 | 0 | 42.52 | 0 | OK | Ground clear controls. | 171 | 65.43 | 584.32
11820 | TIN-INTERP | Interpolated Ground | 75611.89 | -5.28 | 534.89 | 0 | 49.42 | 0 | OK | Ground clear controls. | 171 | 65.43 | 584.31
11821 | TIN-INTERP | Interpolated Ground | 75611.89 | -4.85 | 535.09 | 0 | 60.4 | 0 | OK | Ground clear controls. | 171 | 65.43 | 595.49
11822 | TIN-INTERP | Interpolated Ground | 75651.85 | 4.89 | 552.22 | 0 | 39.63 | 0 | OK | Ground clear controls. | 171 | 65.43 | 591.85
11823 | TIN-INTERP | Interpolated Ground | 75651.87 | -6.76 | 541.76 | 0 | 44.12 | 0 | OK | Ground clear controls. | 171 | 65.43 | 585.88
11824 | TIN-INTERP | Interpolated Ground | 75651.87 | 6.82 | 553.17 | 0 | 32.71 | 0 | OK | Ground clear controls. | 171 | 65.43 | 585.88
11825 | TIN-INTERP | Interpolated Ground | 75651.87 | 5.32 | 552.5 | 0 | 28.07 | 0 | OK | Ground clear controls. | 171 | 65.43 | 580.57
11826 | TIN-INTERP | Interpolated Ground | 75651.89 | -5.26 | 542.86 | 0 | 37.7 | 0 | OK | Ground clear controls. | 171 | 65.43 | 580.56
11827 | TIN-INTERP | Interpolated Ground | 75651.89 | -4.82 | 543.28 | 0 | 48.44 | 0 | OK | Ground clear controls. | 171 | 65.43 | 591.72
11828 | TIN-INTERP | Interpolated Ground | 75691.85 | 4.86 | 547.83 | 0 | 41.11 | 0 | OK | Ground clear controls. | 171 | 65.43 | 588.94
11829 | TIN-INTERP | Interpolated Ground | 75691.87 | -6.74 | 541.45 | 0 | 41.52 | 0 | OK | Ground clear controls. | 171 | 65.43 | 582.97
11830 | TIN-INTERP | Interpolated Ground | 75691.87 | 6.8 | 548.74 | 0 | 34.23 | 0 | OK | Ground clear controls. | 171 | 65.43 | 582.97
11831 | TIN-INTERP | Interpolated Ground | 75691.87 | 5.3 | 548.08 | 0 | 29.6 | 0 | OK | Ground clear controls. | 171 | 65.43 | 577.68
11832 | TIN-INTERP | Interpolated Ground | 75691.89 | -5.24 | 542.28 | 0 | 35.39 | 0 | OK | Ground clear controls. | 171 | 65.43 | 577.67
11833 | TIN-INTERP | Interpolated Ground | 75691.89 | -4.8 | 542.53 | 0 | 46.28 | 0 | OK | Ground clear controls. | 171 | 65.43 | 588.81
11834 | TIN-INTERP | Interpolated Ground | 75731.85 | 4.84 | 533.28 | 0 | 53.6 | 0 | OK | Ground clear controls. | 171 | 65.43 | 586.88
11835 | TIN-INTERP | Interpolated Ground | 75731.87 | -6.72 | 528.24 | 0 | 52.68 | 0 | OK | Ground clear controls. | 171 | 65.43 | 580.92
11836 | TIN-INTERP | Interpolated Ground | 75731.87 | 6.79 | 534.11 | 0 | 46.81 | 0 | OK | Ground clear controls. | 171 | 65.43 | 580.92
11837 | TIN-INTERP | Interpolated Ground | 75731.87 | 5.29 | 533.63 | 0 | 42 | 0 | OK | Ground clear controls. | 171 | 65.43 | 575.63
11838 | TIN-INTERP | Interpolated Ground | 75731.89 | -5.22 | 529.05 | 0 | 46.58 | 0 | OK | Ground clear controls. | 171 | 65.43 | 575.63
11839 | TIN-INTERP | Interpolated Ground | 75731.89 | -4.77 | 529.33 | 0 | 57.41 | 0 | OK | Ground clear controls. | 171 | 65.43 | 586.74
11840 | TIN-INTERP | Interpolated Ground | 75771.85 | 4.81 | 520.24 | 0 | 65.43 | 0 | OK | Ground clear controls. | 171 | 65.43 | 585.67
11841 | TIN-INTERP | Interpolated Ground | 75771.87 | -6.7 | 520.64 | 0 | 59.09 | 0 | OK | Ground clear controls. | 171 | 65.12 | 579.73
11842 | TIN-INTERP | Interpolated Ground | 75771.87 | 6.77 | 520.11 | 0 | 59.62 | 0 | OK | Ground clear controls. | 171 | 65.12 | 579.73
11843 | TIN-INTERP | Interpolated Ground | 75771.87 | 5.27 | 520.21 | 0 | 54.24 | 0 | OK | Ground clear controls. | 171 | 65.12 | 574.45
11844 | TIN-INTERP | Interpolated Ground | 75771.89 | -5.2 | 520.45 | 0 | 53.99 | 0 | OK | Ground clear controls. | 171 | 65.12 | 574.44
11845 | TIN-INTERP | Interpolated Ground | 75771.89 | -4.74 | 520.41 | 0 | 65.12 | 0 | OK | Ground clear controls. | 171 | 65.12 | 585.53
11846 | TIN-INTERP | Interpolated Ground | 75811.85 | 4.79 | 525.61 | 0 | 59.7 | 0 | OK | Ground clear controls. | 171 | 59.7 | 585.31
11847 | TIN-INTERP | Interpolated Ground | 75811.87 | -6.68 | 525.9 | 0 | 53.51 | 0 | OK | Ground clear controls. | 171 | 59.3 | 579.41
11848 | TIN-INTERP | Interpolated Ground | 75811.87 | 6.75 | 525.25 | 0 | 54.15 | 0 | OK | Ground clear controls. | 171 | 59.3 | 579.4
11849 | TIN-INTERP | Interpolated Ground | 75811.87 | 5.25 | 525.56 | 0 | 48.55 | 0 | OK | Ground clear controls. | 171 | 59.3 | 574.11
11850 | TIN-INTERP | Interpolated Ground | 75811.89 | -5.18 | 525.96 | 0 | 48.14 | 0 | OK | Ground clear controls. | 171 | 59.3 | 574.1
11851 | TIN-INTERP | Interpolated Ground | 75811.89 | -4.72 | 525.87 | 0 | 59.3 | 0 | OK | Ground clear controls. | 171 | 59.3 | 585.17
11852 | TIN-INTERP | Interpolated Ground | 75851.85 | 4.76 | 534.12 | 0 | 51.67 | 0 | OK | Ground clear controls. | 171 | 51.87 | 585.79
11853 | TIN-INTERP | Interpolated Ground | 75851.87 | -6.66 | 533.63 | 0 | 46.31 | 0 | OK | Ground clear controls. | 171 | 51.87 | 579.94
11854 | TIN-INTERP | Interpolated Ground | 75851.87 | 6.73 | 534.09 | 0 | 45.84 | 0 | OK | Ground clear controls. | 171 | 51.87 | 579.93
11855 | TIN-INTERP | Interpolated Ground | 75851.87 | 5.23 | 534.1 | 0 | 40.52 | 0 | OK | Ground clear controls. | 171 | 51.87 | 574.62
11856 | TIN-INTERP | Interpolated Ground | 75851.89 | -5.16 | 533.76 | 0 | 40.86 | 0 | OK | Ground clear controls. | 171 | 51.87 | 574.62
11857 | TIN-INTERP | Interpolated Ground | 75851.89 | -4.69 | 533.8 | 0 | 51.87 | 0 | OK | Ground clear controls. | 171 | 51.87 | 585.67
11858 | TIN-INTERP | Interpolated Ground | 75891.85 | 4.74 | 538.1 | 0 | 49.03 | 0 | OK | Ground clear controls. | 171 | 49.03 | 587.13
11859 | TIN-INTERP | Interpolated Ground | 75891.87 | -6.64 | 538.67 | 0 | 42.66 | 0 | OK | Ground clear controls. | 171 | 48.51 | 581.33
11860 | TIN-INTERP | Interpolated Ground | 75891.87 | 6.71 | 537.98 | 0 | 43.34 | 0 | OK | Ground clear controls. | 171 | 48.51 | 581.32
11861 | TIN-INTERP | Interpolated Ground | 75891.87 | 5.21 | 538.1 | 0 | 37.89 | 0 | OK | Ground clear controls. | 171 | 48.51 | 575.99
11862 | TIN-INTERP | Interpolated Ground | 75891.89 | -5.14 | 538.54 | 0 | 37.45 | 0 | OK | Ground clear controls. | 171 | 48.51 | 575.99
11863 | TIN-INTERP | Interpolated Ground | 75891.89 | -4.66 | 538.52 | 0 | 48.51 | 0 | OK | Ground clear controls. | 171 | 48.51 | 587.03
11864 | TIN-INTERP | Interpolated Ground | 75931.85 | 4.71 | 544.56 | 0 | 44.74 | 0 | OK | Ground clear controls. | 171 | 44.74 | 589.3
11865 | TIN-INTERP | Interpolated Ground | 75931.87 | -6.62 | 545.44 | 0 | 38.14 | 0 | OK | Ground clear controls. | 171 | 43.86 | 583.58
11866 | TIN-INTERP | Interpolated Ground | 75931.87 | 6.69 | 544.32 | 0 | 39.25 | 0 | OK | Ground clear controls. | 171 | 43.86 | 583.57
11867 | TIN-INTERP | Interpolated Ground | 75931.87 | 5.19 | 544.49 | 0 | 33.7 | 0 | OK | Ground clear controls. | 171 | 43.86 | 578.19
11868 | TIN-INTERP | Interpolated Ground | 75931.89 | -5.12 | 545.38 | 0 | 32.81 | 0 | OK | Ground clear controls. | 171 | 43.86 | 578.19
11869 | TIN-INTERP | Interpolated Ground | 75931.89 | -4.64 | 545.37 | 0 | 43.86 | 0 | OK | Ground clear controls. | 171 | 43.86 | 589.23
11870 | TIN-INTERP | Interpolated Ground | 75971.85 | 4.69 | 562 | 0 | 30.33 | 0 | OK | Ground clear controls. | 171 | 32.72 | 592.33
11871 | TIN-INTERP | Interpolated Ground | 75971.87 | -6.6 | 558.96 | 0 | 27.73 | 0 | OK | Ground clear controls. | 171 | 32.72 | 586.69
11872 | TIN-INTERP | Interpolated Ground | 75971.87 | 6.67 | 562.42 | 0 | 24.26 | 0 | OK | Ground clear controls. | 171 | 32.72 | 586.68
11873 | TIN-INTERP | Interpolated Ground | 75971.87 | 5.17 | 562.13 | 0 | 19.13 | 0 | OK | Ground clear controls. | 171 | 32.72 | 581.26
11874 | TIN-INTERP | Interpolated Ground | 75971.89 | -5.1 | 559.39 | 0 | 21.88 | 0 | OK | Ground clear controls. | 171 | 32.72 | 581.27
11875 | TIN-INTERP | Interpolated Ground | 75971.89 | -4.61 | 559.56 | 0 | 32.72 | 0 | OK | Ground clear controls. | 171 | 32.72 | 592.28
11876 | TIN-INTERP | Interpolated Ground | 76011.85 | 4.66 | 573.65 | 0 | 22.56 | 0 | OK | Ground clear controls. | 171 | 24.1 | 596.21
11877 | TIN-INTERP | Interpolated Ground | 76011.87 | -6.58 | 570.92 | 0 | 19.75 | 0 | OK | Ground clear controls. | 171 | 24.1 | 590.67
11878 | TIN-INTERP | Interpolated Ground | 76011.87 | 6.66 | 570.8 | 0 | 19.85 | 0 | OK | Ground clear controls. | 171 | 24.1 | 590.65
11879 | TIN-INTERP | Interpolated Ground | 76011.87 | 5.16 | 572.95 | 0 | 12.23 | 0 | OK | Ground clear controls. | 171 | 24.1 | 585.18
11880 | TIN-INTERP | Interpolated Ground | 76011.89 | -5.08 | 571.83 | 0 | 13.36 | 0 | OK | Ground clear controls. | 171 | 24.1 | 585.19
11881 | TIN-INTERP | Interpolated Ground | 76011.89 | -4.58 | 572.1 | 0 | 24.1 | 0 | OK | Ground clear controls. | 171 | 24.1 | 596.2
11882 | TIN-INTERP | Interpolated Ground | 76035.22 | -6.57 | 571.95 | 0 | 21.42 | 0 | OK | Ground clear controls. | 172 | 46.82 | 593.37
11883 | TIN-INTERP | Interpolated Ground | 76035.22 | -4.57 | 572.13 | 0 | 26.74 | 0 | OK | Ground clear controls. | 172 | 46.82 | 598.87
11884 | TIN-INTERP | Interpolated Ground | 76035.25 | -5.07 | 572.12 | 0 | 15.76 | 0 | OK | Ground clear controls. | 172 | 46.82 | 587.88
11885 | TIN-INTERP | Interpolated Ground | 76035.26 | 4.65 | 571.94 | 0 | 26.93 | 0 | OK | Ground clear controls. | 172 | 46.82 | 598.87
11886 | TIN-INTERP | Interpolated Ground | 76035.29 | 5.15 | 571.76 | 0 | 16.12 | 0 | OK | Ground clear controls. | 172 | 46.82 | 587.88
11887 | TIN-INTERP | Interpolated Ground | 76035.3 | 6.65 | 571.43 | 0 | 21.94 | 0 | OK | Ground clear controls. | 172 | 46.82 | 593.37
11888 | TIN-INTERP | Interpolated Ground | 76075.22 | -6.57 | 570.94 | 0 | 20.42 | 0 | OK | Ground clear controls. | 172 | 46.82 | 591.36
11889 | TIN-INTERP | Interpolated Ground | 76075.22 | -4.57 | 570.33 | 0 | 26.55 | 0 | OK | Ground clear controls. | 172 | 46.82 | 596.88
11890 | TIN-INTERP | Interpolated Ground | 76075.25 | -5.07 | 570.45 | 0 | 15.45 | 0 | OK | Ground clear controls. | 172 | 46.82 | 585.9
11891 | TIN-INTERP | Interpolated Ground | 76075.26 | 4.64 | 565.23 | 0 | 31.67 | 0 | OK | Ground clear controls. | 172 | 46.82 | 596.9
11892 | TIN-INTERP | Interpolated Ground | 76075.29 | 5.14 | 564.97 | 0 | 20.92 | 0 | OK | Ground clear controls. | 172 | 46.82 | 585.89
11893 | TIN-INTERP | Interpolated Ground | 76075.3 | 6.64 | 564.22 | 0 | 27.13 | 0 | OK | Ground clear controls. | 172 | 46.82 | 591.35
11894 | TIN-INTERP | Interpolated Ground | 76115.22 | -6.57 | 557.65 | 0 | 32.55 | 0 | OK | Ground clear controls. | 172 | 46.82 | 590.2
11895 | TIN-INTERP | Interpolated Ground | 76115.22 | -4.58 | 556.85 | 0 | 38.89 | 0 | OK | Ground clear controls. | 172 | 46.82 | 595.74
11896 | TIN-INTERP | Interpolated Ground | 76115.25 | -5.07 | 556.99 | 0 | 27.78 | 0 | OK | Ground clear controls. | 172 | 46.82 | 584.77
11897 | TIN-INTERP | Interpolated Ground | 76115.26 | 4.64 | 551.97 | 0 | 43.79 | 0 | OK | Ground clear controls. | 172 | 46.82 | 595.76
11898 | TIN-INTERP | Interpolated Ground | 76115.29 | 5.14 | 551.78 | 0 | 32.97 | 0 | OK | Ground clear controls. | 172 | 46.82 | 584.75
11899 | TIN-INTERP | Interpolated Ground | 76115.3 | 6.64 | 551.21 | 0 | 38.97 | 0 | OK | Ground clear controls. | 172 | 46.82 | 590.18
11900 | TIN-INTERP | Interpolated Ground | 76155.22 | -6.58 | 552.63 | 0 | 37.26 | 0 | OK | Ground clear controls. | 172 | 46.82 | 589.89
11901 | TIN-INTERP | Interpolated Ground | 76155.22 | -4.58 | 551.67 | 0 | 43.77 | 0 | OK | Ground clear controls. | 172 | 46.82 | 595.44
11902 | TIN-INTERP | Interpolated Ground | 76155.25 | -5.08 | 551.92 | 0 | 32.57 | 0 | OK | Ground clear controls. | 172 | 46.82 | 584.49
11903 | TIN-INTERP | Interpolated Ground | 76155.26 | 4.63 | 548.65 | 0 | 46.82 | 0 | OK | Ground clear controls. | 172 | 46.82 | 595.47
11904 | TIN-INTERP | Interpolated Ground | 76155.29 | 5.13 | 548.41 | 0 | 36.04 | 0 | OK | Ground clear controls. | 172 | 44.31 | 584.45
11905 | TIN-INTERP | Interpolated Ground | 76155.3 | 6.63 | 547.71 | 0 | 42.16 | 0 | OK | Ground clear controls. | 172 | 44.31 | 589.87
11906 | TIN-INTERP | Interpolated Ground | 76195.22 | -6.58 | 558.4 | 0 | 32.02 | 0 | OK | Ground clear controls. | 172 | 44.31 | 590.42
11907 | TIN-INTERP | Interpolated Ground | 76195.22 | -4.58 | 557.72 | 0 | 38.27 | 0 | OK | Ground clear controls. | 172 | 44.31 | 595.99
11908 | TIN-INTERP | Interpolated Ground | 76195.25 | -5.08 | 557.9 | 0 | 27.14 | 0 | OK | Ground clear controls. | 172 | 44.31 | 585.04
11909 | TIN-INTERP | Interpolated Ground | 76195.26 | 4.63 | 553.9 | 0 | 42.12 | 0 | OK | Ground clear controls. | 172 | 44.31 | 596.02
11910 | TIN-INTERP | Interpolated Ground | 76195.29 | 5.13 | 553.77 | 0 | 31.23 | 0 | OK | Ground clear controls. | 172 | 44.31 | 585
11911 | TIN-INTERP | Interpolated Ground | 76195.3 | 6.63 | 553.37 | 0 | 37.04 | 0 | OK | Ground clear controls. | 172 | 44.31 | 590.41
11912 | TIN-INTERP | Interpolated Ground | 76235.22 | -6.58 | 554.67 | 0 | 37.14 | 0 | OK | Ground clear controls. | 172 | 44.31 | 591.81
11913 | TIN-INTERP | Interpolated Ground | 76235.22 | -4.58 | 553.42 | 0 | 43.96 | 0 | OK | Ground clear controls. | 172 | 44.31 | 597.38
11914 | TIN-INTERP | Interpolated Ground | 76235.25 | -5.08 | 553.69 | 0 | 32.73 | 0 | OK | Ground clear controls. | 172 | 44.31 | 586.42
11915 | TIN-INTERP | Interpolated Ground | 76235.26 | 4.62 | 553.1 | 0 | 44.31 | 0 | OK | Ground clear controls. | 172 | 44.31 | 597.41
11916 | TIN-INTERP | Interpolated Ground | 76235.29 | 5.12 | 553.41 | 0 | 32.99 | 0 | OK | Ground clear controls. | 172 | 42.25 | 586.4
11917 | TIN-INTERP | Interpolated Ground | 76235.3 | 6.62 | 554.31 | 0 | 37.48 | 0 | OK | Ground clear controls. | 172 | 42.25 | 591.79
11918 | TIN-INTERP | Interpolated Ground | 76275.22 | -6.59 | 556.88 | 0 | 37.16 | 0 | OK | Ground clear controls. | 172 | 42.25 | 594.04
11919 | TIN-INTERP | Interpolated Ground | 76275.22 | -4.59 | 557.35 | 0 | 42.25 | 0 | OK | Ground clear controls. | 172 | 42.25 | 599.6
11920 | TIN-INTERP | Interpolated Ground | 76275.25 | -5.09 | 557 | 0 | 31.66 | 0 | OK | Ground clear controls. | 172 | 40.21 | 588.66
11921 | TIN-INTERP | Interpolated Ground | 76275.26 | 4.62 | 562.91 | 0 | 36.74 | 0 | OK | Ground clear controls. | 172 | 40.21 | 599.65
11922 | TIN-INTERP | Interpolated Ground | 76275.29 | 5.12 | 563.21 | 0 | 25.42 | 0 | OK | Ground clear controls. | 172 | 40.21 | 588.63
11923 | TIN-INTERP | Interpolated Ground | 76275.3 | 6.62 | 564.12 | 0 | 29.91 | 0 | OK | Ground clear controls. | 172 | 40.21 | 594.03
11924 | TIN-INTERP | Interpolated Ground | 76315.22 | -6.59 | 563.33 | 0 | 33.81 | 0 | OK | Ground clear controls. | 172 | 40.21 | 597.14
11925 | TIN-INTERP | Interpolated Ground | 76315.22 | -4.59 | 562.48 | 0 | 40.21 | 0 | OK | Ground clear controls. | 172 | 40.21 | 602.69
11926 | TIN-INTERP | Interpolated Ground | 76315.25 | -5.09 | 562.64 | 0 | 29.1 | 0 | OK | Ground clear controls. | 172 | 38.07 | 591.74
11927 | TIN-INTERP | Interpolated Ground | 76315.26 | 4.62 | 564.65 | 0 | 38.07 | 0 | OK | Ground clear controls. | 172 | 38.07 | 602.72
11928 | TIN-INTERP | Interpolated Ground | 76315.29 | 5.11 | 564.87 | 0 | 26.84 | 0 | OK | Ground clear controls. | 172 | 36.15 | 591.71
11929 | TIN-INTERP | Interpolated Ground | 76315.3 | 6.61 | 565.53 | 0 | 31.58 | 0 | OK | Ground clear controls. | 172 | 36.15 | 597.11
11930 | TIN-INTERP | Interpolated Ground | 76355.22 | -6.59 | 572.98 | 0 | 28.1 | 0 | OK | Ground clear controls. | 172 | 36.15 | 601.08
11931 | TIN-INTERP | Interpolated Ground | 76355.22 | -4.59 | 572.73 | 0 | 33.9 | 0 | OK | Ground clear controls. | 172 | 36.15 | 606.63
11932 | TIN-INTERP | Interpolated Ground | 76355.25 | -5.09 | 572.72 | 0 | 22.94 | 0 | OK | Ground clear controls. | 172 | 36.15 | 595.66
11933 | TIN-INTERP | Interpolated Ground | 76355.26 | 4.61 | 570.5 | 0 | 36.15 | 0 | OK | Ground clear controls. | 172 | 36.15 | 606.65
11934 | TIN-INTERP | Interpolated Ground | 76355.29 | 5.11 | 570.28 | 0 | 25.35 | 0 | OK | Ground clear controls. | 172 | 31.49 | 595.63
11935 | TIN-INTERP | Interpolated Ground | 76355.3 | 6.61 | 569.57 | 0 | 31.49 | 0 | OK | Ground clear controls. | 172 | 31.49 | 601.06
11936 | TIN-INTERP | Interpolated Ground | 76395.22 | -6.6 | 582.97 | 0 | 22.92 | 0 | OK | Ground clear controls. | 172 | 29.2 | 605.89
11937 | TIN-INTERP | Interpolated Ground | 76395.22 | -4.6 | 583.05 | 0 | 28.35 | 0 | OK | Ground clear controls. | 172 | 29.2 | 611.4
11938 | TIN-INTERP | Interpolated Ground | 76395.25 | -5.1 | 583.06 | 0 | 17.37 | 0 | OK | Ground clear controls. | 172 | 29.2 | 600.43
11939 | TIN-INTERP | Interpolated Ground | 76395.26 | 4.61 | 582.21 | 0 | 29.2 | 0 | OK | Ground clear controls. | 172 | 29.2 | 611.41
11940 | TIN-INTERP | Interpolated Ground | 76395.29 | 5.11 | 582.31 | 0 | 18.11 | 0 | OK | Ground clear controls. | 172 | 25.2 | 600.42
11941 | TIN-INTERP | Interpolated Ground | 76395.3 | 6.61 | 582.3 | 0 | 23.57 | 0 | OK | Ground clear controls. | 172 | 25.2 | 605.87
11942 | TIN-INTERP | Interpolated Ground | 76435.22 | -6.6 | 591.08 | 0 | 20.46 | 0 | OK | Ground clear controls. | 172 | 25.2 | 611.54
11943 | TIN-INTERP | Interpolated Ground | 76435.22 | -4.6 | 591.83 | 0 | 25.2 | 0 | OK | Ground clear controls. | 172 | 25.2 | 617.03
11944 | TIN-INTERP | Interpolated Ground | 76435.25 | -5.1 | 591.6 | 0 | 14.45 | 0 | OK | Ground clear controls. | 172 | 24.03 | 606.05
11945 | TIN-INTERP | Interpolated Ground | 76435.26 | 4.6 | 593 | 0 | 24.03 | 0 | OK | Ground clear controls. | 172 | 24.03 | 617.03
11946 | TIN-INTERP | Interpolated Ground | 76435.29 | 5.1 | 593.01 | 0 | 13.04 | 0 | OK | Ground clear controls. | 172 | 18.51 | 606.05
11947 | TIN-INTERP | Interpolated Ground | 76435.3 | 6.6 | 593.02 | 0 | 18.51 | 0 | OK | Ground clear controls. | 172 | 18.51 | 611.53
11948 | TIN-INTERP | Interpolated Ground | 76438.51 | -6.6 | 590.96 | 0 | 21.08 | 0 | OK | Ground clear controls. | 173 | 44.74 | 612.04
11949 | TIN-INTERP | Interpolated Ground | 76438.52 | -5.1 | 591.65 | 0 | 14.89 | 0 | OK | Ground clear controls. | 173 | 44.74 | 606.54
11950 | TIN-INTERP | Interpolated Ground | 76438.58 | -4.6 | 591.9 | 0 | 25.64 | 0 | OK | Ground clear controls. | 173 | 44.74 | 617.54
11951 | TIN-INTERP | Interpolated Ground | 76438.59 | 5.1 | 593.53 | 0 | 13.01 | 0 | OK | Ground clear controls. | 173 | 44.74 | 606.54
11952 | TIN-INTERP | Interpolated Ground | 76438.61 | 6.6 | 593.65 | 0 | 18.39 | 0 | OK | Ground clear controls. | 173 | 44.74 | 612.04
11953 | TIN-INTERP | Interpolated Ground | 76438.65 | 4.6 | 593.45 | 0 | 24.09 | 0 | OK | Ground clear controls. | 173 | 44.74 | 617.54
11954 | TIN-INTERP | Interpolated Ground | 76478.51 | -6.59 | 587.87 | 0 | 18.19 | 0 | OK | Ground clear controls. | 173 | 44.74 | 606.06
11955 | TIN-INTERP | Interpolated Ground | 76478.52 | -5.09 | 588.26 | 0 | 12.32 | 0 | OK | Ground clear controls. | 173 | 44.74 | 600.58
11956 | TIN-INTERP | Interpolated Ground | 76478.58 | -4.59 | 588.38 | 0 | 23.21 | 0 | OK | Ground clear controls. | 173 | 44.74 | 611.59
11957 | TIN-INTERP | Interpolated Ground | 76478.59 | 5.11 | 591.3 | 0 | 9.27 | 0 | OK | Ground clear controls. | 173 | 44.74 | 600.57
11958 | TIN-INTERP | Interpolated Ground | 76478.61 | 6.61 | 591.77 | 0 | 14.28 | 0 | OK | Ground clear controls. | 173 | 44.74 | 606.05
11959 | TIN-INTERP | Interpolated Ground | 76478.65 | 4.61 | 591.1 | 0 | 20.49 | 0 | OK | Ground clear controls. | 173 | 44.74 | 611.59
11960 | TIN-INTERP | Interpolated Ground | 76518.51 | -6.58 | 576.33 | 0 | 24.6 | 0 | OK | Ground clear controls. | 173 | 44.74 | 600.93
11961 | TIN-INTERP | Interpolated Ground | 76518.52 | -5.08 | 577.34 | 0 | 18.11 | 0 | OK | Ground clear controls. | 173 | 44.74 | 595.45
11962 | TIN-INTERP | Interpolated Ground | 76518.58 | -4.58 | 577.59 | 0 | 28.88 | 0 | OK | Ground clear controls. | 173 | 44.74 | 606.47
11963 | TIN-INTERP | Interpolated Ground | 76518.59 | 5.12 | 580.03 | 0 | 15.42 | 0 | OK | Ground clear controls. | 173 | 44.74 | 595.45
11964 | TIN-INTERP | Interpolated Ground | 76518.61 | 6.62 | 580.24 | 0 | 20.67 | 0 | OK | Ground clear controls. | 173 | 44.74 | 600.91
11965 | TIN-INTERP | Interpolated Ground | 76518.65 | 4.62 | 579.81 | 0 | 26.66 | 0 | OK | Ground clear controls. | 173 | 44.74 | 606.47
11966 | TIN-INTERP | Interpolated Ground | 76558.51 | -6.57 | 562.86 | 0 | 33.78 | 0 | OK | Ground clear controls. | 173 | 44.74 | 596.64
11967 | TIN-INTERP | Interpolated Ground | 76558.52 | -5.07 | 563.05 | 0 | 28.13 | 0 | OK | Ground clear controls. | 173 | 44.74 | 591.18
11968 | TIN-INTERP | Interpolated Ground | 76558.58 | -4.57 | 563.05 | 0 | 39.14 | 0 | OK | Ground clear controls. | 173 | 44.74 | 602.19
11969 | TIN-INTERP | Interpolated Ground | 76558.59 | 5.13 | 562.81 | 0 | 28.35 | 0 | OK | Ground clear controls. | 173 | 44.74 | 591.16
11970 | TIN-INTERP | Interpolated Ground | 76558.61 | 6.63 | 562.68 | 0 | 33.94 | 0 | OK | Ground clear controls. | 173 | 44.74 | 596.62
11971 | TIN-INTERP | Interpolated Ground | 76558.65 | 4.63 | 562.86 | 0 | 39.34 | 0 | OK | Ground clear controls. | 173 | 44.74 | 602.2
11972 | TIN-INTERP | Interpolated Ground | 76598.51 | -6.56 | 554.77 | 0 | 38.44 | 0 | OK | Ground clear controls. | 173 | 44.74 | 593.21
11973 | TIN-INTERP | Interpolated Ground | 76598.52 | -5.06 | 554.1 | 0 | 33.64 | 0 | OK | Ground clear controls. | 173 | 44.74 | 587.74
11974 | TIN-INTERP | Interpolated Ground | 76598.58 | -4.56 | 554.01 | 0 | 44.74 | 0 | OK | Ground clear controls. | 173 | 44.74 | 598.75
11975 | TIN-INTERP | Interpolated Ground | 76598.59 | 5.14 | 556.34 | 0 | 31.38 | 0 | OK | Ground clear controls. | 173 | 42.82 | 587.72
11976 | TIN-INTERP | Interpolated Ground | 76598.61 | 6.64 | 556.91 | 0 | 36.28 | 0 | OK | Ground clear controls. | 173 | 42.82 | 593.19
11977 | TIN-INTERP | Interpolated Ground | 76598.65 | 4.64 | 555.94 | 0 | 42.82 | 0 | OK | Ground clear controls. | 173 | 42.82 | 598.76
11978 | TIN-INTERP | Interpolated Ground | 76638.51 | -6.54 | 561.88 | 0 | 28.73 | 0 | OK | Ground clear controls. | 173 | 33.87 | 590.61
11979 | TIN-INTERP | Interpolated Ground | 76638.52 | -5.04 | 562.16 | 0 | 22.98 | 0 | OK | Ground clear controls. | 173 | 33.87 | 585.14
11980 | TIN-INTERP | Interpolated Ground | 76638.58 | -4.54 | 562.27 | 0 | 33.87 | 0 | OK | Ground clear controls. | 173 | 33.87 | 596.14
11981 | TIN-INTERP | Interpolated Ground | 76638.59 | 5.16 | 564.89 | 0 | 20.23 | 0 | OK | Ground clear controls. | 173 | 31.3 | 585.12
11982 | TIN-INTERP | Interpolated Ground | 76638.61 | 6.66 | 565.55 | 0 | 25.06 | 0 | OK | Ground clear controls. | 173 | 31.3 | 590.61
11983 | TIN-INTERP | Interpolated Ground | 76638.65 | 4.66 | 564.84 | 0 | 31.3 | 0 | OK | Ground clear controls. | 173 | 31.3 | 596.14
11984 | TIN-INTERP | Interpolated Ground | 76678.51 | -6.53 | 568.63 | 0 | 20.23 | 0 | OK | Ground clear controls. | 173 | 25.68 | 588.86
11985 | TIN-INTERP | Interpolated Ground | 76678.52 | -5.03 | 568.67 | 0 | 14.69 | 0 | OK | Ground clear controls. | 173 | 25.68 | 583.36
11986 | TIN-INTERP | Interpolated Ground | 76678.58 | -4.53 | 568.68 | 0 | 25.68 | 0 | OK | Ground clear controls. | 173 | 25.68 | 594.36
11987 | TIN-INTERP | Interpolated Ground | 76678.59 | 5.17 | 569.86 | 0 | 13.5 | 0 | OK | Ground clear controls. | 173 | 24.57 | 583.36
11988 | TIN-INTERP | Interpolated Ground | 76678.61 | 6.67 | 570.09 | 0 | 18.77 | 0 | OK | Ground clear controls. | 173 | 24.57 | 588.86
11989 | TIN-INTERP | Interpolated Ground | 76678.65 | 4.67 | 569.79 | 0 | 24.57 | 0 | OK | Ground clear controls. | 173 | 24.57 | 594.36
11990 | TIN-INTERP | Interpolated Ground | 76682.28 | -6.53 | 568.57 | 0 | 20.17 | 0 | OK | Ground clear controls. | 174 | 51.84 | 588.74
11991 | TIN-INTERP | Interpolated Ground | 76682.3 | -5.03 | 568.7 | 0 | 14.54 | 0 | OK | Ground clear controls. | 174 | 51.84 | 583.24
11992 | TIN-INTERP | Interpolated Ground | 76682.31 | -4.53 | 568.78 | 0 | 25.46 | 0 | OK | Ground clear controls. | 174 | 51.84 | 594.24
11993 | TIN-INTERP | Interpolated Ground | 76682.35 | 6.67 | 569.68 | 0 | 19.06 | 0 | OK | Ground clear controls. | 174 | 51.84 | 588.74
11994 | TIN-INTERP | Interpolated Ground | 76682.36 | 5.17 | 569.5 | 0 | 13.74 | 0 | OK | Ground clear controls. | 174 | 51.84 | 583.24
11995 | TIN-INTERP | Interpolated Ground | 76682.38 | 4.67 | 569.45 | 0 | 24.79 | 0 | OK | Ground clear controls. | 174 | 51.84 | 594.24
11996 | TIN-INTERP | Interpolated Ground | 76722.27 | -6.54 | 559.31 | 0 | 24.54 | 0 | OK | Ground clear controls. | 174 | 51.84 | 583.85
11997 | TIN-INTERP | Interpolated Ground | 76722.3 | -5.04 | 559.39 | 0 | 18.99 | 0 | OK | Ground clear controls. | 174 | 51.84 | 578.38
11998 | TIN-INTERP | Interpolated Ground | 76722.3 | -4.54 | 559.41 | 0 | 29.98 | 0 | OK | Ground clear controls. | 174 | 51.84 | 589.39
11999 | TIN-INTERP | Interpolated Ground | 76722.35 | 6.66 | 560.62 | 0 | 23.22 | 0 | OK | Ground clear controls. | 174 | 51.84 | 583.84
12000 | TIN-INTERP | Interpolated Ground | 76722.36 | 5.16 | 560.41 | 0 | 17.96 | 0 | OK | Ground clear controls. | 174 | 51.84 | 578.37
12001 | TIN-INTERP | Interpolated Ground | 76722.38 | 4.66 | 560.37 | 0 | 29.03 | 0 | OK | Ground clear controls. | 174 | 51.84 | 589.4
12002 | TIN-INTERP | Interpolated Ground | 76762.27 | -6.55 | 549.94 | 0 | 29.88 | 0 | OK | Ground clear controls. | 174 | 51.84 | 579.82
12003 | TIN-INTERP | Interpolated Ground | 76762.3 | -5.05 | 550.28 | 0 | 24.08 | 0 | OK | Ground clear controls. | 174 | 51.84 | 574.36
12004 | TIN-INTERP | Interpolated Ground | 76762.3 | -4.55 | 550.39 | 0 | 34.99 | 0 | OK | Ground clear controls. | 174 | 51.84 | 585.38
12005 | TIN-INTERP | Interpolated Ground | 76762.35 | 6.65 | 553.8 | 0 | 26.01 | 0 | OK | Ground clear controls. | 174 | 51.84 | 579.81
12006 | TIN-INTERP | Interpolated Ground | 76762.36 | 5.15 | 553.42 | 0 | 20.92 | 0 | OK | Ground clear controls. | 174 | 51.84 | 574.34
12007 | TIN-INTERP | Interpolated Ground | 76762.38 | 4.65 | 553.23 | 0 | 32.17 | 0 | OK | Ground clear controls. | 174 | 51.84 | 585.4
12008 | TIN-INTERP | Interpolated Ground | 76802.27 | -6.56 | 530.47 | 0 | 46.16 | 0 | OK | Ground clear controls. | 174 | 51.84 | 576.63
12009 | TIN-INTERP | Interpolated Ground | 76802.3 | -5.06 | 530.32 | 0 | 40.86 | 0 | OK | Ground clear controls. | 174 | 51.84 | 571.18
12010 | TIN-INTERP | Interpolated Ground | 76802.3 | -4.56 | 530.36 | 0 | 51.84 | 0 | OK | Ground clear controls. | 174 | 51.84 | 582.2
12011 | TIN-INTERP | Interpolated Ground | 76802.35 | 6.64 | 531.61 | 0 | 45 | 0 | OK | Ground clear controls. | 174 | 50.61 | 576.61
12012 | TIN-INTERP | Interpolated Ground | 76802.36 | 5.14 | 531.75 | 0 | 39.41 | 0 | OK | Ground clear controls. | 174 | 50.61 | 571.16
12013 | TIN-INTERP | Interpolated Ground | 76802.38 | 4.64 | 531.61 | 0 | 50.61 | 0 | OK | Ground clear controls. | 174 | 50.61 | 582.22
12014 | TIN-INTERP | Interpolated Ground | 76842.27 | -6.57 | 533.84 | 0 | 40.45 | 0 | OK | Ground clear controls. | 174 | 45.43 | 574.29
12015 | TIN-INTERP | Interpolated Ground | 76842.3 | -5.07 | 534.28 | 0 | 34.56 | 0 | OK | Ground clear controls. | 174 | 45.43 | 568.84
12016 | TIN-INTERP | Interpolated Ground | 76842.3 | -4.57 | 534.43 | 0 | 45.43 | 0 | OK | Ground clear controls. | 174 | 45.43 | 579.86
12017 | TIN-INTERP | Interpolated Ground | 76842.35 | 6.63 | 536.27 | 0 | 37.99 | 0 | OK | Ground clear controls. | 174 | 44.16 | 574.26
12018 | TIN-INTERP | Interpolated Ground | 76842.36 | 5.13 | 535.86 | 0 | 32.96 | 0 | OK | Ground clear controls. | 174 | 44.16 | 568.82
12019 | TIN-INTERP | Interpolated Ground | 76842.38 | 4.63 | 535.71 | 0 | 44.16 | 0 | OK | Ground clear controls. | 174 | 44.16 | 579.87
12020 | TIN-INTERP | Interpolated Ground | 76882.27 | -6.58 | 546.53 | 0 | 26.25 | 0 | OK | Ground clear controls. | 174 | 34.85 | 572.78
12021 | TIN-INTERP | Interpolated Ground | 76882.3 | -5.08 | 546 | 0 | 21.33 | 0 | OK | Ground clear controls. | 174 | 34.85 | 567.33
12022 | TIN-INTERP | Interpolated Ground | 76882.3 | -4.58 | 545.94 | 0 | 32.4 | 0 | OK | Ground clear controls. | 174 | 34.85 | 578.34
12023 | TIN-INTERP | Interpolated Ground | 76882.35 | 6.62 | 542.84 | 0 | 29.92 | 0 | OK | Ground clear controls. | 174 | 34.85 | 572.76
12024 | TIN-INTERP | Interpolated Ground | 76882.36 | 5.12 | 543.32 | 0 | 24 | 0 | OK | Ground clear controls. | 174 | 34.85 | 567.32
12025 | TIN-INTERP | Interpolated Ground | 76882.38 | 4.62 | 543.51 | 0 | 34.85 | 0 | OK | Ground clear controls. | 174 | 34.85 | 578.36
12026 | TIN-INTERP | Interpolated Ground | 76922.27 | -6.59 | 551.14 | 0 | 20.98 | 0 | OK | Ground clear controls. | 174 | 28.7 | 572.12
12027 | TIN-INTERP | Interpolated Ground | 76922.3 | -5.09 | 551.34 | 0 | 15.32 | 0 | OK | Ground clear controls. | 174 | 28.7 | 566.66
12028 | TIN-INTERP | Interpolated Ground | 76922.3 | -4.59 | 551.43 | 0 | 26.24 | 0 | OK | Ground clear controls. | 174 | 28.7 | 577.67
12029 | TIN-INTERP | Interpolated Ground | 76922.35 | 6.61 | 552.09 | 0 | 20.02 | 0 | OK | Ground clear controls. | 174 | 28.7 | 572.11
12030 | TIN-INTERP | Interpolated Ground | 76922.36 | 5.11 | 551.99 | 0 | 14.66 | 0 | OK | Ground clear controls. | 174 | 28.7 | 566.65
12031 | TIN-INTERP | Interpolated Ground | 76922.38 | 4.61 | 551.99 | 0 | 25.69 | 0 | OK | Ground clear controls. | 174 | 28.7 | 577.68
12032 | TIN-INTERP | Interpolated Ground | 76962.27 | -6.59 | 548.32 | 0 | 23.99 | 0 | OK | Ground clear controls. | 174 | 28.7 | 572.31
12033 | TIN-INTERP | Interpolated Ground | 76962.3 | -5.09 | 548.97 | 0 | 17.86 | 0 | OK | Ground clear controls. | 174 | 28.7 | 566.83
12034 | TIN-INTERP | Interpolated Ground | 76962.3 | -4.59 | 549.13 | 0 | 28.7 | 0 | OK | Ground clear controls. | 174 | 28.7 | 577.83
12035 | TIN-INTERP | Interpolated Ground | 76962.35 | 6.61 | 554.19 | 0 | 18.12 | 0 | OK | Ground clear controls. | 174 | 24.5 | 572.31
12036 | TIN-INTERP | Interpolated Ground | 76962.36 | 5.11 | 553.6 | 0 | 13.23 | 0 | OK | Ground clear controls. | 174 | 24.5 | 566.83
12037 | TIN-INTERP | Interpolated Ground | 76962.38 | 4.61 | 553.33 | 0 | 24.5 | 0 | OK | Ground clear controls. | 174 | 24.5 | 577.83
12038 | TIN-INTERP | Interpolated Ground | 76981.62 | -5.1 | 553.08 | 0 | 14.13 | 0 | OK | Ground clear controls. | 175 | 41.63 | 567.21
12039 | TIN-INTERP | Interpolated Ground | 76981.65 | -6.6 | 553.22 | 0 | 19.48 | 0 | OK | Ground clear controls. | 175 | 41.63 | 572.7
12040 | TIN-INTERP | Interpolated Ground | 76981.68 | -4.6 | 553.02 | 0 | 25.18 | 0 | OK | Ground clear controls. | 175 | 41.63 | 578.2
12041 | TIN-INTERP | Interpolated Ground | 76981.68 | 5.1 | 553.97 | 0 | 13.24 | 0 | OK | Ground clear controls. | 175 | 41.63 | 567.21
12042 | TIN-INTERP | Interpolated Ground | 76981.76 | 4.6 | 553.89 | 0 | 24.31 | 0 | OK | Ground clear controls. | 175 | 41.63 | 578.2
12043 | TIN-INTERP | Interpolated Ground | 76981.79 | 6.6 | 554.43 | 0 | 18.27 | 0 | OK | Ground clear controls. | 175 | 41.63 | 572.7
12044 | TIN-INTERP | Interpolated Ground | 77021.62 | -5.1 | 543.08 | 0 | 19.19 | 0 | OK | Ground clear controls. | 175 | 41.63 | 562.27
12045 | TIN-INTERP | Interpolated Ground | 77021.65 | -6.6 | 543.62 | 0 | 24.13 | 0 | OK | Ground clear controls. | 175 | 41.63 | 567.75
12046 | TIN-INTERP | Interpolated Ground | 77021.68 | -4.6 | 542.94 | 0 | 30.33 | 0 | OK | Ground clear controls. | 175 | 41.63 | 573.27
12047 | TIN-INTERP | Interpolated Ground | 77021.68 | 5.1 | 539.78 | 0 | 22.48 | 0 | OK | Ground clear controls. | 175 | 41.63 | 562.26
12048 | TIN-INTERP | Interpolated Ground | 77021.76 | 4.6 | 539.87 | 0 | 33.42 | 0 | OK | Ground clear controls. | 175 | 41.63 | 573.29
12049 | TIN-INTERP | Interpolated Ground | 77021.79 | 6.6 | 539.52 | 0 | 28.22 | 0 | OK | Ground clear controls. | 175 | 41.63 | 567.74
12050 | TIN-INTERP | Interpolated Ground | 77061.62 | -5.1 | 529.53 | 0 | 28.65 | 0 | OK | Ground clear controls. | 175 | 41.63 | 558.18
12051 | TIN-INTERP | Interpolated Ground | 77061.65 | -6.6 | 529.56 | 0 | 34.09 | 0 | OK | Ground clear controls. | 175 | 41.63 | 563.65
12052 | TIN-INTERP | Interpolated Ground | 77061.68 | -4.6 | 529.45 | 0 | 39.75 | 0 | OK | Ground clear controls. | 175 | 41.63 | 569.2
12053 | TIN-INTERP | Interpolated Ground | 77061.68 | 5.1 | 527.49 | 0 | 30.67 | 0 | OK | Ground clear controls. | 175 | 41.63 | 558.16
12054 | TIN-INTERP | Interpolated Ground | 77061.76 | 4.6 | 527.57 | 0 | 41.63 | 0 | OK | Ground clear controls. | 175 | 41.63 | 569.2
12055 | TIN-INTERP | Interpolated Ground | 77061.79 | 6.6 | 527.11 | 0 | 36.54 | 0 | OK | Ground clear controls. | 175 | 36.54 | 563.65
12056 | TIN-INTERP | Interpolated Ground | 77101.62 | -5.1 | 532.06 | 0 | 22.87 | 0 | OK | Ground clear controls. | 175 | 33.76 | 554.93
12057 | TIN-INTERP | Interpolated Ground | 77101.65 | -6.6 | 531.67 | 0 | 28.74 | 0 | OK | Ground clear controls. | 175 | 33.76 | 560.41
12058 | TIN-INTERP | Interpolated Ground | 77101.68 | -4.6 | 532.19 | 0 | 33.76 | 0 | OK | Ground clear controls. | 175 | 33.76 | 565.95
12059 | TIN-INTERP | Interpolated Ground | 77101.68 | 5.1 | 535.09 | 0 | 19.82 | 0 | OK | Ground clear controls. | 175 | 31.45 | 554.91
12060 | TIN-INTERP | Interpolated Ground | 77101.76 | 4.6 | 534.99 | 0 | 30.96 | 0 | OK | Ground clear controls. | 175 | 31.45 | 565.95
12061 | TIN-INTERP | Interpolated Ground | 77101.79 | 6.6 | 535.62 | 0 | 24.78 | 0 | OK | Ground clear controls. | 175 | 31.45 | 560.4
12062 | TIN-INTERP | Interpolated Ground | 77141.62 | -5.1 | 531.76 | 0 | 20.78 | 0 | OK | Ground clear controls. | 175 | 31.45 | 552.54
12063 | TIN-INTERP | Interpolated Ground | 77141.65 | -6.6 | 530.79 | 0 | 27.24 | 0 | OK | Ground clear controls. | 175 | 31.45 | 558.03
12064 | TIN-INTERP | Interpolated Ground | 77141.68 | -4.6 | 532.1 | 0 | 31.45 | 0 | OK | Ground clear controls. | 175 | 31.45 | 563.55
12065 | TIN-INTERP | Interpolated Ground | 77141.68 | 5.1 | 535.38 | 0 | 17.14 | 0 | OK | Ground clear controls. | 175 | 28.53 | 552.52
12066 | TIN-INTERP | Interpolated Ground | 77141.76 | 4.6 | 535.02 | 0 | 28.53 | 0 | OK | Ground clear controls. | 175 | 28.53 | 563.55
12067 | TIN-INTERP | Interpolated Ground | 77141.79 | 6.6 | 536.6 | 0 | 21.41 | 0 | OK | Ground clear controls. | 175 | 26.02 | 558.01
12068 | TIN-INTERP | Interpolated Ground | 77181.62 | -5.11 | 535.93 | 0 | 15.06 | 0 | OK | Ground clear controls. | 175 | 26.02 | 550.99
12069 | TIN-INTERP | Interpolated Ground | 77181.65 | -6.61 | 535.61 | 0 | 20.87 | 0 | OK | Ground clear controls. | 175 | 26.02 | 556.48
12070 | TIN-INTERP | Interpolated Ground | 77181.68 | -4.61 | 535.97 | 0 | 26.02 | 0 | OK | Ground clear controls. | 175 | 26.02 | 561.99
12071 | TIN-INTERP | Interpolated Ground | 77181.68 | 5.09 | 536.02 | 0 | 14.97 | 0 | OK | Ground clear controls. | 175 | 25.9 | 550.99
12072 | TIN-INTERP | Interpolated Ground | 77181.76 | 4.59 | 536.09 | 0 | 25.9 | 0 | OK | Ground clear controls. | 175 | 25.9 | 561.99
12073 | TIN-INTERP | Interpolated Ground | 77181.79 | 6.59 | 535.28 | 0 | 21.2 | 0 | OK | Ground clear controls. | 175 | 21.2 | 556.48
12074 | TIN-INTERP | Interpolated Ground | 77189.45 | -5.11 | 536.6 | 0 | 14.19 | 0 | OK | Ground clear controls. | 176 | 53.16 | 550.79
12075 | TIN-INTERP | Interpolated Ground | 77189.48 | 5.09 | 535.46 | 0 | 15.33 | 0 | OK | Ground clear controls. | 176 | 53.16 | 550.79
12076 | TIN-INTERP | Interpolated Ground | 77189.5 | 4.59 | 535.68 | 0 | 26.11 | 0 | OK | Ground clear controls. | 176 | 53.16 | 561.79
12077 | TIN-INTERP | Interpolated Ground | 77189.51 | -4.61 | 536.61 | 0 | 25.17 | 0 | OK | Ground clear controls. | 176 | 53.16 | 561.78
12078 | TIN-INTERP | Interpolated Ground | 77189.52 | -6.61 | 536.52 | 0 | 19.76 | 0 | OK | Ground clear controls. | 176 | 53.16 | 556.28
12079 | TIN-INTERP | Interpolated Ground | 77189.55 | 6.59 | 534.86 | 0 | 21.42 | 0 | OK | Ground clear controls. | 176 | 53.16 | 556.28
12080 | TIN-INTERP | Interpolated Ground | 77229.45 | -5.1 | 528.69 | 0 | 15.37 | 0 | OK | Ground clear controls. | 176 | 53.16 | 544.06
12081 | TIN-INTERP | Interpolated Ground | 77229.48 | 5.1 | 526.01 | 0 | 18.04 | 0 | OK | Ground clear controls. | 176 | 53.16 | 544.05
12082 | TIN-INTERP | Interpolated Ground | 77229.5 | 4.6 | 526.19 | 0 | 28.9 | 0 | OK | Ground clear controls. | 176 | 53.16 | 555.09
12083 | TIN-INTERP | Interpolated Ground | 77229.51 | -4.6 | 528.59 | 0 | 26.5 | 0 | OK | Ground clear controls. | 176 | 53.16 | 555.09
12084 | TIN-INTERP | Interpolated Ground | 77229.52 | -6.6 | 528.89 | 0 | 20.66 | 0 | OK | Ground clear controls. | 176 | 53.16 | 549.55
12085 | TIN-INTERP | Interpolated Ground | 77229.55 | 6.6 | 525.55 | 0 | 24 | 0 | OK | Ground clear controls. | 176 | 53.16 | 549.55
12086 | TIN-INTERP | Interpolated Ground | 77269.45 | -5.09 | 515.51 | 0 | 22.7 | 0 | OK | Ground clear controls. | 176 | 53.16 | 538.21
12087 | TIN-INTERP | Interpolated Ground | 77269.48 | 5.11 | 516.79 | 0 | 21.41 | 0 | OK | Ground clear controls. | 176 | 53.16 | 538.2
12088 | TIN-INTERP | Interpolated Ground | 77269.5 | 4.61 | 516.78 | 0 | 32.48 | 0 | OK | Ground clear controls. | 176 | 53.16 | 549.26
12089 | TIN-INTERP | Interpolated Ground | 77269.51 | -4.59 | 515.55 | 0 | 33.7 | 0 | OK | Ground clear controls. | 176 | 53.16 | 549.25
12090 | TIN-INTERP | Interpolated Ground | 77269.52 | -6.59 | 515.34 | 0 | 28.36 | 0 | OK | Ground clear controls. | 176 | 53.16 | 543.7
12091 | TIN-INTERP | Interpolated Ground | 77269.55 | 6.61 | 516.84 | 0 | 26.86 | 0 | OK | Ground clear controls. | 176 | 53.16 | 543.7
12092 | TIN-INTERP | Interpolated Ground | 77309.45 | -5.08 | 500.4 | 0 | 32.83 | 0 | OK | Ground clear controls. | 176 | 53.16 | 533.23
12093 | TIN-INTERP | Interpolated Ground | 77309.48 | 5.12 | 498.81 | 0 | 34.4 | 0 | OK | Ground clear controls. | 176 | 53.16 | 533.21
12094 | TIN-INTERP | Interpolated Ground | 77309.5 | 4.62 | 498.75 | 0 | 45.53 | 0 | OK | Ground clear controls. | 176 | 53.16 | 544.28
12095 | TIN-INTERP | Interpolated Ground | 77309.51 | -4.58 | 500.32 | 0 | 43.95 | 0 | OK | Ground clear controls. | 176 | 53.16 | 544.27
12096 | TIN-INTERP | Interpolated Ground | 77309.52 | -6.58 | 500.86 | 0 | 37.86 | 0 | OK | Ground clear controls. | 176 | 53.16 | 538.72
12097 | TIN-INTERP | Interpolated Ground | 77309.55 | 6.62 | 498.88 | 0 | 39.84 | 0 | OK | Ground clear controls. | 176 | 53.16 | 538.72
12098 | TIN-INTERP | Interpolated Ground | 77349.45 | -5.07 | 486.83 | 0 | 42.29 | 0 | OK | Ground clear controls. | 176 | 53.16 | 529.12
12099 | TIN-INTERP | Interpolated Ground | 77349.48 | 5.13 | 492.65 | 0 | 36.45 | 0 | OK | Ground clear controls. | 176 | 53.16 | 529.1
12100 | TIN-INTERP | Interpolated Ground | 77349.5 | 4.63 | 492.38 | 0 | 47.78 | 0 | OK | Ground clear controls. | 176 | 53.16 | 540.16
12101 | TIN-INTERP | Interpolated Ground | 77349.51 | -4.57 | 486.98 | 0 | 53.16 | 0 | OK | Ground clear controls. | 176 | 53.16 | 540.14
12102 | TIN-INTERP | Interpolated Ground | 77349.52 | -6.57 | 486.76 | 0 | 47.84 | 0 | OK | Ground clear controls. | 176 | 47.84 | 534.6
12103 | TIN-INTERP | Interpolated Ground | 77349.55 | 6.63 | 493.49 | 0 | 41.11 | 0 | OK | Ground clear controls. | 176 | 41.78 | 534.6
12104 | TIN-INTERP | Interpolated Ground | 77389.45 | -5.06 | 494.89 | 0 | 30.97 | 0 | OK | Ground clear controls. | 176 | 41.78 | 525.86
12105 | TIN-INTERP | Interpolated Ground | 77389.48 | 5.14 | 498.48 | 0 | 27.36 | 0 | OK | Ground clear controls. | 176 | 41.78 | 525.84
12106 | TIN-INTERP | Interpolated Ground | 77389.5 | 4.64 | 498.33 | 0 | 38.56 | 0 | OK | Ground clear controls. | 176 | 41.78 | 536.89
12107 | TIN-INTERP | Interpolated Ground | 77389.51 | -4.56 | 495.1 | 0 | 41.78 | 0 | OK | Ground clear controls. | 176 | 41.78 | 536.88
12108 | TIN-INTERP | Interpolated Ground | 77389.52 | -6.56 | 494.26 | 0 | 37.1 | 0 | OK | Ground clear controls. | 176 | 37.1 | 531.36
12109 | TIN-INTERP | Interpolated Ground | 77389.55 | 6.64 | 498.84 | 0 | 32.51 | 0 | OK | Ground clear controls. | 176 | 32.51 | 531.35
12110 | TIN-INTERP | Interpolated Ground | 77429.45 | -5.06 | 507.51 | 0 | 15.95 | 0 | OK | Ground clear controls. | 176 | 26.85 | 523.46
12111 | TIN-INTERP | Interpolated Ground | 77429.48 | 5.14 | 508.61 | 0 | 14.85 | 0 | OK | Ground clear controls. | 176 | 26.85 | 523.46
12112 | TIN-INTERP | Interpolated Ground | 77429.5 | 4.64 | 508.47 | 0 | 26 | 0 | OK | Ground clear controls. | 176 | 26.85 | 534.47
12113 | TIN-INTERP | Interpolated Ground | 77429.51 | -4.56 | 507.61 | 0 | 26.85 | 0 | OK | Ground clear controls. | 176 | 26.85 | 534.46
12114 | TIN-INTERP | Interpolated Ground | 77429.52 | -6.56 | 507.37 | 0 | 21.59 | 0 | OK | Ground clear controls. | 176 | 21.59 | 528.96
12115 | TIN-INTERP | Interpolated Ground | 77429.55 | 6.64 | 508.87 | 0 | 20.09 | 0 | OK | Ground clear controls. | 176 | 20.09 | 528.96
12116 | TIN-INTERP | Interpolated Ground | 77433.09 | 6.65 | 509.25 | 0 | 19.54 | 0 | OK | Ground clear controls. | 177 | 56.46 | 528.79
12117 | TIN-INTERP | Interpolated Ground | 77433.11 | -6.55 | 508.41 | 0 | 20.38 | 0 | OK | Ground clear controls. | 177 | 56.46 | 528.79
12118 | TIN-INTERP | Interpolated Ground | 77433.12 | -4.56 | 508.72 | 0 | 25.57 | 0 | OK | Ground clear controls. | 177 | 56.46 | 534.29
12119 | TIN-INTERP | Interpolated Ground | 77433.13 | 4.64 | 509.12 | 0 | 25.16 | 0 | OK | Ground clear controls. | 177 | 56.46 | 534.28
12120 | TIN-INTERP | Interpolated Ground | 77433.21 | 5.15 | 509.15 | 0 | 14.13 | 0 | OK | Ground clear controls. | 177 | 56.46 | 523.28
12121 | TIN-INTERP | Interpolated Ground | 77433.27 | -5.05 | 508.65 | 0 | 14.63 | 0 | OK | Ground clear controls. | 177 | 56.46 | 523.28
12122 | TIN-INTERP | Interpolated Ground | 77473.08 | 6.64 | 498.05 | 0 | 22.89 | 0 | OK | Ground clear controls. | 177 | 56.46 | 520.94
12123 | TIN-INTERP | Interpolated Ground | 77473.12 | -6.56 | 496 | 0 | 24.96 | 0 | OK | Ground clear controls. | 177 | 56.46 | 520.96
12124 | TIN-INTERP | Interpolated Ground | 77473.12 | -4.56 | 496.63 | 0 | 29.89 | 0 | OK | Ground clear controls. | 177 | 56.46 | 526.52
12125 | TIN-INTERP | Interpolated Ground | 77473.13 | 4.64 | 498.02 | 0 | 28.51 | 0 | OK | Ground clear controls. | 177 | 56.46 | 526.53
12126 | TIN-INTERP | Interpolated Ground | 77473.21 | 5.14 | 498.01 | 0 | 17.46 | 0 | OK | Ground clear controls. | 177 | 56.46 | 515.47
12127 | TIN-INTERP | Interpolated Ground | 77473.27 | -5.06 | 496.39 | 0 | 19.11 | 0 | OK | Ground clear controls. | 177 | 56.46 | 515.5
12128 | TIN-INTERP | Interpolated Ground | 77513.08 | 6.63 | 480.3 | 0 | 33.69 | 0 | OK | Ground clear controls. | 177 | 56.46 | 513.99
12129 | TIN-INTERP | Interpolated Ground | 77513.12 | -6.57 | 479.68 | 0 | 34.33 | 0 | OK | Ground clear controls. | 177 | 56.46 | 514.01
12130 | TIN-INTERP | Interpolated Ground | 77513.12 | -4.57 | 479.67 | 0 | 39.95 | 0 | OK | Ground clear controls. | 177 | 56.46 | 519.62
12131 | TIN-INTERP | Interpolated Ground | 77513.13 | 4.63 | 480.47 | 0 | 39.18 | 0 | OK | Ground clear controls. | 177 | 56.46 | 519.65
12132 | TIN-INTERP | Interpolated Ground | 77513.21 | 5.13 | 480.43 | 0 | 28.11 | 0 | OK | Ground clear controls. | 177 | 56.46 | 508.54
12133 | TIN-INTERP | Interpolated Ground | 77513.27 | -5.07 | 479.6 | 0 | 29.01 | 0 | OK | Ground clear controls. | 177 | 56.46 | 508.61
12134 | TIN-INTERP | Interpolated Ground | 77553.08 | 6.62 | 462.24 | 0 | 45.67 | 0 | OK | Ground clear controls. | 177 | 56.46 | 507.91
12135 | TIN-INTERP | Interpolated Ground | 77553.12 | -6.58 | 456.72 | 0 | 51.22 | 0 | OK | Ground clear controls. | 177 | 56.46 | 507.94
12136 | TIN-INTERP | Interpolated Ground | 77553.12 | -4.58 | 457.14 | 0 | 56.46 | 0 | OK | Ground clear controls. | 177 | 56.46 | 513.6
12137 | TIN-INTERP | Interpolated Ground | 77553.13 | 4.62 | 461.46 | 0 | 52.18 | 0 | OK | Ground clear controls. | 177 | 52.18 | 513.64
12138 | TIN-INTERP | Interpolated Ground | 77553.21 | 5.12 | 461.7 | 0 | 40.79 | 0 | OK | Ground clear controls. | 177 | 51.01 | 502.49
12139 | TIN-INTERP | Interpolated Ground | 77553.27 | -5.08 | 457.04 | 0 | 45.55 | 0 | OK | Ground clear controls. | 177 | 51.01 | 502.59
12140 | TIN-INTERP | Interpolated Ground | 77593.08 | 6.61 | 463.03 | 0 | 39.7 | 0 | OK | Ground clear controls. | 177 | 51.01 | 502.73
12141 | TIN-INTERP | Interpolated Ground | 77593.12 | -6.59 | 459.3 | 0 | 43.46 | 0 | OK | Ground clear controls. | 177 | 51.01 | 502.76
12142 | TIN-INTERP | Interpolated Ground | 77593.12 | -4.59 | 459.77 | 0 | 48.67 | 0 | OK | Ground clear controls. | 177 | 51.01 | 508.44
12143 | TIN-INTERP | Interpolated Ground | 77593.13 | 4.61 | 462.81 | 0 | 45.69 | 0 | OK | Ground clear controls. | 177 | 51.01 | 508.5
12144 | TIN-INTERP | Interpolated Ground | 77593.21 | 5.11 | 462.86 | 0 | 34.46 | 0 | OK | Ground clear controls. | 177 | 51.01 | 497.32
12145 | TIN-INTERP | Interpolated Ground | 77593.27 | -5.09 | 459.67 | 0 | 37.76 | 0 | OK | Ground clear controls. | 177 | 51.01 | 497.43
12146 | TIN-INTERP | Interpolated Ground | 77633.08 | 6.6 | 474.81 | 0 | 23.61 | 0 | OK | Ground clear controls. | 177 | 51.01 | 498.42
12147 | TIN-INTERP | Interpolated Ground | 77633.12 | -6.6 | 469.71 | 0 | 28.76 | 0 | OK | Ground clear controls. | 177 | 51.01 | 498.47
12148 | TIN-INTERP | Interpolated Ground | 77633.12 | -4.6 | 470.54 | 0 | 33.62 | 0 | OK | Ground clear controls. | 177 | 51.01 | 504.16
12149 | TIN-INTERP | Interpolated Ground | 77633.13 | 4.6 | 474.01 | 0 | 30.2 | 0 | OK | Ground clear controls. | 177 | 51.01 | 504.21
12150 | TIN-INTERP | Interpolated Ground | 77633.21 | 5.1 | 474.24 | 0 | 18.78 | 0 | OK | Ground clear controls. | 177 | 51.01 | 493.02
12151 | TIN-INTERP | Interpolated Ground | 77633.27 | -5.1 | 470.34 | 0 | 22.8 | 0 | OK | Ground clear controls. | 177 | 51.01 | 493.14
12152 | TIN-INTERP | Interpolated Ground | 77673.08 | 6.59 | 468.88 | 0 | 26.11 | 0 | OK | Ground clear controls. | 177 | 51.01 | 494.99
12153 | TIN-INTERP | Interpolated Ground | 77673.12 | -6.61 | 465.52 | 0 | 29.52 | 0 | OK | Ground clear controls. | 177 | 51.01 | 495.04
12154 | TIN-INTERP | Interpolated Ground | 77673.12 | -4.61 | 465.94 | 0 | 34.8 | 0 | OK | Ground clear controls. | 177 | 51.01 | 500.74
12155 | TIN-INTERP | Interpolated Ground | 77673.13 | 4.59 | 468.32 | 0 | 32.47 | 0 | OK | Ground clear controls. | 177 | 51.01 | 500.79
12156 | TIN-INTERP | Interpolated Ground | 77673.21 | 5.09 | 468.42 | 0 | 21.18 | 0 | OK | Ground clear controls. | 177 | 51.01 | 489.6
12157 | TIN-INTERP | Interpolated Ground | 77673.27 | -5.11 | 465.76 | 0 | 23.97 | 0 | OK | Ground clear controls. | 177 | 51.01 | 489.73
12158 | TIN-INTERP | Interpolated Ground | 77713.08 | 6.58 | 453.32 | 0 | 39.13 | 0 | OK | Ground clear controls. | 177 | 51.01 | 492.45
12159 | TIN-INTERP | Interpolated Ground | 77713.12 | -6.62 | 454.44 | 0 | 38.06 | 0 | OK | Ground clear controls. | 177 | 51.01 | 492.5
12160 | TIN-INTERP | Interpolated Ground | 77713.12 | -4.62 | 454.31 | 0 | 43.87 | 0 | OK | Ground clear controls. | 177 | 51.01 | 498.18
12161 | TIN-INTERP | Interpolated Ground | 77713.13 | 4.58 | 453.44 | 0 | 44.8 | 0 | OK | Ground clear controls. | 177 | 51.01 | 498.24
12162 | TIN-INTERP | Interpolated Ground | 77713.21 | 5.08 | 453.34 | 0 | 33.71 | 0 | OK | Ground clear controls. | 177 | 51.01 | 487.05
12163 | TIN-INTERP | Interpolated Ground | 77713.27 | -5.12 | 454.29 | 0 | 32.89 | 0 | OK | Ground clear controls. | 177 | 51.01 | 487.18
12164 | TIN-INTERP | Interpolated Ground | 77753.08 | 6.57 | 447.26 | 0 | 43.52 | 0 | OK | Ground clear controls. | 177 | 51.01 | 490.78
12165 | TIN-INTERP | Interpolated Ground | 77753.12 | -6.63 | 446.59 | 0 | 44.23 | 0 | OK | Ground clear controls. | 177 | 51.01 | 490.82
12166 | TIN-INTERP | Interpolated Ground | 77753.12 | -4.63 | 445.48 | 0 | 51.01 | 0 | OK | Ground clear controls. | 177 | 51.01 | 496.49
12167 | TIN-INTERP | Interpolated Ground | 77753.13 | 4.57 | 446.14 | 0 | 50.41 | 0 | OK | Ground clear controls. | 177 | 50.41 | 496.55
12168 | TIN-INTERP | Interpolated Ground | 77753.21 | 5.07 | 446.47 | 0 | 38.9 | 0 | OK | Ground clear controls. | 177 | 39.8 | 485.37
12169 | TIN-INTERP | Interpolated Ground | 77753.27 | -5.13 | 445.69 | 0 | 39.8 | 0 | OK | Ground clear controls. | 177 | 39.8 | 485.49
12170 | TIN-INTERP | Interpolated Ground | 77793.08 | 6.56 | 458.08 | 0 | 31.9 | 0 | OK | Ground clear controls. | 177 | 39.01 | 489.98
12171 | TIN-INTERP | Interpolated Ground | 77793.12 | -6.64 | 456.52 | 0 | 33.5 | 0 | OK | Ground clear controls. | 177 | 39.01 | 490.02
12172 | TIN-INTERP | Interpolated Ground | 77793.12 | -4.64 | 456.65 | 0 | 39.01 | 0 | OK | Ground clear controls. | 177 | 39.01 | 495.66
12173 | TIN-INTERP | Interpolated Ground | 77793.13 | 4.56 | 457.76 | 0 | 37.95 | 0 | OK | Ground clear controls. | 177 | 37.95 | 495.71
12174 | TIN-INTERP | Interpolated Ground | 77793.21 | 5.06 | 457.87 | 0 | 26.69 | 0 | OK | Ground clear controls. | 177 | 34.75 | 484.56
12175 | TIN-INTERP | Interpolated Ground | 77793.27 | -5.14 | 456.67 | 0 | 27.98 | 0 | OK | Ground clear controls. | 177 | 34.75 | 484.65
12176 | TIN-INTERP | Interpolated Ground | 77833.08 | 6.55 | 469.06 | 0 | 21 | 0 | OK | Ground clear controls. | 177 | 34.75 | 490.06
12177 | TIN-INTERP | Interpolated Ground | 77833.12 | -6.65 | 467.9 | 0 | 22.19 | 0 | OK | Ground clear controls. | 177 | 34.75 | 490.09
12178 | TIN-INTERP | Interpolated Ground | 77833.12 | -4.65 | 468.05 | 0 | 27.65 | 0 | OK | Ground clear controls. | 177 | 34.75 | 495.7
12179 | TIN-INTERP | Interpolated Ground | 77833.13 | 4.55 | 468.84 | 0 | 26.89 | 0 | OK | Ground clear controls. | 177 | 34.75 | 495.73
12180 | TIN-INTERP | Interpolated Ground | 77833.21 | 5.05 | 468.88 | 0 | 15.74 | 0 | OK | Ground clear controls. | 177 | 34.75 | 484.62
12181 | TIN-INTERP | Interpolated Ground | 77833.27 | -5.15 | 467.99 | 0 | 16.71 | 0 | OK | Ground clear controls. | 177 | 34.75 | 484.7
12182 | TIN-INTERP | Interpolated Ground | 77873.08 | 6.54 | 462.29 | 0 | 28.73 | 0 | OK | Ground clear controls. | 177 | 34.75 | 491.02
12183 | TIN-INTERP | Interpolated Ground | 77873.12 | -6.65 | 461.82 | 0 | 29.22 | 0 | OK | Ground clear controls. | 177 | 34.75 | 491.04
12184 | TIN-INTERP | Interpolated Ground | 77873.12 | -4.65 | 461.83 | 0 | 34.75 | 0 | OK | Ground clear controls. | 177 | 34.75 | 496.58
12185 | TIN-INTERP | Interpolated Ground | 77873.13 | 4.55 | 462.15 | 0 | 34.46 | 0 | OK | Ground clear controls. | 177 | 34.46 | 496.61
12186 | TIN-INTERP | Interpolated Ground | 77873.21 | 5.05 | 462.17 | 0 | 23.38 | 0 | OK | Ground clear controls. | 177 | 23.7 | 485.55
12187 | TIN-INTERP | Interpolated Ground | 77873.27 | -5.15 | 461.89 | 0 | 23.7 | 0 | OK | Ground clear controls. | 177 | 23.7 | 485.59
12188 | TIN-INTERP | Interpolated Ground | 77906.81 | 4.54 | 459.33 | 0 | 38.69 | 0 | OK | Ground clear controls. | 178 | 60.54 | 498.02
12189 | TIN-INTERP | Interpolated Ground | 77906.82 | -5.16 | 458.25 | 0 | 28.76 | 0 | OK | Ground clear controls. | 178 | 60.54 | 487.01
12190 | TIN-INTERP | Interpolated Ground | 77906.82 | -6.66 | 457.96 | 0 | 34.54 | 0 | OK | Ground clear controls. | 178 | 60.54 | 492.5
12191 | TIN-INTERP | Interpolated Ground | 77906.86 | -4.66 | 458.29 | 0 | 39.71 | 0 | OK | Ground clear controls. | 178 | 60.54 | 498
12192 | TIN-INTERP | Interpolated Ground | 77906.93 | 6.54 | 459.38 | 0 | 33.13 | 0 | OK | Ground clear controls. | 178 | 60.54 | 492.51
12193 | TIN-INTERP | Interpolated Ground | 77906.96 | 5.04 | 459.37 | 0 | 27.63 | 0 | OK | Ground clear controls. | 178 | 60.54 | 487
12194 | TIN-INTERP | Interpolated Ground | 77946.81 | 4.55 | 451.2 | 0 | 42.55 | 0 | OK | Ground clear controls. | 178 | 60.54 | 493.75
12195 | TIN-INTERP | Interpolated Ground | 77946.82 | -5.15 | 455.22 | 0 | 27.52 | 0 | OK | Ground clear controls. | 178 | 60.54 | 482.74
12196 | TIN-INTERP | Interpolated Ground | 77946.82 | -6.65 | 455.62 | 0 | 32.58 | 0 | OK | Ground clear controls. | 178 | 60.54 | 488.2
12197 | TIN-INTERP | Interpolated Ground | 77946.86 | -4.65 | 455.04 | 0 | 38.72 | 0 | OK | Ground clear controls. | 178 | 60.54 | 493.76
12198 | TIN-INTERP | Interpolated Ground | 77946.93 | 6.55 | 450.17 | 0 | 38.01 | 0 | OK | Ground clear controls. | 178 | 60.54 | 488.18
12199 | TIN-INTERP | Interpolated Ground | 77946.96 | 5.05 | 450.93 | 0 | 31.79 | 0 | OK | Ground clear controls. | 178 | 60.54 | 482.72
12200 | TIN-INTERP | Interpolated Ground | 77986.81 | 4.57 | 448.76 | 0 | 41.6 | 0 | OK | Ground clear controls. | 178 | 60.54 | 490.36
12201 | TIN-INTERP | Interpolated Ground | 77986.82 | -5.13 | 447.78 | 0 | 31.58 | 0 | OK | Ground clear controls. | 178 | 60.54 | 479.36
12202 | TIN-INTERP | Interpolated Ground | 77986.82 | -6.63 | 447.58 | 0 | 37.19 | 0 | OK | Ground clear controls. | 178 | 60.54 | 484.77
12203 | TIN-INTERP | Interpolated Ground | 77986.86 | -4.63 | 447.84 | 0 | 42.55 | 0 | OK | Ground clear controls. | 178 | 60.54 | 490.39
12204 | TIN-INTERP | Interpolated Ground | 77986.93 | 6.57 | 448.69 | 0 | 36.05 | 0 | OK | Ground clear controls. | 178 | 60.54 | 484.74
12205 | TIN-INTERP | Interpolated Ground | 77986.96 | 5.07 | 448.67 | 0 | 30.66 | 0 | OK | Ground clear controls. | 178 | 60.54 | 479.33
12206 | TIN-INTERP | Interpolated Ground | 78026.81 | 4.58 | 427.29 | 0 | 60.54 | 0 | OK | Ground clear controls. | 178 | 60.54 | 487.83
12207 | TIN-INTERP | Interpolated Ground | 78026.82 | -5.12 | 428.44 | 0 | 48.41 | 0 | OK | Ground clear controls. | 178 | 59.39 | 476.85
12208 | TIN-INTERP | Interpolated Ground | 78026.82 | -6.62 | 428.21 | 0 | 54.02 | 0 | OK | Ground clear controls. | 178 | 59.39 | 482.23
12209 | TIN-INTERP | Interpolated Ground | 78026.86 | -4.62 | 428.5 | 0 | 59.39 | 0 | OK | Ground clear controls. | 178 | 59.39 | 487.89
12210 | TIN-INTERP | Interpolated Ground | 78026.93 | 6.58 | 427.18 | 0 | 55 | 0 | OK | Ground clear controls. | 178 | 55 | 482.18
12211 | TIN-INTERP | Interpolated Ground | 78026.96 | 5.08 | 427.28 | 0 | 49.52 | 0 | OK | Ground clear controls. | 178 | 51.65 | 476.8
12212 | TIN-INTERP | Interpolated Ground | 78066.81 | 4.59 | 434.84 | 0 | 51.35 | 0 | OK | Ground clear controls. | 178 | 51.65 | 486.19
12213 | TIN-INTERP | Interpolated Ground | 78066.82 | -5.11 | 434.62 | 0 | 40.6 | 0 | OK | Ground clear controls. | 178 | 51.65 | 475.22
12214 | TIN-INTERP | Interpolated Ground | 78066.82 | -6.61 | 434.63 | 0 | 45.94 | 0 | OK | Ground clear controls. | 178 | 51.65 | 480.57
12215 | TIN-INTERP | Interpolated Ground | 78066.86 | -4.61 | 434.61 | 0 | 51.65 | 0 | OK | Ground clear controls. | 178 | 51.65 | 486.26
12216 | TIN-INTERP | Interpolated Ground | 78066.93 | 6.59 | 434.92 | 0 | 45.6 | 0 | OK | Ground clear controls. | 178 | 48.92 | 480.52
12217 | TIN-INTERP | Interpolated Ground | 78066.96 | 5.09 | 434.88 | 0 | 40.28 | 0 | OK | Ground clear controls. | 178 | 48.92 | 475.16
12218 | TIN-INTERP | Interpolated Ground | 78106.81 | 4.61 | 437.06 | 0 | 48.37 | 0 | OK | Ground clear controls. | 178 | 48.92 | 485.43
12219 | TIN-INTERP | Interpolated Ground | 78106.82 | -5.09 | 436.57 | 0 | 37.89 | 0 | OK | Ground clear controls. | 178 | 48.92 | 474.46
12220 | TIN-INTERP | Interpolated Ground | 78106.82 | -6.59 | 436.47 | 0 | 43.33 | 0 | OK | Ground clear controls. | 178 | 48.92 | 479.8
12221 | TIN-INTERP | Interpolated Ground | 78106.86 | -4.59 | 436.59 | 0 | 48.92 | 0 | OK | Ground clear controls. | 178 | 48.92 | 485.51
12222 | TIN-INTERP | Interpolated Ground | 78106.93 | 6.61 | 437.57 | 0 | 42.18 | 0 | OK | Ground clear controls. | 178 | 43.22 | 479.75
12223 | TIN-INTERP | Interpolated Ground | 78106.96 | 5.11 | 437.22 | 0 | 37.18 | 0 | OK | Ground clear controls. | 178 | 43.22 | 474.4
12224 | TIN-INTERP | Interpolated Ground | 78146.81 | 4.62 | 443.45 | 0 | 42.09 | 0 | OK | Ground clear controls. | 178 | 43.22 | 485.54
12225 | TIN-INTERP | Interpolated Ground | 78146.82 | -5.08 | 442.32 | 0 | 32.25 | 0 | OK | Ground clear controls. | 178 | 43.22 | 474.57
12226 | TIN-INTERP | Interpolated Ground | 78146.82 | -6.58 | 442.08 | 0 | 37.84 | 0 | OK | Ground clear controls. | 178 | 43.22 | 479.92
12227 | TIN-INTERP | Interpolated Ground | 78146.86 | -4.58 | 442.41 | 0 | 43.22 | 0 | OK | Ground clear controls. | 178 | 43.22 | 485.63
12228 | TIN-INTERP | Interpolated Ground | 78146.93 | 6.62 | 443.78 | 0 | 36.08 | 0 | OK | Ground clear controls. | 178 | 42.61 | 479.86
12229 | TIN-INTERP | Interpolated Ground | 78146.96 | 5.12 | 443.57 | 0 | 30.94 | 0 | OK | Ground clear controls. | 178 | 42.61 | 474.51
12230 | TIN-INTERP | Interpolated Ground | 78186.81 | 4.64 | 448.78 | 0 | 37.75 | 0 | OK | Ground clear controls. | 178 | 42.61 | 486.53
12231 | TIN-INTERP | Interpolated Ground | 78186.82 | -5.06 | 447.76 | 0 | 27.8 | 0 | OK | Ground clear controls. | 178 | 42.61 | 475.56
12232 | TIN-INTERP | Interpolated Ground | 78186.82 | -6.56 | 447.64 | 0 | 33.27 | 0 | OK | Ground clear controls. | 178 | 42.61 | 480.91
12233 | TIN-INTERP | Interpolated Ground | 78186.86 | -4.56 | 447.82 | 0 | 38.79 | 0 | OK | Ground clear controls. | 178 | 42.61 | 486.61
12234 | TIN-INTERP | Interpolated Ground | 78186.93 | 6.64 | 449.03 | 0 | 31.83 | 0 | OK | Ground clear controls. | 178 | 42.61 | 480.86
12235 | TIN-INTERP | Interpolated Ground | 78186.96 | 5.14 | 448.87 | 0 | 26.64 | 0 | OK | Ground clear controls. | 178 | 42.61 | 475.51
12236 | TIN-INTERP | Interpolated Ground | 78226.81 | 4.65 | 460.83 | 0 | 27.56 | 0 | OK | Ground clear controls. | 178 | 42.61 | 488.39
12237 | TIN-INTERP | Interpolated Ground | 78226.82 | -5.05 | 460.35 | 0 | 17.07 | 0 | OK | Ground clear controls. | 178 | 42.61 | 477.42
12238 | TIN-INTERP | Interpolated Ground | 78226.82 | -6.55 | 460.24 | 0 | 22.55 | 0 | OK | Ground clear controls. | 178 | 42.61 | 482.79
12239 | TIN-INTERP | Interpolated Ground | 78226.86 | -4.55 | 460.4 | 0 | 28.06 | 0 | OK | Ground clear controls. | 178 | 42.61 | 488.46
12240 | TIN-INTERP | Interpolated Ground | 78226.93 | 6.65 | 460.85 | 0 | 21.9 | 0 | OK | Ground clear controls. | 178 | 42.61 | 482.75
12241 | TIN-INTERP | Interpolated Ground | 78226.96 | 5.15 | 460.9 | 0 | 16.47 | 0 | OK | Ground clear controls. | 178 | 42.61 | 477.37
12242 | TIN-INTERP | Interpolated Ground | 78266.81 | 4.67 | 461.1 | 0 | 30.02 | 0 | OK | Ground clear controls. | 178 | 42.61 | 491.12
12243 | TIN-INTERP | Interpolated Ground | 78266.82 | -5.04 | 459.25 | 0 | 20.91 | 0 | OK | Ground clear controls. | 178 | 42.61 | 480.16
12244 | TIN-INTERP | Interpolated Ground | 78266.82 | -6.54 | 458.89 | 0 | 26.66 | 0 | OK | Ground clear controls. | 178 | 42.61 | 485.55
12245 | TIN-INTERP | Interpolated Ground | 78266.86 | -4.54 | 459.34 | 0 | 31.86 | 0 | OK | Ground clear controls. | 178 | 42.61 | 491.2
12246 | TIN-INTERP | Interpolated Ground | 78266.93 | 6.66 | 461.27 | 0 | 24.25 | 0 | OK | Ground clear controls. | 178 | 42.61 | 485.52
12247 | TIN-INTERP | Interpolated Ground | 78266.96 | 5.16 | 461.08 | 0 | 19.04 | 0 | OK | Ground clear controls. | 178 | 42.61 | 480.12
12248 | TIN-INTERP | Interpolated Ground | 78306.81 | 4.68 | 456.23 | 0 | 38.52 | 0 | OK | Ground clear controls. | 178 | 42.61 | 494.75
12249 | TIN-INTERP | Interpolated Ground | 78306.82 | -5.02 | 452.11 | 0 | 31.67 | 0 | OK | Ground clear controls. | 178 | 42.61 | 483.78
12250 | TIN-INTERP | Interpolated Ground | 78306.82 | -6.52 | 451.91 | 0 | 37.3 | 0 | OK | Ground clear controls. | 178 | 42.61 | 489.21
12251 | TIN-INTERP | Interpolated Ground | 78306.86 | -4.52 | 452.19 | 0 | 42.61 | 0 | OK | Ground clear controls. | 178 | 42.61 | 494.8
12252 | TIN-INTERP | Interpolated Ground | 78306.93 | 6.68 | 456.93 | 0 | 32.26 | 0 | OK | Ground clear controls. | 178 | 35.72 | 489.19
12253 | TIN-INTERP | Interpolated Ground | 78306.96 | 5.18 | 456.4 | 0 | 27.35 | 0 | OK | Ground clear controls. | 178 | 35.72 | 483.75
12254 | TIN-INTERP | Interpolated Ground | 78346.81 | 4.69 | 464.63 | 0 | 34.61 | 0 | OK | Ground clear controls. | 178 | 35.72 | 499.24
12255 | TIN-INTERP | Interpolated Ground | 78346.82 | -5.01 | 463.44 | 0 | 24.83 | 0 | OK | Ground clear controls. | 178 | 35.72 | 488.27
12256 | TIN-INTERP | Interpolated Ground | 78346.82 | -6.51 | 463.24 | 0 | 30.51 | 0 | OK | Ground clear controls. | 178 | 35.72 | 493.75
12257 | TIN-INTERP | Interpolated Ground | 78346.86 | -4.51 | 463.56 | 0 | 35.72 | 0 | OK | Ground clear controls. | 178 | 35.72 | 499.28
12258 | TIN-INTERP | Interpolated Ground | 78346.93 | 6.69 | 464.47 | 0 | 29.27 | 0 | OK | Ground clear controls. | 178 | 29.27 | 493.74
12259 | TIN-INTERP | Interpolated Ground | 78346.96 | 5.19 | 464.6 | 0 | 23.67 | 0 | OK | Ground clear controls. | 178 | 23.67 | 488.27
12260 | TIN-INTERP | Interpolated Ground | 78357.01 | -4.5 | 464.94 | 0 | 35.61 | 0 | OK | Ground clear controls. | 179 | 59.47 | 500.55
12261 | TIN-INTERP | Interpolated Ground | 78357.02 | -6.5 | 464.75 | 0 | 30.29 | 0 | OK | Ground clear controls. | 179 | 59.47 | 495.04
12262 | TIN-INTERP | Interpolated Ground | 78357.02 | -5 | 464.95 | 0 | 24.59 | 0 | OK | Ground clear controls. | 179 | 59.47 | 489.54
12263 | TIN-INTERP | Interpolated Ground | 78357.11 | 5.2 | 465.48 | 0 | 24.07 | 0 | OK | Ground clear controls. | 179 | 59.47 | 489.55
12264 | TIN-INTERP | Interpolated Ground | 78357.12 | 6.7 | 465.59 | 0 | 29.45 | 0 | OK | Ground clear controls. | 179 | 59.47 | 495.04
12265 | TIN-INTERP | Interpolated Ground | 78357.16 | 4.7 | 465.45 | 0 | 35.09 | 0 | OK | Ground clear controls. | 179 | 59.47 | 500.54
12266 | TIN-INTERP | Interpolated Ground | 78396.97 | -6.52 | 447.23 | 0 | 42.09 | 0 | OK | Ground clear controls. | 179 | 59.47 | 489.32
12267 | TIN-INTERP | Interpolated Ground | 78396.98 | -4.52 | 447.58 | 0 | 47.31 | 0 | OK | Ground clear controls. | 179 | 59.47 | 494.89
12268 | TIN-INTERP | Interpolated Ground | 78396.98 | -5.02 | 447.47 | 0 | 36.4 | 0 | OK | Ground clear controls. | 179 | 59.47 | 483.87
12269 | TIN-INTERP | Interpolated Ground | 78397.15 | 5.18 | 449.43 | 0 | 34.44 | 0 | OK | Ground clear controls. | 179 | 59.47 | 483.87
12270 | TIN-INTERP | Interpolated Ground | 78397.18 | 6.68 | 449.95 | 0 | 39.37 | 0 | OK | Ground clear controls. | 179 | 59.47 | 489.32
12271 | TIN-INTERP | Interpolated Ground | 78397.2 | 4.68 | 449.31 | 0 | 45.6 | 0 | OK | Ground clear controls. | 179 | 59.47 | 494.91
12272 | TIN-INTERP | Interpolated Ground | 78436.97 | -6.54 | 437.01 | 0 | 47.49 | 0 | OK | Ground clear controls. | 179 | 59.47 | 484.5
12273 | TIN-INTERP | Interpolated Ground | 78436.98 | -4.54 | 437.54 | 0 | 52.57 | 0 | OK | Ground clear controls. | 179 | 59.47 | 490.11
12274 | TIN-INTERP | Interpolated Ground | 78436.98 | -5.04 | 437.41 | 0 | 41.68 | 0 | OK | Ground clear controls. | 179 | 59.47 | 479.09
12275 | TIN-INTERP | Interpolated Ground | 78437.15 | 5.16 | 439.4 | 0 | 39.69 | 0 | OK | Ground clear controls. | 179 | 59.47 | 479.09
12276 | TIN-INTERP | Interpolated Ground | 78437.18 | 6.66 | 439.8 | 0 | 44.71 | 0 | OK | Ground clear controls. | 179 | 59.47 | 484.51
12277 | TIN-INTERP | Interpolated Ground | 78437.2 | 4.66 | 439.26 | 0 | 50.9 | 0 | OK | Ground clear controls. | 179 | 59.47 | 490.16
12278 | TIN-INTERP | Interpolated Ground | 78476.97 | -6.56 | 428.94 | 0 | 51.65 | 0 | OK | Ground clear controls. | 179 | 59.47 | 480.59
12279 | TIN-INTERP | Interpolated Ground | 78476.98 | -4.56 | 429.76 | 0 | 56.48 | 0 | OK | Ground clear controls. | 179 | 59.47 | 486.24
12280 | TIN-INTERP | Interpolated Ground | 78476.98 | -5.06 | 429.58 | 0 | 45.64 | 0 | OK | Ground clear controls. | 179 | 59.47 | 475.22
12281 | TIN-INTERP | Interpolated Ground | 78477.15 | 5.14 | 431.99 | 0 | 43.22 | 0 | OK | Ground clear controls. | 179 | 59.47 | 475.21
12282 | TIN-INTERP | Interpolated Ground | 78477.18 | 6.64 | 432.61 | 0 | 47.99 | 0 | OK | Ground clear controls. | 179 | 59.47 | 480.6
12283 | TIN-INTERP | Interpolated Ground | 78477.2 | 4.64 | 431.76 | 0 | 54.54 | 0 | OK | Ground clear controls. | 179 | 59.47 | 486.3
12284 | TIN-INTERP | Interpolated Ground | 78516.97 | -6.58 | 428.9 | 0 | 48.69 | 0 | OK | Ground clear controls. | 179 | 59.47 | 477.59
12285 | TIN-INTERP | Interpolated Ground | 78516.98 | -4.57 | 429.58 | 0 | 53.67 | 0 | OK | Ground clear controls. | 179 | 59.47 | 483.25
12286 | TIN-INTERP | Interpolated Ground | 78516.98 | -5.08 | 429.42 | 0 | 42.81 | 0 | OK | Ground clear controls. | 179 | 59.47 | 472.23
12287 | TIN-INTERP | Interpolated Ground | 78517.15 | 5.12 | 432.74 | 0 | 39.48 | 0 | OK | Ground clear controls. | 179 | 59.47 | 472.22
12288 | TIN-INTERP | Interpolated Ground | 78517.18 | 6.62 | 433.14 | 0 | 44.45 | 0 | OK | Ground clear controls. | 179 | 59.47 | 477.59
12289 | TIN-INTERP | Interpolated Ground | 78517.2 | 4.62 | 432.39 | 0 | 50.94 | 0 | OK | Ground clear controls. | 179 | 59.47 | 483.33
12290 | TIN-INTERP | Interpolated Ground | 78556.97 | -6.59 | 449.69 | 0 | 25.79 | 0 | OK | Ground clear controls. | 179 | 59.47 | 475.48
12291 | TIN-INTERP | Interpolated Ground | 78556.98 | -4.59 | 450.5 | 0 | 30.66 | 0 | OK | Ground clear controls. | 179 | 59.47 | 481.16
12292 | TIN-INTERP | Interpolated Ground | 78556.98 | -5.09 | 450.3 | 0 | 19.83 | 0 | OK | Ground clear controls. | 179 | 59.47 | 470.13
12293 | TIN-INTERP | Interpolated Ground | 78557.15 | 5.11 | 454.49 | 0 | 15.63 | 0 | OK | Ground clear controls. | 179 | 59.47 | 470.12
12294 | TIN-INTERP | Interpolated Ground | 78557.18 | 6.61 | 455.26 | 0 | 20.23 | 0 | OK | Ground clear controls. | 179 | 59.47 | 475.49
12295 | TIN-INTERP | Interpolated Ground | 78557.2 | 4.61 | 454.25 | 0 | 27 | 0 | OK | Ground clear controls. | 179 | 59.47 | 481.25
12296 | TIN-INTERP | Interpolated Ground | 78596.97 | -6.61 | 448.87 | 0 | 25.41 | 0 | OK | Ground clear controls. | 179 | 59.47 | 474.28
12297 | TIN-INTERP | Interpolated Ground | 78596.98 | -4.61 | 449.36 | 0 | 30.6 | 0 | OK | Ground clear controls. | 179 | 59.47 | 479.96
12298 | TIN-INTERP | Interpolated Ground | 78596.98 | -5.11 | 449.22 | 0 | 19.71 | 0 | OK | Ground clear controls. | 179 | 59.47 | 468.93
12299 | TIN-INTERP | Interpolated Ground | 78597.15 | 5.09 | 452.88 | 0 | 16.04 | 0 | OK | Ground clear controls. | 179 | 59.47 | 468.92
12300 | TIN-INTERP | Interpolated Ground | 78597.18 | 6.59 | 453.57 | 0 | 20.73 | 0 | OK | Ground clear controls. | 179 | 59.47 | 474.3
12301 | TIN-INTERP | Interpolated Ground | 78597.2 | 4.59 | 452.67 | 0 | 27.38 | 0 | OK | Ground clear controls. | 179 | 59.47 | 480.05
12302 | TIN-INTERP | Interpolated Ground | 78636.97 | -6.63 | 447.76 | 0 | 26.22 | 0 | OK | Ground clear controls. | 179 | 59.47 | 473.98
12303 | TIN-INTERP | Interpolated Ground | 78636.98 | -4.63 | 448.59 | 0 | 31.06 | 0 | OK | Ground clear controls. | 179 | 59.47 | 479.65
12304 | TIN-INTERP | Interpolated Ground | 78636.98 | -5.13 | 448.41 | 0 | 20.21 | 0 | OK | Ground clear controls. | 179 | 59.47 | 468.62
12305 | TIN-INTERP | Interpolated Ground | 78637.15 | 5.07 | 452.74 | 0 | 15.88 | 0 | OK | Ground clear controls. | 179 | 59.47 | 468.62
12306 | TIN-INTERP | Interpolated Ground | 78637.18 | 6.57 | 453.24 | 0 | 20.75 | 0 | OK | Ground clear controls. | 179 | 59.47 | 473.99
12307 | TIN-INTERP | Interpolated Ground | 78637.2 | 4.57 | 452.59 | 0 | 27.13 | 0 | OK | Ground clear controls. | 179 | 59.47 | 479.72
12308 | TIN-INTERP | Interpolated Ground | 78676.97 | -6.65 | 431.21 | 0 | 43.36 | 0 | OK | Ground clear controls. | 179 | 59.47 | 474.57
12309 | TIN-INTERP | Interpolated Ground | 78676.98 | -4.65 | 432.15 | 0 | 48.07 | 0 | OK | Ground clear controls. | 179 | 59.47 | 480.22
12310 | TIN-INTERP | Interpolated Ground | 78676.98 | -5.15 | 431.97 | 0 | 37.23 | 0 | OK | Ground clear controls. | 179 | 59.47 | 469.2
12311 | TIN-INTERP | Interpolated Ground | 78677.15 | 5.05 | 435.04 | 0 | 34.15 | 0 | OK | Ground clear controls. | 179 | 59.47 | 469.19
12312 | TIN-INTERP | Interpolated Ground | 78677.18 | 6.55 | 435.5 | 0 | 39.09 | 0 | OK | Ground clear controls. | 179 | 59.47 | 474.59
12313 | TIN-INTERP | Interpolated Ground | 78677.2 | 4.55 | 434.86 | 0 | 45.44 | 0 | OK | Ground clear controls. | 179 | 59.47 | 480.3
12314 | TIN-INTERP | Interpolated Ground | 78716.97 | -6.67 | 421.77 | 0 | 54.31 | 0 | OK | Ground clear controls. | 179 | 59.47 | 476.08
12315 | TIN-INTERP | Interpolated Ground | 78716.98 | -4.67 | 422.22 | 0 | 59.47 | 0 | OK | Ground clear controls. | 179 | 59.47 | 481.69
12316 | TIN-INTERP | Interpolated Ground | 78716.98 | -5.17 | 422.1 | 0 | 48.58 | 0 | OK | Ground clear controls. | 179 | 57.03 | 470.68
12317 | TIN-INTERP | Interpolated Ground | 78717.15 | 5.03 | 424.86 | 0 | 45.81 | 0 | OK | Ground clear controls. | 179 | 57.03 | 470.67
12318 | TIN-INTERP | Interpolated Ground | 78717.18 | 6.53 | 425.35 | 0 | 50.74 | 0 | OK | Ground clear controls. | 179 | 57.03 | 476.09
12319 | TIN-INTERP | Interpolated Ground | 78717.2 | 4.53 | 424.72 | 0 | 57.03 | 0 | OK | Ground clear controls. | 179 | 57.03 | 481.75
12320 | TIN-INTERP | Interpolated Ground | 78756.97 | -6.68 | 433.49 | 0 | 44.99 | 0 | OK | Ground clear controls. | 179 | 50.48 | 478.48
12321 | TIN-INTERP | Interpolated Ground | 78756.98 | -4.68 | 433.57 | 0 | 50.48 | 0 | OK | Ground clear controls. | 179 | 50.48 | 484.05
12322 | TIN-INTERP | Interpolated Ground | 78756.98 | -5.19 | 433.46 | 0 | 39.57 | 0 | OK | Ground clear controls. | 179 | 46.91 | 473.03
12323 | TIN-INTERP | Interpolated Ground | 78757.15 | 5.01 | 437.35 | 0 | 35.68 | 0 | OK | Ground clear controls. | 179 | 46.91 | 473.03
12324 | TIN-INTERP | Interpolated Ground | 78757.18 | 6.51 | 438.28 | 0 | 40.22 | 0 | OK | Ground clear controls. | 179 | 46.91 | 478.5
12325 | TIN-INTERP | Interpolated Ground | 78757.2 | 4.51 | 437.17 | 0 | 46.91 | 0 | OK | Ground clear controls. | 179 | 46.91 | 484.08
12326 | TIN-INTERP | Interpolated Ground | 78794.02 | -4.7 | 453.38 | 0 | 33.65 | 0 | OK | Ground clear controls. | 180 | 52.33 | 487.03
12327 | TIN-INTERP | Interpolated Ground | 78794.06 | -5.2 | 453.28 | 0 | 22.74 | 0 | OK | Ground clear controls. | 180 | 52.33 | 476.02
12328 | TIN-INTERP | Interpolated Ground | 78794.08 | -6.7 | 452.77 | 0 | 28.75 | 0 | OK | Ground clear controls. | 180 | 52.33 | 481.52
12329 | TIN-INTERP | Interpolated Ground | 78794.12 | 4.5 | 454.76 | 0 | 32.27 | 0 | OK | Ground clear controls. | 180 | 52.33 | 487.03
12330 | TIN-INTERP | Interpolated Ground | 78794.17 | 6.5 | 454.93 | 0 | 26.59 | 0 | OK | Ground clear controls. | 180 | 52.33 | 481.52
12331 | TIN-INTERP | Interpolated Ground | 78794.19 | 5 | 454.76 | 0 | 21.25 | 0 | OK | Ground clear controls. | 180 | 52.33 | 476.01
12332 | TIN-INTERP | Interpolated Ground | 78834.06 | 4.47 | 436.97 | 0 | 40.84 | 0 | OK | Ground clear controls. | 180 | 52.33 | 477.81
12333 | TIN-INTERP | Interpolated Ground | 78834.08 | -4.73 | 436.6 | 0 | 41.16 | 0 | OK | Ground clear controls. | 180 | 52.33 | 477.76
12334 | TIN-INTERP | Interpolated Ground | 78834.09 | 6.47 | 437.62 | 0 | 34.62 | 0 | OK | Ground clear controls. | 180 | 52.33 | 472.24
12335 | TIN-INTERP | Interpolated Ground | 78834.12 | 4.97 | 437.08 | 0 | 29.73 | 0 | OK | Ground clear controls. | 180 | 52.33 | 466.81
12336 | TIN-INTERP | Interpolated Ground | 78834.13 | -5.23 | 436.64 | 0 | 30.14 | 0 | OK | Ground clear controls. | 180 | 52.33 | 466.78
12337 | TIN-INTERP | Interpolated Ground | 78834.16 | -6.73 | 436.71 | 0 | 35.52 | 0 | OK | Ground clear controls. | 180 | 52.33 | 472.23
12338 | TIN-INTERP | Interpolated Ground | 78874.06 | 4.44 | 423.7 | 0 | 45.83 | 0 | OK | Ground clear controls. | 180 | 52.33 | 469.53
12339 | TIN-INTERP | Interpolated Ground | 78874.08 | -4.76 | 423.19 | 0 | 46.25 | 0 | OK | Ground clear controls. | 180 | 52.33 | 469.44
12340 | TIN-INTERP | Interpolated Ground | 78874.09 | 6.44 | 423.89 | 0 | 40.02 | 0 | OK | Ground clear controls. | 180 | 52.33 | 463.91
12341 | TIN-INTERP | Interpolated Ground | 78874.12 | 4.94 | 423.74 | 0 | 34.8 | 0 | OK | Ground clear controls. | 180 | 52.33 | 458.54
12342 | TIN-INTERP | Interpolated Ground | 78874.13 | -5.26 | 423.13 | 0 | 35.34 | 0 | OK | Ground clear controls. | 180 | 52.33 | 458.47
12343 | TIN-INTERP | Interpolated Ground | 78874.16 | -6.76 | 423.1 | 0 | 40.8 | 0 | OK | Ground clear controls. | 180 | 52.33 | 463.9
12344 | TIN-INTERP | Interpolated Ground | 78914.06 | 4.41 | 419.41 | 0 | 42.77 | 0 | OK | Ground clear controls. | 180 | 52.33 | 462.18
12345 | TIN-INTERP | Interpolated Ground | 78914.08 | -4.79 | 418.26 | 0 | 43.8 | 0 | OK | Ground clear controls. | 180 | 52.33 | 462.06
12346 | TIN-INTERP | Interpolated Ground | 78914.09 | 6.41 | 419.65 | 0 | 36.87 | 0 | OK | Ground clear controls. | 180 | 52.33 | 456.52
12347 | TIN-INTERP | Interpolated Ground | 78914.12 | 4.91 | 419.5 | 0 | 31.68 | 0 | OK | Ground clear controls. | 180 | 52.33 | 451.18
12348 | TIN-INTERP | Interpolated Ground | 78914.13 | -5.29 | 418.21 | 0 | 32.88 | 0 | OK | Ground clear controls. | 180 | 52.33 | 451.09
12349 | TIN-INTERP | Interpolated Ground | 78914.16 | -6.79 | 418.05 | 0 | 38.45 | 0 | OK | Ground clear controls. | 180 | 52.33 | 456.5
12350 | TIN-INTERP | Interpolated Ground | 78954.06 | 4.38 | 417.93 | 0 | 37.82 | 0 | OK | Ground clear controls. | 180 | 52.33 | 455.75
12351 | TIN-INTERP | Interpolated Ground | 78954.08 | -4.82 | 417.68 | 0 | 37.92 | 0 | OK | Ground clear controls. | 180 | 52.33 | 455.6
12352 | TIN-INTERP | Interpolated Ground | 78954.09 | 6.38 | 418.11 | 0 | 31.95 | 0 | OK | Ground clear controls. | 180 | 52.33 | 450.06
12353 | TIN-INTERP | Interpolated Ground | 78954.12 | 4.88 | 417.94 | 0 | 26.82 | 0 | OK | Ground clear controls. | 180 | 52.33 | 444.76
12354 | TIN-INTERP | Interpolated Ground | 78954.13 | -5.32 | 417.61 | 0 | 27.03 | 0 | OK | Ground clear controls. | 180 | 52.33 | 444.64
12355 | TIN-INTERP | Interpolated Ground | 78954.16 | -6.82 | 417.59 | 0 | 32.45 | 0 | OK | Ground clear controls. | 180 | 52.33 | 450.04
12356 | TIN-INTERP | Interpolated Ground | 78994.06 | 4.35 | 416.26 | 0 | 33.99 | 0 | OK | Ground clear controls. | 180 | 52.33 | 450.25
12357 | TIN-INTERP | Interpolated Ground | 78994.08 | -4.85 | 415.93 | 0 | 34.16 | 0 | OK | Ground clear controls. | 180 | 52.33 | 450.09
12358 | TIN-INTERP | Interpolated Ground | 78994.09 | 6.35 | 416.44 | 0 | 28.11 | 0 | OK | Ground clear controls. | 180 | 52.33 | 444.55
12359 | TIN-INTERP | Interpolated Ground | 78994.12 | 4.85 | 416.31 | 0 | 22.95 | 0 | OK | Ground clear controls. | 180 | 52.33 | 439.26
12360 | TIN-INTERP | Interpolated Ground | 78994.13 | -5.35 | 415.92 | 0 | 23.21 | 0 | OK | Ground clear controls. | 180 | 52.33 | 439.13
12361 | TIN-INTERP | Interpolated Ground | 78994.16 | -6.85 | 415.82 | 0 | 28.7 | 0 | OK | Ground clear controls. | 180 | 52.33 | 444.52
12362 | TIN-INTERP | Interpolated Ground | 79034.06 | 4.32 | 414 | 0 | 31.67 | 0 | OK | Ground clear controls. | 180 | 52.33 | 445.67
12363 | TIN-INTERP | Interpolated Ground | 79034.08 | -4.88 | 413.89 | 0 | 31.62 | 0 | OK | Ground clear controls. | 180 | 52.33 | 445.51
12364 | TIN-INTERP | Interpolated Ground | 79034.09 | 6.33 | 413.8 | 0 | 26.16 | 0 | OK | Ground clear controls. | 180 | 52.33 | 439.96
12365 | TIN-INTERP | Interpolated Ground | 79034.12 | 4.82 | 413.95 | 0 | 20.72 | 0 | OK | Ground clear controls. | 180 | 52.33 | 434.67
12366 | TIN-INTERP | Interpolated Ground | 79034.13 | -5.38 | 413.83 | 0 | 20.72 | 0 | OK | Ground clear controls. | 180 | 52.33 | 434.55
12367 | TIN-INTERP | Interpolated Ground | 79034.16 | -6.87 | 413.64 | 0 | 26.3 | 0 | OK | Ground clear controls. | 180 | 52.33 | 439.94
12368 | TIN-INTERP | Interpolated Ground | 79074.06 | 4.29 | 394.31 | 0 | 47.69 | 0 | OK | Ground clear controls. | 180 | 52.33 | 442
12369 | TIN-INTERP | Interpolated Ground | 79074.08 | -4.9 | 403.01 | 0 | 38.84 | 0 | OK | Ground clear controls. | 180 | 52.33 | 441.85
12370 | TIN-INTERP | Interpolated Ground | 79074.09 | 6.3 | 393.07 | 0 | 43.23 | 0 | OK | Ground clear controls. | 180 | 52.33 | 436.3
12371 | TIN-INTERP | Interpolated Ground | 79074.12 | 4.79 | 393.98 | 0 | 37.02 | 0 | OK | Ground clear controls. | 180 | 52.33 | 431
12372 | TIN-INTERP | Interpolated Ground | 79074.13 | -5.4 | 403.49 | 0 | 27.4 | 0 | OK | Ground clear controls. | 180 | 52.33 | 430.89
12373 | TIN-INTERP | Interpolated Ground | 79074.16 | -6.9 | 404.55 | 0 | 31.73 | 0 | OK | Ground clear controls. | 180 | 52.33 | 436.28
12374 | TIN-INTERP | Interpolated Ground | 79114.06 | 4.26 | 388.47 | 0 | 50.77 | 0 | OK | Ground clear controls. | 180 | 52.33 | 439.24
12375 | TIN-INTERP | Interpolated Ground | 79114.08 | -4.93 | 392.13 | 0 | 46.98 | 0 | OK | Ground clear controls. | 180 | 52.33 | 439.11
12376 | TIN-INTERP | Interpolated Ground | 79114.09 | 6.27 | 385.58 | 0 | 47.99 | 0 | OK | Ground clear controls. | 180 | 52.33 | 433.57
12377 | TIN-INTERP | Interpolated Ground | 79114.12 | 4.77 | 387.89 | 0 | 40.36 | 0 | OK | Ground clear controls. | 180 | 52.33 | 428.25
12378 | TIN-INTERP | Interpolated Ground | 79114.13 | -5.43 | 392.36 | 0 | 35.79 | 0 | OK | Ground clear controls. | 180 | 52.33 | 428.15
12379 | TIN-INTERP | Interpolated Ground | 79114.16 | -6.93 | 393.44 | 0 | 40.11 | 0 | OK | Ground clear controls. | 180 | 52.33 | 433.55
12380 | TIN-INTERP | Interpolated Ground | 79154.06 | 4.24 | 390.19 | 0 | 47.21 | 0 | OK | Ground clear controls. | 180 | 52.33 | 437.4
12381 | TIN-INTERP | Interpolated Ground | 79154.08 | -4.96 | 384.97 | 0 | 52.33 | 0 | OK | Ground clear controls. | 180 | 52.33 | 437.3
12382 | TIN-INTERP | Interpolated Ground | 79154.09 | 6.24 | 391.31 | 0 | 40.45 | 0 | OK | Ground clear controls. | 180 | 48.13 | 431.76
12383 | TIN-INTERP | Interpolated Ground | 79154.12 | 4.74 | 390.47 | 0 | 35.95 | 0 | OK | Ground clear controls. | 180 | 48.13 | 426.42
12384 | TIN-INTERP | Interpolated Ground | 79154.13 | -5.46 | 384.77 | 0 | 41.56 | 0 | OK | Ground clear controls. | 180 | 48.13 | 426.33
12385 | TIN-INTERP | Interpolated Ground | 79154.16 | -6.96 | 383.62 | 0 | 48.13 | 0 | OK | Ground clear controls. | 180 | 48.13 | 431.75
12386 | TIN-INTERP | Interpolated Ground | 79194.06 | 4.21 | 398.9 | 0 | 37.58 | 0 | OK | Ground clear controls. | 180 | 44.11 | 436.48
12387 | TIN-INTERP | Interpolated Ground | 79194.08 | -4.99 | 392.3 | 0 | 44.11 | 0 | OK | Ground clear controls. | 180 | 44.11 | 436.41
12388 | TIN-INTERP | Interpolated Ground | 79194.09 | 6.21 | 400.31 | 0 | 30.57 | 0 | OK | Ground clear controls. | 180 | 41.68 | 430.88
12389 | TIN-INTERP | Interpolated Ground | 79194.12 | 4.71 | 399.33 | 0 | 26.16 | 0 | OK | Ground clear controls. | 180 | 41.68 | 425.49
12390 | TIN-INTERP | Interpolated Ground | 79194.13 | -5.49 | 391.66 | 0 | 33.77 | 0 | OK | Ground clear controls. | 180 | 41.68 | 425.43
12391 | TIN-INTERP | Interpolated Ground | 79194.16 | -6.99 | 389.2 | 0 | 41.68 | 0 | OK | Ground clear controls. | 180 | 41.68 | 430.88
12392 | TIN-INTERP | Interpolated Ground | 79234.06 | 4.18 | 407.74 | 0 | 28.72 | 0 | OK | Ground clear controls. | 180 | 28.72 | 436.46
12393 | TIN-INTERP | Interpolated Ground | 79234.08 | -5.02 | 408.67 | 0 | 27.77 | 0 | OK | Ground clear controls. | 180 | 27.77 | 436.44
12394 | TIN-INTERP | Interpolated Ground | 79234.09 | 6.18 | 407.7 | 0 | 23.23 | 0 | OK | Ground clear controls. | 180 | 23.23 | 430.93
12395 | TIN-INTERP | Interpolated Ground | 79234.12 | 4.68 | 407.74 | 0 | 17.73 | 0 | OK | Ground clear controls. | 180 | 22.43 | 425.47
12396 | TIN-INTERP | Interpolated Ground | 79234.13 | -5.52 | 408.66 | 0 | 16.79 | 0 | OK | Ground clear controls. | 180 | 22.43 | 425.45
12397 | TIN-INTERP | Interpolated Ground | 79234.16 | -7.01 | 408.5 | 0 | 22.43 | 0 | OK | Ground clear controls. | 180 | 22.43 | 430.93
12398 | TIN-INTERP | Interpolated Ground | 79248.22 | -7.02 | 410.88 | 0 | 20.29 | 0 | OK | Ground clear controls. | 181 | 33.23 | 431.17
12399 | TIN-INTERP | Interpolated Ground | 79248.23 | -5.53 | 411.06 | 0 | 14.61 | 0 | OK | Ground clear controls. | 181 | 33.23 | 425.67
12400 | TIN-INTERP | Interpolated Ground | 79248.27 | -5.03 | 411.14 | 0 | 25.53 | 0 | OK | Ground clear controls. | 181 | 33.23 | 436.67
12401 | TIN-INTERP | Interpolated Ground | 79248.33 | 4.67 | 411.51 | 0 | 14.17 | 0 | OK | Ground clear controls. | 181 | 33.23 | 425.68
12402 | TIN-INTERP | Interpolated Ground | 79248.36 | 4.17 | 411.49 | 0 | 25.18 | 0 | OK | Ground clear controls. | 181 | 33.23 | 436.67
12403 | TIN-INTERP | Interpolated Ground | 79248.43 | 6.17 | 411.46 | 0 | 19.71 | 0 | OK | Ground clear controls. | 181 | 33.23 | 431.17
12404 | TIN-INTERP | Interpolated Ground | 79288.17 | 4.72 | 407.09 | 0 | 12.62 | 0 | OK | Ground clear controls. | 181 | 33.23 | 419.71
12405 | TIN-INTERP | Interpolated Ground | 79288.22 | 4.22 | 407.02 | 0 | 23.69 | 0 | OK | Ground clear controls. | 181 | 33.23 | 430.71
12406 | TIN-INTERP | Interpolated Ground | 79288.23 | 6.22 | 407.36 | 0 | 17.81 | 0 | OK | Ground clear controls. | 181 | 33.23 | 425.17
12407 | TIN-INTERP | Interpolated Ground | 79288.41 | -5.48 | 405.06 | 0 | 14.63 | 0 | OK | Ground clear controls. | 181 | 33.23 | 419.69
12408 | TIN-INTERP | Interpolated Ground | 79288.44 | -4.98 | 405.15 | 0 | 25.54 | 0 | OK | Ground clear controls. | 181 | 33.23 | 430.69
12409 | TIN-INTERP | Interpolated Ground | 79288.45 | -6.98 | 404.71 | 0 | 20.46 | 0 | OK | Ground clear controls. | 181 | 33.23 | 425.17
12410 | TIN-INTERP | Interpolated Ground | 79328.17 | 4.77 | 396.57 | 0 | 18.11 | 0 | OK | Ground clear controls. | 181 | 33.23 | 414.68
12411 | TIN-INTERP | Interpolated Ground | 79328.22 | 4.27 | 396.58 | 0 | 29.12 | 0 | OK | Ground clear controls. | 181 | 33.23 | 425.7
12412 | TIN-INTERP | Interpolated Ground | 79328.23 | 6.28 | 396.54 | 0 | 23.59 | 0 | OK | Ground clear controls. | 181 | 33.23 | 420.13
12413 | TIN-INTERP | Interpolated Ground | 79328.41 | -5.42 | 396.6 | 0 | 18.06 | 0 | OK | Ground clear controls. | 181 | 33.23 | 414.66
12414 | TIN-INTERP | Interpolated Ground | 79328.44 | -4.92 | 396.57 | 0 | 29.08 | 0 | OK | Ground clear controls. | 181 | 33.23 | 425.65
12415 | TIN-INTERP | Interpolated Ground | 79328.45 | -6.92 | 396.5 | 0 | 23.61 | 0 | OK | Ground clear controls. | 181 | 33.23 | 420.11
12416 | TIN-INTERP | Interpolated Ground | 79368.17 | 4.83 | 395.19 | 0 | 15.4 | 0 | OK | Ground clear controls. | 181 | 33.23 | 410.59
12417 | TIN-INTERP | Interpolated Ground | 79368.22 | 4.33 | 395.2 | 0 | 26.41 | 0 | OK | Ground clear controls. | 181 | 33.23 | 421.61
12418 | TIN-INTERP | Interpolated Ground | 79368.23 | 6.33 | 395.17 | 0 | 20.85 | 0 | OK | Ground clear controls. | 181 | 33.23 | 416.02
12419 | TIN-INTERP | Interpolated Ground | 79368.41 | -5.37 | 395.16 | 0 | 15.41 | 0 | OK | Ground clear controls. | 181 | 33.23 | 410.57
12420 | TIN-INTERP | Interpolated Ground | 79368.44 | -4.87 | 395.16 | 0 | 26.4 | 0 | OK | Ground clear controls. | 181 | 33.23 | 421.56
12421 | TIN-INTERP | Interpolated Ground | 79368.45 | -6.87 | 395.14 | 0 | 20.87 | 0 | OK | Ground clear controls. | 181 | 33.23 | 416.01
12422 | TIN-INTERP | Interpolated Ground | 79408.17 | 4.89 | 394.51 | 0 | 12.92 | 0 | OK | Ground clear controls. | 181 | 33.23 | 407.43
12423 | TIN-INTERP | Interpolated Ground | 79408.22 | 4.39 | 394.49 | 0 | 23.96 | 0 | OK | Ground clear controls. | 181 | 33.23 | 418.45
12424 | TIN-INTERP | Interpolated Ground | 79408.23 | 6.39 | 394.57 | 0 | 18.28 | 0 | OK | Ground clear controls. | 181 | 33.23 | 412.85
12425 | TIN-INTERP | Interpolated Ground | 79408.41 | -5.31 | 394.36 | 0 | 13.05 | 0 | OK | Ground clear controls. | 181 | 33.23 | 407.41
12426 | TIN-INTERP | Interpolated Ground | 79408.44 | -4.81 | 394.37 | 0 | 24.03 | 0 | OK | Ground clear controls. | 181 | 33.23 | 418.4
12427 | TIN-INTERP | Interpolated Ground | 79408.45 | -6.81 | 394.33 | 0 | 18.52 | 0 | OK | Ground clear controls. | 181 | 33.23 | 412.85
12428 | TIN-INTERP | Interpolated Ground | 79448.17 | 4.94 | 391.35 | 0 | 13.85 | 0 | OK | Ground clear controls. | 181 | 33.23 | 405.2
12429 | TIN-INTERP | Interpolated Ground | 79448.22 | 4.44 | 391.34 | 0 | 24.88 | 0 | OK | Ground clear controls. | 181 | 33.23 | 416.22
12430 | TIN-INTERP | Interpolated Ground | 79448.23 | 6.44 | 391.38 | 0 | 19.25 | 0 | OK | Ground clear controls. | 181 | 33.23 | 410.63
12431 | TIN-INTERP | Interpolated Ground | 79448.41 | -5.26 | 390.99 | 0 | 14.19 | 0 | OK | Ground clear controls. | 181 | 33.23 | 405.18
12432 | TIN-INTERP | Interpolated Ground | 79448.44 | -4.76 | 391 | 0 | 25.16 | 0 | OK | Ground clear controls. | 181 | 33.23 | 416.16
12433 | TIN-INTERP | Interpolated Ground | 79448.45 | -6.76 | 390.87 | 0 | 19.75 | 0 | OK | Ground clear controls. | 181 | 33.23 | 410.62
12434 | TIN-INTERP | Interpolated Ground | 79488.17 | 5 | 383.03 | 0 | 20.87 | 0 | OK | Ground clear controls. | 181 | 33.23 | 403.9
12435 | TIN-INTERP | Interpolated Ground | 79488.22 | 4.5 | 383.03 | 0 | 31.89 | 0 | OK | Ground clear controls. | 181 | 33.23 | 414.92
12436 | TIN-INTERP | Interpolated Ground | 79488.23 | 6.5 | 383.17 | 0 | 26.18 | 0 | OK | Ground clear controls. | 181 | 33.23 | 409.35
12437 | TIN-INTERP | Interpolated Ground | 79488.41 | -5.2 | 383.31 | 0 | 20.58 | 0 | OK | Ground clear controls. | 181 | 33.23 | 403.89
12438 | TIN-INTERP | Interpolated Ground | 79488.44 | -4.7 | 383.29 | 0 | 31.58 | 0 | OK | Ground clear controls. | 181 | 33.23 | 414.87
12439 | TIN-INTERP | Interpolated Ground | 79488.45 | -6.7 | 383.25 | 0 | 26.09 | 0 | OK | Ground clear controls. | 181 | 33.23 | 409.34
12440 | TIN-INTERP | Interpolated Ground | 79528.17 | 5.05 | 381.61 | 0 | 21.92 | 0 | OK | Ground clear controls. | 181 | 33.23 | 403.53
12441 | TIN-INTERP | Interpolated Ground | 79528.22 | 4.55 | 381.58 | 0 | 32.96 | 0 | OK | Ground clear controls. | 181 | 33.23 | 414.54
12442 | TIN-INTERP | Interpolated Ground | 79528.23 | 6.56 | 381.88 | 0 | 27.11 | 0 | OK | Ground clear controls. | 181 | 33.23 | 408.99
12443 | TIN-INTERP | Interpolated Ground | 79528.41 | -5.15 | 381.5 | 0 | 22.03 | 0 | OK | Ground clear controls. | 181 | 33.23 | 403.53
12444 | TIN-INTERP | Interpolated Ground | 79528.44 | -4.65 | 381.53 | 0 | 32.99 | 0 | OK | Ground clear controls. | 181 | 33.23 | 414.52
12445 | TIN-INTERP | Interpolated Ground | 79528.45 | -6.65 | 381.4 | 0 | 27.59 | 0 | OK | Ground clear controls. | 181 | 33.23 | 408.99
12446 | TIN-INTERP | Interpolated Ground | 79568.17 | 5.11 | 382.17 | 0 | 21.93 | 0 | OK | Ground clear controls. | 181 | 33.23 | 404.1
12447 | TIN-INTERP | Interpolated Ground | 79568.22 | 4.61 | 382.15 | 0 | 32.95 | 0 | OK | Ground clear controls. | 181 | 33.23 | 415.1
12448 | TIN-INTERP | Interpolated Ground | 79568.23 | 6.61 | 382.19 | 0 | 27.4 | 0 | OK | Ground clear controls. | 181 | 33.23 | 409.59
12449 | TIN-INTERP | Interpolated Ground | 79568.41 | -5.09 | 381.85 | 0 | 22.25 | 0 | OK | Ground clear controls. | 181 | 33.23 | 404.1
12450 | TIN-INTERP | Interpolated Ground | 79568.44 | -4.59 | 381.87 | 0 | 33.23 | 0 | OK | Ground clear controls. | 181 | 33.23 | 415.1
12451 | TIN-INTERP | Interpolated Ground | 79568.45 | -6.59 | 381.77 | 0 | 27.83 | 0 | OK | Ground clear controls. | 181 | 27.83 | 409.6
12452 | TIN-INTERP | Interpolated Ground | 79579.82 | 4.63 | 382.62 | 0 | 32.82 | 0 | OK | Ground clear controls. | 182 | 84.22 | 415.44
12453 | TIN-INTERP | Interpolated Ground | 79579.83 | 5.13 | 382.63 | 0 | 21.81 | 0 | OK | Ground clear controls. | 182 | 84.22 | 404.44
12454 | TIN-INTERP | Interpolated Ground | 79579.85 | -5.08 | 382.44 | 0 | 21.99 | 0 | OK | Ground clear controls. | 182 | 84.22 | 404.43
12455 | TIN-INTERP | Interpolated Ground | 79579.86 | -6.58 | 382.49 | 0 | 27.44 | 0 | OK | Ground clear controls. | 182 | 84.22 | 409.93
12456 | TIN-INTERP | Interpolated Ground | 79579.87 | 6.63 | 382.62 | 0 | 27.32 | 0 | OK | Ground clear controls. | 182 | 84.22 | 409.94
12457 | TIN-INTERP | Interpolated Ground | 79579.89 | -4.58 | 382.43 | 0 | 33 | 0 | OK | Ground clear controls. | 182 | 84.22 | 415.43
12458 | TIN-INTERP | Interpolated Ground | 79619.82 | 4.62 | 373.46 | 0 | 37.63 | 0 | OK | Ground clear controls. | 182 | 84.22 | 411.09
12459 | TIN-INTERP | Interpolated Ground | 79619.83 | 5.12 | 374.18 | 0 | 25.91 | 0 | OK | Ground clear controls. | 182 | 84.22 | 400.09
12460 | TIN-INTERP | Interpolated Ground | 79619.85 | -5.09 | 366.78 | 0 | 33.3 | 0 | OK | Ground clear controls. | 182 | 84.22 | 400.08
12461 | TIN-INTERP | Interpolated Ground | 79619.86 | -6.59 | 365.72 | 0 | 39.83 | 0 | OK | Ground clear controls. | 182 | 84.22 | 405.55
12462 | TIN-INTERP | Interpolated Ground | 79619.87 | 6.62 | 374.8 | 0 | 30.76 | 0 | OK | Ground clear controls. | 182 | 84.22 | 405.56
12463 | TIN-INTERP | Interpolated Ground | 79619.89 | -4.59 | 367 | 0 | 44.08 | 0 | OK | Ground clear controls. | 182 | 84.22 | 411.08
12464 | TIN-INTERP | Interpolated Ground | 79659.82 | 4.61 | 346.92 | 0 | 60.78 | 0 | OK | Ground clear controls. | 182 | 84.22 | 407.7
12465 | TIN-INTERP | Interpolated Ground | 79659.83 | 5.11 | 347.06 | 0 | 49.62 | 0 | OK | Ground clear controls. | 182 | 84.22 | 396.68
12466 | TIN-INTERP | Interpolated Ground | 79659.85 | -5.1 | 344.37 | 0 | 52.31 | 0 | OK | Ground clear controls. | 182 | 84.22 | 396.68
12467 | TIN-INTERP | Interpolated Ground | 79659.86 | -6.6 | 344.33 | 0 | 57.79 | 0 | OK | Ground clear controls. | 182 | 84.22 | 402.12
12468 | TIN-INTERP | Interpolated Ground | 79659.87 | 6.61 | 347.7 | 0 | 54.44 | 0 | OK | Ground clear controls. | 182 | 84.22 | 402.14
12469 | TIN-INTERP | Interpolated Ground | 79659.89 | -4.6 | 344.41 | 0 | 63.27 | 0 | OK | Ground clear controls. | 182 | 84.22 | 407.68
12470 | TIN-INTERP | Interpolated Ground | 79699.82 | 4.6 | 330.88 | 0 | 74.38 | 0 | OK | Ground clear controls. | 182 | 84.22 | 405.26
12471 | TIN-INTERP | Interpolated Ground | 79699.83 | 5.11 | 331.39 | 0 | 62.85 | 0 | OK | Ground clear controls. | 182 | 84.22 | 394.24
12472 | TIN-INTERP | Interpolated Ground | 79699.85 | -5.12 | 326.65 | 0 | 67.58 | 0 | OK | Ground clear controls. | 182 | 84.22 | 394.23
12473 | TIN-INTERP | Interpolated Ground | 79699.86 | -6.62 | 326.72 | 0 | 72.93 | 0 | OK | Ground clear controls. | 182 | 84.22 | 399.65
12474 | TIN-INTERP | Interpolated Ground | 79699.87 | 6.61 | 332.15 | 0 | 67.52 | 0 | OK | Ground clear controls. | 182 | 84.22 | 399.67
12475 | TIN-INTERP | Interpolated Ground | 79699.89 | -4.62 | 326.68 | 0 | 78.56 | 0 | OK | Ground clear controls. | 182 | 84.22 | 405.24
12476 | TIN-INTERP | Interpolated Ground | 79739.82 | 4.6 | 319.54 | 0 | 84.22 | 0 | OK | Ground clear controls. | 182 | 84.22 | 403.76
12477 | TIN-INTERP | Interpolated Ground | 79739.83 | 5.1 | 319.54 | 0 | 73.19 | 0 | OK | Ground clear controls. | 182 | 84.22 | 392.73
12478 | TIN-INTERP | Interpolated Ground | 79739.85 | -5.13 | 319.52 | 0 | 73.21 | 0 | OK | Ground clear controls. | 182 | 84.22 | 392.73
12479 | TIN-INTERP | Interpolated Ground | 79739.86 | -6.63 | 319.51 | 0 | 78.63 | 0 | OK | Ground clear controls. | 182 | 84.22 | 398.14
12480 | TIN-INTERP | Interpolated Ground | 79739.87 | 6.6 | 319.54 | 0 | 78.63 | 0 | OK | Ground clear controls. | 182 | 84.22 | 398.17
12481 | TIN-INTERP | Interpolated Ground | 79739.89 | -4.63 | 319.52 | 0 | 84.22 | 0 | OK | Ground clear controls. | 182 | 84.22 | 403.74
12482 | TIN-INTERP | Interpolated Ground | 79779.82 | 4.59 | 330.6 | 0 | 72.6 | 0 | OK | Ground clear controls. | 182 | 72.6 | 403.2
12483 | TIN-INTERP | Interpolated Ground | 79779.83 | 5.09 | 330.32 | 0 | 61.86 | 0 | OK | Ground clear controls. | 182 | 69.74 | 392.18
12484 | TIN-INTERP | Interpolated Ground | 79779.85 | -5.15 | 333.56 | 0 | 58.61 | 0 | OK | Ground clear controls. | 182 | 69.74 | 392.17
12485 | TIN-INTERP | Interpolated Ground | 79779.86 | -6.65 | 333.91 | 0 | 63.68 | 0 | OK | Ground clear controls. | 182 | 69.74 | 397.59
12486 | TIN-INTERP | Interpolated Ground | 79779.87 | 6.59 | 329.59 | 0 | 68.02 | 0 | OK | Ground clear controls. | 182 | 69.74 | 397.61
12487 | TIN-INTERP | Interpolated Ground | 79779.89 | -4.65 | 333.44 | 0 | 69.74 | 0 | OK | Ground clear controls. | 182 | 69.74 | 403.18
12488 | TIN-INTERP | Interpolated Ground | 79819.82 | 4.58 | 369.37 | 0 | 34.22 | 0 | OK | Ground clear controls. | 182 | 34.22 | 403.59
12489 | TIN-INTERP | Interpolated Ground | 79819.83 | 5.09 | 369.43 | 0 | 23.13 | 0 | OK | Ground clear controls. | 182 | 33.57 | 392.56
12490 | TIN-INTERP | Interpolated Ground | 79819.85 | -5.16 | 370.18 | 0 | 22.38 | 0 | OK | Ground clear controls. | 182 | 33.57 | 392.56
12491 | TIN-INTERP | Interpolated Ground | 79819.86 | -6.66 | 370.58 | 0 | 27.4 | 0 | OK | Ground clear controls. | 182 | 33.57 | 397.98
12492 | TIN-INTERP | Interpolated Ground | 79819.87 | 6.59 | 369.49 | 0 | 28.51 | 0 | OK | Ground clear controls. | 182 | 33.57 | 398
12493 | TIN-INTERP | Interpolated Ground | 79819.89 | -4.66 | 370 | 0 | 33.57 | 0 | OK | Ground clear controls. | 182 | 33.57 | 403.57
12494 | TIN-INTERP | Interpolated Ground | 79859.82 | 4.57 | 374.41 | 0 | 30.52 | 0 | OK | Ground clear controls. | 182 | 32.6 | 404.93
12495 | TIN-INTERP | Interpolated Ground | 79859.83 | 5.08 | 374.43 | 0 | 19.48 | 0 | OK | Ground clear controls. | 182 | 32.6 | 393.91
12496 | TIN-INTERP | Interpolated Ground | 79859.85 | -5.18 | 374.11 | 0 | 19.8 | 0 | OK | Ground clear controls. | 182 | 32.6 | 393.91
12497 | TIN-INTERP | Interpolated Ground | 79859.86 | -6.68 | 374.03 | 0 | 25.3 | 0 | OK | Ground clear controls. | 182 | 32.6 | 399.33
12498 | TIN-INTERP | Interpolated Ground | 79859.87 | 6.58 | 374.42 | 0 | 24.93 | 0 | OK | Ground clear controls. | 182 | 32.6 | 399.35
12499 | TIN-INTERP | Interpolated Ground | 79859.89 | -4.67 | 374.12 | 0 | 30.8 | 0 | OK | Ground clear controls. | 182 | 32.6 | 404.92
12500 | TIN-INTERP | Interpolated Ground | 79899.82 | 4.57 | 375.52 | 0 | 31.68 | 0 | OK | Ground clear controls. | 182 | 32.6 | 407.2
12501 | TIN-INTERP | Interpolated Ground | 79899.83 | 5.07 | 375.46 | 0 | 20.72 | 0 | OK | Ground clear controls. | 182 | 32.6 | 396.18
12502 | TIN-INTERP | Interpolated Ground | 79899.85 | -5.19 | 376.7 | 0 | 19.49 | 0 | OK | Ground clear controls. | 182 | 32.6 | 396.19
12503 | TIN-INTERP | Interpolated Ground | 79899.86 | -6.69 | 376.75 | 0 | 24.88 | 0 | OK | Ground clear controls. | 182 | 32.6 | 401.63
12504 | TIN-INTERP | Interpolated Ground | 79899.87 | 6.57 | 375.34 | 0 | 26.31 | 0 | OK | Ground clear controls. | 182 | 32.6 | 401.65
12505 | TIN-INTERP | Interpolated Ground | 79899.89 | -4.69 | 376.7 | 0 | 30.49 | 0 | OK | Ground clear controls. | 182 | 32.6 | 407.19
12506 | TIN-INTERP | Interpolated Ground | 79939.82 | 4.56 | 377.83 | 0 | 32.6 | 0 | OK | Ground clear controls. | 182 | 32.6 | 410.43
12507 | TIN-INTERP | Interpolated Ground | 79939.83 | 5.06 | 377.83 | 0 | 21.59 | 0 | OK | Ground clear controls. | 182 | 32.21 | 399.42
12508 | TIN-INTERP | Interpolated Ground | 79939.85 | -5.21 | 378.26 | 0 | 21.18 | 0 | OK | Ground clear controls. | 182 | 32.21 | 399.44
12509 | TIN-INTERP | Interpolated Ground | 79939.86 | -6.71 | 378.33 | 0 | 26.57 | 0 | OK | Ground clear controls. | 182 | 32.21 | 404.9
12510 | TIN-INTERP | Interpolated Ground | 79939.87 | 6.56 | 377.74 | 0 | 27.16 | 0 | OK | Ground clear controls. | 182 | 32.21 | 404.9
12511 | TIN-INTERP | Interpolated Ground | 79939.89 | -4.7 | 378.22 | 0 | 32.21 | 0 | OK | Ground clear controls. | 182 | 32.21 | 410.43
12512 | TIN-INTERP | Interpolated Ground | 79976.19 | -5.22 | 379.65 | 0 | 23.55 | 0 | OK | Ground clear controls. | 183 | 39.34 | 403.2
12513 | TIN-INTERP | Interpolated Ground | 79976.26 | 6.56 | 379.46 | 0 | 29.24 | 0 | OK | Ground clear controls. | 183 | 39.34 | 408.7
12514 | TIN-INTERP | Interpolated Ground | 79976.27 | -6.72 | 379.64 | 0 | 29.06 | 0 | OK | Ground clear controls. | 183 | 39.34 | 408.7
12515 | TIN-INTERP | Interpolated Ground | 79976.27 | -4.72 | 379.65 | 0 | 34.55 | 0 | OK | Ground clear controls. | 183 | 39.34 | 414.2
12516 | TIN-INTERP | Interpolated Ground | 79976.3 | 5.06 | 379.47 | 0 | 23.72 | 0 | OK | Ground clear controls. | 183 | 39.34 | 403.19
12517 | TIN-INTERP | Interpolated Ground | 79976.32 | 4.55 | 379.48 | 0 | 34.72 | 0 | OK | Ground clear controls. | 183 | 39.34 | 414.2
12518 | TIN-INTERP | Interpolated Ground | 80016.19 | -5.4 | 379.98 | 0 | 21.53 | 0 | OK | Ground clear controls. | 183 | 39.34 | 401.51
12519 | TIN-INTERP | Interpolated Ground | 80016.26 | 6.59 | 379.78 | 0 | 27.22 | 0 | OK | Ground clear controls. | 183 | 39.34 | 407
12520 | TIN-INTERP | Interpolated Ground | 80016.27 | -6.9 | 379.94 | 0 | 27.09 | 0 | OK | Ground clear controls. | 183 | 39.34 | 407.03
12521 | TIN-INTERP | Interpolated Ground | 80016.27 | -4.88 | 379.96 | 0 | 32.67 | 0 | OK | Ground clear controls. | 183 | 39.34 | 412.63
12522 | TIN-INTERP | Interpolated Ground | 80016.3 | 5.1 | 379.8 | 0 | 21.74 | 0 | OK | Ground clear controls. | 183 | 39.34 | 401.54
12523 | TIN-INTERP | Interpolated Ground | 80016.32 | 4.58 | 379.79 | 0 | 32.85 | 0 | OK | Ground clear controls. | 183 | 39.34 | 412.64
12524 | TIN-INTERP | Interpolated Ground | 80056.19 | -5.58 | 380.04 | 0 | 20.74 | 0 | OK | Ground clear controls. | 183 | 39.34 | 400.78
12525 | TIN-INTERP | Interpolated Ground | 80056.26 | 6.63 | 379.81 | 0 | 26.46 | 0 | OK | Ground clear controls. | 183 | 39.34 | 406.27
12526 | TIN-INTERP | Interpolated Ground | 80056.26 | -7.08 | 380.09 | 0 | 26.23 | 0 | OK | Ground clear controls. | 183 | 39.34 | 406.32
12527 | TIN-INTERP | Interpolated Ground | 80056.27 | -5.05 | 380.03 | 0 | 31.99 | 0 | OK | Ground clear controls. | 183 | 39.34 | 412.02
12528 | TIN-INTERP | Interpolated Ground | 80056.3 | 5.13 | 379.85 | 0 | 20.99 | 0 | OK | Ground clear controls. | 183 | 39.34 | 400.84
12529 | TIN-INTERP | Interpolated Ground | 80056.32 | 4.6 | 379.83 | 0 | 32.2 | 0 | OK | Ground clear controls. | 183 | 39.34 | 412.03
12530 | TIN-INTERP | Interpolated Ground | 80096.19 | -5.76 | 380.04 | 0 | 20.98 | 0 | OK | Ground clear controls. | 183 | 39.34 | 401.02
12531 | TIN-INTERP | Interpolated Ground | 80096.26 | -7.25 | 380.05 | 0 | 26.52 | 0 | OK | Ground clear controls. | 183 | 39.34 | 406.57
12532 | TIN-INTERP | Interpolated Ground | 80096.26 | 6.67 | 379.68 | 0 | 26.82 | 0 | OK | Ground clear controls. | 183 | 39.34 | 406.5
12533 | TIN-INTERP | Interpolated Ground | 80096.27 | -5.21 | 380.03 | 0 | 32.33 | 0 | OK | Ground clear controls. | 183 | 39.34 | 412.36
12534 | TIN-INTERP | Interpolated Ground | 80096.3 | 5.17 | 379.73 | 0 | 21.35 | 0 | OK | Ground clear controls. | 183 | 39.34 | 401.08
12535 | TIN-INTERP | Interpolated Ground | 80096.32 | 4.63 | 379.75 | 0 | 32.63 | 0 | OK | Ground clear controls. | 183 | 39.34 | 412.38
12536 | TIN-INTERP | Interpolated Ground | 80136.19 | -5.94 | 381.3 | 0 | 20.92 | 0 | OK | Ground clear controls. | 183 | 39.34 | 402.22
12537 | TIN-INTERP | Interpolated Ground | 80136.26 | -7.43 | 381.3 | 0 | 26.49 | 0 | OK | Ground clear controls. | 183 | 39.34 | 407.79
12538 | TIN-INTERP | Interpolated Ground | 80136.26 | 6.71 | 381.1 | 0 | 26.6 | 0 | OK | Ground clear controls. | 183 | 39.34 | 407.7
12539 | TIN-INTERP | Interpolated Ground | 80136.27 | -5.38 | 381.32 | 0 | 32.35 | 0 | OK | Ground clear controls. | 183 | 39.34 | 413.67
12540 | TIN-INTERP | Interpolated Ground | 80136.3 | 5.21 | 381.15 | 0 | 21.14 | 0 | OK | Ground clear controls. | 183 | 39.34 | 402.29
12541 | TIN-INTERP | Interpolated Ground | 80136.32 | 4.65 | 381.14 | 0 | 32.54 | 0 | OK | Ground clear controls. | 183 | 39.34 | 413.68
12542 | TIN-INTERP | Interpolated Ground | 80176.19 | -6.11 | 381.31 | 0 | 23.07 | 0 | OK | Ground clear controls. | 183 | 39.34 | 404.38
12543 | TIN-INTERP | Interpolated Ground | 80176.26 | -7.61 | 381.3 | 0 | 28.67 | 0 | OK | Ground clear controls. | 183 | 39.34 | 409.97
12544 | TIN-INTERP | Interpolated Ground | 80176.26 | 6.74 | 380.76 | 0 | 29.09 | 0 | OK | Ground clear controls. | 183 | 39.34 | 409.85
12545 | TIN-INTERP | Interpolated Ground | 80176.27 | -5.54 | 381.32 | 0 | 34.6 | 0 | OK | Ground clear controls. | 183 | 39.34 | 415.92
12546 | TIN-INTERP | Interpolated Ground | 80176.3 | 5.25 | 380.94 | 0 | 23.51 | 0 | OK | Ground clear controls. | 183 | 39.34 | 404.45
12547 | TIN-INTERP | Interpolated Ground | 80176.32 | 4.67 | 380.99 | 0 | 34.94 | 0 | OK | Ground clear controls. | 183 | 39.34 | 415.93
12548 | TIN-INTERP | Interpolated Ground | 80216.19 | -6.29 | 382.06 | 0 | 25.45 | 0 | OK | Ground clear controls. | 183 | 39.34 | 407.51
12549 | TIN-INTERP | Interpolated Ground | 80216.26 | -7.79 | 382.1 | 0 | 31.03 | 0 | OK | Ground clear controls. | 183 | 39.34 | 413.13
12550 | TIN-INTERP | Interpolated Ground | 80216.26 | 6.78 | 382.67 | 0 | 30.31 | 0 | OK | Ground clear controls. | 183 | 39.34 | 412.98
12551 | TIN-INTERP | Interpolated Ground | 80216.27 | -5.71 | 382.09 | 0 | 37.05 | 0 | OK | Ground clear controls. | 183 | 39.34 | 419.14
12552 | TIN-INTERP | Interpolated Ground | 80216.3 | 5.29 | 382.65 | 0 | 24.91 | 0 | OK | Ground clear controls. | 183 | 39.34 | 407.56
12553 | TIN-INTERP | Interpolated Ground | 80216.32 | 4.7 | 382.62 | 0 | 36.51 | 0 | OK | Ground clear controls. | 183 | 39.34 | 419.13
12554 | TIN-INTERP | Interpolated Ground | 80256.19 | -6.47 | 392.65 | 0 | 18.95 | 0 | OK | Ground clear controls. | 183 | 39.34 | 411.6
12555 | TIN-INTERP | Interpolated Ground | 80256.26 | -7.97 | 392.84 | 0 | 24.41 | 0 | OK | Ground clear controls. | 183 | 39.34 | 417.25
12556 | TIN-INTERP | Interpolated Ground | 80256.26 | 6.82 | 389.76 | 0 | 27.31 | 0 | OK | Ground clear controls. | 183 | 39.34 | 417.07
12557 | TIN-INTERP | Interpolated Ground | 80256.27 | -5.87 | 392.69 | 0 | 30.63 | 0 | OK | Ground clear controls. | 183 | 39.34 | 423.32
12558 | TIN-INTERP | Interpolated Ground | 80256.3 | 5.32 | 390.14 | 0 | 21.5 | 0 | OK | Ground clear controls. | 183 | 39.34 | 411.64
12559 | TIN-INTERP | Interpolated Ground | 80256.32 | 4.72 | 390.27 | 0 | 33.02 | 0 | OK | Ground clear controls. | 183 | 39.34 | 423.29
12560 | TIN-INTERP | Interpolated Ground | 80296.19 | -6.65 | 398.45 | 0 | 18.22 | 0 | OK | Ground clear controls. | 183 | 39.34 | 416.67
12561 | TIN-INTERP | Interpolated Ground | 80296.26 | -8.15 | 398.52 | 0 | 23.83 | 0 | OK | Ground clear controls. | 183 | 39.34 | 422.35
12562 | TIN-INTERP | Interpolated Ground | 80296.26 | 6.86 | 398.1 | 0 | 24.02 | 0 | OK | Ground clear controls. | 183 | 39.34 | 422.12
12563 | TIN-INTERP | Interpolated Ground | 80296.27 | -6.04 | 398.44 | 0 | 30.02 | 0 | OK | Ground clear controls. | 183 | 39.34 | 428.46
12564 | TIN-INTERP | Interpolated Ground | 80296.3 | 5.36 | 398.14 | 0 | 18.53 | 0 | OK | Ground clear controls. | 183 | 39.34 | 416.67
12565 | TIN-INTERP | Interpolated Ground | 80296.32 | 4.75 | 398.15 | 0 | 30.26 | 0 | OK | Ground clear controls. | 183 | 39.34 | 428.41
12566 | TIN-INTERP | Interpolated Ground | 80336.19 | -6.83 | 407.48 | 0 | 15.23 | 0 | OK | Ground clear controls. | 183 | 39.34 | 422.71
12567 | TIN-INTERP | Interpolated Ground | 80336.26 | -8.32 | 407.42 | 0 | 21 | 0 | OK | Ground clear controls. | 183 | 39.34 | 428.42
12568 | TIN-INTERP | Interpolated Ground | 80336.26 | 6.89 | 407.1 | 0 | 21.06 | 0 | OK | Ground clear controls. | 183 | 39.34 | 428.16
12569 | TIN-INTERP | Interpolated Ground | 80336.26 | -6.2 | 407.49 | 0 | 27.08 | 0 | OK | Ground clear controls. | 183 | 39.34 | 434.57
12570 | TIN-INTERP | Interpolated Ground | 80336.3 | 5.4 | 407.21 | 0 | 15.46 | 0 | OK | Ground clear controls. | 183 | 39.34 | 422.67
12571 | TIN-INTERP | Interpolated Ground | 80336.32 | 4.77 | 407.26 | 0 | 27.23 | 0 | OK | Ground clear controls. | 183 | 39.34 | 434.49
12572 | TIN-INTERP | Interpolated Ground | 80376.19 | -7.01 | 409.18 | 0 | 20.54 | 0 | OK | Ground clear controls. | 183 | 39.34 | 429.72
12573 | TIN-INTERP | Interpolated Ground | 80376.26 | -8.5 | 409.14 | 0 | 26.31 | 0 | OK | Ground clear controls. | 183 | 39.34 | 435.45
12574 | TIN-INTERP | Interpolated Ground | 80376.26 | 6.93 | 409.89 | 0 | 25.27 | 0 | OK | Ground clear controls. | 183 | 39.34 | 435.16
12575 | TIN-INTERP | Interpolated Ground | 80376.26 | -6.37 | 409.19 | 0 | 32.45 | 0 | OK | Ground clear controls. | 183 | 39.34 | 441.64
12576 | TIN-INTERP | Interpolated Ground | 80376.3 | 5.44 | 409.76 | 0 | 19.88 | 0 | OK | Ground clear controls. | 183 | 39.34 | 429.64
12577 | TIN-INTERP | Interpolated Ground | 80376.32 | 4.79 | 409.77 | 0 | 31.75 | 0 | OK | Ground clear controls. | 183 | 39.34 | 441.52
12578 | TIN-INTERP | Interpolated Ground | 80416.19 | -7.19 | 416.45 | 0 | 21.26 | 0 | OK | Ground clear controls. | 183 | 39.34 | 437.71
12579 | TIN-INTERP | Interpolated Ground | 80416.26 | -8.68 | 415.99 | 0 | 27.49 | 0 | OK | Ground clear controls. | 183 | 39.34 | 443.48
12580 | TIN-INTERP | Interpolated Ground | 80416.26 | -6.53 | 416.58 | 0 | 33.11 | 0 | OK | Ground clear controls. | 183 | 39.34 | 449.69
12581 | TIN-INTERP | Interpolated Ground | 80416.26 | 6.97 | 417.32 | 0 | 25.83 | 0 | OK | Ground clear controls. | 183 | 39.34 | 443.15
12582 | TIN-INTERP | Interpolated Ground | 80416.3 | 5.48 | 417.38 | 0 | 20.2 | 0 | OK | Ground clear controls. | 183 | 39.34 | 437.58
12583 | TIN-INTERP | Interpolated Ground | 80416.32 | 4.82 | 417.45 | 0 | 32.08 | 0 | OK | Ground clear controls. | 183 | 39.34 | 449.53
12584 | TIN-INTERP | Interpolated Ground | 80456.19 | -7.37 | 420.47 | 0 | 26.22 | 0 | OK | Ground clear controls. | 183 | 39.34 | 446.69
12585 | TIN-INTERP | Interpolated Ground | 80456.26 | -8.86 | 420.04 | 0 | 32.46 | 0 | OK | Ground clear controls. | 183 | 39.34 | 452.5
12586 | TIN-INTERP | Interpolated Ground | 80456.26 | -6.7 | 420.69 | 0 | 38.03 | 0 | OK | Ground clear controls. | 183 | 39.34 | 458.72
12587 | TIN-INTERP | Interpolated Ground | 80456.26 | 7.01 | 427.33 | 0 | 24.79 | 0 | OK | Ground clear controls. | 183 | 39.34 | 452.12
12588 | TIN-INTERP | Interpolated Ground | 80456.3 | 5.51 | 426.75 | 0 | 19.73 | 0 | OK | Ground clear controls. | 183 | 39.34 | 446.48
12589 | TIN-INTERP | Interpolated Ground | 80456.32 | 4.84 | 426.51 | 0 | 31.99 | 0 | OK | Ground clear controls. | 183 | 39.34 | 458.5
12590 | TIN-INTERP | Interpolated Ground | 80496.19 | -7.55 | 429.22 | 0 | 27.44 | 0 | OK | Ground clear controls. | 183 | 39.34 | 456.66
12591 | TIN-INTERP | Interpolated Ground | 80496.26 | -9.04 | 428.85 | 0 | 33.66 | 0 | OK | Ground clear controls. | 183 | 39.34 | 462.51
12592 | TIN-INTERP | Interpolated Ground | 80496.26 | -6.86 | 429.39 | 0 | 39.34 | 0 | OK | Ground clear controls. | 183 | 39.34 | 468.73
12593 | TIN-INTERP | Interpolated Ground | 80496.26 | 7.04 | 433.88 | 0 | 28.2 | 0 | OK | Ground clear controls. | 183 | 34.91 | 462.08
12594 | TIN-INTERP | Interpolated Ground | 80496.3 | 5.55 | 433.67 | 0 | 22.71 | 0 | OK | Ground clear controls. | 183 | 34.91 | 456.38
12595 | TIN-INTERP | Interpolated Ground | 80496.32 | 4.87 | 433.55 | 0 | 34.91 | 0 | OK | Ground clear controls. | 183 | 34.91 | 468.46
12596 | TIN-INTERP | Interpolated Ground | 80507.31 | -9.09 | 432.01 | 0 | 33.43 | 0 | OK | Ground clear controls. | 184 | 42.87 | 465.44
12597 | TIN-INTERP | Interpolated Ground | 80507.46 | -7.6 | 432.12 | 0 | 27.52 | 0 | OK | Ground clear controls. | 184 | 42.87 | 459.64
12598 | TIN-INTERP | Interpolated Ground | 80507.58 | -6.91 | 432.18 | 0 | 39.56 | 0 | OK | Ground clear controls. | 184 | 42.87 | 471.74
12599 | TIN-INTERP | Interpolated Ground | 80508.31 | 4.9 | 434.28 | 0 | 37.49 | 0 | OK | Ground clear controls. | 184 | 42.87 | 471.77
12600 | TIN-INTERP | Interpolated Ground | 80508.31 | 5.59 | 434.42 | 0 | 25.25 | 0 | OK | Ground clear controls. | 184 | 42.87 | 459.67
12601 | TIN-INTERP | Interpolated Ground | 80508.31 | 7.09 | 434.69 | 0 | 30.78 | 0 | OK | Ground clear controls. | 184 | 42.87 | 465.47
12602 | TIN-INTERP | Interpolated Ground | 80547.7 | 7.01 | 428.6 | 0 | 31.38 | 0 | OK | Ground clear controls. | 184 | 42.87 | 459.98
12603 | TIN-INTERP | Interpolated Ground | 80547.77 | 5.51 | 428.18 | 0 | 26.03 | 0 | OK | Ground clear controls. | 184 | 42.87 | 454.21
12604 | TIN-INTERP | Interpolated Ground | 80547.86 | 4.85 | 428 | 0 | 38.22 | 0 | OK | Ground clear controls. | 184 | 42.87 | 466.22
12605 | TIN-INTERP | Interpolated Ground | 80548.88 | -6.66 | 424.35 | 0 | 41.85 | 0 | OK | Ground clear controls. | 184 | 42.87 | 466.2
12606 | TIN-INTERP | Interpolated Ground | 80548.88 | -7.34 | 424.18 | 0 | 29.98 | 0 | OK | Ground clear controls. | 184 | 42.87 | 454.16
12607 | TIN-INTERP | Interpolated Ground | 80549.01 | -8.83 | 423.81 | 0 | 36.11 | 0 | OK | Ground clear controls. | 184 | 42.87 | 459.92
12608 | TIN-INTERP | Interpolated Ground | 80587.7 | 6.96 | 431.8 | 0 | 23.67 | 0 | OK | Ground clear controls. | 184 | 42.87 | 455.47
12609 | TIN-INTERP | Interpolated Ground | 80587.77 | 5.46 | 431.55 | 0 | 18.19 | 0 | OK | Ground clear controls. | 184 | 42.87 | 449.74
12610 | TIN-INTERP | Interpolated Ground | 80587.86 | 4.82 | 431.4 | 0 | 30.24 | 0 | OK | Ground clear controls. | 184 | 42.87 | 461.64
12611 | TIN-INTERP | Interpolated Ground | 80588.88 | -6.4 | 429.06 | 0 | 32.56 | 0 | OK | Ground clear controls. | 184 | 42.87 | 461.62
12612 | TIN-INTERP | Interpolated Ground | 80588.88 | -7.06 | 428.94 | 0 | 20.72 | 0 | OK | Ground clear controls. | 184 | 42.87 | 449.66
12613 | TIN-INTERP | Interpolated Ground | 80589.01 | -8.55 | 428.68 | 0 | 26.71 | 0 | OK | Ground clear controls. | 184 | 42.87 | 455.39
12614 | TIN-INTERP | Interpolated Ground | 80627.7 | 6.91 | 433.05 | 0 | 18.88 | 0 | OK | Ground clear controls. | 184 | 42.87 | 451.93
12615 | TIN-INTERP | Interpolated Ground | 80627.77 | 5.41 | 432.73 | 0 | 13.5 | 0 | OK | Ground clear controls. | 184 | 42.87 | 446.23
12616 | TIN-INTERP | Interpolated Ground | 80627.86 | 4.78 | 432.56 | 0 | 25.46 | 0 | OK | Ground clear controls. | 184 | 42.87 | 458.02
12617 | TIN-INTERP | Interpolated Ground | 80628.87 | -6.14 | 430.78 | 0 | 27.23 | 0 | OK | Ground clear controls. | 184 | 42.87 | 458.01
12618 | TIN-INTERP | Interpolated Ground | 80628.88 | -6.78 | 430.67 | 0 | 15.48 | 0 | OK | Ground clear controls. | 184 | 42.87 | 446.15
12619 | TIN-INTERP | Interpolated Ground | 80629.01 | -8.27 | 430.33 | 0 | 21.51 | 0 | OK | Ground clear controls. | 184 | 42.87 | 451.84
12620 | TIN-INTERP | Interpolated Ground | 80667.7 | 6.86 | 421.31 | 0 | 28.04 | 0 | OK | Ground clear controls. | 184 | 42.87 | 449.35
12621 | TIN-INTERP | Interpolated Ground | 80667.77 | 5.36 | 421.17 | 0 | 22.52 | 0 | OK | Ground clear controls. | 184 | 42.87 | 443.69
12622 | TIN-INTERP | Interpolated Ground | 80667.86 | 4.75 | 421.1 | 0 | 34.27 | 0 | OK | Ground clear controls. | 184 | 42.87 | 455.37
12623 | TIN-INTERP | Interpolated Ground | 80668.87 | -5.88 | 419.35 | 0 | 36.01 | 0 | OK | Ground clear controls. | 184 | 42.87 | 455.36
12624 | TIN-INTERP | Interpolated Ground | 80668.88 | -6.49 | 419.27 | 0 | 24.34 | 0 | OK | Ground clear controls. | 184 | 42.87 | 443.61
12625 | TIN-INTERP | Interpolated Ground | 80669.01 | -7.99 | 419.07 | 0 | 30.2 | 0 | OK | Ground clear controls. | 184 | 42.87 | 449.27
12626 | TIN-INTERP | Interpolated Ground | 80707.7 | 6.81 | 413.7 | 0 | 34.05 | 0 | OK | Ground clear controls. | 184 | 42.87 | 447.75
12627 | TIN-INTERP | Interpolated Ground | 80707.77 | 5.3 | 413.77 | 0 | 28.35 | 0 | OK | Ground clear controls. | 184 | 42.87 | 442.12
12628 | TIN-INTERP | Interpolated Ground | 80707.86 | 4.72 | 413.75 | 0 | 39.92 | 0 | OK | Ground clear controls. | 184 | 42.87 | 453.67
12629 | TIN-INTERP | Interpolated Ground | 80708.87 | -5.62 | 412.79 | 0 | 40.89 | 0 | OK | Ground clear controls. | 184 | 42.87 | 453.68
12630 | TIN-INTERP | Interpolated Ground | 80708.88 | -6.21 | 412.68 | 0 | 29.38 | 0 | OK | Ground clear controls. | 184 | 42.87 | 442.06
12631 | TIN-INTERP | Interpolated Ground | 80709.01 | -7.71 | 412.13 | 0 | 35.55 | 0 | OK | Ground clear controls. | 184 | 42.87 | 447.68
12632 | TIN-INTERP | Interpolated Ground | 80747.7 | 6.75 | 413.54 | 0 | 33.58 | 0 | OK | Ground clear controls. | 184 | 42.87 | 447.12
12633 | TIN-INTERP | Interpolated Ground | 80747.77 | 5.25 | 413.43 | 0 | 28.09 | 0 | OK | Ground clear controls. | 184 | 42.87 | 441.52
12634 | TIN-INTERP | Interpolated Ground | 80747.86 | 4.69 | 413.4 | 0 | 39.54 | 0 | OK | Ground clear controls. | 184 | 42.87 | 452.94
12635 | TIN-INTERP | Interpolated Ground | 80748.87 | -5.36 | 412.8 | 0 | 40.15 | 0 | OK | Ground clear controls. | 184 | 42.87 | 452.95
12636 | TIN-INTERP | Interpolated Ground | 80748.88 | -5.93 | 412.76 | 0 | 28.73 | 0 | OK | Ground clear controls. | 184 | 42.87 | 441.49
12637 | TIN-INTERP | Interpolated Ground | 80749.01 | -7.43 | 412.64 | 0 | 34.44 | 0 | OK | Ground clear controls. | 184 | 42.87 | 447.08
12638 | TIN-INTERP | Interpolated Ground | 80787.7 | 6.7 | 410.78 | 0 | 36.67 | 0 | OK | Ground clear controls. | 184 | 42.87 | 447.45
12639 | TIN-INTERP | Interpolated Ground | 80787.77 | 5.2 | 410.85 | 0 | 31.04 | 0 | OK | Ground clear controls. | 184 | 42.87 | 441.89
12640 | TIN-INTERP | Interpolated Ground | 80787.86 | 4.66 | 410.84 | 0 | 42.33 | 0 | OK | Ground clear controls. | 184 | 42.87 | 453.17
12641 | TIN-INTERP | Interpolated Ground | 80788.87 | -5.11 | 411.33 | 0 | 41.87 | 0 | OK | Ground clear controls. | 184 | 42.87 | 453.2
12642 | TIN-INTERP | Interpolated Ground | 80788.88 | -5.65 | 411.33 | 0 | 30.55 | 0 | OK | Ground clear controls. | 184 | 42.87 | 441.88
12643 | TIN-INTERP | Interpolated Ground | 80789.01 | -7.14 | 411.23 | 0 | 36.22 | 0 | OK | Ground clear controls. | 184 | 42.87 | 447.45
12644 | TIN-INTERP | Interpolated Ground | 80827.7 | 6.65 | 411.77 | 0 | 36.98 | 0 | OK | Ground clear controls. | 184 | 42.87 | 448.75
12645 | TIN-INTERP | Interpolated Ground | 80827.77 | 5.15 | 411.69 | 0 | 31.53 | 0 | OK | Ground clear controls. | 184 | 42.87 | 443.22
12646 | TIN-INTERP | Interpolated Ground | 80827.86 | 4.63 | 411.68 | 0 | 42.67 | 0 | OK | Ground clear controls. | 184 | 42.87 | 454.35
12647 | TIN-INTERP | Interpolated Ground | 80828.87 | -4.85 | 411.52 | 0 | 42.87 | 0 | OK | Ground clear controls. | 184 | 42.87 | 454.39
12648 | TIN-INTERP | Interpolated Ground | 80828.88 | -5.37 | 411.47 | 0 | 31.8 | 0 | OK | Ground clear controls. | 184 | 37.39 | 443.27
12649 | TIN-INTERP | Interpolated Ground | 80829.01 | -6.86 | 411.41 | 0 | 37.39 | 0 | OK | Ground clear controls. | 184 | 37.39 | 448.8
12650 | TIN-INTERP | Interpolated Ground | 80855.39 | -6.68 | 411.92 | 0 | 38.3 | 0 | OK | Ground clear controls. | 185 | 44.79 | 450.22
12651 | TIN-INTERP | Interpolated Ground | 80855.42 | -4.67 | 412 | 0 | 43.72 | 0 | OK | Ground clear controls. | 185 | 44.79 | 455.72
12652 | TIN-INTERP | Interpolated Ground | 80855.51 | 4.61 | 412.25 | 0 | 43.47 | 0 | OK | Ground clear controls. | 185 | 44.79 | 455.72
12653 | TIN-INTERP | Interpolated Ground | 80855.53 | 5.12 | 412.31 | 0 | 32.41 | 0 | OK | Ground clear controls. | 185 | 44.79 | 444.72
12654 | TIN-INTERP | Interpolated Ground | 80855.54 | -5.18 | 412.02 | 0 | 32.7 | 0 | OK | Ground clear controls. | 185 | 44.79 | 444.72
12655 | TIN-INTERP | Interpolated Ground | 80855.54 | 6.62 | 412.35 | 0 | 37.87 | 0 | OK | Ground clear controls. | 185 | 44.79 | 450.22
12656 | TIN-INTERP | Interpolated Ground | 80895.39 | -6.67 | 411.72 | 0 | 32.56 | 0 | OK | Ground clear controls. | 185 | 44.79 | 444.28
12657 | TIN-INTERP | Interpolated Ground | 80895.41 | -4.67 | 412.04 | 0 | 37.87 | 0 | OK | Ground clear controls. | 185 | 44.79 | 449.91
12658 | TIN-INTERP | Interpolated Ground | 80895.51 | 4.61 | 413.04 | 0 | 36.87 | 0 | OK | Ground clear controls. | 185 | 44.79 | 449.91
12659 | TIN-INTERP | Interpolated Ground | 80895.53 | 5.11 | 413.06 | 0 | 25.79 | 0 | OK | Ground clear controls. | 185 | 44.79 | 438.85
12660 | TIN-INTERP | Interpolated Ground | 80895.54 | -5.17 | 411.93 | 0 | 26.95 | 0 | OK | Ground clear controls. | 185 | 44.79 | 438.88
12661 | TIN-INTERP | Interpolated Ground | 80895.54 | 6.61 | 413.26 | 0 | 31.09 | 0 | OK | Ground clear controls. | 185 | 44.79 | 444.35
12662 | TIN-INTERP | Interpolated Ground | 80935.39 | -6.67 | 406.66 | 0 | 32.68 | 0 | OK | Ground clear controls. | 185 | 44.79 | 439.34
12663 | TIN-INTERP | Interpolated Ground | 80935.41 | -4.67 | 406.88 | 0 | 38.2 | 0 | OK | Ground clear controls. | 185 | 44.79 | 445.08
12664 | TIN-INTERP | Interpolated Ground | 80935.51 | 4.61 | 407.69 | 0 | 37.4 | 0 | OK | Ground clear controls. | 185 | 44.79 | 445.09
12665 | TIN-INTERP | Interpolated Ground | 80935.53 | 5.11 | 407.67 | 0 | 26.29 | 0 | OK | Ground clear controls. | 185 | 44.79 | 433.96
12666 | TIN-INTERP | Interpolated Ground | 80935.54 | -5.17 | 406.79 | 0 | 27.22 | 0 | OK | Ground clear controls. | 185 | 44.79 | 434.01
12667 | TIN-INTERP | Interpolated Ground | 80935.54 | 6.61 | 407.86 | 0 | 31.6 | 0 | OK | Ground clear controls. | 185 | 44.79 | 439.46
12668 | TIN-INTERP | Interpolated Ground | 80975.39 | -6.66 | 404.96 | 0 | 30.42 | 0 | OK | Ground clear controls. | 185 | 44.79 | 435.38
12669 | TIN-INTERP | Interpolated Ground | 80975.41 | -4.66 | 404.44 | 0 | 36.77 | 0 | OK | Ground clear controls. | 185 | 44.79 | 441.21
12670 | TIN-INTERP | Interpolated Ground | 80975.51 | 4.61 | 402.88 | 0 | 38.35 | 0 | OK | Ground clear controls. | 185 | 44.79 | 441.23
12671 | TIN-INTERP | Interpolated Ground | 80975.53 | 5.11 | 403.06 | 0 | 27 | 0 | OK | Ground clear controls. | 185 | 44.79 | 430.06
12672 | TIN-INTERP | Interpolated Ground | 80975.54 | -5.16 | 404.61 | 0 | 25.52 | 0 | OK | Ground clear controls. | 185 | 44.79 | 430.13
12673 | TIN-INTERP | Interpolated Ground | 80975.54 | 6.61 | 403.78 | 0 | 31.78 | 0 | OK | Ground clear controls. | 185 | 44.79 | 435.56
12674 | TIN-INTERP | Interpolated Ground | 81015.39 | -6.66 | 397.09 | 0 | 35.31 | 0 | OK | Ground clear controls. | 185 | 44.79 | 432.4
12675 | TIN-INTERP | Interpolated Ground | 81015.41 | -4.66 | 396.92 | 0 | 41.4 | 0 | OK | Ground clear controls. | 185 | 44.79 | 438.32
12676 | TIN-INTERP | Interpolated Ground | 81015.51 | 4.61 | 398.84 | 0 | 39.49 | 0 | OK | Ground clear controls. | 185 | 44.79 | 438.33
12677 | TIN-INTERP | Interpolated Ground | 81015.53 | 5.11 | 398.99 | 0 | 28.14 | 0 | OK | Ground clear controls. | 185 | 44.79 | 427.13
12678 | TIN-INTERP | Interpolated Ground | 81015.54 | -5.16 | 396.96 | 0 | 30.25 | 0 | OK | Ground clear controls. | 185 | 44.79 | 427.21
12679 | TIN-INTERP | Interpolated Ground | 81015.54 | 6.61 | 399.38 | 0 | 33.25 | 0 | OK | Ground clear controls. | 185 | 44.79 | 432.63
12680 | TIN-INTERP | Interpolated Ground | 81055.39 | -6.66 | 391.76 | 0 | 38.67 | 0 | OK | Ground clear controls. | 185 | 44.79 | 430.43
12681 | TIN-INTERP | Interpolated Ground | 81055.41 | -4.65 | 391.76 | 0 | 44.65 | 0 | OK | Ground clear controls. | 185 | 44.79 | 436.41
12682 | TIN-INTERP | Interpolated Ground | 81055.51 | 4.61 | 391.63 | 0 | 44.79 | 0 | OK | Ground clear controls. | 185 | 44.79 | 436.42
12683 | TIN-INTERP | Interpolated Ground | 81055.53 | 5.11 | 391.67 | 0 | 33.52 | 0 | OK | Ground clear controls. | 185 | 44.21 | 425.19
12684 | TIN-INTERP | Interpolated Ground | 81055.54 | -5.16 | 391.77 | 0 | 33.51 | 0 | OK | Ground clear controls. | 185 | 44.21 | 425.28
12685 | TIN-INTERP | Interpolated Ground | 81055.54 | 6.61 | 391.89 | 0 | 38.79 | 0 | OK | Ground clear controls. | 185 | 44.21 | 430.68
12686 | TIN-INTERP | Interpolated Ground | 81095.39 | -6.65 | 399.66 | 0 | 29.77 | 0 | OK | Ground clear controls. | 185 | 44.21 | 429.43
12687 | TIN-INTERP | Interpolated Ground | 81095.41 | -4.65 | 399.42 | 0 | 36.03 | 0 | OK | Ground clear controls. | 185 | 44.21 | 435.45
12688 | TIN-INTERP | Interpolated Ground | 81095.51 | 4.6 | 397.36 | 0 | 38.11 | 0 | OK | Ground clear controls. | 185 | 44.21 | 435.47
12689 | TIN-INTERP | Interpolated Ground | 81095.53 | 5.11 | 397.1 | 0 | 27.11 | 0 | OK | Ground clear controls. | 185 | 44.21 | 424.21
12690 | TIN-INTERP | Interpolated Ground | 81095.54 | -5.15 | 399.5 | 0 | 24.81 | 0 | OK | Ground clear controls. | 185 | 44.21 | 424.31
12691 | TIN-INTERP | Interpolated Ground | 81095.54 | 6.61 | 396.12 | 0 | 33.59 | 0 | OK | Ground clear controls. | 185 | 44.21 | 429.71
12692 | TIN-INTERP | Interpolated Ground | 81135.39 | -6.65 | 401.58 | 0 | 27.84 | 0 | OK | Ground clear controls. | 185 | 44.21 | 429.42
12693 | TIN-INTERP | Interpolated Ground | 81135.41 | -4.65 | 401.52 | 0 | 33.94 | 0 | OK | Ground clear controls. | 185 | 44.21 | 435.46
12694 | TIN-INTERP | Interpolated Ground | 81135.51 | 4.6 | 404.99 | 0 | 30.48 | 0 | OK | Ground clear controls. | 185 | 44.21 | 435.47
12695 | TIN-INTERP | Interpolated Ground | 81135.53 | 5.11 | 405.07 | 0 | 19.15 | 0 | OK | Ground clear controls. | 185 | 44.21 | 424.22
12696 | TIN-INTERP | Interpolated Ground | 81135.54 | -5.15 | 401.55 | 0 | 22.77 | 0 | OK | Ground clear controls. | 185 | 44.21 | 424.32
12697 | TIN-INTERP | Interpolated Ground | 81135.54 | 6.61 | 405.31 | 0 | 24.4 | 0 | OK | Ground clear controls. | 185 | 44.21 | 429.71
12698 | TIN-INTERP | Interpolated Ground | 81175.39 | -6.64 | 403.78 | 0 | 26.63 | 0 | OK | Ground clear controls. | 185 | 44.21 | 430.41
12699 | TIN-INTERP | Interpolated Ground | 81175.41 | -4.64 | 403.75 | 0 | 32.69 | 0 | OK | Ground clear controls. | 185 | 44.21 | 436.44
12700 | TIN-INTERP | Interpolated Ground | 81175.51 | 4.6 | 404.3 | 0 | 32.17 | 0 | OK | Ground clear controls. | 185 | 44.21 | 436.47
12701 | TIN-INTERP | Interpolated Ground | 81175.53 | 5.1 | 404.32 | 0 | 20.88 | 0 | OK | Ground clear controls. | 185 | 44.21 | 425.2
12702 | TIN-INTERP | Interpolated Ground | 81175.54 | -5.14 | 403.76 | 0 | 21.55 | 0 | OK | Ground clear controls. | 185 | 44.21 | 425.31
12703 | TIN-INTERP | Interpolated Ground | 81175.54 | 6.6 | 404.39 | 0 | 26.31 | 0 | OK | Ground clear controls. | 185 | 44.21 | 430.7
12704 | TIN-INTERP | Interpolated Ground | 81215.39 | -6.64 | 397.34 | 0 | 35.02 | 0 | OK | Ground clear controls. | 185 | 44.21 | 432.36
12705 | TIN-INTERP | Interpolated Ground | 81215.41 | -4.64 | 397.76 | 0 | 40.64 | 0 | OK | Ground clear controls. | 185 | 44.21 | 438.4
12706 | TIN-INTERP | Interpolated Ground | 81215.51 | 4.6 | 394.21 | 0 | 44.21 | 0 | OK | Ground clear controls. | 185 | 44.21 | 438.42
12707 | TIN-INTERP | Interpolated Ground | 81215.53 | 5.1 | 394.23 | 0 | 32.93 | 0 | OK | Ground clear controls. | 185 | 41.49 | 427.16
12708 | TIN-INTERP | Interpolated Ground | 81215.54 | -5.14 | 397.78 | 0 | 29.49 | 0 | OK | Ground clear controls. | 185 | 41.49 | 427.27
12709 | TIN-INTERP | Interpolated Ground | 81215.54 | 6.6 | 394.28 | 0 | 38.37 | 0 | OK | Ground clear controls. | 185 | 41.49 | 432.65
12710 | TIN-INTERP | Interpolated Ground | 81255.39 | -6.63 | 406.42 | 0 | 28.89 | 0 | OK | Ground clear controls. | 185 | 41.49 | 435.31
12711 | TIN-INTERP | Interpolated Ground | 81255.41 | -4.63 | 406.22 | 0 | 35.1 | 0 | OK | Ground clear controls. | 185 | 41.49 | 441.32
12712 | TIN-INTERP | Interpolated Ground | 81255.51 | 4.6 | 404.87 | 0 | 36.47 | 0 | OK | Ground clear controls. | 185 | 41.49 | 441.34
12713 | TIN-INTERP | Interpolated Ground | 81255.53 | 5.1 | 404.84 | 0 | 25.24 | 0 | OK | Ground clear controls. | 185 | 41.49 | 430.08
12714 | TIN-INTERP | Interpolated Ground | 81255.54 | -5.13 | 406.22 | 0 | 23.98 | 0 | OK | Ground clear controls. | 185 | 41.49 | 430.2
12715 | TIN-INTERP | Interpolated Ground | 81255.54 | 6.6 | 404.98 | 0 | 30.6 | 0 | OK | Ground clear controls. | 185 | 41.49 | 435.58
12716 | TIN-INTERP | Interpolated Ground | 81295.39 | -6.63 | 410.55 | 0 | 28.7 | 0 | OK | Ground clear controls. | 185 | 41.49 | 439.25
12717 | TIN-INTERP | Interpolated Ground | 81295.41 | -4.63 | 409.98 | 0 | 35.24 | 0 | OK | Ground clear controls. | 185 | 41.49 | 445.22
12718 | TIN-INTERP | Interpolated Ground | 81295.51 | 4.6 | 405.21 | 0 | 40.04 | 0 | OK | Ground clear controls. | 185 | 41.49 | 445.25
12719 | TIN-INTERP | Interpolated Ground | 81295.53 | 5.1 | 404.94 | 0 | 29.07 | 0 | OK | Ground clear controls. | 185 | 41.49 | 434.01
12720 | TIN-INTERP | Interpolated Ground | 81295.54 | -5.13 | 410.24 | 0 | 23.87 | 0 | OK | Ground clear controls. | 185 | 41.49 | 434.11
12721 | TIN-INTERP | Interpolated Ground | 81295.54 | 6.6 | 404.33 | 0 | 35.18 | 0 | OK | Ground clear controls. | 185 | 41.49 | 439.51
12722 | TIN-INTERP | Interpolated Ground | 81335.39 | -6.63 | 419.02 | 0 | 25.17 | 0 | OK | Ground clear controls. | 185 | 41.49 | 444.19
12723 | TIN-INTERP | Interpolated Ground | 81335.41 | -4.62 | 417.27 | 0 | 32.82 | 0 | OK | Ground clear controls. | 185 | 41.49 | 450.09
12724 | TIN-INTERP | Interpolated Ground | 81335.51 | 4.6 | 408.62 | 0 | 41.49 | 0 | OK | Ground clear controls. | 185 | 41.49 | 450.11
12725 | TIN-INTERP | Interpolated Ground | 81335.53 | 5.1 | 408.07 | 0 | 30.84 | 0 | OK | Ground clear controls. | 185 | 37.78 | 438.91
12726 | TIN-INTERP | Interpolated Ground | 81335.54 | -5.13 | 417.75 | 0 | 21.26 | 0 | OK | Ground clear controls. | 185 | 37.78 | 439.01
12727 | TIN-INTERP | Interpolated Ground | 81335.54 | 6.6 | 406.63 | 0 | 37.78 | 0 | OK | Ground clear controls. | 185 | 37.78 | 444.41
12728 | TIN-INTERP | Interpolated Ground | 81375.39 | -6.62 | 422.84 | 0 | 27.27 | 0 | OK | Ground clear controls. | 185 | 37.53 | 450.11
12729 | TIN-INTERP | Interpolated Ground | 81375.41 | -4.62 | 423.38 | 0 | 32.55 | 0 | OK | Ground clear controls. | 185 | 37.53 | 455.93
12730 | TIN-INTERP | Interpolated Ground | 81375.51 | 4.6 | 424.98 | 0 | 30.97 | 0 | OK | Ground clear controls. | 185 | 37.53 | 455.95
12731 | TIN-INTERP | Interpolated Ground | 81375.53 | 5.1 | 424.96 | 0 | 19.83 | 0 | OK | Ground clear controls. | 185 | 37.53 | 444.79
12732 | TIN-INTERP | Interpolated Ground | 81375.54 | -5.12 | 423.39 | 0 | 21.49 | 0 | OK | Ground clear controls. | 185 | 37.53 | 444.88
12733 | TIN-INTERP | Interpolated Ground | 81375.54 | 6.6 | 425 | 0 | 25.28 | 0 | OK | Ground clear controls. | 185 | 37.53 | 450.28
12734 | TIN-INTERP | Interpolated Ground | 81415.39 | -6.62 | 426.95 | 0 | 30.08 | 0 | OK | Ground clear controls. | 185 | 37.53 | 457.03
12735 | TIN-INTERP | Interpolated Ground | 81415.41 | -4.62 | 426.65 | 0 | 36.11 | 0 | OK | Ground clear controls. | 185 | 37.53 | 462.76
12736 | TIN-INTERP | Interpolated Ground | 81415.51 | 4.6 | 425.65 | 0 | 37.13 | 0 | OK | Ground clear controls. | 185 | 37.53 | 462.78
12737 | TIN-INTERP | Interpolated Ground | 81415.53 | 5.1 | 425.66 | 0 | 26 | 0 | OK | Ground clear controls. | 185 | 37.53 | 451.66
12738 | TIN-INTERP | Interpolated Ground | 81415.54 | -5.12 | 426.66 | 0 | 25.07 | 0 | OK | Ground clear controls. | 185 | 37.53 | 451.73
12739 | TIN-INTERP | Interpolated Ground | 81415.54 | 6.6 | 425.61 | 0 | 31.55 | 0 | OK | Ground clear controls. | 185 | 37.53 | 457.16
12740 | TIN-INTERP | Interpolated Ground | 81455.39 | -6.61 | 434.45 | 0 | 30.52 | 0 | OK | Ground clear controls. | 185 | 37.53 | 464.97
12741 | TIN-INTERP | Interpolated Ground | 81455.41 | -4.61 | 434.32 | 0 | 36.26 | 0 | OK | Ground clear controls. | 185 | 37.53 | 470.58
12742 | TIN-INTERP | Interpolated Ground | 81455.51 | 4.59 | 433.06 | 0 | 37.53 | 0 | OK | Ground clear controls. | 185 | 37.53 | 470.59
12743 | TIN-INTERP | Interpolated Ground | 81455.53 | 5.1 | 433.04 | 0 | 26.49 | 0 | OK | Ground clear controls. | 185 | 32.41 | 459.53
12744 | TIN-INTERP | Interpolated Ground | 81455.54 | -5.11 | 434.4 | 0 | 25.18 | 0 | OK | Ground clear controls. | 185 | 32.41 | 459.58
12745 | TIN-INTERP | Interpolated Ground | 81455.54 | 6.6 | 432.62 | 0 | 32.41 | 0 | OK | Ground clear controls. | 185 | 32.41 | 465.03
12746 | TIN-INTERP | Interpolated Ground | 81491.33 | -6.61 | 436.29 | 0 | 36.65 | 0 | OK | Ground clear controls. | 186 | 46.61 | 472.94
12747 | TIN-INTERP | Interpolated Ground | 81491.35 | -5.11 | 436.39 | 0 | 31.05 | 0 | OK | Ground clear controls. | 186 | 46.61 | 467.44
12748 | TIN-INTERP | Interpolated Ground | 81491.41 | -4.61 | 436.38 | 0 | 42.06 | 0 | OK | Ground clear controls. | 186 | 46.61 | 478.44
12749 | TIN-INTERP | Interpolated Ground | 81491.41 | 4.59 | 434.98 | 0 | 43.46 | 0 | OK | Ground clear controls. | 186 | 46.61 | 478.44
12750 | TIN-INTERP | Interpolated Ground | 81491.48 | 6.59 | 434.28 | 0 | 38.66 | 0 | OK | Ground clear controls. | 186 | 46.61 | 472.94
12751 | TIN-INTERP | Interpolated Ground | 81491.48 | 5.09 | 434.81 | 0 | 32.63 | 0 | OK | Ground clear controls. | 186 | 46.61 | 467.44
12752 | TIN-INTERP | Interpolated Ground | 81531.34 | -6.62 | 436.11 | 0 | 39.18 | 0 | OK | Ground clear controls. | 186 | 46.61 | 475.29
12753 | TIN-INTERP | Interpolated Ground | 81531.35 | -5.12 | 435.83 | 0 | 34.01 | 0 | OK | Ground clear controls. | 186 | 46.61 | 469.84
12754 | TIN-INTERP | Interpolated Ground | 81531.41 | -4.62 | 435.7 | 0 | 45.18 | 0 | OK | Ground clear controls. | 186 | 46.61 | 480.88
12755 | TIN-INTERP | Interpolated Ground | 81531.41 | 4.59 | 434.26 | 0 | 46.61 | 0 | OK | Ground clear controls. | 186 | 46.61 | 480.87
12756 | TIN-INTERP | Interpolated Ground | 81531.48 | 6.59 | 433.88 | 0 | 41.46 | 0 | OK | Ground clear controls. | 186 | 45.53 | 475.34
12757 | TIN-INTERP | Interpolated Ground | 81531.48 | 5.09 | 434.27 | 0 | 35.57 | 0 | OK | Ground clear controls. | 186 | 45.53 | 469.84
12758 | TIN-INTERP | Interpolated Ground | 81571.34 | -6.63 | 444.12 | 0 | 34.5 | 0 | OK | Ground clear controls. | 186 | 45.53 | 478.62
12759 | TIN-INTERP | Interpolated Ground | 81571.35 | -5.13 | 443.63 | 0 | 29.59 | 0 | OK | Ground clear controls. | 186 | 45.53 | 473.22
12760 | TIN-INTERP | Interpolated Ground | 81571.41 | -4.63 | 443.47 | 0 | 40.82 | 0 | OK | Ground clear controls. | 186 | 45.53 | 484.29
12761 | TIN-INTERP | Interpolated Ground | 81571.41 | 4.58 | 440.57 | 0 | 43.68 | 0 | OK | Ground clear controls. | 186 | 45.53 | 484.25
12762 | TIN-INTERP | Interpolated Ground | 81571.48 | 6.59 | 439.91 | 0 | 38.8 | 0 | OK | Ground clear controls. | 186 | 45.53 | 478.71
12763 | TIN-INTERP | Interpolated Ground | 81571.48 | 5.09 | 440.48 | 0 | 32.74 | 0 | OK | Ground clear controls. | 186 | 45.53 | 473.22
12764 | TIN-INTERP | Interpolated Ground | 81611.34 | -6.63 | 446.99 | 0 | 35.95 | 0 | OK | Ground clear controls. | 186 | 45.53 | 482.94
12765 | TIN-INTERP | Interpolated Ground | 81611.35 | -5.13 | 446.59 | 0 | 30.98 | 0 | OK | Ground clear controls. | 186 | 45.53 | 477.57
12766 | TIN-INTERP | Interpolated Ground | 81611.41 | -4.63 | 446.5 | 0 | 42.17 | 0 | OK | Ground clear controls. | 186 | 45.53 | 488.67
12767 | TIN-INTERP | Interpolated Ground | 81611.41 | 4.58 | 443.08 | 0 | 45.53 | 0 | OK | Ground clear controls. | 186 | 45.53 | 488.61
12768 | TIN-INTERP | Interpolated Ground | 81611.48 | 6.58 | 442.48 | 0 | 40.58 | 0 | OK | Ground clear controls. | 186 | 43.21 | 483.06
12769 | TIN-INTERP | Interpolated Ground | 81611.48 | 5.08 | 442.94 | 0 | 34.63 | 0 | OK | Ground clear controls. | 186 | 43.21 | 477.57
12770 | TIN-INTERP | Interpolated Ground | 81651.34 | -6.64 | 452.97 | 0 | 35.27 | 0 | OK | Ground clear controls. | 186 | 43.21 | 488.24
12771 | TIN-INTERP | Interpolated Ground | 81651.35 | -5.14 | 452.52 | 0 | 30.38 | 0 | OK | Ground clear controls. | 186 | 43.21 | 482.9
12772 | TIN-INTERP | Interpolated Ground | 81651.41 | -4.64 | 452.4 | 0 | 41.6 | 0 | OK | Ground clear controls. | 186 | 43.21 | 494
12773 | TIN-INTERP | Interpolated Ground | 81651.41 | 4.58 | 450.73 | 0 | 43.21 | 0 | OK | Ground clear controls. | 186 | 43.21 | 493.94
12774 | TIN-INTERP | Interpolated Ground | 81651.48 | 6.58 | 450.64 | 0 | 37.75 | 0 | OK | Ground clear controls. | 186 | 37.75 | 488.39
12775 | TIN-INTERP | Interpolated Ground | 81651.48 | 5.08 | 450.73 | 0 | 32.17 | 0 | OK | Ground clear controls. | 186 | 37.11 | 482.9
12776 | TIN-INTERP | Interpolated Ground | 81691.34 | -6.65 | 470.37 | 0 | 24.17 | 0 | OK | Ground clear controls. | 186 | 37.11 | 494.54
12777 | TIN-INTERP | Interpolated Ground | 81691.35 | -5.15 | 469.93 | 0 | 19.28 | 0 | OK | Ground clear controls. | 186 | 37.11 | 489.21
12778 | TIN-INTERP | Interpolated Ground | 81691.41 | -4.65 | 469.57 | 0 | 30.75 | 0 | OK | Ground clear controls. | 186 | 37.11 | 500.32
12779 | TIN-INTERP | Interpolated Ground | 81691.41 | 4.57 | 467.36 | 0 | 32.89 | 0 | OK | Ground clear controls. | 186 | 37.11 | 500.25
12780 | TIN-INTERP | Interpolated Ground | 81691.48 | 6.57 | 467.23 | 0 | 27.46 | 0 | OK | Ground clear controls. | 186 | 37.11 | 494.69
12781 | TIN-INTERP | Interpolated Ground | 81691.48 | 5.07 | 467.38 | 0 | 21.83 | 0 | OK | Ground clear controls. | 186 | 37.11 | 489.21
12782 | TIN-INTERP | Interpolated Ground | 81731.34 | -6.66 | 483.65 | 0 | 18.19 | 0 | OK | Ground clear controls. | 186 | 37.11 | 501.84
12783 | TIN-INTERP | Interpolated Ground | 81731.35 | -5.16 | 482.86 | 0 | 13.64 | 0 | OK | Ground clear controls. | 186 | 37.11 | 496.5
12784 | TIN-INTERP | Interpolated Ground | 81731.41 | -4.66 | 482.64 | 0 | 24.97 | 0 | OK | Ground clear controls. | 186 | 37.11 | 507.61
12785 | TIN-INTERP | Interpolated Ground | 81731.41 | 4.57 | 477.46 | 0 | 30.08 | 0 | OK | Ground clear controls. | 186 | 37.11 | 507.54
12786 | TIN-INTERP | Interpolated Ground | 81731.48 | 6.57 | 476.35 | 0 | 25.64 | 0 | OK | Ground clear controls. | 186 | 37.11 | 501.99
12787 | TIN-INTERP | Interpolated Ground | 81731.48 | 5.07 | 477.2 | 0 | 19.3 | 0 | OK | Ground clear controls. | 186 | 37.11 | 496.5
12788 | TIN-INTERP | Interpolated Ground | 81771.34 | -6.67 | 492.91 | 0 | 17.23 | 0 | OK | Ground clear controls. | 186 | 37.11 | 510.14
12789 | TIN-INTERP | Interpolated Ground | 81771.35 | -5.17 | 492.54 | 0 | 12.25 | 0 | OK | Ground clear controls. | 186 | 37.11 | 504.79
12790 | TIN-INTERP | Interpolated Ground | 81771.41 | -4.67 | 492.36 | 0 | 23.53 | 0 | OK | Ground clear controls. | 186 | 37.11 | 515.89
12791 | TIN-INTERP | Interpolated Ground | 81771.41 | 4.56 | 488.31 | 0 | 27.52 | 0 | OK | Ground clear controls. | 186 | 37.11 | 515.83
12792 | TIN-INTERP | Interpolated Ground | 81771.48 | 6.56 | 487.49 | 0 | 22.79 | 0 | OK | Ground clear controls. | 186 | 37.11 | 510.28
12793 | TIN-INTERP | Interpolated Ground | 81771.48 | 5.06 | 488.12 | 0 | 16.68 | 0 | OK | Ground clear controls. | 186 | 37.11 | 504.8
12794 | TIN-INTERP | Interpolated Ground | 81811.34 | -6.68 | 498.15 | 0 | 21.3 | 0 | OK | Ground clear controls. | 186 | 37.11 | 519.45
12795 | TIN-INTERP | Interpolated Ground | 81811.35 | -5.18 | 497.79 | 0 | 16.28 | 0 | OK | Ground clear controls. | 186 | 37.11 | 514.07
12796 | TIN-INTERP | Interpolated Ground | 81811.41 | -4.67 | 497.66 | 0 | 27.49 | 0 | OK | Ground clear controls. | 186 | 37.11 | 525.15
12797 | TIN-INTERP | Interpolated Ground | 81811.41 | 4.56 | 494.87 | 0 | 30.22 | 0 | OK | Ground clear controls. | 186 | 37.11 | 525.09
12798 | TIN-INTERP | Interpolated Ground | 81811.48 | 6.56 | 494.26 | 0 | 25.3 | 0 | OK | Ground clear controls. | 186 | 37.11 | 519.56
12799 | TIN-INTERP | Interpolated Ground | 81811.48 | 5.06 | 494.69 | 0 | 19.38 | 0 | OK | Ground clear controls. | 186 | 37.11 | 514.07
12800 | TIN-INTERP | Interpolated Ground | 81851.34 | -6.69 | 505.8 | 0 | 23.98 | 0 | OK | Ground clear controls. | 186 | 37.11 | 529.78
12801 | TIN-INTERP | Interpolated Ground | 81851.35 | -5.18 | 505.51 | 0 | 18.84 | 0 | OK | Ground clear controls. | 186 | 37.11 | 524.35
12802 | TIN-INTERP | Interpolated Ground | 81851.41 | -4.68 | 505.47 | 0 | 29.92 | 0 | OK | Ground clear controls. | 186 | 37.11 | 535.39
12803 | TIN-INTERP | Interpolated Ground | 81851.41 | 4.55 | 504.64 | 0 | 30.72 | 0 | OK | Ground clear controls. | 186 | 37.11 | 535.36
12804 | TIN-INTERP | Interpolated Ground | 81851.48 | 6.56 | 504.42 | 0 | 25.42 | 0 | OK | Ground clear controls. | 186 | 37.11 | 529.84
12805 | TIN-INTERP | Interpolated Ground | 81851.48 | 5.06 | 504.59 | 0 | 19.76 | 0 | OK | Ground clear controls. | 186 | 37.11 | 524.35
12806 | TIN-INTERP | Interpolated Ground | 81891.34 | -6.69 | 512.61 | 0 | 28.5 | 0 | OK | Ground clear controls. | 186 | 37.11 | 541.11
12807 | TIN-INTERP | Interpolated Ground | 81891.35 | -5.19 | 512.22 | 0 | 23.42 | 0 | OK | Ground clear controls. | 186 | 37.11 | 535.64
12808 | TIN-INTERP | Interpolated Ground | 81891.41 | -4.69 | 512.01 | 0 | 34.63 | 0 | OK | Ground clear controls. | 186 | 37.11 | 546.64
12809 | TIN-INTERP | Interpolated Ground | 81891.41 | 4.55 | 509.52 | 0 | 37.11 | 0 | OK | Ground clear controls. | 186 | 37.11 | 546.63
12810 | TIN-INTERP | Interpolated Ground | 81891.48 | 6.55 | 509.18 | 0 | 31.95 | 0 | OK | Ground clear controls. | 186 | 31.95 | 541.13
12811 | TIN-INTERP | Interpolated Ground | 81891.48 | 5.05 | 509.44 | 0 | 26.19 | 0 | OK | Ground clear controls. | 186 | 26.19 | 535.63
12812 | TIN-INTERP | Interpolated Ground | 81895.15 | -5.19 | 512.33 | 0 | 24.43 | 0 | OK | Ground clear controls. | 187 | 51.66 | 536.76
12813 | TIN-INTERP | Interpolated Ground | 81895.2 | -6.69 | 512.58 | 0 | 29.68 | 0 | OK | Ground clear controls. | 187 | 51.66 | 542.26
12814 | TIN-INTERP | Interpolated Ground | 81895.23 | -4.69 | 512.26 | 0 | 35.5 | 0 | OK | Ground clear controls. | 187 | 51.66 | 547.76
12815 | TIN-INTERP | Interpolated Ground | 81895.28 | 4.55 | 509.9 | 0 | 37.86 | 0 | OK | Ground clear controls. | 187 | 51.66 | 547.76
12816 | TIN-INTERP | Interpolated Ground | 81895.3 | 6.55 | 509.46 | 0 | 32.8 | 0 | OK | Ground clear controls. | 187 | 51.66 | 542.26
12817 | TIN-INTERP | Interpolated Ground | 81895.3 | 5.05 | 509.82 | 0 | 26.94 | 0 | OK | Ground clear controls. | 187 | 51.66 | 536.76
12818 | TIN-INTERP | Interpolated Ground | 81935.15 | -5.59 | 517.61 | 0 | 13.44 | 0 | OK | Ground clear controls. | 187 | 51.66 | 531.05
12819 | TIN-INTERP | Interpolated Ground | 81935.2 | -7.1 | 517.09 | 0 | 19.49 | 0 | OK | Ground clear controls. | 187 | 51.66 | 536.58
12820 | TIN-INTERP | Interpolated Ground | 81935.23 | -5.07 | 517.72 | 0 | 24.54 | 0 | OK | Ground clear controls. | 187 | 51.66 | 542.26
12821 | TIN-INTERP | Interpolated Ground | 81935.28 | 4.45 | 519.34 | 0 | 22.87 | 0 | OK | Ground clear controls. | 187 | 51.66 | 542.21
12822 | TIN-INTERP | Interpolated Ground | 81935.3 | 6.47 | 518.58 | 0 | 18.03 | 0 | OK | Ground clear controls. | 187 | 51.66 | 536.61
12823 | TIN-INTERP | Interpolated Ground | 81935.3 | 4.97 | 519 | 0 | 12.08 | 0 | OK | Ground clear controls. | 187 | 51.66 | 531.08
12824 | TIN-INTERP | Interpolated Ground | 81975.14 | -5.98 | 507.98 | 0 | 18.33 | 0 | OK | Ground clear controls. | 187 | 51.66 | 526.31
12825 | TIN-INTERP | Interpolated Ground | 81975.19 | -7.5 | 507.62 | 0 | 24.25 | 0 | OK | Ground clear controls. | 187 | 51.66 | 531.87
12826 | TIN-INTERP | Interpolated Ground | 81975.23 | -5.44 | 508.05 | 0 | 29.66 | 0 | OK | Ground clear controls. | 187 | 51.66 | 537.71
12827 | TIN-INTERP | Interpolated Ground | 81975.28 | 4.34 | 509.72 | 0 | 27.91 | 0 | OK | Ground clear controls. | 187 | 51.66 | 537.63
12828 | TIN-INTERP | Interpolated Ground | 81975.3 | 6.39 | 509.99 | 0 | 21.92 | 0 | OK | Ground clear controls. | 187 | 51.66 | 531.91
12829 | TIN-INTERP | Interpolated Ground | 81975.3 | 4.89 | 509.78 | 0 | 16.58 | 0 | OK | Ground clear controls. | 187 | 51.66 | 526.36
12830 | TIN-INTERP | Interpolated Ground | 82015.14 | -6.37 | 505.93 | 0 | 16.61 | 0 | OK | Ground clear controls. | 187 | 51.66 | 522.54
12831 | TIN-INTERP | Interpolated Ground | 82015.19 | -7.9 | 505.15 | 0 | 22.98 | 0 | OK | Ground clear controls. | 187 | 51.66 | 528.13
12832 | TIN-INTERP | Interpolated Ground | 82015.23 | -5.82 | 506.08 | 0 | 28.02 | 0 | OK | Ground clear controls. | 187 | 51.66 | 534.1
12833 | TIN-INTERP | Interpolated Ground | 82015.28 | 4.24 | 508.91 | 0 | 25.09 | 0 | OK | Ground clear controls. | 187 | 51.66 | 534
12834 | TIN-INTERP | Interpolated Ground | 82015.3 | 6.3 | 509.54 | 0 | 18.64 | 0 | OK | Ground clear controls. | 187 | 51.66 | 528.18
12835 | TIN-INTERP | Interpolated Ground | 82015.3 | 4.81 | 509.06 | 0 | 13.55 | 0 | OK | Ground clear controls. | 187 | 51.66 | 522.61
12836 | TIN-INTERP | Interpolated Ground | 82055.14 | -6.77 | 501.8 | 0 | 17.94 | 0 | OK | Ground clear controls. | 187 | 51.66 | 519.74
12837 | TIN-INTERP | Interpolated Ground | 82055.19 | -8.31 | 501.04 | 0 | 24.33 | 0 | OK | Ground clear controls. | 187 | 51.66 | 525.37
12838 | TIN-INTERP | Interpolated Ground | 82055.22 | -6.2 | 502.04 | 0 | 29.4 | 0 | OK | Ground clear controls. | 187 | 51.66 | 531.44
12839 | TIN-INTERP | Interpolated Ground | 82055.28 | 4.14 | 506.79 | 0 | 24.54 | 0 | OK | Ground clear controls. | 187 | 51.66 | 531.33
12840 | TIN-INTERP | Interpolated Ground | 82055.3 | 6.22 | 508.33 | 0 | 17.08 | 0 | OK | Ground clear controls. | 187 | 51.66 | 525.41
12841 | TIN-INTERP | Interpolated Ground | 82055.3 | 4.72 | 507.23 | 0 | 12.58 | 0 | OK | Ground clear controls. | 187 | 51.66 | 519.81
12842 | TIN-INTERP | Interpolated Ground | 82095.14 | -7.16 | 496.51 | 0 | 21.38 | 0 | OK | Ground clear controls. | 187 | 51.66 | 517.89
12843 | TIN-INTERP | Interpolated Ground | 82095.19 | -8.71 | 496.38 | 0 | 27.18 | 0 | OK | Ground clear controls. | 187 | 51.66 | 523.56
12844 | TIN-INTERP | Interpolated Ground | 82095.22 | -6.57 | 496.59 | 0 | 33.14 | 0 | OK | Ground clear controls. | 187 | 51.66 | 529.73
12845 | TIN-INTERP | Interpolated Ground | 82095.28 | 4.04 | 498.85 | 0 | 30.76 | 0 | OK | Ground clear controls. | 187 | 51.66 | 529.61
12846 | TIN-INTERP | Interpolated Ground | 82095.3 | 6.14 | 499.01 | 0 | 24.59 | 0 | OK | Ground clear controls. | 187 | 51.66 | 523.6
12847 | TIN-INTERP | Interpolated Ground | 82095.3 | 4.64 | 498.83 | 0 | 19.14 | 0 | OK | Ground clear controls. | 187 | 51.66 | 517.97
12848 | TIN-INTERP | Interpolated Ground | 82135.14 | -7.55 | 486.93 | 0 | 30.08 | 0 | OK | Ground clear controls. | 187 | 51.66 | 517.01
12849 | TIN-INTERP | Interpolated Ground | 82135.19 | -9.11 | 486.08 | 0 | 36.64 | 0 | OK | Ground clear controls. | 187 | 51.66 | 522.72
12850 | TIN-INTERP | Interpolated Ground | 82135.22 | -6.95 | 487.2 | 0 | 41.75 | 0 | OK | Ground clear controls. | 187 | 51.66 | 528.95
12851 | TIN-INTERP | Interpolated Ground | 82135.28 | 3.93 | 492.17 | 0 | 36.68 | 0 | OK | Ground clear controls. | 187 | 51.66 | 528.85
12852 | TIN-INTERP | Interpolated Ground | 82135.3 | 6.06 | 493.12 | 0 | 29.63 | 0 | OK | Ground clear controls. | 187 | 51.66 | 522.75
12853 | TIN-INTERP | Interpolated Ground | 82135.3 | 4.56 | 492.47 | 0 | 24.61 | 0 | OK | Ground clear controls. | 187 | 51.66 | 517.08
12854 | TIN-INTERP | Interpolated Ground | 82175.13 | -7.95 | 477.19 | 0 | 39.92 | 0 | OK | Ground clear controls. | 187 | 51.66 | 517.11
12855 | TIN-INTERP | Interpolated Ground | 82175.18 | -9.52 | 476.62 | 0 | 46.23 | 0 | OK | Ground clear controls. | 187 | 51.66 | 522.85
12856 | TIN-INTERP | Interpolated Ground | 82175.22 | -7.32 | 477.46 | 0 | 51.66 | 0 | OK | Ground clear controls. | 187 | 51.66 | 529.12
12857 | TIN-INTERP | Interpolated Ground | 82175.28 | 3.83 | 482.66 | 0 | 46.37 | 0 | OK | Ground clear controls. | 187 | 46.37 | 529.03
12858 | TIN-INTERP | Interpolated Ground | 82175.3 | 5.98 | 483.63 | 0 | 39.23 | 0 | OK | Ground clear controls. | 187 | 40.32 | 522.86
12859 | TIN-INTERP | Interpolated Ground | 82175.3 | 4.48 | 482.89 | 0 | 34.25 | 0 | OK | Ground clear controls. | 187 | 40.32 | 517.14
12860 | TIN-INTERP | Interpolated Ground | 82215.13 | -8.34 | 489.86 | 0 | 28.3 | 0 | OK | Ground clear controls. | 187 | 40.32 | 518.16
12861 | TIN-INTERP | Interpolated Ground | 82215.18 | -9.92 | 490.06 | 0 | 33.87 | 0 | OK | Ground clear controls. | 187 | 40.32 | 523.93
12862 | TIN-INTERP | Interpolated Ground | 82215.22 | -7.7 | 489.91 | 0 | 40.32 | 0 | OK | Ground clear controls. | 187 | 40.32 | 530.23
12863 | TIN-INTERP | Interpolated Ground | 82215.28 | 3.73 | 490.59 | 0 | 39.58 | 0 | OK | Ground clear controls. | 187 | 39.58 | 530.17
12864 | TIN-INTERP | Interpolated Ground | 82215.3 | 5.89 | 490.8 | 0 | 33.12 | 0 | OK | Ground clear controls. | 187 | 33.12 | 523.92
12865 | TIN-INTERP | Interpolated Ground | 82215.3 | 4.4 | 490.59 | 0 | 27.58 | 0 | OK | Ground clear controls. | 187 | 27.58 | 518.17
12866 | TIN-INTERP | Interpolated Ground | 82234.4 | 3.71 | 496.14 | 0 | 34.94 | 0 | OK | Ground clear controls. | 188 | 67.27 | 531.08
12867 | TIN-INTERP | Interpolated Ground | 82234.4 | 4.39 | 496.32 | 0 | 22.69 | 0 | OK | Ground clear controls. | 188 | 67.27 | 519.01
12868 | TIN-INTERP | Interpolated Ground | 82234.4 | 5.89 | 496.58 | 0 | 28.22 | 0 | OK | Ground clear controls. | 188 | 67.27 | 524.8
12869 | TIN-INTERP | Interpolated Ground | 82235.29 | -7.87 | 495.24 | 0 | 35.81 | 0 | OK | Ground clear controls. | 188 | 67.27 | 531.05
12870 | TIN-INTERP | Interpolated Ground | 82235.38 | -8.52 | 495.15 | 0 | 23.8 | 0 | OK | Ground clear controls. | 188 | 67.27 | 518.95
12871 | TIN-INTERP | Interpolated Ground | 82235.55 | -10.1 | 494.98 | 0 | 29.76 | 0 | OK | Ground clear controls. | 188 | 67.27 | 524.74
12872 | TIN-INTERP | Interpolated Ground | 82273.77 | 5.92 | 487.27 | 0 | 33.98 | 0 | OK | Ground clear controls. | 188 | 67.27 | 521.25
12873 | TIN-INTERP | Interpolated Ground | 82273.9 | 4.42 | 487.01 | 0 | 28.48 | 0 | OK | Ground clear controls. | 188 | 67.27 | 515.49
12874 | TIN-INTERP | Interpolated Ground | 82274.03 | 3.77 | 486.8 | 0 | 40.69 | 0 | OK | Ground clear controls. | 188 | 67.27 | 527.49
12875 | TIN-INTERP | Interpolated Ground | 82275.29 | -7.56 | 482.48 | 0 | 45.03 | 0 | OK | Ground clear controls. | 188 | 67.27 | 527.51
12876 | TIN-INTERP | Interpolated Ground | 82275.37 | -8.2 | 482.28 | 0 | 33.15 | 0 | OK | Ground clear controls. | 188 | 67.27 | 515.43
12877 | TIN-INTERP | Interpolated Ground | 82275.55 | -9.77 | 481.63 | 0 | 39.55 | 0 | OK | Ground clear controls. | 188 | 67.27 | 521.18
12878 | TIN-INTERP | Interpolated Ground | 82313.77 | 5.98 | 469.64 | 0 | 49.02 | 0 | OK | Ground clear controls. | 188 | 67.27 | 518.66
12879 | TIN-INTERP | Interpolated Ground | 82313.9 | 4.48 | 469.8 | 0 | 43.12 | 0 | OK | Ground clear controls. | 188 | 67.27 | 512.92
12880 | TIN-INTERP | Interpolated Ground | 82314.03 | 3.84 | 469.84 | 0 | 55 | 0 | OK | Ground clear controls. | 188 | 67.27 | 524.84
12881 | TIN-INTERP | Interpolated Ground | 82315.29 | -7.26 | 468.02 | 0 | 56.89 | 0 | OK | Ground clear controls. | 188 | 67.27 | 524.91
12882 | TIN-INTERP | Interpolated Ground | 82315.37 | -7.88 | 467.79 | 0 | 45.07 | 0 | OK | Ground clear controls. | 188 | 67.27 | 512.86
12883 | TIN-INTERP | Interpolated Ground | 82315.55 | -9.44 | 467.22 | 0 | 51.37 | 0 | OK | Ground clear controls. | 188 | 67.27 | 518.59
12884 | TIN-INTERP | Interpolated Ground | 82353.77 | 6.04 | 459.5 | 0 | 57.52 | 0 | OK | Ground clear controls. | 188 | 67.27 | 517.02
12885 | TIN-INTERP | Interpolated Ground | 82353.9 | 4.54 | 459.01 | 0 | 52.29 | 0 | OK | Ground clear controls. | 188 | 67.27 | 511.3
12886 | TIN-INTERP | Interpolated Ground | 82354.03 | 3.92 | 458.8 | 0 | 64.35 | 0 | OK | Ground clear controls. | 188 | 67.27 | 523.15
12887 | TIN-INTERP | Interpolated Ground | 82355.29 | -6.95 | 455.97 | 0 | 67.27 | 0 | OK | Ground clear controls. | 188 | 67.27 | 523.24
12888 | TIN-INTERP | Interpolated Ground | 82355.37 | -7.56 | 455.85 | 0 | 55.41 | 0 | OK | Ground clear controls. | 188 | 61.19 | 511.26
12889 | TIN-INTERP | Interpolated Ground | 82355.54 | -9.11 | 455.76 | 0 | 61.19 | 0 | OK | Ground clear controls. | 188 | 61.19 | 516.95
12890 | TIN-INTERP | Interpolated Ground | 82393.77 | 6.1 | 471.01 | 0 | 45.33 | 0 | OK | Ground clear controls. | 188 | 50.33 | 516.34
12891 | TIN-INTERP | Interpolated Ground | 82393.9 | 4.6 | 471.75 | 0 | 38.89 | 0 | OK | Ground clear controls. | 188 | 50.33 | 510.64
12892 | TIN-INTERP | Interpolated Ground | 82394.03 | 4 | 472.07 | 0 | 50.33 | 0 | OK | Ground clear controls. | 188 | 50.33 | 522.4
12893 | TIN-INTERP | Interpolated Ground | 82395.29 | -6.65 | 476.62 | 0 | 45.9 | 0 | OK | Ground clear controls. | 188 | 46.11 | 522.52
12894 | TIN-INTERP | Interpolated Ground | 82395.37 | -7.24 | 476.54 | 0 | 34.07 | 0 | OK | Ground clear controls. | 188 | 46.11 | 510.61
12895 | TIN-INTERP | Interpolated Ground | 82395.54 | -8.79 | 476.21 | 0 | 40.07 | 0 | OK | Ground clear controls. | 188 | 46.11 | 516.28
12896 | TIN-INTERP | Interpolated Ground | 82433.77 | 6.16 | 487.23 | 0 | 29.36 | 0 | OK | Ground clear controls. | 188 | 46.11 | 516.59
12897 | TIN-INTERP | Interpolated Ground | 82433.9 | 4.66 | 487.39 | 0 | 23.55 | 0 | OK | Ground clear controls. | 188 | 46.11 | 510.94
12898 | TIN-INTERP | Interpolated Ground | 82434.03 | 4.07 | 487.46 | 0 | 35.13 | 0 | OK | Ground clear controls. | 188 | 46.11 | 522.59
12899 | TIN-INTERP | Interpolated Ground | 82435.29 | -6.34 | 486.83 | 0 | 35.91 | 0 | OK | Ground clear controls. | 188 | 46.11 | 522.74
12900 | TIN-INTERP | Interpolated Ground | 82435.37 | -6.92 | 486.85 | 0 | 24.09 | 0 | OK | Ground clear controls. | 188 | 46.11 | 510.94
12901 | TIN-INTERP | Interpolated Ground | 82435.54 | -8.46 | 486.49 | 0 | 30.09 | 0 | OK | Ground clear controls. | 188 | 46.11 | 516.58
12902 | TIN-INTERP | Interpolated Ground | 82473.77 | 6.22 | 490.56 | 0 | 27.26 | 0 | OK | Ground clear controls. | 188 | 46.11 | 517.82
12903 | TIN-INTERP | Interpolated Ground | 82473.9 | 4.72 | 489.84 | 0 | 22.35 | 0 | OK | Ground clear controls. | 188 | 46.11 | 512.19
12904 | TIN-INTERP | Interpolated Ground | 82474.03 | 4.15 | 489.6 | 0 | 34.13 | 0 | OK | Ground clear controls. | 188 | 46.11 | 523.73
12905 | TIN-INTERP | Interpolated Ground | 82475.29 | -6.04 | 484.41 | 0 | 39.49 | 0 | OK | Ground clear controls. | 188 | 46.11 | 523.9
12906 | TIN-INTERP | Interpolated Ground | 82475.37 | -6.6 | 484.05 | 0 | 28.16 | 0 | OK | Ground clear controls. | 188 | 46.11 | 512.21
12907 | TIN-INTERP | Interpolated Ground | 82475.54 | -8.13 | 483.14 | 0 | 34.69 | 0 | OK | Ground clear controls. | 188 | 46.11 | 517.83
12908 | TIN-INTERP | Interpolated Ground | 82513.77 | 6.28 | 485.25 | 0 | 34.74 | 0 | OK | Ground clear controls. | 188 | 46.11 | 519.99
12909 | TIN-INTERP | Interpolated Ground | 82513.9 | 4.78 | 485.04 | 0 | 29.36 | 0 | OK | Ground clear controls. | 188 | 46.11 | 514.4
12910 | TIN-INTERP | Interpolated Ground | 82514.03 | 4.23 | 484.93 | 0 | 40.89 | 0 | OK | Ground clear controls. | 188 | 46.11 | 525.82
12911 | TIN-INTERP | Interpolated Ground | 82515.29 | -5.73 | 483.27 | 0 | 42.75 | 0 | OK | Ground clear controls. | 188 | 46.11 | 526.02
12912 | TIN-INTERP | Interpolated Ground | 82515.37 | -6.28 | 483.11 | 0 | 31.34 | 0 | OK | Ground clear controls. | 188 | 46.11 | 514.45
12913 | TIN-INTERP | Interpolated Ground | 82515.54 | -7.8 | 482.28 | 0 | 37.77 | 0 | OK | Ground clear controls. | 188 | 46.11 | 520.05
12914 | TIN-INTERP | Interpolated Ground | 82553.77 | 6.34 | 484.06 | 0 | 39.07 | 0 | OK | Ground clear controls. | 188 | 46.11 | 523.13
12915 | TIN-INTERP | Interpolated Ground | 82553.9 | 4.84 | 483.91 | 0 | 33.65 | 0 | OK | Ground clear controls. | 188 | 46.11 | 517.56
12916 | TIN-INTERP | Interpolated Ground | 82554.03 | 4.31 | 483.88 | 0 | 44.99 | 0 | OK | Ground clear controls. | 188 | 46.11 | 528.87
12917 | TIN-INTERP | Interpolated Ground | 82555.28 | -5.42 | 482.95 | 0 | 46.11 | 0 | OK | Ground clear controls. | 188 | 46.11 | 529.06
12918 | TIN-INTERP | Interpolated Ground | 82555.37 | -5.96 | 482.89 | 0 | 34.77 | 0 | OK | Ground clear controls. | 188 | 40.48 | 517.66
12919 | TIN-INTERP | Interpolated Ground | 82555.54 | -7.47 | 482.75 | 0 | 40.48 | 0 | OK | Ground clear controls. | 188 | 40.48 | 523.23
12920 | TIN-INTERP | Interpolated Ground | 82593.77 | 6.4 | 497.04 | 0 | 30.17 | 0 | OK | Ground clear controls. | 188 | 35.56 | 527.21
12921 | TIN-INTERP | Interpolated Ground | 82593.9 | 4.9 | 497.25 | 0 | 24.43 | 0 | OK | Ground clear controls. | 188 | 35.56 | 521.68
12922 | TIN-INTERP | Interpolated Ground | 82594.03 | 4.38 | 497.3 | 0 | 35.56 | 0 | OK | Ground clear controls. | 188 | 35.56 | 532.86
12923 | TIN-INTERP | Interpolated Ground | 82595.28 | -5.12 | 498.68 | 0 | 34.37 | 0 | OK | Ground clear controls. | 188 | 34.37 | 533.05
12924 | TIN-INTERP | Interpolated Ground | 82595.36 | -5.64 | 498.75 | 0 | 23.08 | 0 | OK | Ground clear controls. | 188 | 28.49 | 521.83
12925 | TIN-INTERP | Interpolated Ground | 82595.54 | -7.14 | 498.89 | 0 | 28.49 | 0 | OK | Ground clear controls. | 188 | 28.49 | 527.38
12926 | TIN-INTERP | Interpolated Ground | 82633.77 | 6.47 | 513.89 | 0 | 18.37 | 0 | OK | Ground clear controls. | 188 | 25.72 | 532.26
12927 | TIN-INTERP | Interpolated Ground | 82633.9 | 4.97 | 513.6 | 0 | 13.16 | 0 | OK | Ground clear controls. | 188 | 25.72 | 526.76
12928 | TIN-INTERP | Interpolated Ground | 82634.03 | 4.46 | 513.47 | 0 | 24.33 | 0 | OK | Ground clear controls. | 188 | 25.72 | 537.8
12929 | TIN-INTERP | Interpolated Ground | 82635.28 | -4.81 | 512.27 | 0 | 25.72 | 0 | OK | Ground clear controls. | 188 | 25.72 | 537.99
12930 | TIN-INTERP | Interpolated Ground | 82635.36 | -5.32 | 512.2 | 0 | 14.76 | 0 | OK | Ground clear controls. | 188 | 20.34 | 526.96
12931 | TIN-INTERP | Interpolated Ground | 82635.53 | -6.82 | 512.16 | 0 | 20.34 | 0 | OK | Ground clear controls. | 188 | 20.34 | 532.5
12932 | TIN-INTERP | Interpolated Ground | 82638.72 | -4.79 | 512.36 | 0 | 26.09 | 0 | OK | Ground clear controls. | 189 | 54.53 | 538.45
12933 | TIN-INTERP | Interpolated Ground | 82638.77 | 6.47 | 514.37 | 0 | 18.58 | 0 | OK | Ground clear controls. | 189 | 54.53 | 532.95
12934 | TIN-INTERP | Interpolated Ground | 82638.77 | -6.79 | 512.25 | 0 | 20.7 | 0 | OK | Ground clear controls. | 189 | 54.53 | 532.95
12935 | TIN-INTERP | Interpolated Ground | 82638.78 | 4.47 | 514.04 | 0 | 24.41 | 0 | OK | Ground clear controls. | 189 | 54.53 | 538.45
12936 | TIN-INTERP | Interpolated Ground | 82638.85 | 4.97 | 514.15 | 0 | 13.3 | 0 | OK | Ground clear controls. | 189 | 54.53 | 527.45
12937 | TIN-INTERP | Interpolated Ground | 82638.87 | -5.29 | 512.3 | 0 | 15.15 | 0 | OK | Ground clear controls. | 189 | 54.53 | 527.45
12938 | TIN-INTERP | Interpolated Ground | 82678.72 | -4.82 | 499.72 | 0 | 34.41 | 0 | OK | Ground clear controls. | 189 | 54.53 | 534.13
12939 | TIN-INTERP | Interpolated Ground | 82678.77 | 6.43 | 500.68 | 0 | 27.9 | 0 | OK | Ground clear controls. | 189 | 54.53 | 528.58
12940 | TIN-INTERP | Interpolated Ground | 82678.77 | -6.82 | 499.57 | 0 | 28.98 | 0 | OK | Ground clear controls. | 189 | 54.53 | 528.55
12941 | TIN-INTERP | Interpolated Ground | 82678.78 | 4.43 | 500.76 | 0 | 33.36 | 0 | OK | Ground clear controls. | 189 | 54.53 | 534.12
12942 | TIN-INTERP | Interpolated Ground | 82678.85 | 4.93 | 500.77 | 0 | 22.34 | 0 | OK | Ground clear controls. | 189 | 54.53 | 523.11
12943 | TIN-INTERP | Interpolated Ground | 82678.87 | -5.32 | 499.63 | 0 | 23.48 | 0 | OK | Ground clear controls. | 189 | 54.53 | 523.11
12944 | TIN-INTERP | Interpolated Ground | 82718.72 | -4.85 | 488.27 | 0 | 42.48 | 0 | OK | Ground clear controls. | 189 | 54.53 | 530.75
12945 | TIN-INTERP | Interpolated Ground | 82718.77 | 6.4 | 486.9 | 0 | 38.26 | 0 | OK | Ground clear controls. | 189 | 54.53 | 525.16
12946 | TIN-INTERP | Interpolated Ground | 82718.77 | -6.85 | 488.99 | 0 | 36.13 | 0 | OK | Ground clear controls. | 189 | 54.53 | 525.12
12947 | TIN-INTERP | Interpolated Ground | 82718.78 | 4.39 | 486.65 | 0 | 44.09 | 0 | OK | Ground clear controls. | 189 | 54.53 | 530.74
12948 | TIN-INTERP | Interpolated Ground | 82718.85 | 4.9 | 486.6 | 0 | 33.13 | 0 | OK | Ground clear controls. | 189 | 54.53 | 519.73
12949 | TIN-INTERP | Interpolated Ground | 82718.87 | -5.35 | 488.51 | 0 | 31.21 | 0 | OK | Ground clear controls. | 189 | 54.53 | 519.72
12950 | TIN-INTERP | Interpolated Ground | 82758.72 | -4.88 | 473.8 | 0 | 54.53 | 0 | OK | Ground clear controls. | 189 | 54.53 | 528.33
12951 | TIN-INTERP | Interpolated Ground | 82758.77 | 6.36 | 475.27 | 0 | 47.43 | 0 | OK | Ground clear controls. | 189 | 52.77 | 522.7
12952 | TIN-INTERP | Interpolated Ground | 82758.77 | -6.88 | 473.97 | 0 | 48.67 | 0 | OK | Ground clear controls. | 189 | 52.77 | 522.64
12953 | TIN-INTERP | Interpolated Ground | 82758.78 | 4.36 | 475.53 | 0 | 52.77 | 0 | OK | Ground clear controls. | 189 | 52.77 | 528.3
12954 | TIN-INTERP | Interpolated Ground | 82758.85 | 4.86 | 475.51 | 0 | 41.78 | 0 | OK | Ground clear controls. | 189 | 47.47 | 517.29
12955 | TIN-INTERP | Interpolated Ground | 82758.87 | -5.38 | 473.63 | 0 | 43.64 | 0 | OK | Ground clear controls. | 189 | 47.47 | 517.27
12956 | TIN-INTERP | Interpolated Ground | 82798.72 | -4.91 | 481.45 | 0 | 45.39 | 0 | OK | Ground clear controls. | 189 | 47.47 | 526.84
12957 | TIN-INTERP | Interpolated Ground | 82798.77 | 6.32 | 478.7 | 0 | 42.5 | 0 | OK | Ground clear controls. | 189 | 47.47 | 521.2
12958 | TIN-INTERP | Interpolated Ground | 82798.77 | -6.91 | 481.46 | 0 | 39.67 | 0 | OK | Ground clear controls. | 189 | 47.47 | 521.13
12959 | TIN-INTERP | Interpolated Ground | 82798.78 | 4.32 | 479.34 | 0 | 47.47 | 0 | OK | Ground clear controls. | 189 | 47.47 | 526.81
12960 | TIN-INTERP | Interpolated Ground | 82798.85 | 4.82 | 479.17 | 0 | 36.63 | 0 | OK | Ground clear controls. | 189 | 45.94 | 515.8
12961 | TIN-INTERP | Interpolated Ground | 82798.87 | -5.41 | 481.56 | 0 | 34.21 | 0 | OK | Ground clear controls. | 189 | 45.94 | 515.77
12962 | TIN-INTERP | Interpolated Ground | 82838.72 | -4.95 | 480.36 | 0 | 45.94 | 0 | OK | Ground clear controls. | 189 | 45.94 | 526.3
12963 | TIN-INTERP | Interpolated Ground | 82838.77 | 6.28 | 485.35 | 0 | 35.3 | 0 | OK | Ground clear controls. | 189 | 45.58 | 520.65
12964 | TIN-INTERP | Interpolated Ground | 82838.77 | -6.94 | 479.67 | 0 | 40.91 | 0 | OK | Ground clear controls. | 189 | 45.58 | 520.58
12965 | TIN-INTERP | Interpolated Ground | 82838.78 | 4.28 | 484.54 | 0 | 41.73 | 0 | OK | Ground clear controls. | 189 | 45.58 | 526.27
12966 | TIN-INTERP | Interpolated Ground | 82838.85 | 4.78 | 484.7 | 0 | 30.56 | 0 | OK | Ground clear controls. | 189 | 45.58 | 515.26
12967 | TIN-INTERP | Interpolated Ground | 82838.87 | -5.45 | 480.11 | 0 | 35.12 | 0 | OK | Ground clear controls. | 189 | 45.58 | 515.23
12968 | TIN-INTERP | Interpolated Ground | 82878.72 | -4.98 | 486.16 | 0 | 40.54 | 0 | OK | Ground clear controls. | 189 | 45.58 | 526.7
12969 | TIN-INTERP | Interpolated Ground | 82878.77 | 6.24 | 480.35 | 0 | 40.7 | 0 | OK | Ground clear controls. | 189 | 45.58 | 521.05
12970 | TIN-INTERP | Interpolated Ground | 82878.77 | -6.97 | 486.8 | 0 | 34.19 | 0 | OK | Ground clear controls. | 189 | 45.58 | 520.99
12971 | TIN-INTERP | Interpolated Ground | 82878.78 | 4.24 | 481.09 | 0 | 45.58 | 0 | OK | Ground clear controls. | 189 | 45.58 | 526.67
12972 | TIN-INTERP | Interpolated Ground | 82878.85 | 4.75 | 480.76 | 0 | 34.89 | 0 | OK | Ground clear controls. | 189 | 44.75 | 515.65
12973 | TIN-INTERP | Interpolated Ground | 82878.87 | -5.48 | 486.38 | 0 | 29.26 | 0 | OK | Ground clear controls. | 189 | 44.75 | 515.64
12974 | TIN-INTERP | Interpolated Ground | 82918.72 | -5.01 | 499.82 | 0 | 28.23 | 0 | OK | Ground clear controls. | 189 | 44.75 | 528.05
12975 | TIN-INTERP | Interpolated Ground | 82918.77 | 6.21 | 493.2 | 0 | 29.19 | 0 | OK | Ground clear controls. | 189 | 44.75 | 522.39
12976 | TIN-INTERP | Interpolated Ground | 82918.77 | -7 | 500.52 | 0 | 21.84 | 0 | OK | Ground clear controls. | 189 | 44.75 | 522.36
12977 | TIN-INTERP | Interpolated Ground | 82918.78 | 4.21 | 494.26 | 0 | 33.74 | 0 | OK | Ground clear controls. | 189 | 44.75 | 528
12978 | TIN-INTERP | Interpolated Ground | 82918.85 | 4.71 | 494.09 | 0 | 22.91 | 0 | OK | Ground clear controls. | 189 | 44.75 | 517
12979 | TIN-INTERP | Interpolated Ground | 82918.87 | -5.51 | 500.03 | 0 | 16.97 | 0 | OK | Ground clear controls. | 189 | 44.75 | 517
12980 | TIN-INTERP | Interpolated Ground | 82958.72 | -5.04 | 492.21 | 0 | 38.13 | 0 | OK | Ground clear controls. | 189 | 44.75 | 530.34
12981 | TIN-INTERP | Interpolated Ground | 82958.77 | 6.17 | 494.47 | 0 | 30.22 | 0 | OK | Ground clear controls. | 189 | 44.75 | 524.69
12982 | TIN-INTERP | Interpolated Ground | 82958.77 | -7.03 | 491.87 | 0 | 32.82 | 0 | OK | Ground clear controls. | 189 | 44.75 | 524.69
12983 | TIN-INTERP | Interpolated Ground | 82958.78 | 4.17 | 493.99 | 0 | 36.3 | 0 | OK | Ground clear controls. | 189 | 44.75 | 530.29
12984 | TIN-INTERP | Interpolated Ground | 82958.85 | 4.67 | 494.08 | 0 | 25.2 | 0 | OK | Ground clear controls. | 189 | 44.75 | 519.28
12985 | TIN-INTERP | Interpolated Ground | 82958.87 | -5.54 | 492.14 | 0 | 27.16 | 0 | OK | Ground clear controls. | 189 | 44.75 | 519.3
12986 | TIN-INTERP | Interpolated Ground | 82998.72 | -5.07 | 488.83 | 0 | 44.75 | 0 | OK | Ground clear controls. | 189 | 44.75 | 533.58
12987 | TIN-INTERP | Interpolated Ground | 82998.77 | 6.13 | 492.75 | 0 | 35.2 | 0 | OK | Ground clear controls. | 189 | 41.44 | 527.95
12988 | TIN-INTERP | Interpolated Ground | 82998.77 | -7.06 | 488.23 | 0 | 39.76 | 0 | OK | Ground clear controls. | 189 | 41.44 | 527.99
12989 | TIN-INTERP | Interpolated Ground | 82998.78 | 4.13 | 492.09 | 0 | 41.44 | 0 | OK | Ground clear controls. | 189 | 41.44 | 533.53
12990 | TIN-INTERP | Interpolated Ground | 82998.85 | 4.63 | 492.39 | 0 | 30.14 | 0 | OK | Ground clear controls. | 189 | 34.51 | 522.53
12991 | TIN-INTERP | Interpolated Ground | 82998.87 | -5.57 | 488.68 | 0 | 33.88 | 0 | OK | Ground clear controls. | 189 | 34.51 | 522.56
12992 | TIN-INTERP | Interpolated Ground | 83038.72 | -5.1 | 503.25 | 0 | 34.51 | 0 | OK | Ground clear controls. | 189 | 34.51 | 537.76
12993 | TIN-INTERP | Interpolated Ground | 83038.77 | 6.09 | 506.89 | 0 | 25.27 | 0 | OK | Ground clear controls. | 189 | 31.26 | 532.16
12994 | TIN-INTERP | Interpolated Ground | 83038.77 | -7.09 | 502.43 | 0 | 29.82 | 0 | OK | Ground clear controls. | 189 | 31.26 | 532.25
12995 | TIN-INTERP | Interpolated Ground | 83038.78 | 4.09 | 506.45 | 0 | 31.26 | 0 | OK | Ground clear controls. | 189 | 31.26 | 537.71
12996 | TIN-INTERP | Interpolated Ground | 83038.85 | 4.59 | 506.57 | 0 | 20.15 | 0 | OK | Ground clear controls. | 189 | 23.64 | 526.72
12997 | TIN-INTERP | Interpolated Ground | 83038.87 | -5.6 | 503.12 | 0 | 23.64 | 0 | OK | Ground clear controls. | 189 | 23.64 | 526.76
12998 | TIN-INTERP | Interpolated Ground | 83058.25 | -7.11 | 508.35 | 0 | 26.32 | 0 | OK | Ground clear controls. | 190 | 55.97 | 534.67
12999 | TIN-INTERP | Interpolated Ground | 83058.33 | -5.12 | 508.44 | 0 | 31.72 | 0 | OK | Ground clear controls. | 190 | 55.97 | 540.16
13000 | TIN-INTERP | Interpolated Ground | 83058.37 | -5.62 | 508.43 | 0 | 20.74 | 0 | OK | Ground clear controls. | 190 | 55.97 | 529.17
13001 | TIN-INTERP | Interpolated Ground | 83058.65 | 4.58 | 508.28 | 0 | 20.88 | 0 | OK | Ground clear controls. | 190 | 55.97 | 529.16
13002 | TIN-INTERP | Interpolated Ground | 83058.67 | 4.08 | 508.35 | 0 | 31.81 | 0 | OK | Ground clear controls. | 190 | 55.97 | 540.16
13003 | TIN-INTERP | Interpolated Ground | 83058.78 | 6.08 | 508.08 | 0 | 26.58 | 0 | OK | Ground clear controls. | 190 | 55.97 | 534.66
13004 | TIN-INTERP | Interpolated Ground | 83098.53 | -7.02 | 500.81 | 0 | 32.51 | 0 | OK | Ground clear controls. | 190 | 55.97 | 533.32
13005 | TIN-INTERP | Interpolated Ground | 83098.54 | -5.03 | 500.62 | 0 | 38.23 | 0 | OK | Ground clear controls. | 190 | 55.97 | 538.85
13006 | TIN-INTERP | Interpolated Ground | 83098.59 | -5.52 | 500.67 | 0 | 27.18 | 0 | OK | Ground clear controls. | 190 | 55.97 | 527.85
13007 | TIN-INTERP | Interpolated Ground | 83098.65 | 4.7 | 497.89 | 0 | 29.95 | 0 | OK | Ground clear controls. | 190 | 55.97 | 527.84
13008 | TIN-INTERP | Interpolated Ground | 83098.67 | 4.2 | 498.04 | 0 | 40.8 | 0 | OK | Ground clear controls. | 190 | 55.97 | 538.84
13009 | TIN-INTERP | Interpolated Ground | 83098.78 | 6.2 | 497.84 | 0 | 35.49 | 0 | OK | Ground clear controls. | 190 | 55.97 | 533.33
13010 | TIN-INTERP | Interpolated Ground | 83138.53 | -6.92 | 482.85 | 0 | 50.09 | 0 | OK | Ground clear controls. | 190 | 55.97 | 532.94
13011 | TIN-INTERP | Interpolated Ground | 83138.54 | -4.92 | 483.01 | 0 | 55.48 | 0 | OK | Ground clear controls. | 190 | 55.97 | 538.49
13012 | TIN-INTERP | Interpolated Ground | 83138.59 | -5.42 | 482.92 | 0 | 44.57 | 0 | OK | Ground clear controls. | 190 | 55.97 | 527.49
13013 | TIN-INTERP | Interpolated Ground | 83138.65 | 4.82 | 485.45 | 0 | 42.01 | 0 | OK | Ground clear controls. | 190 | 55.97 | 527.46
13014 | TIN-INTERP | Interpolated Ground | 83138.67 | 4.31 | 485.41 | 0 | 53.06 | 0 | OK | Ground clear controls. | 190 | 55.97 | 538.47
13015 | TIN-INTERP | Interpolated Ground | 83138.78 | 6.32 | 485.52 | 0 | 47.43 | 0 | OK | Ground clear controls. | 190 | 55.97 | 532.95
13016 | TIN-INTERP | Interpolated Ground | 83178.53 | -6.82 | 483.67 | 0 | 49.84 | 0 | OK | Ground clear controls. | 190 | 55.97 | 533.51
13017 | TIN-INTERP | Interpolated Ground | 83178.54 | -4.82 | 483.58 | 0 | 55.49 | 0 | OK | Ground clear controls. | 190 | 55.97 | 539.07
13018 | TIN-INTERP | Interpolated Ground | 83178.59 | -5.32 | 483.63 | 0 | 44.44 | 0 | OK | Ground clear controls. | 190 | 55.97 | 528.07
13019 | TIN-INTERP | Interpolated Ground | 83178.65 | 4.93 | 483.1 | 0 | 44.94 | 0 | OK | Ground clear controls. | 190 | 55.97 | 528.04
13020 | TIN-INTERP | Interpolated Ground | 83178.67 | 4.43 | 483.08 | 0 | 55.97 | 0 | OK | Ground clear controls. | 190 | 55.97 | 539.05
13021 | TIN-INTERP | Interpolated Ground | 83178.78 | 6.43 | 483.12 | 0 | 50.42 | 0 | OK | Ground clear controls. | 190 | 50.42 | 533.54
13022 | TIN-INTERP | Interpolated Ground | 83218.53 | -6.72 | 495.47 | 0 | 39.58 | 0 | OK | Ground clear controls. | 190 | 44.29 | 535.05
13023 | TIN-INTERP | Interpolated Ground | 83218.54 | -4.72 | 496.29 | 0 | 44.29 | 0 | OK | Ground clear controls. | 190 | 44.29 | 540.58
13024 | TIN-INTERP | Interpolated Ground | 83218.59 | -5.22 | 496.01 | 0 | 33.59 | 0 | OK | Ground clear controls. | 190 | 40.43 | 529.6
13025 | TIN-INTERP | Interpolated Ground | 83218.65 | 5.05 | 500.39 | 0 | 29.18 | 0 | OK | Ground clear controls. | 190 | 40.43 | 529.57
13026 | TIN-INTERP | Interpolated Ground | 83218.67 | 4.55 | 500.14 | 0 | 40.43 | 0 | OK | Ground clear controls. | 190 | 40.43 | 540.57
13027 | TIN-INTERP | Interpolated Ground | 83218.78 | 6.55 | 500.75 | 0 | 34.32 | 0 | OK | Ground clear controls. | 190 | 35.96 | 535.07
13028 | TIN-INTERP | Interpolated Ground | 83258.53 | -6.63 | 506.76 | 0 | 30.78 | 0 | OK | Ground clear controls. | 190 | 35.96 | 537.54
13029 | TIN-INTERP | Interpolated Ground | 83258.54 | -4.62 | 507.09 | 0 | 35.96 | 0 | OK | Ground clear controls. | 190 | 35.96 | 543.05
13030 | TIN-INTERP | Interpolated Ground | 83258.59 | -5.12 | 507.07 | 0 | 25 | 0 | OK | Ground clear controls. | 190 | 35.21 | 532.07
13031 | TIN-INTERP | Interpolated Ground | 83258.65 | 5.17 | 507.81 | 0 | 24.24 | 0 | OK | Ground clear controls. | 190 | 35.21 | 532.05
13032 | TIN-INTERP | Interpolated Ground | 83258.67 | 4.66 | 507.84 | 0 | 35.21 | 0 | OK | Ground clear controls. | 190 | 35.21 | 543.05
13033 | TIN-INTERP | Interpolated Ground | 83258.78 | 6.67 | 507.75 | 0 | 29.81 | 0 | OK | Ground clear controls. | 190 | 29.81 | 537.56
13034 | TIN-INTERP | Interpolated Ground | 83271.14 | -5.09 | 510.17 | 0 | 22.86 | 0 | OK | Ground clear controls. | 191 | 59.68 | 533.03
13035 | TIN-INTERP | Interpolated Ground | 83271.25 | -4.59 | 510.27 | 0 | 33.76 | 0 | OK | Ground clear controls. | 191 | 59.68 | 544.03
13036 | TIN-INTERP | Interpolated Ground | 83271.26 | -6.59 | 509.7 | 0 | 28.83 | 0 | OK | Ground clear controls. | 191 | 59.68 | 538.53
13037 | TIN-INTERP | Interpolated Ground | 83271.29 | 5.21 | 512.37 | 0 | 20.67 | 0 | OK | Ground clear controls. | 191 | 59.68 | 533.04
13038 | TIN-INTERP | Interpolated Ground | 83271.3 | 6.71 | 512.33 | 0 | 26.2 | 0 | OK | Ground clear controls. | 191 | 59.68 | 538.53
13039 | TIN-INTERP | Interpolated Ground | 83271.31 | 4.7 | 512.35 | 0 | 31.68 | 0 | OK | Ground clear controls. | 191 | 59.68 | 544.03
13040 | TIN-INTERP | Interpolated Ground | 83311.14 | -5.07 | 498.47 | 0 | 33.79 | 0 | OK | Ground clear controls. | 191 | 59.68 | 532.26
13041 | TIN-INTERP | Interpolated Ground | 83311.25 | -4.56 | 498.71 | 0 | 44.66 | 0 | OK | Ground clear controls. | 191 | 59.68 | 543.37
13042 | TIN-INTERP | Interpolated Ground | 83311.26 | -6.58 | 497.78 | 0 | 39.95 | 0 | OK | Ground clear controls. | 191 | 59.68 | 537.73
13043 | TIN-INTERP | Interpolated Ground | 83311.29 | 5.43 | 504.11 | 0 | 28.14 | 0 | OK | Ground clear controls. | 191 | 59.68 | 532.25
13044 | TIN-INTERP | Interpolated Ground | 83311.3 | 6.93 | 504.63 | 0 | 33.15 | 0 | OK | Ground clear controls. | 191 | 59.68 | 537.78
13045 | TIN-INTERP | Interpolated Ground | 83311.31 | 4.9 | 503.86 | 0 | 39.5 | 0 | OK | Ground clear controls. | 191 | 59.68 | 543.36
13046 | TIN-INTERP | Interpolated Ground | 83351.14 | -5.04 | 494.18 | 0 | 38.24 | 0 | OK | Ground clear controls. | 191 | 59.68 | 532.42
13047 | TIN-INTERP | Interpolated Ground | 83351.25 | -4.52 | 494.06 | 0 | 49.59 | 0 | OK | Ground clear controls. | 191 | 59.68 | 543.65
13048 | TIN-INTERP | Interpolated Ground | 83351.26 | -6.56 | 494.16 | 0 | 43.71 | 0 | OK | Ground clear controls. | 191 | 59.68 | 537.87
13049 | TIN-INTERP | Interpolated Ground | 83351.29 | 5.65 | 493.32 | 0 | 39.1 | 0 | OK | Ground clear controls. | 191 | 59.68 | 532.42
13050 | TIN-INTERP | Interpolated Ground | 83351.3 | 7.15 | 493.33 | 0 | 44.64 | 0 | OK | Ground clear controls. | 191 | 59.68 | 537.97
13051 | TIN-INTERP | Interpolated Ground | 83351.3 | 5.11 | 493.25 | 0 | 50.38 | 0 | OK | Ground clear controls. | 191 | 59.68 | 543.63
13052 | TIN-INTERP | Interpolated Ground | 83391.14 | -5.02 | 507.39 | 0 | 26.16 | 0 | OK | Ground clear controls. | 191 | 59.68 | 533.55
13053 | TIN-INTERP | Interpolated Ground | 83391.25 | -4.49 | 507.48 | 0 | 37.41 | 0 | OK | Ground clear controls. | 191 | 59.68 | 544.89
13054 | TIN-INTERP | Interpolated Ground | 83391.26 | -6.54 | 506.82 | 0 | 32.17 | 0 | OK | Ground clear controls. | 191 | 59.68 | 538.99
13055 | TIN-INTERP | Interpolated Ground | 83391.29 | 5.87 | 511 | 0 | 22.56 | 0 | OK | Ground clear controls. | 191 | 59.68 | 533.56
13056 | TIN-INTERP | Interpolated Ground | 83391.3 | 7.37 | 511.64 | 0 | 27.49 | 0 | OK | Ground clear controls. | 191 | 59.68 | 539.13
13057 | TIN-INTERP | Interpolated Ground | 83391.3 | 5.32 | 510.94 | 0 | 33.92 | 0 | OK | Ground clear controls. | 191 | 59.68 | 544.86
13058 | TIN-INTERP | Interpolated Ground | 83431.14 | -5 | 492.79 | 0 | 42.83 | 0 | OK | Ground clear controls. | 191 | 59.68 | 535.62
13059 | TIN-INTERP | Interpolated Ground | 83431.25 | -4.46 | 493 | 0 | 54.06 | 0 | OK | Ground clear controls. | 191 | 59.68 | 547.06
13060 | TIN-INTERP | Interpolated Ground | 83431.26 | -6.53 | 492.34 | 0 | 48.72 | 0 | OK | Ground clear controls. | 191 | 59.68 | 541.06
13061 | TIN-INTERP | Interpolated Ground | 83431.29 | 6.09 | 496.94 | 0 | 38.71 | 0 | OK | Ground clear controls. | 191 | 59.68 | 535.65
13062 | TIN-INTERP | Interpolated Ground | 83431.3 | 7.59 | 497.49 | 0 | 43.77 | 0 | OK | Ground clear controls. | 191 | 59.68 | 541.26
13063 | TIN-INTERP | Interpolated Ground | 83431.3 | 5.52 | 496.62 | 0 | 50.43 | 0 | OK | Ground clear controls. | 191 | 59.68 | 547.05
13064 | TIN-INTERP | Interpolated Ground | 83471.14 | -4.97 | 502.65 | 0 | 36 | 0 | OK | Ground clear controls. | 191 | 59.68 | 538.65
13065 | TIN-INTERP | Interpolated Ground | 83471.25 | -4.42 | 502.46 | 0 | 47.74 | 0 | OK | Ground clear controls. | 191 | 59.68 | 550.2
13066 | TIN-INTERP | Interpolated Ground | 83471.26 | -6.51 | 503.23 | 0 | 40.87 | 0 | OK | Ground clear controls. | 191 | 59.68 | 544.1
13067 | TIN-INTERP | Interpolated Ground | 83471.29 | 6.31 | 500.35 | 0 | 38.37 | 0 | OK | Ground clear controls. | 191 | 59.68 | 538.72
13068 | TIN-INTERP | Interpolated Ground | 83471.3 | 7.81 | 500.39 | 0 | 43.95 | 0 | OK | Ground clear controls. | 191 | 59.68 | 544.34
13069 | TIN-INTERP | Interpolated Ground | 83471.3 | 5.73 | 500.41 | 0 | 49.8 | 0 | OK | Ground clear controls. | 191 | 59.68 | 550.21
13070 | TIN-INTERP | Interpolated Ground | 83511.14 | -4.95 | 522.55 | 0 | 20.1 | 0 | OK | Ground clear controls. | 191 | 59.68 | 542.65
13071 | TIN-INTERP | Interpolated Ground | 83511.25 | -4.39 | 522.66 | 0 | 31.62 | 0 | OK | Ground clear controls. | 191 | 59.68 | 554.28
13072 | TIN-INTERP | Interpolated Ground | 83511.26 | -6.49 | 522.58 | 0 | 25.53 | 0 | OK | Ground clear controls. | 191 | 59.68 | 548.11
13073 | TIN-INTERP | Interpolated Ground | 83511.29 | 6.53 | 521.18 | 0 | 21.56 | 0 | OK | Ground clear controls. | 191 | 59.68 | 542.74
13074 | TIN-INTERP | Interpolated Ground | 83511.3 | 8.03 | 520.57 | 0 | 27.81 | 0 | OK | Ground clear controls. | 191 | 59.68 | 548.38
13075 | TIN-INTERP | Interpolated Ground | 83511.3 | 5.93 | 521.33 | 0 | 32.98 | 0 | OK | Ground clear controls. | 191 | 59.68 | 554.31
13076 | TIN-INTERP | Interpolated Ground | 83551.14 | -4.93 | 515.35 | 0 | 32.26 | 0 | OK | Ground clear controls. | 191 | 59.68 | 547.61
13077 | TIN-INTERP | Interpolated Ground | 83551.25 | -4.36 | 515.62 | 0 | 43.71 | 0 | OK | Ground clear controls. | 191 | 59.68 | 559.33
13078 | TIN-INTERP | Interpolated Ground | 83551.26 | -6.47 | 514.58 | 0 | 38.51 | 0 | OK | Ground clear controls. | 191 | 59.68 | 553.09
13079 | TIN-INTERP | Interpolated Ground | 83551.29 | 6.75 | 521.4 | 0 | 26.32 | 0 | OK | Ground clear controls. | 191 | 59.68 | 547.72
13080 | TIN-INTERP | Interpolated Ground | 83551.3 | 8.25 | 522.13 | 0 | 31.27 | 0 | OK | Ground clear controls. | 191 | 59.68 | 553.4
13081 | TIN-INTERP | Interpolated Ground | 83551.3 | 6.14 | 521.1 | 0 | 38.28 | 0 | OK | Ground clear controls. | 191 | 59.68 | 559.38
13082 | TIN-INTERP | Interpolated Ground | 83591.14 | -4.9 | 512.25 | 0 | 41.27 | 0 | OK | Ground clear controls. | 191 | 59.68 | 553.52
13083 | TIN-INTERP | Interpolated Ground | 83591.25 | -4.32 | 512.35 | 0 | 52.97 | 0 | OK | Ground clear controls. | 191 | 59.68 | 565.32
13084 | TIN-INTERP | Interpolated Ground | 83591.26 | -6.46 | 511.49 | 0 | 47.54 | 0 | OK | Ground clear controls. | 191 | 59.68 | 559.03
13085 | TIN-INTERP | Interpolated Ground | 83591.29 | 6.97 | 515.86 | 0 | 37.82 | 0 | OK | Ground clear controls. | 191 | 59.68 | 553.68
13086 | TIN-INTERP | Interpolated Ground | 83591.3 | 8.47 | 516.22 | 0 | 43.17 | 0 | OK | Ground clear controls. | 191 | 59.68 | 559.39
13087 | TIN-INTERP | Interpolated Ground | 83591.3 | 6.34 | 515.69 | 0 | 49.73 | 0 | OK | Ground clear controls. | 191 | 59.68 | 565.42
13088 | TIN-INTERP | Interpolated Ground | 83631.14 | -4.88 | 512.87 | 0 | 47.53 | 0 | OK | Ground clear controls. | 191 | 59.68 | 560.4
13089 | TIN-INTERP | Interpolated Ground | 83631.25 | -4.29 | 512.89 | 0 | 59.4 | 0 | OK | Ground clear controls. | 191 | 59.68 | 572.29
13090 | TIN-INTERP | Interpolated Ground | 83631.26 | -6.44 | 512.7 | 0 | 53.25 | 0 | OK | Ground clear controls. | 191 | 59.68 | 565.95
13091 | TIN-INTERP | Interpolated Ground | 83631.29 | 7.19 | 512.8 | 0 | 47.81 | 0 | OK | Ground clear controls. | 191 | 59.68 | 560.61
13092 | TIN-INTERP | Interpolated Ground | 83631.3 | 8.69 | 513.01 | 0 | 53.33 | 0 | OK | Ground clear controls. | 191 | 59.68 | 566.34
13093 | TIN-INTERP | Interpolated Ground | 83631.3 | 6.55 | 512.74 | 0 | 59.68 | 0 | OK | Ground clear controls. | 191 | 59.68 | 572.42
13094 | TIN-INTERP | Interpolated Ground | 83671.14 | -4.85 | 521.9 | 0 | 46.36 | 0 | OK | Ground clear controls. | 191 | 58.02 | 568.26
13095 | TIN-INTERP | Interpolated Ground | 83671.25 | -4.26 | 522.2 | 0 | 58.02 | 0 | OK | Ground clear controls. | 191 | 58.02 | 580.22
13096 | TIN-INTERP | Interpolated Ground | 83671.26 | -6.42 | 520.93 | 0 | 52.92 | 0 | OK | Ground clear controls. | 191 | 52.92 | 573.85
13097 | TIN-INTERP | Interpolated Ground | 83671.29 | 7.41 | 528.63 | 0 | 39.89 | 0 | OK | Ground clear controls. | 191 | 52.29 | 568.52
13098 | TIN-INTERP | Interpolated Ground | 83671.3 | 8.91 | 529.5 | 0 | 44.79 | 0 | OK | Ground clear controls. | 191 | 52.29 | 574.29
13099 | TIN-INTERP | Interpolated Ground | 83671.3 | 6.75 | 528.12 | 0 | 52.29 | 0 | OK | Ground clear controls. | 191 | 52.29 | 580.41
13100 | TIN-INTERP | Interpolated Ground | 83711.14 | -4.83 | 541.37 | 0 | 35.72 | 0 | OK | Ground clear controls. | 191 | 47.63 | 577.09
13101 | TIN-INTERP | Interpolated Ground | 83711.25 | -4.22 | 541.48 | 0 | 47.63 | 0 | OK | Ground clear controls. | 191 | 47.63 | 589.11
13102 | TIN-INTERP | Interpolated Ground | 83711.26 | -6.4 | 541.16 | 0 | 41.57 | 0 | OK | Ground clear controls. | 191 | 46.01 | 582.73
13103 | TIN-INTERP | Interpolated Ground | 83711.29 | 7.63 | 543.55 | 0 | 33.86 | 0 | OK | Ground clear controls. | 191 | 46.01 | 577.41
13104 | TIN-INTERP | Interpolated Ground | 83711.3 | 9.13 | 544.03 | 0 | 39.17 | 0 | OK | Ground clear controls. | 191 | 46.01 | 583.2
13105 | TIN-INTERP | Interpolated Ground | 83711.3 | 6.96 | 543.36 | 0 | 46.01 | 0 | OK | Ground clear controls. | 191 | 46.01 | 589.37
13106 | TIN-INTERP | Interpolated Ground | 83751.14 | -4.81 | 567.1 | 0 | 19.8 | 0 | OK | Ground clear controls. | 191 | 31.39 | 586.9
13107 | TIN-INTERP | Interpolated Ground | 83751.25 | -4.19 | 567.59 | 0 | 31.39 | 0 | OK | Ground clear controls. | 191 | 31.39 | 598.98
13108 | TIN-INTERP | Interpolated Ground | 83751.26 | -6.39 | 566.46 | 0 | 26.13 | 0 | OK | Ground clear controls. | 191 | 28.26 | 592.59
13109 | TIN-INTERP | Interpolated Ground | 83751.29 | 7.86 | 571.16 | 0 | 16.13 | 0 | OK | Ground clear controls. | 191 | 28.26 | 587.29
13110 | TIN-INTERP | Interpolated Ground | 83751.29 | 9.35 | 571.57 | 0 | 21.54 | 0 | OK | Ground clear controls. | 191 | 28.26 | 593.11
13111 | TIN-INTERP | Interpolated Ground | 83751.3 | 7.16 | 571.04 | 0 | 28.26 | 0 | OK | Ground clear controls. | 191 | 28.26 | 599.3
13112 | TIN-INTERP | Interpolated Ground | 83787.19 | -6.43 | 578.06 | 0 | 24.48 | 0 | OK | Ground clear controls. | 192 | 49.82 | 602.54
13113 | TIN-INTERP | Interpolated Ground | 83787.19 | -4.82 | 578.16 | 0 | 18.59 | 0 | OK | Ground clear controls. | 192 | 49.82 | 596.75
13114 | TIN-INTERP | Interpolated Ground | 83787.19 | -4.19 | 578.19 | 0 | 30.64 | 0 | OK | Ground clear controls. | 192 | 49.82 | 608.83
13115 | TIN-INTERP | Interpolated Ground | 83788.3 | 7.32 | 581.19 | 0 | 27.6 | 0 | OK | Ground clear controls. | 192 | 49.82 | 608.79
13116 | TIN-INTERP | Interpolated Ground | 83788.39 | 8.03 | 581.49 | 0 | 15.21 | 0 | OK | Ground clear controls. | 192 | 49.82 | 596.7
13117 | TIN-INTERP | Interpolated Ground | 83788.65 | 9.5 | 582.44 | 0 | 20.06 | 0 | OK | Ground clear controls. | 192 | 49.82 | 602.5
13118 | TIN-INTERP | Interpolated Ground | 83826.24 | -6.37 | 563.26 | 0 | 37.71 | 0 | OK | Ground clear controls. | 192 | 49.82 | 600.97
13119 | TIN-INTERP | Interpolated Ground | 83826.44 | -4.8 | 563.2 | 0 | 32.04 | 0 | OK | Ground clear controls. | 192 | 49.82 | 595.24
13120 | TIN-INTERP | Interpolated Ground | 83826.54 | -4.2 | 563.23 | 0 | 43.91 | 0 | OK | Ground clear controls. | 192 | 49.82 | 607.14
13121 | TIN-INTERP | Interpolated Ground | 83828.3 | 6.89 | 563.54 | 0 | 43.56 | 0 | OK | Ground clear controls. | 192 | 49.82 | 607.1
13122 | TIN-INTERP | Interpolated Ground | 83828.39 | 7.56 | 563.58 | 0 | 31.61 | 0 | OK | Ground clear controls. | 192 | 49.82 | 595.19
13123 | TIN-INTERP | Interpolated Ground | 83828.65 | 9.03 | 563.41 | 0 | 37.54 | 0 | OK | Ground clear controls. | 192 | 49.82 | 600.95
13124 | TIN-INTERP | Interpolated Ground | 83866.24 | -6.39 | 561.01 | 0 | 39.36 | 0 | OK | Ground clear controls. | 192 | 49.82 | 600.37
13125 | TIN-INTERP | Interpolated Ground | 83866.44 | -4.84 | 560.31 | 0 | 34.36 | 0 | OK | Ground clear controls. | 192 | 49.82 | 594.67
13126 | TIN-INTERP | Interpolated Ground | 83866.54 | -4.25 | 559.95 | 0 | 46.44 | 0 | OK | Ground clear controls. | 192 | 49.82 | 606.39
13127 | TIN-INTERP | Interpolated Ground | 83868.29 | 6.45 | 556.54 | 0 | 49.82 | 0 | OK | Ground clear controls. | 192 | 49.82 | 606.36
13128 | TIN-INTERP | Interpolated Ground | 83868.39 | 7.08 | 556.27 | 0 | 38.39 | 0 | OK | Ground clear controls. | 192 | 44.62 | 594.66
13129 | TIN-INTERP | Interpolated Ground | 83868.65 | 8.57 | 555.75 | 0 | 44.62 | 0 | OK | Ground clear controls. | 192 | 44.62 | 600.37
13130 | TIN-INTERP | Interpolated Ground | 83906.24 | -6.41 | 575.27 | 0 | 25.44 | 0 | OK | Ground clear controls. | 192 | 40.24 | 600.71
13131 | TIN-INTERP | Interpolated Ground | 83906.44 | -4.87 | 574.64 | 0 | 20.43 | 0 | OK | Ground clear controls. | 192 | 40.24 | 595.07
13132 | TIN-INTERP | Interpolated Ground | 83906.54 | -4.31 | 574.49 | 0 | 32.1 | 0 | OK | Ground clear controls. | 192 | 40.24 | 606.59
13133 | TIN-INTERP | Interpolated Ground | 83908.29 | 6.02 | 572.87 | 0 | 33.73 | 0 | OK | Ground clear controls. | 192 | 40.24 | 606.6
13134 | TIN-INTERP | Interpolated Ground | 83908.38 | 6.61 | 572.94 | 0 | 22.14 | 0 | OK | Ground clear controls. | 192 | 40.24 | 595.08
13135 | TIN-INTERP | Interpolated Ground | 83908.64 | 8.1 | 573.06 | 0 | 27.69 | 0 | OK | Ground clear controls. | 192 | 40.24 | 600.75
13136 | TIN-INTERP | Interpolated Ground | 83946.24 | -6.43 | 570.83 | 0 | 31.17 | 0 | OK | Ground clear controls. | 192 | 40.24 | 602
13137 | TIN-INTERP | Interpolated Ground | 83946.44 | -4.91 | 570.73 | 0 | 25.69 | 0 | OK | Ground clear controls. | 192 | 40.24 | 596.42
13138 | TIN-INTERP | Interpolated Ground | 83946.54 | -4.36 | 570.71 | 0 | 37.03 | 0 | OK | Ground clear controls. | 192 | 40.24 | 607.74
13139 | TIN-INTERP | Interpolated Ground | 83948.29 | 5.58 | 567.54 | 0 | 40.24 | 0 | OK | Ground clear controls. | 192 | 40.24 | 607.78
13140 | TIN-INTERP | Interpolated Ground | 83948.38 | 6.14 | 567.32 | 0 | 29.16 | 0 | OK | Ground clear controls. | 192 | 35.21 | 596.48
13141 | TIN-INTERP | Interpolated Ground | 83948.64 | 7.63 | 566.88 | 0 | 35.21 | 0 | OK | Ground clear controls. | 192 | 35.21 | 602.09
13142 | TIN-INTERP | Interpolated Ground | 83986.24 | -6.45 | 577.46 | 0 | 26.78 | 0 | OK | Ground clear controls. | 192 | 32.43 | 604.24
13143 | TIN-INTERP | Interpolated Ground | 83986.44 | -4.95 | 577.44 | 0 | 21.28 | 0 | OK | Ground clear controls. | 192 | 32.43 | 598.72
13144 | TIN-INTERP | Interpolated Ground | 83986.54 | -4.42 | 577.4 | 0 | 32.43 | 0 | OK | Ground clear controls. | 192 | 32.43 | 609.83
13145 | TIN-INTERP | Interpolated Ground | 83988.29 | 5.14 | 579.28 | 0 | 30.65 | 0 | OK | Ground clear controls. | 192 | 30.65 | 609.93
13146 | TIN-INTERP | Interpolated Ground | 83988.38 | 5.66 | 579.46 | 0 | 19.38 | 0 | OK | Ground clear controls. | 192 | 24.37 | 598.84
13147 | TIN-INTERP | Interpolated Ground | 83988.64 | 7.16 | 580.02 | 0 | 24.37 | 0 | OK | Ground clear controls. | 192 | 24.37 | 604.39
13148 | TIN-INTERP | Interpolated Ground | 84004.35 | -6.46 | 583.35 | 0 | 22.23 | 0 | OK | Ground clear controls. | 193 | 82.26 | 605.58
13149 | TIN-INTERP | Interpolated Ground | 84004.41 | -4.44 | 583.77 | 0 | 27.3 | 0 | OK | Ground clear controls. | 193 | 82.26 | 611.07
13150 | TIN-INTERP | Interpolated Ground | 84004.48 | -4.96 | 583.7 | 0 | 16.38 | 0 | OK | Ground clear controls. | 193 | 82.26 | 600.08
13151 | TIN-INTERP | Interpolated Ground | 84004.64 | 6.97 | 585.02 | 0 | 20.57 | 0 | OK | Ground clear controls. | 193 | 82.26 | 605.59
13152 | TIN-INTERP | Interpolated Ground | 84004.68 | 4.97 | 585.09 | 0 | 25.99 | 0 | OK | Ground clear controls. | 193 | 82.26 | 611.08
13153 | TIN-INTERP | Interpolated Ground | 84004.79 | 5.47 | 585.08 | 0 | 15 | 0 | OK | Ground clear controls. | 193 | 82.26 | 600.08
13154 | TIN-INTERP | Interpolated Ground | 84044.35 | -6.44 | 575.33 | 0 | 27.38 | 0 | OK | Ground clear controls. | 193 | 82.26 | 602.71
13155 | TIN-INTERP | Interpolated Ground | 84044.41 | -4.41 | 575.72 | 0 | 32.6 | 0 | OK | Ground clear controls. | 193 | 82.26 | 608.32
13156 | TIN-INTERP | Interpolated Ground | 84044.48 | -4.95 | 575.6 | 0 | 21.63 | 0 | OK | Ground clear controls. | 193 | 82.26 | 597.23
13157 | TIN-INTERP | Interpolated Ground | 84044.64 | 7.16 | 576.04 | 0 | 26.71 | 0 | OK | Ground clear controls. | 193 | 82.26 | 602.75
13158 | TIN-INTERP | Interpolated Ground | 84044.68 | 5.14 | 576.12 | 0 | 32.23 | 0 | OK | Ground clear controls. | 193 | 82.26 | 608.35
13159 | TIN-INTERP | Interpolated Ground | 84044.79 | 5.66 | 576.1 | 0 | 21.18 | 0 | OK | Ground clear controls. | 193 | 82.26 | 597.28
13160 | TIN-INTERP | Interpolated Ground | 84084.35 | -6.41 | 566.23 | 0 | 34.58 | 0 | OK | Ground clear controls. | 193 | 82.26 | 600.81
13161 | TIN-INTERP | Interpolated Ground | 84084.41 | -4.37 | 567.2 | 0 | 39.33 | 0 | OK | Ground clear controls. | 193 | 82.26 | 606.53
13162 | TIN-INTERP | Interpolated Ground | 84084.48 | -4.93 | 566.92 | 0 | 28.44 | 0 | OK | Ground clear controls. | 193 | 82.26 | 595.36
13163 | TIN-INTERP | Interpolated Ground | 84084.64 | 7.34 | 571.99 | 0 | 28.9 | 0 | OK | Ground clear controls. | 193 | 82.26 | 600.89
13164 | TIN-INTERP | Interpolated Ground | 84084.68 | 5.32 | 571.44 | 0 | 35.13 | 0 | OK | Ground clear controls. | 193 | 82.26 | 606.57
13165 | TIN-INTERP | Interpolated Ground | 84084.79 | 5.84 | 571.57 | 0 | 23.86 | 0 | OK | Ground clear controls. | 193 | 82.26 | 595.43
13166 | TIN-INTERP | Interpolated Ground | 84124.35 | -6.38 | 550.79 | 0 | 49.08 | 0 | OK | Ground clear controls. | 193 | 82.26 | 599.87
13167 | TIN-INTERP | Interpolated Ground | 84124.41 | -4.34 | 550.83 | 0 | 54.85 | 0 | OK | Ground clear controls. | 193 | 82.26 | 605.68
13168 | TIN-INTERP | Interpolated Ground | 84124.48 | -4.92 | 550.7 | 0 | 43.74 | 0 | OK | Ground clear controls. | 193 | 82.26 | 594.44
13169 | TIN-INTERP | Interpolated Ground | 84124.64 | 7.52 | 551.69 | 0 | 48.31 | 0 | OK | Ground clear controls. | 193 | 82.26 | 600
13170 | TIN-INTERP | Interpolated Ground | 84124.68 | 5.5 | 551.05 | 0 | 54.71 | 0 | OK | Ground clear controls. | 193 | 82.26 | 605.76
13171 | TIN-INTERP | Interpolated Ground | 84124.79 | 6.03 | 551.17 | 0 | 43.38 | 0 | OK | Ground clear controls. | 193 | 82.26 | 594.55
13172 | TIN-INTERP | Interpolated Ground | 84164.35 | -6.35 | 541.05 | 0 | 58.83 | 0 | OK | Ground clear controls. | 193 | 82.26 | 599.88
13173 | TIN-INTERP | Interpolated Ground | 84164.41 | -4.3 | 541.08 | 0 | 64.72 | 0 | OK | Ground clear controls. | 193 | 82.26 | 605.8
13174 | TIN-INTERP | Interpolated Ground | 84164.48 | -4.9 | 541.13 | 0 | 53.34 | 0 | OK | Ground clear controls. | 193 | 82.26 | 594.47
13175 | TIN-INTERP | Interpolated Ground | 84164.64 | 7.71 | 537.38 | 0 | 62.69 | 0 | OK | Ground clear controls. | 193 | 82.26 | 600.07
13176 | TIN-INTERP | Interpolated Ground | 84164.68 | 5.68 | 537.8 | 0 | 68.11 | 0 | OK | Ground clear controls. | 193 | 82.26 | 605.91
13177 | TIN-INTERP | Interpolated Ground | 84164.79 | 6.21 | 537.73 | 0 | 56.89 | 0 | OK | Ground clear controls. | 193 | 82.26 | 594.62
13178 | TIN-INTERP | Interpolated Ground | 84204.35 | -6.32 | 558.01 | 0 | 42.87 | 0 | OK | Ground clear controls. | 193 | 82.26 | 600.88
13179 | TIN-INTERP | Interpolated Ground | 84204.41 | -4.27 | 557.81 | 0 | 49.06 | 0 | OK | Ground clear controls. | 193 | 82.26 | 606.87
13180 | TIN-INTERP | Interpolated Ground | 84204.48 | -4.89 | 557.83 | 0 | 37.64 | 0 | OK | Ground clear controls. | 193 | 82.26 | 595.47
13181 | TIN-INTERP | Interpolated Ground | 84204.64 | 7.89 | 555.3 | 0 | 45.8 | 0 | OK | Ground clear controls. | 193 | 82.26 | 601.1
13182 | TIN-INTERP | Interpolated Ground | 84204.68 | 5.86 | 556.11 | 0 | 50.89 | 0 | OK | Ground clear controls. | 193 | 82.26 | 607
13183 | TIN-INTERP | Interpolated Ground | 84204.78 | 6.4 | 555.92 | 0 | 39.73 | 0 | OK | Ground clear controls. | 193 | 82.26 | 595.65
13184 | TIN-INTERP | Interpolated Ground | 84244.35 | -6.3 | 569.43 | 0 | 33.39 | 0 | OK | Ground clear controls. | 193 | 82.26 | 602.82
13185 | TIN-INTERP | Interpolated Ground | 84244.41 | -4.23 | 568.64 | 0 | 40.26 | 0 | OK | Ground clear controls. | 193 | 82.26 | 608.9
13186 | TIN-INTERP | Interpolated Ground | 84244.48 | -4.87 | 568.92 | 0 | 28.49 | 0 | OK | Ground clear controls. | 193 | 82.26 | 597.41
13187 | TIN-INTERP | Interpolated Ground | 84244.64 | 8.08 | 556.69 | 0 | 46.4 | 0 | OK | Ground clear controls. | 193 | 82.26 | 603.09
13188 | TIN-INTERP | Interpolated Ground | 84244.68 | 6.04 | 558.13 | 0 | 50.93 | 0 | OK | Ground clear controls. | 193 | 82.26 | 609.06
13189 | TIN-INTERP | Interpolated Ground | 84244.78 | 6.58 | 557.8 | 0 | 39.84 | 0 | OK | Ground clear controls. | 193 | 82.26 | 597.64
13190 | TIN-INTERP | Interpolated Ground | 84284.35 | -6.27 | 546.2 | 0 | 59.54 | 0 | OK | Ground clear controls. | 193 | 82.26 | 605.74
13191 | TIN-INTERP | Interpolated Ground | 84284.41 | -4.2 | 547.08 | 0 | 64.79 | 0 | OK | Ground clear controls. | 193 | 82.26 | 611.87
13192 | TIN-INTERP | Interpolated Ground | 84284.48 | -4.86 | 546.67 | 0 | 53.65 | 0 | OK | Ground clear controls. | 193 | 82.26 | 600.32
13193 | TIN-INTERP | Interpolated Ground | 84284.64 | 8.26 | 550.05 | 0 | 56.01 | 0 | OK | Ground clear controls. | 193 | 82.26 | 606.06
13194 | TIN-INTERP | Interpolated Ground | 84284.68 | 6.22 | 549.48 | 0 | 62.6 | 0 | OK | Ground clear controls. | 193 | 82.26 | 612.08
13195 | TIN-INTERP | Interpolated Ground | 84284.78 | 6.77 | 549.5 | 0 | 51.09 | 0 | OK | Ground clear controls. | 193 | 82.26 | 600.59
13196 | TIN-INTERP | Interpolated Ground | 84324.35 | -6.24 | 532.48 | 0 | 77.14 | 0 | OK | Ground clear controls. | 193 | 82.26 | 609.62
13197 | TIN-INTERP | Interpolated Ground | 84324.41 | -4.16 | 533.56 | 0 | 82.26 | 0 | OK | Ground clear controls. | 193 | 82.26 | 615.82
13198 | TIN-INTERP | Interpolated Ground | 84324.48 | -4.85 | 533.13 | 0 | 71.06 | 0 | OK | Ground clear controls. | 193 | 75.35 | 604.19
13199 | TIN-INTERP | Interpolated Ground | 84324.64 | 8.45 | 541.03 | 0 | 68.96 | 0 | OK | Ground clear controls. | 193 | 75.35 | 609.99
13200 | TIN-INTERP | Interpolated Ground | 84324.68 | 6.4 | 540.71 | 0 | 75.35 | 0 | OK | Ground clear controls. | 193 | 75.35 | 616.06
13201 | TIN-INTERP | Interpolated Ground | 84324.78 | 6.95 | 540.83 | 0 | 63.67 | 0 | OK | Ground clear controls. | 193 | 69.26 | 604.5
13202 | TIN-INTERP | Interpolated Ground | 84364.35 | -6.21 | 550.37 | 0 | 64.1 | 0 | OK | Ground clear controls. | 193 | 69.26 | 614.47
13203 | TIN-INTERP | Interpolated Ground | 84364.41 | -4.13 | 551.47 | 0 | 69.26 | 0 | OK | Ground clear controls. | 193 | 69.26 | 620.73
13204 | TIN-INTERP | Interpolated Ground | 84364.48 | -4.83 | 551.23 | 0 | 57.79 | 0 | OK | Ground clear controls. | 193 | 69.15 | 609.02
13205 | TIN-INTERP | Interpolated Ground | 84364.64 | 8.63 | 551.83 | 0 | 63.06 | 0 | OK | Ground clear controls. | 193 | 69.15 | 614.89
13206 | TIN-INTERP | Interpolated Ground | 84364.68 | 6.58 | 551.84 | 0 | 69.15 | 0 | OK | Ground clear controls. | 193 | 69.15 | 620.99
13207 | TIN-INTERP | Interpolated Ground | 84364.78 | 7.14 | 551.83 | 0 | 57.54 | 0 | OK | Ground clear controls. | 193 | 68.95 | 609.37
13208 | TIN-INTERP | Interpolated Ground | 84404.35 | -6.19 | 559.82 | 0 | 60.47 | 0 | OK | Ground clear controls. | 193 | 68.95 | 620.29
13209 | TIN-INTERP | Interpolated Ground | 84404.41 | -4.09 | 559.99 | 0 | 66.59 | 0 | OK | Ground clear controls. | 193 | 68.95 | 626.58
13210 | TIN-INTERP | Interpolated Ground | 84404.48 | -4.82 | 559.94 | 0 | 54.88 | 0 | OK | Ground clear controls. | 193 | 68.95 | 614.82
13211 | TIN-INTERP | Interpolated Ground | 84404.64 | 8.81 | 557.87 | 0 | 62.89 | 0 | OK | Ground clear controls. | 193 | 68.95 | 620.76
13212 | TIN-INTERP | Interpolated Ground | 84404.68 | 6.76 | 557.95 | 0 | 68.95 | 0 | OK | Ground clear controls. | 193 | 68.95 | 626.9
13213 | TIN-INTERP | Interpolated Ground | 84404.78 | 7.33 | 557.9 | 0 | 57.31 | 0 | OK | Ground clear controls. | 193 | 62.42 | 615.21
13214 | TIN-INTERP | Interpolated Ground | 84444.35 | -6.16 | 572.84 | 0 | 54.25 | 0 | OK | Ground clear controls. | 193 | 62.42 | 627.09
13215 | TIN-INTERP | Interpolated Ground | 84444.41 | -4.06 | 572.7 | 0 | 60.72 | 0 | OK | Ground clear controls. | 193 | 62.42 | 633.42
13216 | TIN-INTERP | Interpolated Ground | 84444.48 | -4.8 | 572.84 | 0 | 48.74 | 0 | OK | Ground clear controls. | 193 | 62.42 | 621.58
13217 | TIN-INTERP | Interpolated Ground | 84444.64 | 9 | 571.84 | 0 | 55.77 | 0 | OK | Ground clear controls. | 193 | 62.42 | 627.61
13218 | TIN-INTERP | Interpolated Ground | 84444.68 | 6.94 | 571.36 | 0 | 62.42 | 0 | OK | Ground clear controls. | 193 | 62.42 | 633.78
13219 | TIN-INTERP | Interpolated Ground | 84444.78 | 7.51 | 571.51 | 0 | 50.52 | 0 | OK | Ground clear controls. | 193 | 58.42 | 622.03
13220 | TIN-INTERP | Interpolated Ground | 84484.35 | -6.13 | 587.73 | 0 | 47.14 | 0 | OK | Ground clear controls. | 193 | 58.42 | 634.87
13221 | TIN-INTERP | Interpolated Ground | 84484.41 | -4.02 | 585.66 | 0 | 55.56 | 0 | OK | Ground clear controls. | 193 | 58.42 | 641.22
13222 | TIN-INTERP | Interpolated Ground | 84484.48 | -4.79 | 586.61 | 0 | 42.7 | 0 | OK | Ground clear controls. | 193 | 58.42 | 629.31
13223 | TIN-INTERP | Interpolated Ground | 84484.64 | 9.18 | 583.94 | 0 | 51.5 | 0 | OK | Ground clear controls. | 193 | 58.42 | 635.44
13224 | TIN-INTERP | Interpolated Ground | 84484.68 | 7.12 | 583.21 | 0 | 58.42 | 0 | OK | Ground clear controls. | 193 | 58.42 | 641.63
13225 | TIN-INTERP | Interpolated Ground | 84484.78 | 7.7 | 583.36 | 0 | 46.45 | 0 | OK | Ground clear controls. | 193 | 48.04 | 629.81
13226 | TIN-INTERP | Interpolated Ground | 84524.35 | -6.1 | 601.18 | 0 | 42.44 | 0 | OK | Ground clear controls. | 193 | 48.04 | 643.62
13227 | TIN-INTERP | Interpolated Ground | 84524.41 | -3.98 | 601.97 | 0 | 48.04 | 0 | OK | Ground clear controls. | 193 | 48.04 | 650.01
13228 | TIN-INTERP | Interpolated Ground | 84524.48 | -4.77 | 601.7 | 0 | 36.33 | 0 | OK | Ground clear controls. | 193 | 45.81 | 638.03
13229 | TIN-INTERP | Interpolated Ground | 84524.63 | 9.37 | 605.54 | 0 | 38.71 | 0 | OK | Ground clear controls. | 193 | 45.81 | 644.25
13230 | TIN-INTERP | Interpolated Ground | 84524.68 | 7.3 | 604.65 | 0 | 45.81 | 0 | OK | Ground clear controls. | 193 | 45.81 | 650.46
13231 | TIN-INTERP | Interpolated Ground | 84524.78 | 7.88 | 604.9 | 0 | 33.66 | 0 | OK | Ground clear controls. | 193 | 37.15 | 638.56
13232 | TIN-INTERP | Interpolated Ground | 84564.35 | -6.08 | 622.33 | 0 | 31.05 | 0 | OK | Ground clear controls. | 193 | 37.15 | 653.38
13233 | TIN-INTERP | Interpolated Ground | 84564.41 | -3.95 | 622.63 | 0 | 37.15 | 0 | OK | Ground clear controls. | 193 | 37.15 | 659.78
13234 | TIN-INTERP | Interpolated Ground | 84564.48 | -4.76 | 622.66 | 0 | 25.06 | 0 | OK | Ground clear controls. | 193 | 35.36 | 647.72
13235 | TIN-INTERP | Interpolated Ground | 84564.63 | 9.55 | 625.45 | 0 | 28.61 | 0 | OK | Ground clear controls. | 193 | 35.36 | 654.06
13236 | TIN-INTERP | Interpolated Ground | 84564.68 | 7.48 | 624.92 | 0 | 35.36 | 0 | OK | Ground clear controls. | 193 | 35.36 | 660.28
13237 | TIN-INTERP | Interpolated Ground | 84564.78 | 8.07 | 625.11 | 0 | 23.21 | 0 | OK | Ground clear controls. | 193 | 23.21 | 648.32
13238 | TIN-INTERP | Interpolated Ground | 84603.93 | -6.12 | 642.53 | 0 | 21.73 | 0 | OK | Ground clear controls. | 194 | 21.73 | 664.26
13239 | TIN-INTERP | Interpolated Ground | 84603.93 | -6.06 | 642.55 | 0 | 21.58 | 0 | OK | Ground clear controls. | 193 | 21.58 | 664.13
13240 | TIN-INTERP | Interpolated Ground | 84603.93 | -4.81 | 642.97 | 0 | 15.5 | 0 | OK | Ground clear controls. | 194 | 15.5 | 658.47
13241 | TIN-INTERP | Interpolated Ground | 84603.93 | -4.78 | 642.95 | 0 | 15.45 | 0 | OK | Ground clear controls. | 193 | 15.45 | 658.4
13242 | TIN-INTERP | Interpolated Ground | 84603.93 | -3.96 | 643.23 | 0 | 27.33 | 0 | OK | Ground clear controls. | 194 | 27.33 | 670.56
13243 | TIN-INTERP | Interpolated Ground | 84603.93 | -3.94 | 643.22 | 0 | 27.3 | 0 | OK | Ground clear controls. | 193 | 27.3 | 670.52
13244 | TIN-INTERP | Interpolated Ground | 84605.21 | 7.62 | 644.43 | 0 | 26.13 | 0 | OK | Ground clear controls. | 194 | 58.2 | 670.56
13245 | TIN-INTERP | Interpolated Ground | 84605.28 | 8.22 | 644.5 | 0 | 13.96 | 0 | OK | Ground clear controls. | 194 | 58.2 | 658.46
13246 | TIN-INTERP | Interpolated Ground | 84605.56 | 9.69 | 644.79 | 0 | 19.47 | 0 | OK | Ground clear controls. | 194 | 58.2 | 664.26
13247 | TIN-INTERP | Interpolated Ground | 84642.94 | -6.29 | 635.11 | 0 | 26.69 | 0 | OK | Ground clear controls. | 194 | 58.2 | 661.8
13248 | TIN-INTERP | Interpolated Ground | 84643.2 | -4.98 | 635.6 | 0 | 20.44 | 0 | OK | Ground clear controls. | 194 | 58.2 | 656.04
13249 | TIN-INTERP | Interpolated Ground | 84643.33 | -4.16 | 635.95 | 0 | 32.18 | 0 | OK | Ground clear controls. | 194 | 58.2 | 668.13
13250 | TIN-INTERP | Interpolated Ground | 84645.21 | 7.41 | 639.71 | 0 | 28.43 | 0 | OK | Ground clear controls. | 194 | 58.2 | 668.14
13251 | TIN-INTERP | Interpolated Ground | 84645.28 | 8.02 | 639.98 | 0 | 16.09 | 0 | OK | Ground clear controls. | 194 | 58.2 | 656.07
13252 | TIN-INTERP | Interpolated Ground | 84645.56 | 9.49 | 640.69 | 0 | 21.14 | 0 | OK | Ground clear controls. | 194 | 58.2 | 661.83
13253 | TIN-INTERP | Interpolated Ground | 84682.94 | -6.54 | 635.57 | 0 | 24.71 | 0 | OK | Ground clear controls. | 194 | 58.2 | 660.28
13254 | TIN-INTERP | Interpolated Ground | 84683.2 | -5.22 | 635.53 | 0 | 19.02 | 0 | OK | Ground clear controls. | 194 | 58.2 | 654.55
13255 | TIN-INTERP | Interpolated Ground | 84683.33 | -4.41 | 635.55 | 0 | 31.08 | 0 | OK | Ground clear controls. | 194 | 58.2 | 666.63
13256 | TIN-INTERP | Interpolated Ground | 84685.21 | 7.2 | 636.53 | 0 | 30.13 | 0 | OK | Ground clear controls. | 194 | 58.2 | 666.66
13257 | TIN-INTERP | Interpolated Ground | 84685.28 | 7.82 | 636.63 | 0 | 17.98 | 0 | OK | Ground clear controls. | 194 | 58.2 | 654.61
13258 | TIN-INTERP | Interpolated Ground | 84685.56 | 9.29 | 636.86 | 0 | 23.49 | 0 | OK | Ground clear controls. | 194 | 58.2 | 660.35
13259 | TIN-INTERP | Interpolated Ground | 84722.94 | -6.79 | 633.49 | 0 | 26.21 | 0 | OK | Ground clear controls. | 194 | 58.2 | 659.7
13260 | TIN-INTERP | Interpolated Ground | 84723.2 | -5.45 | 633.29 | 0 | 20.7 | 0 | OK | Ground clear controls. | 194 | 58.2 | 653.99
13261 | TIN-INTERP | Interpolated Ground | 84723.32 | -4.65 | 633.2 | 0 | 32.88 | 0 | OK | Ground clear controls. | 194 | 58.2 | 666.08
13262 | TIN-INTERP | Interpolated Ground | 84725.21 | 6.98 | 631.33 | 0 | 34.79 | 0 | OK | Ground clear controls. | 194 | 58.2 | 666.12
13263 | TIN-INTERP | Interpolated Ground | 84725.28 | 7.61 | 631.27 | 0 | 22.81 | 0 | OK | Ground clear controls. | 194 | 58.2 | 654.08
13264 | TIN-INTERP | Interpolated Ground | 84725.56 | 9.09 | 631.32 | 0 | 28.49 | 0 | OK | Ground clear controls. | 194 | 58.2 | 659.81
13265 | TIN-INTERP | Interpolated Ground | 84762.94 | -7.04 | 629.6 | 0 | 30.48 | 0 | OK | Ground clear controls. | 194 | 58.2 | 660.08
13266 | TIN-INTERP | Interpolated Ground | 84763.2 | -5.68 | 629.26 | 0 | 25.12 | 0 | OK | Ground clear controls. | 194 | 58.2 | 654.38
13267 | TIN-INTERP | Interpolated Ground | 84763.32 | -4.9 | 628.99 | 0 | 37.48 | 0 | OK | Ground clear controls. | 194 | 58.2 | 666.47
13268 | TIN-INTERP | Interpolated Ground | 84765.21 | 6.77 | 625.71 | 0 | 40.83 | 0 | OK | Ground clear controls. | 194 | 58.2 | 666.54
13269 | TIN-INTERP | Interpolated Ground | 84765.28 | 7.41 | 625.62 | 0 | 28.88 | 0 | OK | Ground clear controls. | 194 | 58.2 | 654.5
13270 | TIN-INTERP | Interpolated Ground | 84765.56 | 8.89 | 625.56 | 0 | 34.65 | 0 | OK | Ground clear controls. | 194 | 58.2 | 660.21
13271 | TIN-INTERP | Interpolated Ground | 84802.94 | -7.3 | 625.79 | 0 | 35.61 | 0 | OK | Ground clear controls. | 194 | 58.2 | 661.4
13272 | TIN-INTERP | Interpolated Ground | 84803.2 | -5.91 | 625.45 | 0 | 30.26 | 0 | OK | Ground clear controls. | 194 | 58.2 | 655.71
13273 | TIN-INTERP | Interpolated Ground | 84803.32 | -5.14 | 625.29 | 0 | 42.51 | 0 | OK | Ground clear controls. | 194 | 58.2 | 667.8
13274 | TIN-INTERP | Interpolated Ground | 84805.21 | 6.56 | 622.34 | 0 | 45.54 | 0 | OK | Ground clear controls. | 194 | 58.2 | 667.88
13275 | TIN-INTERP | Interpolated Ground | 84805.28 | 7.21 | 622.21 | 0 | 33.63 | 0 | OK | Ground clear controls. | 194 | 58.2 | 655.84
13276 | TIN-INTERP | Interpolated Ground | 84805.56 | 8.69 | 621.94 | 0 | 39.62 | 0 | OK | Ground clear controls. | 194 | 58.2 | 661.56
13277 | TIN-INTERP | Interpolated Ground | 84842.94 | -7.55 | 630.25 | 0 | 33.41 | 0 | OK | Ground clear controls. | 194 | 58.2 | 663.66
13278 | TIN-INTERP | Interpolated Ground | 84843.2 | -6.14 | 629.96 | 0 | 28 | 0 | OK | Ground clear controls. | 194 | 58.2 | 657.96
13279 | TIN-INTERP | Interpolated Ground | 84843.32 | -5.39 | 629.82 | 0 | 40.24 | 0 | OK | Ground clear controls. | 194 | 58.2 | 670.06
13280 | TIN-INTERP | Interpolated Ground | 84845.21 | 6.34 | 626.1 | 0 | 44.07 | 0 | OK | Ground clear controls. | 194 | 58.2 | 670.17
13281 | TIN-INTERP | Interpolated Ground | 84845.28 | 7 | 625.81 | 0 | 32.32 | 0 | OK | Ground clear controls. | 194 | 58.2 | 658.13
13282 | TIN-INTERP | Interpolated Ground | 84845.56 | 8.49 | 625.16 | 0 | 38.69 | 0 | OK | Ground clear controls. | 194 | 58.2 | 663.85
13283 | TIN-INTERP | Interpolated Ground | 84882.94 | -7.8 | 615.9 | 0 | 50.97 | 0 | OK | Ground clear controls. | 194 | 58.2 | 666.87
13284 | TIN-INTERP | Interpolated Ground | 84883.2 | -6.38 | 615.24 | 0 | 45.93 | 0 | OK | Ground clear controls. | 194 | 58.2 | 661.17
13285 | TIN-INTERP | Interpolated Ground | 84883.32 | -5.63 | 615.07 | 0 | 58.2 | 0 | OK | Ground clear controls. | 194 | 58.2 | 673.27
13286 | TIN-INTERP | Interpolated Ground | 84885.2 | 6.13 | 615.79 | 0 | 57.61 | 0 | OK | Ground clear controls. | 194 | 57.61 | 673.4
13287 | TIN-INTERP | Interpolated Ground | 84885.28 | 6.8 | 615.93 | 0 | 45.44 | 0 | OK | Ground clear controls. | 194 | 52.39 | 661.37
13288 | TIN-INTERP | Interpolated Ground | 84885.56 | 8.29 | 615.98 | 0 | 51.11 | 0 | OK | Ground clear controls. | 194 | 52.39 | 667.09
13289 | TIN-INTERP | Interpolated Ground | 84922.94 | -8.05 | 624.8 | 0 | 46.23 | 0 | OK | Ground clear controls. | 194 | 52.39 | 671.03
13290 | TIN-INTERP | Interpolated Ground | 84923.2 | -6.61 | 624.96 | 0 | 40.36 | 0 | OK | Ground clear controls. | 194 | 52.39 | 665.32
13291 | TIN-INTERP | Interpolated Ground | 84923.32 | -5.88 | 625.04 | 0 | 52.39 | 0 | OK | Ground clear controls. | 194 | 52.39 | 677.43
13292 | TIN-INTERP | Interpolated Ground | 84925.2 | 5.92 | 626.07 | 0 | 51.51 | 0 | OK | Ground clear controls. | 194 | 51.51 | 677.58
13293 | TIN-INTERP | Interpolated Ground | 84925.28 | 6.6 | 626.13 | 0 | 39.4 | 0 | OK | Ground clear controls. | 194 | 45.41 | 665.53
13294 | TIN-INTERP | Interpolated Ground | 84925.56 | 8.09 | 626.25 | 0 | 45.03 | 0 | OK | Ground clear controls. | 194 | 45.41 | 671.28
13295 | TIN-INTERP | Interpolated Ground | 84962.94 | -8.3 | 637.32 | 0 | 38.82 | 0 | OK | Ground clear controls. | 194 | 45.41 | 676.14
13296 | TIN-INTERP | Interpolated Ground | 84963.2 | -6.84 | 637.38 | 0 | 33.03 | 0 | OK | Ground clear controls. | 194 | 45.41 | 670.41
13297 | TIN-INTERP | Interpolated Ground | 84963.32 | -6.12 | 637.45 | 0 | 45.07 | 0 | OK | Ground clear controls. | 194 | 45.41 | 682.52
13298 | TIN-INTERP | Interpolated Ground | 84965.2 | 5.71 | 637.29 | 0 | 45.41 | 0 | OK | Ground clear controls. | 194 | 45.41 | 682.7
13299 | TIN-INTERP | Interpolated Ground | 84965.28 | 6.39 | 636.89 | 0 | 33.75 | 0 | OK | Ground clear controls. | 194 | 42.12 | 670.64
13300 | TIN-INTERP | Interpolated Ground | 84965.56 | 7.89 | 636.17 | 0 | 40.25 | 0 | OK | Ground clear controls. | 194 | 42.12 | 676.42
13301 | TIN-INTERP | Interpolated Ground | 85002.94 | -8.55 | 652.7 | 0 | 29.51 | 0 | OK | Ground clear controls. | 194 | 42.12 | 682.21
13302 | TIN-INTERP | Interpolated Ground | 85003.2 | -7.07 | 652.38 | 0 | 24.08 | 0 | OK | Ground clear controls. | 194 | 42.12 | 676.46
13303 | TIN-INTERP | Interpolated Ground | 85003.32 | -6.36 | 652.18 | 0 | 36.39 | 0 | OK | Ground clear controls. | 194 | 42.12 | 688.57
13304 | TIN-INTERP | Interpolated Ground | 85005.2 | 5.49 | 646.65 | 0 | 42.12 | 0 | OK | Ground clear controls. | 194 | 42.12 | 688.77
13305 | TIN-INTERP | Interpolated Ground | 85005.28 | 6.19 | 646.38 | 0 | 30.32 | 0 | OK | Ground clear controls. | 194 | 36.98 | 676.7
13306 | TIN-INTERP | Interpolated Ground | 85005.56 | 7.69 | 645.54 | 0 | 36.98 | 0 | OK | Ground clear controls. | 194 | 36.98 | 682.52
13307 | TIN-INTERP | Interpolated Ground | 85019.98 | -8.66 | 650.9 | 0 | 34.18 | 0 | OK | Ground clear controls. | 195 | 67.91 | 685.08
13308 | TIN-INTERP | Interpolated Ground | 85020.05 | -7.17 | 651.01 | 0 | 28.28 | 0 | OK | Ground clear controls. | 195 | 67.91 | 679.29
13309 | TIN-INTERP | Interpolated Ground | 85020.08 | -6.47 | 651.06 | 0 | 40.32 | 0 | OK | Ground clear controls. | 195 | 67.91 | 691.38
13310 | TIN-INTERP | Interpolated Ground | 85020.42 | 5.42 | 650.55 | 0 | 40.83 | 0 | OK | Ground clear controls. | 195 | 67.91 | 691.38
13311 | TIN-INTERP | Interpolated Ground | 85020.42 | 6.12 | 650.49 | 0 | 28.8 | 0 | OK | Ground clear controls. | 195 | 67.91 | 679.29
13312 | TIN-INTERP | Interpolated Ground | 85020.42 | 7.62 | 650.17 | 0 | 34.91 | 0 | OK | Ground clear controls. | 195 | 67.91 | 685.08
13313 | TIN-INTERP | Interpolated Ground | 85060.14 | 7.53 | 639.52 | 0 | 38.08 | 0 | OK | Ground clear controls. | 195 | 67.91 | 677.6
13314 | TIN-INTERP | Interpolated Ground | 85060.21 | 6.02 | 639.77 | 0 | 32.1 | 0 | OK | Ground clear controls. | 195 | 67.91 | 671.87
13315 | TIN-INTERP | Interpolated Ground | 85060.28 | 5.33 | 639.8 | 0 | 44.19 | 0 | OK | Ground clear controls. | 195 | 67.91 | 683.99
13316 | TIN-INTERP | Interpolated Ground | 85060.61 | -6.56 | 637.38 | 0 | 46.58 | 0 | OK | Ground clear controls. | 195 | 67.91 | 683.96
13317 | TIN-INTERP | Interpolated Ground | 85060.63 | -7.26 | 637.09 | 0 | 34.77 | 0 | OK | Ground clear controls. | 195 | 67.91 | 671.86
13318 | TIN-INTERP | Interpolated Ground | 85060.68 | -8.76 | 636.18 | 0 | 41.44 | 0 | OK | Ground clear controls. | 195 | 67.91 | 677.62
13319 | TIN-INTERP | Interpolated Ground | 85100.14 | 7.43 | 618.85 | 0 | 52.22 | 0 | OK | Ground clear controls. | 195 | 67.91 | 671.07
13320 | TIN-INTERP | Interpolated Ground | 85100.21 | 5.93 | 619.79 | 0 | 45.61 | 0 | OK | Ground clear controls. | 195 | 67.91 | 665.4
13321 | TIN-INTERP | Interpolated Ground | 85100.28 | 5.24 | 620.13 | 0 | 57.4 | 0 | OK | Ground clear controls. | 195 | 67.91 | 677.53
13322 | TIN-INTERP | Interpolated Ground | 85100.61 | -6.65 | 627.72 | 0 | 49.76 | 0 | OK | Ground clear controls. | 195 | 67.91 | 677.48
13323 | TIN-INTERP | Interpolated Ground | 85100.63 | -7.35 | 628.02 | 0 | 37.37 | 0 | OK | Ground clear controls. | 195 | 67.91 | 665.39
13324 | TIN-INTERP | Interpolated Ground | 85100.68 | -8.84 | 628.38 | 0 | 42.74 | 0 | OK | Ground clear controls. | 195 | 67.91 | 671.12
13325 | TIN-INTERP | Interpolated Ground | 85140.14 | 7.34 | 623.63 | 0 | 41.86 | 0 | OK | Ground clear controls. | 195 | 67.91 | 665.49
13326 | TIN-INTERP | Interpolated Ground | 85140.21 | 5.84 | 624.58 | 0 | 35.3 | 0 | OK | Ground clear controls. | 195 | 67.91 | 659.88
13327 | TIN-INTERP | Interpolated Ground | 85140.28 | 5.15 | 624.98 | 0 | 47.04 | 0 | OK | Ground clear controls. | 195 | 67.91 | 672.02
13328 | TIN-INTERP | Interpolated Ground | 85140.61 | -6.74 | 630.5 | 0 | 41.47 | 0 | OK | Ground clear controls. | 195 | 67.91 | 671.97
13329 | TIN-INTERP | Interpolated Ground | 85140.63 | -7.44 | 630.92 | 0 | 28.96 | 0 | OK | Ground clear controls. | 195 | 67.91 | 659.88
13330 | TIN-INTERP | Interpolated Ground | 85140.68 | -8.93 | 632.17 | 0 | 33.41 | 0 | OK | Ground clear controls. | 195 | 67.91 | 665.58
13331 | TIN-INTERP | Interpolated Ground | 85180.14 | 7.25 | 631.21 | 0 | 29.67 | 0 | OK | Ground clear controls. | 195 | 67.91 | 660.88
13332 | TIN-INTERP | Interpolated Ground | 85180.21 | 5.75 | 631.84 | 0 | 23.47 | 0 | OK | Ground clear controls. | 195 | 67.91 | 655.31
13333 | TIN-INTERP | Interpolated Ground | 85180.28 | 5.06 | 632.04 | 0 | 35.42 | 0 | OK | Ground clear controls. | 195 | 67.91 | 667.46
13334 | TIN-INTERP | Interpolated Ground | 85180.61 | -6.83 | 636.91 | 0 | 30.49 | 0 | OK | Ground clear controls. | 195 | 67.91 | 667.4
13335 | TIN-INTERP | Interpolated Ground | 85180.63 | -7.53 | 637.19 | 0 | 18.12 | 0 | OK | Ground clear controls. | 195 | 67.91 | 655.31
13336 | TIN-INTERP | Interpolated Ground | 85180.68 | -9.02 | 637.76 | 0 | 23.23 | 0 | OK | Ground clear controls. | 195 | 67.91 | 660.99
13337 | TIN-INTERP | Interpolated Ground | 85220.14 | 7.16 | 633.56 | 0 | 23.66 | 0 | OK | Ground clear controls. | 195 | 67.91 | 657.22
13338 | TIN-INTERP | Interpolated Ground | 85220.21 | 5.66 | 633.64 | 0 | 18.04 | 0 | OK | Ground clear controls. | 195 | 67.91 | 651.68
13339 | TIN-INTERP | Interpolated Ground | 85220.28 | 4.96 | 633.77 | 0 | 30.06 | 0 | OK | Ground clear controls. | 195 | 67.91 | 663.83
13340 | TIN-INTERP | Interpolated Ground | 85220.61 | -6.92 | 635.73 | 0 | 28.05 | 0 | OK | Ground clear controls. | 195 | 67.91 | 663.78
13341 | TIN-INTERP | Interpolated Ground | 85220.63 | -7.62 | 635.91 | 0 | 15.78 | 0 | OK | Ground clear controls. | 195 | 67.91 | 651.69
13342 | TIN-INTERP | Interpolated Ground | 85220.68 | -9.11 | 636.28 | 0 | 21.07 | 0 | OK | Ground clear controls. | 195 | 67.91 | 657.35
13343 | TIN-INTERP | Interpolated Ground | 85260.14 | 7.07 | 631.65 | 0 | 22.86 | 0 | OK | Ground clear controls. | 195 | 67.91 | 654.51
13344 | TIN-INTERP | Interpolated Ground | 85260.21 | 5.57 | 631.81 | 0 | 17.18 | 0 | OK | Ground clear controls. | 195 | 67.91 | 648.99
13345 | TIN-INTERP | Interpolated Ground | 85260.28 | 4.87 | 631.91 | 0 | 29.24 | 0 | OK | Ground clear controls. | 195 | 67.91 | 661.15
13346 | TIN-INTERP | Interpolated Ground | 85260.61 | -7.01 | 633.12 | 0 | 27.97 | 0 | OK | Ground clear controls. | 195 | 67.91 | 661.09
13347 | TIN-INTERP | Interpolated Ground | 85260.63 | -7.71 | 633.1 | 0 | 15.91 | 0 | OK | Ground clear controls. | 195 | 67.91 | 649.01
13348 | TIN-INTERP | Interpolated Ground | 85260.68 | -9.2 | 633.08 | 0 | 21.59 | 0 | OK | Ground clear controls. | 195 | 67.91 | 654.67
13349 | TIN-INTERP | Interpolated Ground | 85300.14 | 6.98 | 627.44 | 0 | 25.31 | 0 | OK | Ground clear controls. | 195 | 67.91 | 652.75
13350 | TIN-INTERP | Interpolated Ground | 85300.21 | 5.48 | 627.32 | 0 | 19.92 | 0 | OK | Ground clear controls. | 195 | 67.91 | 647.24
13351 | TIN-INTERP | Interpolated Ground | 85300.28 | 4.78 | 627.28 | 0 | 32.13 | 0 | OK | Ground clear controls. | 195 | 67.91 | 659.41
13352 | TIN-INTERP | Interpolated Ground | 85300.61 | -7.1 | 625.27 | 0 | 34.09 | 0 | OK | Ground clear controls. | 195 | 67.91 | 659.36
13353 | TIN-INTERP | Interpolated Ground | 85300.63 | -7.8 | 625.09 | 0 | 22.19 | 0 | OK | Ground clear controls. | 195 | 67.91 | 647.28
13354 | TIN-INTERP | Interpolated Ground | 85300.68 | -9.29 | 624.74 | 0 | 28.18 | 0 | OK | Ground clear controls. | 195 | 67.91 | 652.92
13355 | TIN-INTERP | Interpolated Ground | 85340.14 | 6.89 | 617.98 | 0 | 33.96 | 0 | OK | Ground clear controls. | 195 | 67.91 | 651.94
13356 | TIN-INTERP | Interpolated Ground | 85340.21 | 5.39 | 617.53 | 0 | 28.9 | 0 | OK | Ground clear controls. | 195 | 67.91 | 646.43
13357 | TIN-INTERP | Interpolated Ground | 85340.28 | 4.69 | 617.41 | 0 | 41.18 | 0 | OK | Ground clear controls. | 195 | 67.91 | 658.59
13358 | TIN-INTERP | Interpolated Ground | 85340.61 | -7.18 | 615.17 | 0 | 43.39 | 0 | OK | Ground clear controls. | 195 | 67.91 | 658.56
13359 | TIN-INTERP | Interpolated Ground | 85340.63 | -7.89 | 614.96 | 0 | 31.52 | 0 | OK | Ground clear controls. | 195 | 67.91 | 646.48
13360 | TIN-INTERP | Interpolated Ground | 85340.68 | -9.37 | 614.72 | 0 | 37.41 | 0 | OK | Ground clear controls. | 195 | 67.91 | 652.13
13361 | TIN-INTERP | Interpolated Ground | 85380.14 | 6.8 | 614.18 | 0 | 37.9 | 0 | OK | Ground clear controls. | 195 | 67.91 | 652.08
13362 | TIN-INTERP | Interpolated Ground | 85380.21 | 5.3 | 614.3 | 0 | 32.25 | 0 | OK | Ground clear controls. | 195 | 67.91 | 646.55
13363 | TIN-INTERP | Interpolated Ground | 85380.28 | 4.6 | 614.33 | 0 | 44.39 | 0 | OK | Ground clear controls. | 195 | 67.91 | 658.72
13364 | TIN-INTERP | Interpolated Ground | 85380.61 | -7.27 | 612.4 | 0 | 46.31 | 0 | OK | Ground clear controls. | 195 | 67.91 | 658.71
13365 | TIN-INTERP | Interpolated Ground | 85380.63 | -7.98 | 611.94 | 0 | 34.68 | 0 | OK | Ground clear controls. | 195 | 67.91 | 646.62
13366 | TIN-INTERP | Interpolated Ground | 85380.68 | -9.46 | 610.84 | 0 | 41.45 | 0 | OK | Ground clear controls. | 195 | 67.91 | 652.29
13367 | TIN-INTERP | Interpolated Ground | 85420.14 | 6.71 | 599.32 | 0 | 53.85 | 0 | OK | Ground clear controls. | 195 | 67.91 | 653.17
13368 | TIN-INTERP | Interpolated Ground | 85420.21 | 5.21 | 598.45 | 0 | 49.17 | 0 | OK | Ground clear controls. | 195 | 67.91 | 647.62
13369 | TIN-INTERP | Interpolated Ground | 85420.28 | 4.51 | 598.23 | 0 | 61.56 | 0 | OK | Ground clear controls. | 195 | 67.91 | 659.79
13370 | TIN-INTERP | Interpolated Ground | 85420.61 | -7.36 | 591.89 | 0 | 67.91 | 0 | OK | Ground clear controls. | 195 | 67.91 | 659.8
13371 | TIN-INTERP | Interpolated Ground | 85420.63 | -8.06 | 591.75 | 0 | 55.97 | 0 | OK | Ground clear controls. | 195 | 65.85 | 647.72
13372 | TIN-INTERP | Interpolated Ground | 85420.68 | -9.55 | 591.38 | 0 | 62.02 | 0 | OK | Ground clear controls. | 195 | 65.85 | 653.4
13373 | TIN-INTERP | Interpolated Ground | 85460.14 | 6.62 | 595.46 | 0 | 59.75 | 0 | OK | Ground clear controls. | 195 | 65.85 | 655.21
13374 | TIN-INTERP | Interpolated Ground | 85460.21 | 5.12 | 595.85 | 0 | 53.78 | 0 | OK | Ground clear controls. | 195 | 65.85 | 649.63
13375 | TIN-INTERP | Interpolated Ground | 85460.28 | 4.42 | 595.94 | 0 | 65.85 | 0 | OK | Ground clear controls. | 195 | 65.85 | 661.79
13376 | TIN-INTERP | Interpolated Ground | 85460.61 | -7.45 | 601.14 | 0 | 60.7 | 0 | OK | Ground clear controls. | 195 | 60.7 | 661.84
13377 | TIN-INTERP | Interpolated Ground | 85460.63 | -8.15 | 601.51 | 0 | 48.24 | 0 | OK | Ground clear controls. | 195 | 54.2 | 649.75
13378 | TIN-INTERP | Interpolated Ground | 85460.68 | -9.64 | 602.21 | 0 | 53.24 | 0 | OK | Ground clear controls. | 195 | 54.2 | 655.45
13379 | TIN-INTERP | Interpolated Ground | 85500.14 | 6.53 | 611.69 | 0 | 46.51 | 0 | OK | Ground clear controls. | 195 | 54.2 | 658.2
13380 | TIN-INTERP | Interpolated Ground | 85500.21 | 5.02 | 612.17 | 0 | 40.41 | 0 | OK | Ground clear controls. | 195 | 54.2 | 652.58
13381 | TIN-INTERP | Interpolated Ground | 85500.28 | 4.33 | 612.37 | 0 | 52.37 | 0 | OK | Ground clear controls. | 195 | 54.2 | 664.74
13382 | TIN-INTERP | Interpolated Ground | 85500.61 | -7.54 | 610.62 | 0 | 54.2 | 0 | OK | Ground clear controls. | 195 | 54.2 | 664.82
13383 | TIN-INTERP | Interpolated Ground | 85500.63 | -8.24 | 610.5 | 0 | 42.23 | 0 | OK | Ground clear controls. | 195 | 51.64 | 652.73
13384 | TIN-INTERP | Interpolated Ground | 85500.68 | -9.73 | 610.44 | 0 | 48.02 | 0 | OK | Ground clear controls. | 195 | 51.64 | 658.46
13385 | TIN-INTERP | Interpolated Ground | 85540.14 | 6.44 | 616.43 | 0 | 45.71 | 0 | OK | Ground clear controls. | 195 | 51.64 | 662.14
13386 | TIN-INTERP | Interpolated Ground | 85540.21 | 4.93 | 616.8 | 0 | 39.67 | 0 | OK | Ground clear controls. | 195 | 51.64 | 656.47
13387 | TIN-INTERP | Interpolated Ground | 85540.28 | 4.24 | 616.98 | 0 | 51.64 | 0 | OK | Ground clear controls. | 195 | 51.64 | 668.62
13388 | TIN-INTERP | Interpolated Ground | 85540.61 | -7.63 | 619.28 | 0 | 49.45 | 0 | OK | Ground clear controls. | 195 | 49.45 | 668.73
13389 | TIN-INTERP | Interpolated Ground | 85540.63 | -8.33 | 619.33 | 0 | 37.32 | 0 | OK | Ground clear controls. | 195 | 43.05 | 656.65
13390 | TIN-INTERP | Interpolated Ground | 85540.68 | -9.82 | 619.36 | 0 | 43.05 | 0 | OK | Ground clear controls. | 195 | 43.05 | 662.41
13391 | TIN-INTERP | Interpolated Ground | 85580.14 | 6.35 | 635.43 | 0 | 31.6 | 0 | OK | Ground clear controls. | 195 | 37.33 | 667.03
13392 | TIN-INTERP | Interpolated Ground | 85580.21 | 4.84 | 635.92 | 0 | 25.39 | 0 | OK | Ground clear controls. | 195 | 37.33 | 661.31
13393 | TIN-INTERP | Interpolated Ground | 85580.28 | 4.15 | 636.11 | 0 | 37.33 | 0 | OK | Ground clear controls. | 195 | 37.33 | 673.44
13394 | TIN-INTERP | Interpolated Ground | 85580.61 | -7.72 | 640.43 | 0 | 33.17 | 0 | OK | Ground clear controls. | 195 | 33.17 | 673.6
13395 | TIN-INTERP | Interpolated Ground | 85580.63 | -8.42 | 640.74 | 0 | 20.78 | 0 | OK | Ground clear controls. | 195 | 26.08 | 661.52
13396 | TIN-INTERP | Interpolated Ground | 85580.68 | -9.91 | 641.24 | 0 | 26.08 | 0 | OK | Ground clear controls. | 195 | 26.08 | 667.32
13397 | TIN-INTERP | Interpolated Ground | 85594.77 | 4.13 | 639.12 | 0 | 36.34 | 0 | OK | Ground clear controls. | 196 | 59.45 | 675.46
13398 | TIN-INTERP | Interpolated Ground | 85594.77 | 4.83 | 639.01 | 0 | 24.35 | 0 | OK | Ground clear controls. | 196 | 59.45 | 663.36
13399 | TIN-INTERP | Interpolated Ground | 85594.77 | 6.35 | 638.73 | 0 | 30.41 | 0 | OK | Ground clear controls. | 196 | 59.45 | 669.14
13400 | TIN-INTERP | Interpolated Ground | 85595.5 | -7.74 | 641.84 | 0 | 33.63 | 0 | OK | Ground clear controls. | 196 | 59.45 | 675.47
13401 | TIN-INTERP | Interpolated Ground | 85595.58 | -8.44 | 641.94 | 0 | 21.42 | 0 | OK | Ground clear controls. | 196 | 59.45 | 663.36
13402 | TIN-INTERP | Interpolated Ground | 85595.7 | -9.92 | 642.18 | 0 | 26.97 | 0 | OK | Ground clear controls. | 196 | 59.45 | 669.15
13403 | TIN-INTERP | Interpolated Ground | 85634.3 | 6.47 | 627.29 | 0 | 40.66 | 0 | OK | Ground clear controls. | 196 | 59.45 | 667.95
13404 | TIN-INTERP | Interpolated Ground | 85634.41 | 4.96 | 627.14 | 0 | 35.09 | 0 | OK | Ground clear controls. | 196 | 59.45 | 662.23
13405 | TIN-INTERP | Interpolated Ground | 85634.41 | 4.26 | 627.08 | 0 | 47.22 | 0 | OK | Ground clear controls. | 196 | 59.45 | 674.3
13406 | TIN-INTERP | Interpolated Ground | 85635.5 | -7.6 | 626.86 | 0 | 47.48 | 0 | OK | Ground clear controls. | 196 | 59.45 | 674.34
13407 | TIN-INTERP | Interpolated Ground | 85635.58 | -8.29 | 626.86 | 0 | 35.4 | 0 | OK | Ground clear controls. | 196 | 59.45 | 662.26
13408 | TIN-INTERP | Interpolated Ground | 85635.7 | -9.78 | 626.92 | 0 | 41.09 | 0 | OK | Ground clear controls. | 196 | 59.45 | 668.01
13409 | TIN-INTERP | Interpolated Ground | 85674.29 | 6.62 | 615.66 | 0 | 52.03 | 0 | OK | Ground clear controls. | 196 | 59.45 | 667.69
13410 | TIN-INTERP | Interpolated Ground | 85674.41 | 5.11 | 615.78 | 0 | 46.25 | 0 | OK | Ground clear controls. | 196 | 59.45 | 662.03
13411 | TIN-INTERP | Interpolated Ground | 85674.41 | 4.4 | 615.86 | 0 | 58.21 | 0 | OK | Ground clear controls. | 196 | 59.45 | 674.07
13412 | TIN-INTERP | Interpolated Ground | 85675.5 | -7.45 | 617.99 | 0 | 56.15 | 0 | OK | Ground clear controls. | 196 | 59.45 | 674.14
13413 | TIN-INTERP | Interpolated Ground | 85675.58 | -8.15 | 618.22 | 0 | 43.86 | 0 | OK | Ground clear controls. | 196 | 59.45 | 662.08
13414 | TIN-INTERP | Interpolated Ground | 85675.7 | -9.64 | 618.76 | 0 | 49.03 | 0 | OK | Ground clear controls. | 196 | 59.45 | 667.79
13415 | TIN-INTERP | Interpolated Ground | 85714.29 | 6.76 | 618.97 | 0 | 49.4 | 0 | OK | Ground clear controls. | 196 | 59.45 | 668.37
13416 | TIN-INTERP | Interpolated Ground | 85714.41 | 5.25 | 618.99 | 0 | 43.75 | 0 | OK | Ground clear controls. | 196 | 59.45 | 662.74
13417 | TIN-INTERP | Interpolated Ground | 85714.41 | 4.55 | 619.15 | 0 | 55.64 | 0 | OK | Ground clear controls. | 196 | 59.45 | 674.79
13418 | TIN-INTERP | Interpolated Ground | 85715.5 | -7.31 | 620.29 | 0 | 54.59 | 0 | OK | Ground clear controls. | 196 | 59.45 | 674.88
13419 | TIN-INTERP | Interpolated Ground | 85715.58 | -8.01 | 620.43 | 0 | 42.4 | 0 | OK | Ground clear controls. | 196 | 59.45 | 662.83
13420 | TIN-INTERP | Interpolated Ground | 85715.7 | -9.5 | 620.69 | 0 | 47.82 | 0 | OK | Ground clear controls. | 196 | 59.45 | 668.51
13421 | TIN-INTERP | Interpolated Ground | 85754.29 | 6.9 | 616.67 | 0 | 53.32 | 0 | OK | Ground clear controls. | 196 | 59.45 | 669.99
13422 | TIN-INTERP | Interpolated Ground | 85754.41 | 5.4 | 616.92 | 0 | 47.49 | 0 | OK | Ground clear controls. | 196 | 59.45 | 664.41
13423 | TIN-INTERP | Interpolated Ground | 85754.41 | 4.69 | 616.99 | 0 | 59.45 | 0 | OK | Ground clear controls. | 196 | 59.45 | 676.44
13424 | TIN-INTERP | Interpolated Ground | 85755.5 | -7.17 | 618.75 | 0 | 57.81 | 0 | OK | Ground clear controls. | 196 | 57.81 | 676.56
13425 | TIN-INTERP | Interpolated Ground | 85755.58 | -7.87 | 618.78 | 0 | 45.74 | 0 | OK | Ground clear controls. | 196 | 55.67 | 664.52
13426 | TIN-INTERP | Interpolated Ground | 85755.7 | -9.36 | 618.68 | 0 | 51.49 | 0 | OK | Ground clear controls. | 196 | 55.67 | 670.17
13427 | TIN-INTERP | Interpolated Ground | 85794.29 | 7.05 | 633.64 | 0 | 38.91 | 0 | OK | Ground clear controls. | 196 | 55.67 | 672.55
13428 | TIN-INTERP | Interpolated Ground | 85794.41 | 5.54 | 633.78 | 0 | 33.22 | 0 | OK | Ground clear controls. | 196 | 55.67 | 667
13429 | TIN-INTERP | Interpolated Ground | 85794.41 | 4.84 | 633.86 | 0 | 45.16 | 0 | OK | Ground clear controls. | 196 | 55.67 | 679.02
13430 | TIN-INTERP | Interpolated Ground | 85795.5 | -7.03 | 633.4 | 0 | 45.75 | 0 | OK | Ground clear controls. | 196 | 55.67 | 679.15
13431 | TIN-INTERP | Interpolated Ground | 85795.58 | -7.73 | 633.46 | 0 | 33.67 | 0 | OK | Ground clear controls. | 196 | 55.67 | 667.13
13432 | TIN-INTERP | Interpolated Ground | 85795.7 | -9.22 | 633.39 | 0 | 39.37 | 0 | OK | Ground clear controls. | 196 | 55.67 | 672.76
13433 | TIN-INTERP | Interpolated Ground | 85834.29 | 7.19 | 644.58 | 0 | 31.49 | 0 | OK | Ground clear controls. | 196 | 55.67 | 676.07
13434 | TIN-INTERP | Interpolated Ground | 85834.41 | 5.68 | 645.24 | 0 | 25.3 | 0 | OK | Ground clear controls. | 196 | 55.67 | 670.54
13435 | TIN-INTERP | Interpolated Ground | 85834.41 | 4.98 | 646.14 | 0 | 36.41 | 0 | OK | Ground clear controls. | 196 | 55.67 | 682.55
13436 | TIN-INTERP | Interpolated Ground | 85835.5 | -6.89 | 650.59 | 0 | 32.12 | 0 | OK | Ground clear controls. | 196 | 55.67 | 682.71
13437 | TIN-INTERP | Interpolated Ground | 85835.58 | -7.59 | 650.62 | 0 | 20.08 | 0 | OK | Ground clear controls. | 196 | 55.67 | 670.7
13438 | TIN-INTERP | Interpolated Ground | 85835.7 | -9.08 | 650.69 | 0 | 25.62 | 0 | OK | Ground clear controls. | 196 | 55.67 | 676.31
13439 | TIN-INTERP | Interpolated Ground | 85874.29 | 7.33 | 631.89 | 0 | 48.64 | 0 | OK | Ground clear controls. | 196 | 55.67 | 680.53
13440 | TIN-INTERP | Interpolated Ground | 85874.41 | 5.83 | 632.64 | 0 | 42.37 | 0 | OK | Ground clear controls. | 196 | 55.67 | 675.01
13441 | TIN-INTERP | Interpolated Ground | 85874.41 | 5.12 | 632.93 | 0 | 54.09 | 0 | OK | Ground clear controls. | 196 | 55.67 | 687.02
13442 | TIN-INTERP | Interpolated Ground | 85875.5 | -6.75 | 639.28 | 0 | 47.92 | 0 | OK | Ground clear controls. | 196 | 55.67 | 687.2
13443 | TIN-INTERP | Interpolated Ground | 85875.58 | -7.44 | 639.71 | 0 | 35.48 | 0 | OK | Ground clear controls. | 196 | 55.67 | 675.19
13444 | TIN-INTERP | Interpolated Ground | 85875.7 | -8.94 | 640.79 | 0 | 40.01 | 0 | OK | Ground clear controls. | 196 | 55.67 | 680.8
13445 | TIN-INTERP | Interpolated Ground | 85914.29 | 7.47 | 651.76 | 0 | 34.17 | 0 | OK | Ground clear controls. | 196 | 55.67 | 685.93
13446 | TIN-INTERP | Interpolated Ground | 85914.41 | 5.97 | 651.75 | 0 | 28.67 | 0 | OK | Ground clear controls. | 196 | 55.67 | 680.42
13447 | TIN-INTERP | Interpolated Ground | 85914.41 | 5.27 | 651.7 | 0 | 40.73 | 0 | OK | Ground clear controls. | 196 | 55.67 | 692.43
13448 | TIN-INTERP | Interpolated Ground | 85915.5 | -6.6 | 655.3 | 0 | 37.32 | 0 | OK | Ground clear controls. | 196 | 55.67 | 692.62
13449 | TIN-INTERP | Interpolated Ground | 85915.58 | -7.3 | 655.61 | 0 | 25 | 0 | OK | Ground clear controls. | 196 | 55.67 | 680.61
13450 | TIN-INTERP | Interpolated Ground | 85915.7 | -8.8 | 656.01 | 0 | 30.22 | 0 | OK | Ground clear controls. | 196 | 55.67 | 686.23
13451 | TIN-INTERP | Interpolated Ground | 85954.29 | 7.62 | 660.3 | 0 | 32.01 | 0 | OK | Ground clear controls. | 196 | 55.67 | 692.31
13452 | TIN-INTERP | Interpolated Ground | 85954.41 | 6.12 | 660.88 | 0 | 25.91 | 0 | OK | Ground clear controls. | 196 | 55.67 | 686.79
13453 | TIN-INTERP | Interpolated Ground | 85954.41 | 5.41 | 661.43 | 0 | 37.37 | 0 | OK | Ground clear controls. | 196 | 55.67 | 698.8
13454 | TIN-INTERP | Interpolated Ground | 85955.5 | -6.46 | 668.09 | 0 | 30.91 | 0 | OK | Ground clear controls. | 196 | 55.67 | 699
13455 | TIN-INTERP | Interpolated Ground | 85955.58 | -7.16 | 668.33 | 0 | 18.67 | 0 | OK | Ground clear controls. | 196 | 55.67 | 687
13456 | TIN-INTERP | Interpolated Ground | 85955.7 | -8.66 | 668.82 | 0 | 23.79 | 0 | OK | Ground clear controls. | 196 | 55.67 | 692.61
13457 | TIN-INTERP | Interpolated Ground | 85994.29 | 7.76 | 659.13 | 0 | 40.49 | 0 | OK | Ground clear controls. | 196 | 55.67 | 699.62
13458 | TIN-INTERP | Interpolated Ground | 85994.41 | 6.26 | 659.57 | 0 | 34.52 | 0 | OK | Ground clear controls. | 196 | 55.67 | 694.09
13459 | TIN-INTERP | Interpolated Ground | 85994.41 | 5.55 | 659.77 | 0 | 46.35 | 0 | OK | Ground clear controls. | 196 | 55.67 | 706.12
13460 | TIN-INTERP | Interpolated Ground | 85995.49 | -6.32 | 664.05 | 0 | 42.28 | 0 | OK | Ground clear controls. | 196 | 55.67 | 706.33
13461 | TIN-INTERP | Interpolated Ground | 85995.58 | -7.02 | 664.3 | 0 | 30.02 | 0 | OK | Ground clear controls. | 196 | 55.67 | 694.32
13462 | TIN-INTERP | Interpolated Ground | 85995.7 | -8.52 | 664.91 | 0 | 35.04 | 0 | OK | Ground clear controls. | 196 | 55.67 | 699.95
13463 | TIN-INTERP | Interpolated Ground | 86034.29 | 7.9 | 658.37 | 0 | 49.52 | 0 | OK | Ground clear controls. | 196 | 55.67 | 707.89
13464 | TIN-INTERP | Interpolated Ground | 86034.41 | 6.41 | 658.64 | 0 | 43.7 | 0 | OK | Ground clear controls. | 196 | 55.67 | 702.34
13465 | TIN-INTERP | Interpolated Ground | 86034.41 | 5.7 | 658.71 | 0 | 55.67 | 0 | OK | Ground clear controls. | 196 | 55.67 | 714.38
13466 | TIN-INTERP | Interpolated Ground | 86035.49 | -6.18 | 663.3 | 0 | 51.3 | 0 | OK | Ground clear controls. | 196 | 53.96 | 714.6
13467 | TIN-INTERP | Interpolated Ground | 86035.58 | -6.88 | 664.07 | 0 | 38.52 | 0 | OK | Ground clear controls. | 196 | 53.96 | 702.59
13468 | TIN-INTERP | Interpolated Ground | 86035.7 | -8.38 | 665.36 | 0 | 42.88 | 0 | OK | Ground clear controls. | 196 | 53.96 | 708.24
13469 | TIN-INTERP | Interpolated Ground | 86074.29 | 8.05 | 669.98 | 0 | 47.17 | 0 | OK | Ground clear controls. | 196 | 53.96 | 717.15
13470 | TIN-INTERP | Interpolated Ground | 86074.41 | 6.55 | 669.81 | 0 | 41.75 | 0 | OK | Ground clear controls. | 196 | 53.96 | 711.56
13471 | TIN-INTERP | Interpolated Ground | 86074.41 | 5.84 | 669.65 | 0 | 53.96 | 0 | OK | Ground clear controls. | 196 | 53.96 | 723.61
13472 | TIN-INTERP | Interpolated Ground | 86075.49 | -6.04 | 673.42 | 0 | 50.43 | 0 | OK | Ground clear controls. | 196 | 50.43 | 723.85
13473 | TIN-INTERP | Interpolated Ground | 86075.58 | -6.74 | 673.84 | 0 | 37.98 | 0 | OK | Ground clear controls. | 196 | 48.11 | 711.82
13474 | TIN-INTERP | Interpolated Ground | 86075.7 | -8.24 | 674.77 | 0 | 42.72 | 0 | OK | Ground clear controls. | 196 | 48.11 | 717.49
13475 | TIN-INTERP | Interpolated Ground | 86114.29 | 8.19 | 686.96 | 0 | 40.39 | 0 | OK | Ground clear controls. | 196 | 48.11 | 727.35
13476 | TIN-INTERP | Interpolated Ground | 86114.41 | 6.7 | 686.8 | 0 | 34.94 | 0 | OK | Ground clear controls. | 196 | 48.11 | 721.74
13477 | TIN-INTERP | Interpolated Ground | 86114.41 | 5.98 | 686.71 | 0 | 47.09 | 0 | OK | Ground clear controls. | 196 | 48.11 | 733.8
13478 | TIN-INTERP | Interpolated Ground | 86115.49 | -5.9 | 685.93 | 0 | 48.11 | 0 | OK | Ground clear controls. | 196 | 48.11 | 734.04
13479 | TIN-INTERP | Interpolated Ground | 86115.58 | -6.59 | 685.86 | 0 | 36.16 | 0 | OK | Ground clear controls. | 196 | 44.56 | 722.02
13480 | TIN-INTERP | Interpolated Ground | 86115.7 | -8.1 | 685.75 | 0 | 41.97 | 0 | OK | Ground clear controls. | 196 | 44.56 | 727.72
13481 | TIN-INTERP | Interpolated Ground | 86154.29 | 8.33 | 701.73 | 0 | 36.81 | 0 | OK | Ground clear controls. | 196 | 44.56 | 738.54
13482 | TIN-INTERP | Interpolated Ground | 86154.4 | 6.84 | 701.94 | 0 | 30.93 | 0 | OK | Ground clear controls. | 196 | 44.56 | 732.87
13483 | TIN-INTERP | Interpolated Ground | 86154.41 | 6.13 | 702.03 | 0 | 42.93 | 0 | OK | Ground clear controls. | 196 | 44.56 | 744.96
13484 | TIN-INTERP | Interpolated Ground | 86155.49 | -5.75 | 700.65 | 0 | 44.56 | 0 | OK | Ground clear controls. | 196 | 44.56 | 745.21
13485 | TIN-INTERP | Interpolated Ground | 86155.58 | -6.45 | 700.49 | 0 | 32.67 | 0 | OK | Ground clear controls. | 196 | 39.3 | 733.16
13486 | TIN-INTERP | Interpolated Ground | 86155.7 | -7.96 | 700.21 | 0 | 38.7 | 0 | OK | Ground clear controls. | 196 | 39.3 | 738.91
13487 | TIN-INTERP | Interpolated Ground | 86194.29 | 8.48 | 717.34 | 0 | 33.37 | 0 | OK | Ground clear controls. | 196 | 39.3 | 750.71
13488 | TIN-INTERP | Interpolated Ground | 86194.4 | 6.99 | 717.66 | 0 | 27.32 | 0 | OK | Ground clear controls. | 196 | 39.3 | 744.98
13489 | TIN-INTERP | Interpolated Ground | 86194.41 | 6.27 | 717.79 | 0 | 39.3 | 0 | OK | Ground clear controls. | 196 | 39.3 | 757.09
13490 | TIN-INTERP | Interpolated Ground | 86195.49 | -5.61 | 718.82 | 0 | 38.52 | 0 | OK | Ground clear controls. | 196 | 38.52 | 757.34
13491 | TIN-INTERP | Interpolated Ground | 86195.58 | -6.31 | 718.81 | 0 | 26.47 | 0 | OK | Ground clear controls. | 196 | 33.87 | 745.28
13492 | TIN-INTERP | Interpolated Ground | 86195.7 | -7.82 | 718.75 | 0 | 32.33 | 0 | OK | Ground clear controls. | 196 | 33.87 | 751.08
13493 | TIN-INTERP | Interpolated Ground | 86234.29 | 8.62 | 736.25 | 0 | 27.63 | 0 | OK | Ground clear controls. | 196 | 33.87 | 763.88
13494 | TIN-INTERP | Interpolated Ground | 86234.4 | 7.13 | 736.32 | 0 | 21.76 | 0 | OK | Ground clear controls. | 196 | 33.87 | 758.08
13495 | TIN-INTERP | Interpolated Ground | 86234.41 | 6.42 | 736.35 | 0 | 33.87 | 0 | OK | Ground clear controls. | 196 | 33.87 | 770.22
13496 | TIN-INTERP | Interpolated Ground | 86235.49 | -5.47 | 737.06 | 0 | 33.41 | 0 | OK | Ground clear controls. | 196 | 33.41 | 770.47
13497 | TIN-INTERP | Interpolated Ground | 86235.58 | -6.17 | 737.16 | 0 | 21.23 | 0 | OK | Ground clear controls. | 196 | 27.2 | 758.39
13498 | TIN-INTERP | Interpolated Ground | 86235.7 | -7.67 | 737.03 | 0 | 27.2 | 0 | OK | Ground clear controls. | 196 | 27.2 | 764.23
13499 | TIN-INTERP | Interpolated Ground | 86238 | -7.68 | 737.97 | 0 | 27.19 | 0 | OK | Ground clear controls. | 197 | 60.72 | 765.16
13500 | TIN-INTERP | Interpolated Ground | 86238 | -6.17 | 737.73 | 0 | 21.63 | 0 | OK | Ground clear controls. | 197 | 60.72 | 759.36
13501 | TIN-INTERP | Interpolated Ground | 86238 | -5.48 | 737.58 | 0 | 33.88 | 0 | OK | Ground clear controls. | 197 | 60.72 | 771.46
13502 | TIN-INTERP | Interpolated Ground | 86238.52 | 6.41 | 736.58 | 0 | 34.87 | 0 | OK | Ground clear controls. | 197 | 60.72 | 771.45
13503 | TIN-INTERP | Interpolated Ground | 86238.73 | 8.6 | 736.45 | 0 | 28.71 | 0 | OK | Ground clear controls. | 197 | 60.72 | 765.16
13504 | TIN-INTERP | Interpolated Ground | 86238.79 | 7.1 | 736.56 | 0 | 22.82 | 0 | OK | Ground clear controls. | 197 | 60.72 | 759.38
13505 | TIN-INTERP | Interpolated Ground | 86277.81 | -7.78 | 737.17 | 0 | 26.75 | 0 | OK | Ground clear controls. | 197 | 60.72 | 763.92
13506 | TIN-INTERP | Interpolated Ground | 86277.95 | -6.28 | 736.01 | 0 | 22.18 | 0 | OK | Ground clear controls. | 197 | 60.72 | 758.19
13507 | TIN-INTERP | Interpolated Ground | 86277.98 | -5.58 | 735.46 | 0 | 34.81 | 0 | OK | Ground clear controls. | 197 | 60.72 | 770.27
13508 | TIN-INTERP | Interpolated Ground | 86278.52 | 6.31 | 729.01 | 0 | 41.2 | 0 | OK | Ground clear controls. | 197 | 60.72 | 770.21
13509 | TIN-INTERP | Interpolated Ground | 86278.73 | 8.5 | 728.16 | 0 | 35.79 | 0 | OK | Ground clear controls. | 197 | 60.72 | 763.95
13510 | TIN-INTERP | Interpolated Ground | 86278.79 | 7 | 728.72 | 0 | 29.57 | 0 | OK | Ground clear controls. | 197 | 60.72 | 758.29
13511 | TIN-INTERP | Interpolated Ground | 86317.81 | -7.88 | 733.98 | 0 | 29.61 | 0 | OK | Ground clear controls. | 197 | 60.72 | 763.59
13512 | TIN-INTERP | Interpolated Ground | 86317.95 | -6.38 | 733.38 | 0 | 24.53 | 0 | OK | Ground clear controls. | 197 | 60.72 | 757.91
13513 | TIN-INTERP | Interpolated Ground | 86317.98 | -5.68 | 732.94 | 0 | 37.04 | 0 | OK | Ground clear controls. | 197 | 60.72 | 769.98
13514 | TIN-INTERP | Interpolated Ground | 86318.52 | 6.2 | 725.74 | 0 | 44.14 | 0 | OK | Ground clear controls. | 197 | 60.72 | 769.88
13515 | TIN-INTERP | Interpolated Ground | 86318.73 | 8.4 | 724.27 | 0 | 39.37 | 0 | OK | Ground clear controls. | 197 | 60.72 | 763.64
13516 | TIN-INTERP | Interpolated Ground | 86318.79 | 6.9 | 724.99 | 0 | 33.09 | 0 | OK | Ground clear controls. | 197 | 60.72 | 758.08
13517 | TIN-INTERP | Interpolated Ground | 86357.81 | -7.98 | 731.11 | 0 | 33.07 | 0 | OK | Ground clear controls. | 197 | 60.72 | 764.18
13518 | TIN-INTERP | Interpolated Ground | 86357.95 | -6.48 | 730.28 | 0 | 28.25 | 0 | OK | Ground clear controls. | 197 | 60.72 | 758.53
13519 | TIN-INTERP | Interpolated Ground | 86357.98 | -5.78 | 729.89 | 0 | 40.69 | 0 | OK | Ground clear controls. | 197 | 60.72 | 770.58
13520 | TIN-INTERP | Interpolated Ground | 86358.52 | 6.1 | 724.69 | 0 | 45.77 | 0 | OK | Ground clear controls. | 197 | 60.72 | 770.46
13521 | TIN-INTERP | Interpolated Ground | 86358.73 | 8.3 | 723.11 | 0 | 41.14 | 0 | OK | Ground clear controls. | 197 | 60.72 | 764.25
13522 | TIN-INTERP | Interpolated Ground | 86358.79 | 6.8 | 724.18 | 0 | 34.56 | 0 | OK | Ground clear controls. | 197 | 60.72 | 758.74
13523 | TIN-INTERP | Interpolated Ground | 86397.81 | -8.08 | 718.28 | 0 | 47.38 | 0 | OK | Ground clear controls. | 197 | 60.72 | 765.66
13524 | TIN-INTERP | Interpolated Ground | 86397.95 | -6.59 | 717.56 | 0 | 42.47 | 0 | OK | Ground clear controls. | 197 | 60.72 | 760.03
13525 | TIN-INTERP | Interpolated Ground | 86397.98 | -5.89 | 717.37 | 0 | 54.72 | 0 | OK | Ground clear controls. | 197 | 60.72 | 772.09
13526 | TIN-INTERP | Interpolated Ground | 86398.52 | 6 | 711.23 | 0 | 60.72 | 0 | OK | Ground clear controls. | 197 | 60.72 | 771.95
13527 | TIN-INTERP | Interpolated Ground | 86398.73 | 8.2 | 710.5 | 0 | 55.25 | 0 | OK | Ground clear controls. | 197 | 55.25 | 765.75
13528 | TIN-INTERP | Interpolated Ground | 86398.79 | 6.7 | 710.81 | 0 | 49.47 | 0 | OK | Ground clear controls. | 197 | 49.47 | 760.28
13529 | TIN-INTERP | Interpolated Ground | 86437.81 | -8.19 | 728.87 | 0 | 39.2 | 0 | OK | Ground clear controls. | 197 | 49.14 | 768.07
13530 | TIN-INTERP | Interpolated Ground | 86437.95 | -6.69 | 728.12 | 0 | 34.32 | 0 | OK | Ground clear controls. | 197 | 49.14 | 762.44
13531 | TIN-INTERP | Interpolated Ground | 86437.98 | -5.99 | 727.82 | 0 | 46.68 | 0 | OK | Ground clear controls. | 197 | 49.14 | 774.5
13532 | TIN-INTERP | Interpolated Ground | 86438.52 | 5.9 | 725.21 | 0 | 49.14 | 0 | OK | Ground clear controls. | 197 | 49.14 | 774.35
13533 | TIN-INTERP | Interpolated Ground | 86438.73 | 8.1 | 724.51 | 0 | 43.64 | 0 | OK | Ground clear controls. | 197 | 43.64 | 768.15
13534 | TIN-INTERP | Interpolated Ground | 86438.79 | 6.6 | 725.09 | 0 | 37.61 | 0 | OK | Ground clear controls. | 197 | 37.61 | 762.7
13535 | TIN-INTERP | Interpolated Ground | 86477.81 | -8.29 | 749.25 | 0 | 22.11 | 0 | OK | Ground clear controls. | 197 | 36.77 | 771.36
13536 | TIN-INTERP | Interpolated Ground | 86477.95 | -6.79 | 748.74 | 0 | 17 | 0 | OK | Ground clear controls. | 197 | 36.77 | 765.74
13537 | TIN-INTERP | Interpolated Ground | 86477.98 | -6.09 | 748.26 | 0 | 29.54 | 0 | OK | Ground clear controls. | 197 | 36.77 | 777.8
13538 | TIN-INTERP | Interpolated Ground | 86478.52 | 5.8 | 743.8 | 0 | 33.86 | 0 | OK | Ground clear controls. | 197 | 36.77 | 777.66
13539 | TIN-INTERP | Interpolated Ground | 86478.73 | 8 | 743.23 | 0 | 28.24 | 0 | OK | Ground clear controls. | 197 | 36.77 | 771.47
13540 | TIN-INTERP | Interpolated Ground | 86478.79 | 6.49 | 743.65 | 0 | 22.35 | 0 | OK | Ground clear controls. | 197 | 36.77 | 766
13541 | TIN-INTERP | Interpolated Ground | 86517.81 | -8.39 | 749.93 | 0 | 25.66 | 0 | OK | Ground clear controls. | 197 | 36.77 | 775.59
13542 | TIN-INTERP | Interpolated Ground | 86517.95 | -6.9 | 749.37 | 0 | 20.57 | 0 | OK | Ground clear controls. | 197 | 36.77 | 769.94
13543 | TIN-INTERP | Interpolated Ground | 86517.98 | -6.19 | 749.1 | 0 | 32.91 | 0 | OK | Ground clear controls. | 197 | 36.77 | 782.01
13544 | TIN-INTERP | Interpolated Ground | 86518.52 | 5.7 | 745.12 | 0 | 36.77 | 0 | OK | Ground clear controls. | 197 | 36.77 | 781.89
13545 | TIN-INTERP | Interpolated Ground | 86518.73 | 7.89 | 744.25 | 0 | 31.44 | 0 | OK | Ground clear controls. | 197 | 31.84 | 775.69
13546 | TIN-INTERP | Interpolated Ground | 86518.79 | 6.39 | 744.87 | 0 | 25.31 | 0 | OK | Ground clear controls. | 197 | 31.84 | 770.18
13547 | TIN-INTERP | Interpolated Ground | 86557.81 | -8.5 | 759.83 | 0 | 20.89 | 0 | OK | Ground clear controls. | 197 | 31.84 | 780.72
13548 | TIN-INTERP | Interpolated Ground | 86557.95 | -7 | 759.44 | 0 | 15.6 | 0 | OK | Ground clear controls. | 197 | 31.84 | 775.04
13549 | TIN-INTERP | Interpolated Ground | 86557.98 | -6.29 | 759.17 | 0 | 27.95 | 0 | OK | Ground clear controls. | 197 | 31.84 | 787.12
13550 | TIN-INTERP | Interpolated Ground | 86558.52 | 5.6 | 755.21 | 0 | 31.84 | 0 | OK | Ground clear controls. | 197 | 31.84 | 787.05
13551 | TIN-INTERP | Interpolated Ground | 86558.73 | 7.79 | 753.69 | 0 | 27.13 | 0 | OK | Ground clear controls. | 197 | 28.64 | 780.82
13552 | TIN-INTERP | Interpolated Ground | 86558.79 | 6.29 | 754.92 | 0 | 20.32 | 0 | OK | Ground clear controls. | 197 | 28.64 | 775.24
13553 | TIN-INTERP | Interpolated Ground | 86597.81 | -8.6 | 766.24 | 0 | 20.53 | 0 | OK | Ground clear controls. | 197 | 28.64 | 786.77
13554 | TIN-INTERP | Interpolated Ground | 86597.95 | -7.1 | 765.68 | 0 | 15.36 | 0 | OK | Ground clear controls. | 197 | 28.64 | 781.04
13555 | TIN-INTERP | Interpolated Ground | 86597.98 | -6.4 | 765.31 | 0 | 27.82 | 0 | OK | Ground clear controls. | 197 | 28.64 | 793.13
13556 | TIN-INTERP | Interpolated Ground | 86598.52 | 5.5 | 764.47 | 0 | 28.64 | 0 | OK | Ground clear controls. | 197 | 28.64 | 793.11
13557 | TIN-INTERP | Interpolated Ground | 86598.73 | 7.69 | 764.28 | 0 | 22.57 | 0 | OK | Ground clear controls. | 197 | 22.57 | 786.85
13558 | TIN-INTERP | Interpolated Ground | 86598.79 | 6.19 | 764.48 | 0 | 16.71 | 0 | OK | Ground clear controls. | 197 | 16.71 | 781.19
13559 | TIN-INTERP | Interpolated Ground | 86631.6 | 5.42 | 766.53 | 0 | 32.34 | 0 | OK | Ground clear controls. | 198 | 41.8 | 798.87
13560 | TIN-INTERP | Interpolated Ground | 86631.6 | 6.11 | 766.39 | 0 | 20.38 | 0 | OK | Ground clear controls. | 198 | 41.8 | 786.77
13561 | TIN-INTERP | Interpolated Ground | 86631.6 | 7.62 | 765.91 | 0 | 26.66 | 0 | OK | Ground clear controls. | 198 | 41.8 | 792.57
13562 | TIN-INTERP | Interpolated Ground | 86631.95 | -6.48 | 767.33 | 0 | 31.54 | 0 | OK | Ground clear controls. | 198 | 41.8 | 798.87
13563 | TIN-INTERP | Interpolated Ground | 86632.11 | -7.17 | 767.36 | 0 | 19.41 | 0 | OK | Ground clear controls. | 198 | 41.8 | 786.77
13564 | TIN-INTERP | Interpolated Ground | 86632.17 | -8.67 | 767.44 | 0 | 25.12 | 0 | OK | Ground clear controls. | 198 | 41.8 | 792.56
13565 | TIN-INTERP | Interpolated Ground | 86671.29 | 6.21 | 758 | 0 | 21.98 | 0 | OK | Ground clear controls. | 198 | 41.8 | 779.98
13566 | TIN-INTERP | Interpolated Ground | 86671.29 | 7.72 | 757.88 | 0 | 27.81 | 0 | OK | Ground clear controls. | 198 | 41.8 | 785.69
13567 | TIN-INTERP | Interpolated Ground | 86671.42 | 5.53 | 758 | 0 | 33.96 | 0 | OK | Ground clear controls. | 198 | 41.8 | 791.96
13568 | TIN-INTERP | Interpolated Ground | 86671.95 | -6.36 | 758.91 | 0 | 33.07 | 0 | OK | Ground clear controls. | 198 | 41.8 | 791.98
13569 | TIN-INTERP | Interpolated Ground | 86672.11 | -7.06 | 758.96 | 0 | 21.05 | 0 | OK | Ground clear controls. | 198 | 41.8 | 780.01
13570 | TIN-INTERP | Interpolated Ground | 86672.17 | -8.55 | 759.35 | 0 | 26.37 | 0 | OK | Ground clear controls. | 198 | 41.8 | 785.72
13571 | TIN-INTERP | Interpolated Ground | 86711.29 | 6.33 | 750.02 | 0 | 24.07 | 0 | OK | Ground clear controls. | 198 | 41.8 | 774.09
13572 | TIN-INTERP | Interpolated Ground | 86711.29 | 7.83 | 750.36 | 0 | 29.35 | 0 | OK | Ground clear controls. | 198 | 41.8 | 779.71
13573 | TIN-INTERP | Interpolated Ground | 86711.42 | 5.64 | 749.82 | 0 | 36.14 | 0 | OK | Ground clear controls. | 198 | 41.8 | 785.96
13574 | TIN-INTERP | Interpolated Ground | 86711.95 | -6.25 | 749.83 | 0 | 36.17 | 0 | OK | Ground clear controls. | 198 | 41.8 | 786
13575 | TIN-INTERP | Interpolated Ground | 86712.11 | -6.94 | 749.61 | 0 | 24.52 | 0 | OK | Ground clear controls. | 198 | 41.8 | 774.13
13576 | TIN-INTERP | Interpolated Ground | 86712.17 | -8.44 | 749.21 | 0 | 30.55 | 0 | OK | Ground clear controls. | 198 | 41.8 | 779.76
13577 | TIN-INTERP | Interpolated Ground | 86751.29 | 6.44 | 745 | 0 | 24.07 | 0 | OK | Ground clear controls. | 198 | 41.8 | 769.07
13578 | TIN-INTERP | Interpolated Ground | 86751.29 | 7.94 | 745.01 | 0 | 29.62 | 0 | OK | Ground clear controls. | 198 | 41.8 | 774.63
13579 | TIN-INTERP | Interpolated Ground | 86751.42 | 5.75 | 744.71 | 0 | 36.14 | 0 | OK | Ground clear controls. | 198 | 41.8 | 780.85
13580 | TIN-INTERP | Interpolated Ground | 86751.95 | -6.13 | 739.13 | 0 | 41.8 | 0 | OK | Ground clear controls. | 198 | 41.8 | 780.93
13581 | TIN-INTERP | Interpolated Ground | 86752.11 | -6.82 | 738.75 | 0 | 30.38 | 0 | OK | Ground clear controls. | 198 | 39.06 | 769.13
13582 | TIN-INTERP | Interpolated Ground | 86752.17 | -8.32 | 737.93 | 0 | 36.77 | 0 | OK | Ground clear controls. | 198 | 39.06 | 774.7
13583 | TIN-INTERP | Interpolated Ground | 86791.29 | 6.55 | 745.68 | 0 | 19.26 | 0 | OK | Ground clear controls. | 198 | 39.06 | 764.94
13584 | TIN-INTERP | Interpolated Ground | 86791.29 | 8.05 | 746.15 | 0 | 24.31 | 0 | OK | Ground clear controls. | 198 | 39.06 | 770.46
13585 | TIN-INTERP | Interpolated Ground | 86791.42 | 5.86 | 745.5 | 0 | 31.17 | 0 | OK | Ground clear controls. | 198 | 39.06 | 776.67
13586 | TIN-INTERP | Interpolated Ground | 86791.95 | -6.02 | 741.64 | 0 | 35.12 | 0 | OK | Ground clear controls. | 198 | 39.06 | 776.76
13587 | TIN-INTERP | Interpolated Ground | 86792.11 | -6.71 | 741.54 | 0 | 23.48 | 0 | OK | Ground clear controls. | 198 | 39.06 | 765.02
13588 | TIN-INTERP | Interpolated Ground | 86792.17 | -8.21 | 741.15 | 0 | 29.38 | 0 | OK | Ground clear controls. | 198 | 39.06 | 770.53
13589 | TIN-INTERP | Interpolated Ground | 86831.29 | 6.66 | 745.17 | 0 | 16.52 | 0 | OK | Ground clear controls. | 198 | 39.06 | 761.69
13590 | TIN-INTERP | Interpolated Ground | 86831.29 | 8.16 | 745.47 | 0 | 21.71 | 0 | OK | Ground clear controls. | 198 | 39.06 | 767.18
13591 | TIN-INTERP | Interpolated Ground | 86831.42 | 5.97 | 744.98 | 0 | 28.38 | 0 | OK | Ground clear controls. | 198 | 39.06 | 773.36
13592 | TIN-INTERP | Interpolated Ground | 86831.95 | -5.91 | 743.23 | 0 | 30.24 | 0 | OK | Ground clear controls. | 198 | 39.06 | 773.47
13593 | TIN-INTERP | Interpolated Ground | 86832.11 | -6.59 | 743.12 | 0 | 18.65 | 0 | OK | Ground clear controls. | 198 | 39.06 | 761.77
13594 | TIN-INTERP | Interpolated Ground | 86832.17 | -8.09 | 742.91 | 0 | 24.35 | 0 | OK | Ground clear controls. | 198 | 39.06 | 767.26
13595 | TIN-INTERP | Interpolated Ground | 86871.29 | 6.78 | 741.56 | 0 | 17.76 | 0 | OK | Ground clear controls. | 198 | 39.06 | 759.32
13596 | TIN-INTERP | Interpolated Ground | 86871.29 | 8.28 | 741.93 | 0 | 22.85 | 0 | OK | Ground clear controls. | 198 | 39.06 | 764.78
13597 | TIN-INTERP | Interpolated Ground | 86871.42 | 6.08 | 741.57 | 0 | 29.41 | 0 | OK | Ground clear controls. | 198 | 39.06 | 770.98
13598 | TIN-INTERP | Interpolated Ground | 86871.95 | -5.79 | 739.77 | 0 | 31.32 | 0 | OK | Ground clear controls. | 198 | 39.06 | 771.09
13599 | TIN-INTERP | Interpolated Ground | 86872.11 | -6.47 | 739.74 | 0 | 19.66 | 0 | OK | Ground clear controls. | 198 | 39.06 | 759.4
13600 | TIN-INTERP | Interpolated Ground | 86872.17 | -7.98 | 740.01 | 0 | 24.87 | 0 | OK | Ground clear controls. | 198 | 39.06 | 764.88
13601 | TIN-INTERP | Interpolated Ground | 86911.29 | 6.89 | 737.57 | 0 | 20.25 | 0 | OK | Ground clear controls. | 198 | 39.06 | 757.82
13602 | TIN-INTERP | Interpolated Ground | 86911.29 | 8.39 | 737.65 | 0 | 25.64 | 0 | OK | Ground clear controls. | 198 | 39.06 | 763.29
13603 | TIN-INTERP | Interpolated Ground | 86911.42 | 6.19 | 737.44 | 0 | 32.04 | 0 | OK | Ground clear controls. | 198 | 39.06 | 769.48
13604 | TIN-INTERP | Interpolated Ground | 86911.95 | -5.68 | 736.37 | 0 | 33.23 | 0 | OK | Ground clear controls. | 198 | 39.06 | 769.6
13605 | TIN-INTERP | Interpolated Ground | 86912.11 | -6.36 | 736.38 | 0 | 21.54 | 0 | OK | Ground clear controls. | 198 | 39.06 | 757.92
13606 | TIN-INTERP | Interpolated Ground | 86912.17 | -7.86 | 736.5 | 0 | 26.88 | 0 | OK | Ground clear controls. | 198 | 39.06 | 763.38
13607 | TIN-INTERP | Interpolated Ground | 86951.29 | 7 | 733.58 | 0 | 23.61 | 0 | OK | Ground clear controls. | 198 | 39.06 | 757.19
13608 | TIN-INTERP | Interpolated Ground | 86951.29 | 8.5 | 733.7 | 0 | 28.99 | 0 | OK | Ground clear controls. | 198 | 39.06 | 762.69
13609 | TIN-INTERP | Interpolated Ground | 86951.42 | 6.3 | 733.55 | 0 | 35.33 | 0 | OK | Ground clear controls. | 198 | 39.06 | 768.88
13610 | TIN-INTERP | Interpolated Ground | 86951.95 | -5.56 | 732.12 | 0 | 36.88 | 0 | OK | Ground clear controls. | 198 | 39.06 | 769
13611 | TIN-INTERP | Interpolated Ground | 86952.11 | -6.24 | 732.01 | 0 | 25.3 | 0 | OK | Ground clear controls. | 198 | 39.06 | 757.31
13612 | TIN-INTERP | Interpolated Ground | 86952.17 | -7.75 | 731.83 | 0 | 30.96 | 0 | OK | Ground clear controls. | 198 | 39.06 | 762.79
13613 | TIN-INTERP | Interpolated Ground | 86991.29 | 7.12 | 731.53 | 0 | 25.92 | 0 | OK | Ground clear controls. | 198 | 39.06 | 757.45
13614 | TIN-INTERP | Interpolated Ground | 86991.29 | 8.61 | 731.89 | 0 | 31.09 | 0 | OK | Ground clear controls. | 198 | 39.06 | 762.98
13615 | TIN-INTERP | Interpolated Ground | 86991.41 | 6.41 | 731.44 | 0 | 37.75 | 0 | OK | Ground clear controls. | 198 | 39.06 | 769.19
13616 | TIN-INTERP | Interpolated Ground | 86991.95 | -5.45 | 730.23 | 0 | 39.06 | 0 | OK | Ground clear controls. | 198 | 39.06 | 769.29
13617 | TIN-INTERP | Interpolated Ground | 86992.11 | -6.13 | 730.12 | 0 | 27.44 | 0 | OK | Ground clear controls. | 198 | 34.97 | 757.56
13618 | TIN-INTERP | Interpolated Ground | 86992.17 | -7.63 | 730.03 | 0 | 33.05 | 0 | OK | Ground clear controls. | 198 | 34.97 | 763.08
13619 | TIN-INTERP | Interpolated Ground | 87031.29 | 7.23 | 741.59 | 0 | 17.01 | 0 | OK | Ground clear controls. | 198 | 34.97 | 758.6
13620 | TIN-INTERP | Interpolated Ground | 87031.29 | 8.72 | 742.16 | 0 | 22 | 0 | OK | Ground clear controls. | 198 | 34.97 | 764.16
13621 | TIN-INTERP | Interpolated Ground | 87031.41 | 6.52 | 741.26 | 0 | 29.13 | 0 | OK | Ground clear controls. | 198 | 34.97 | 770.39
13622 | TIN-INTERP | Interpolated Ground | 87031.95 | -5.34 | 735.51 | 0 | 34.97 | 0 | OK | Ground clear controls. | 198 | 34.97 | 770.48
13623 | TIN-INTERP | Interpolated Ground | 87032.11 | -6.01 | 735.25 | 0 | 23.44 | 0 | OK | Ground clear controls. | 198 | 31.8 | 758.69
13624 | TIN-INTERP | Interpolated Ground | 87032.17 | -7.52 | 734.8 | 0 | 29.45 | 0 | OK | Ground clear controls. | 198 | 31.8 | 764.25
13625 | TIN-INTERP | Interpolated Ground | 87071.29 | 7.34 | 740.76 | 0 | 19.84 | 0 | OK | Ground clear controls. | 198 | 31.8 | 760.6
13626 | TIN-INTERP | Interpolated Ground | 87071.29 | 8.83 | 740.6 | 0 | 25.64 | 0 | OK | Ground clear controls. | 198 | 31.8 | 766.24
13627 | TIN-INTERP | Interpolated Ground | 87071.41 | 6.63 | 740.69 | 0 | 31.8 | 0 | OK | Ground clear controls. | 198 | 31.8 | 772.49
13628 | TIN-INTERP | Interpolated Ground | 87071.95 | -5.22 | 740.85 | 0 | 31.72 | 0 | OK | Ground clear controls. | 198 | 31.72 | 772.57
13629 | TIN-INTERP | Interpolated Ground | 87072.11 | -5.89 | 740.91 | 0 | 19.79 | 0 | OK | Ground clear controls. | 198 | 30.41 | 760.7
13630 | TIN-INTERP | Interpolated Ground | 87072.17 | -7.41 | 741.04 | 0 | 25.29 | 0 | OK | Ground clear controls. | 198 | 30.41 | 766.33
13631 | TIN-INTERP | Interpolated Ground | 87111.29 | 7.46 | 747.83 | 0 | 15.67 | 0 | OK | Ground clear controls. | 198 | 30.41 | 763.5
13632 | TIN-INTERP | Interpolated Ground | 87111.29 | 8.94 | 747.82 | 0 | 21.39 | 0 | OK | Ground clear controls. | 198 | 30.41 | 769.21
13633 | TIN-INTERP | Interpolated Ground | 87111.41 | 6.74 | 747.88 | 0 | 27.61 | 0 | OK | Ground clear controls. | 198 | 30.41 | 775.49
13634 | TIN-INTERP | Interpolated Ground | 87111.95 | -5.11 | 745.13 | 0 | 30.41 | 0 | OK | Ground clear controls. | 198 | 30.41 | 775.54
13635 | TIN-INTERP | Interpolated Ground | 87112.11 | -5.78 | 744.88 | 0 | 18.69 | 0 | OK | Ground clear controls. | 198 | 25.55 | 763.57
13636 | TIN-INTERP | Interpolated Ground | 87112.17 | -7.29 | 743.74 | 0 | 25.55 | 0 | OK | Ground clear controls. | 198 | 25.55 | 769.29
13637 | TIN-INTERP | Interpolated Ground | 87147.06 | -7.19 | 746.84 | 0 | 25.78 | 0 | OK | Ground clear controls. | 199 | 37.27 | 772.62
13638 | TIN-INTERP | Interpolated Ground | 87147.06 | -5.68 | 746.64 | 0 | 20.19 | 0 | OK | Ground clear controls. | 199 | 37.27 | 766.83
13639 | TIN-INTERP | Interpolated Ground | 87147.06 | -5.01 | 746.59 | 0 | 32.32 | 0 | OK | Ground clear controls. | 199 | 37.27 | 778.91
13640 | TIN-INTERP | Interpolated Ground | 87147.48 | 6.83 | 746.83 | 0 | 32.07 | 0 | OK | Ground clear controls. | 199 | 37.27 | 778.9
13641 | TIN-INTERP | Interpolated Ground | 87147.53 | 7.54 | 747 | 0 | 19.8 | 0 | OK | Ground clear controls. | 199 | 37.27 | 766.8
13642 | TIN-INTERP | Interpolated Ground | 87147.63 | 9.02 | 747.58 | 0 | 25.01 | 0 | OK | Ground clear controls. | 199 | 37.27 | 772.59
13643 | TIN-INTERP | Interpolated Ground | 87186.7 | -7.02 | 743.42 | 0 | 25.19 | 0 | OK | Ground clear controls. | 199 | 37.27 | 768.61
13644 | TIN-INTERP | Interpolated Ground | 87186.75 | -5.51 | 743.85 | 0 | 19.05 | 0 | OK | Ground clear controls. | 199 | 37.27 | 762.9
13645 | TIN-INTERP | Interpolated Ground | 87186.83 | -4.87 | 744.01 | 0 | 30.82 | 0 | OK | Ground clear controls. | 199 | 37.27 | 774.83
13646 | TIN-INTERP | Interpolated Ground | 87187.48 | 6.76 | 745.59 | 0 | 29.21 | 0 | OK | Ground clear controls. | 199 | 37.27 | 774.8
13647 | TIN-INTERP | Interpolated Ground | 87187.53 | 7.44 | 745.69 | 0 | 17.19 | 0 | OK | Ground clear controls. | 199 | 37.27 | 762.88
13648 | TIN-INTERP | Interpolated Ground | 87187.63 | 8.92 | 745.89 | 0 | 22.71 | 0 | OK | Ground clear controls. | 199 | 37.27 | 768.6
13649 | TIN-INTERP | Interpolated Ground | 87226.7 | -6.86 | 736.8 | 0 | 28.67 | 0 | OK | Ground clear controls. | 199 | 37.27 | 765.47
13650 | TIN-INTERP | Interpolated Ground | 87226.75 | -5.35 | 737.16 | 0 | 22.67 | 0 | OK | Ground clear controls. | 199 | 37.27 | 759.83
13651 | TIN-INTERP | Interpolated Ground | 87226.83 | -4.74 | 737.37 | 0 | 34.27 | 0 | OK | Ground clear controls. | 199 | 37.27 | 771.64
13652 | TIN-INTERP | Interpolated Ground | 87227.48 | 6.69 | 741.12 | 0 | 30.48 | 0 | OK | Ground clear controls. | 199 | 37.27 | 771.6
13653 | TIN-INTERP | Interpolated Ground | 87227.53 | 7.34 | 741.4 | 0 | 18.43 | 0 | OK | Ground clear controls. | 199 | 37.27 | 759.83
13654 | TIN-INTERP | Interpolated Ground | 87227.63 | 8.82 | 742.1 | 0 | 23.37 | 0 | OK | Ground clear controls. | 199 | 37.27 | 765.47
13655 | TIN-INTERP | Interpolated Ground | 87266.7 | -6.7 | 733.85 | 0 | 29.38 | 0 | OK | Ground clear controls. | 199 | 37.27 | 763.23
13656 | TIN-INTERP | Interpolated Ground | 87266.75 | -5.19 | 734.63 | 0 | 23.02 | 0 | OK | Ground clear controls. | 199 | 37.27 | 757.65
13657 | TIN-INTERP | Interpolated Ground | 87266.83 | -4.61 | 734.78 | 0 | 34.55 | 0 | OK | Ground clear controls. | 199 | 37.27 | 769.33
13658 | TIN-INTERP | Interpolated Ground | 87267.48 | 6.62 | 738.28 | 0 | 31.02 | 0 | OK | Ground clear controls. | 199 | 37.27 | 769.3
13659 | TIN-INTERP | Interpolated Ground | 87267.53 | 7.24 | 738.53 | 0 | 19.14 | 0 | OK | Ground clear controls. | 199 | 37.27 | 757.67
13660 | TIN-INTERP | Interpolated Ground | 87267.63 | 8.72 | 739.14 | 0 | 24.1 | 0 | OK | Ground clear controls. | 199 | 37.27 | 763.24
13661 | TIN-INTERP | Interpolated Ground | 87306.7 | -6.54 | 730.26 | 0 | 31.61 | 0 | OK | Ground clear controls. | 199 | 37.27 | 761.87
13662 | TIN-INTERP | Interpolated Ground | 87306.75 | -5.03 | 730.57 | 0 | 25.76 | 0 | OK | Ground clear controls. | 199 | 37.27 | 756.33
13663 | TIN-INTERP | Interpolated Ground | 87306.83 | -4.48 | 730.65 | 0 | 37.27 | 0 | OK | Ground clear controls. | 199 | 37.27 | 767.92
13664 | TIN-INTERP | Interpolated Ground | 87307.48 | 6.55 | 733.47 | 0 | 34.42 | 0 | OK | Ground clear controls. | 199 | 36.97 | 767.89
13665 | TIN-INTERP | Interpolated Ground | 87307.53 | 7.13 | 733.7 | 0 | 22.67 | 0 | OK | Ground clear controls. | 199 | 36.97 | 756.37
13666 | TIN-INTERP | Interpolated Ground | 87307.63 | 8.62 | 734.29 | 0 | 27.6 | 0 | OK | Ground clear controls. | 199 | 36.97 | 761.89
13667 | TIN-INTERP | Interpolated Ground | 87346.7 | -6.38 | 729.7 | 0 | 31.69 | 0 | OK | Ground clear controls. | 199 | 36.97 | 761.39
13668 | TIN-INTERP | Interpolated Ground | 87346.75 | -4.87 | 730.27 | 0 | 25.63 | 0 | OK | Ground clear controls. | 199 | 36.97 | 755.9
13669 | TIN-INTERP | Interpolated Ground | 87346.83 | -4.35 | 730.42 | 0 | 36.97 | 0 | OK | Ground clear controls. | 199 | 36.97 | 767.39
13670 | TIN-INTERP | Interpolated Ground | 87347.48 | 6.48 | 733.39 | 0 | 33.98 | 0 | OK | Ground clear controls. | 199 | 36.38 | 767.37
13671 | TIN-INTERP | Interpolated Ground | 87347.53 | 7.03 | 733.51 | 0 | 22.43 | 0 | OK | Ground clear controls. | 199 | 36.38 | 755.94
13672 | TIN-INTERP | Interpolated Ground | 87347.63 | 8.51 | 733.79 | 0 | 27.65 | 0 | OK | Ground clear controls. | 199 | 36.38 | 761.44
13673 | TIN-INTERP | Interpolated Ground | 87386.7 | -6.22 | 730.86 | 0 | 30.94 | 0 | OK | Ground clear controls. | 199 | 36.38 | 761.8
13674 | TIN-INTERP | Interpolated Ground | 87386.75 | -4.71 | 731.26 | 0 | 25.06 | 0 | OK | Ground clear controls. | 199 | 36.38 | 756.32
13675 | TIN-INTERP | Interpolated Ground | 87386.83 | -4.22 | 731.37 | 0 | 36.38 | 0 | OK | Ground clear controls. | 199 | 36.38 | 767.75
13676 | TIN-INTERP | Interpolated Ground | 87387.48 | 6.41 | 734.27 | 0 | 33.48 | 0 | OK | Ground clear controls. | 199 | 33.48 | 767.75
13677 | TIN-INTERP | Interpolated Ground | 87387.53 | 6.93 | 734.44 | 0 | 21.95 | 0 | OK | Ground clear controls. | 199 | 31.3 | 756.39
13678 | TIN-INTERP | Interpolated Ground | 87387.63 | 8.41 | 734.86 | 0 | 27.01 | 0 | OK | Ground clear controls. | 199 | 31.3 | 761.87
13679 | TIN-INTERP | Interpolated Ground | 87426.7 | -6.06 | 737.15 | 0 | 25.94 | 0 | OK | Ground clear controls. | 199 | 31.3 | 763.09
13680 | TIN-INTERP | Interpolated Ground | 87426.75 | -4.55 | 737.53 | 0 | 20.09 | 0 | OK | Ground clear controls. | 199 | 31.3 | 757.62
13681 | TIN-INTERP | Interpolated Ground | 87426.83 | -4.09 | 737.7 | 0 | 31.3 | 0 | OK | Ground clear controls. | 199 | 31.3 | 769
13682 | TIN-INTERP | Interpolated Ground | 87427.48 | 6.34 | 741.44 | 0 | 27.59 | 0 | OK | Ground clear controls. | 199 | 27.59 | 769.03
13683 | TIN-INTERP | Interpolated Ground | 87427.53 | 6.82 | 741.73 | 0 | 15.99 | 0 | OK | Ground clear controls. | 199 | 27.46 | 757.72
13684 | TIN-INTERP | Interpolated Ground | 87427.63 | 8.31 | 742.29 | 0 | 20.91 | 0 | OK | Ground clear controls. | 199 | 27.46 | 763.2
13685 | TIN-INTERP | Interpolated Ground | 87466.7 | -5.9 | 743.78 | 0 | 21.48 | 0 | OK | Ground clear controls. | 199 | 27.46 | 765.26
13686 | TIN-INTERP | Interpolated Ground | 87466.75 | -4.39 | 744.23 | 0 | 15.57 | 0 | OK | Ground clear controls. | 199 | 27.46 | 759.8
13687 | TIN-INTERP | Interpolated Ground | 87466.83 | -3.96 | 744.36 | 0 | 26.77 | 0 | OK | Ground clear controls. | 199 | 27.46 | 771.13
13688 | TIN-INTERP | Interpolated Ground | 87467.48 | 6.27 | 747.79 | 0 | 23.41 | 0 | OK | Ground clear controls. | 199 | 27.46 | 771.2
13689 | TIN-INTERP | Interpolated Ground | 87467.53 | 6.72 | 747.98 | 0 | 11.93 | 0 | OK | Ground clear controls. | 199 | 27.46 | 759.91
13690 | TIN-INTERP | Interpolated Ground | 87467.63 | 8.21 | 748.6 | 0 | 16.8 | 0 | OK | Ground clear controls. | 199 | 27.46 | 765.4
13691 | TIN-INTERP | Interpolated Ground | 87506.7 | -5.74 | 746.28 | 0 | 22.05 | 0 | OK | Ground clear controls. | 199 | 27.46 | 768.33
13692 | TIN-INTERP | Interpolated Ground | 87506.75 | -4.23 | 746.61 | 0 | 16.23 | 0 | OK | Ground clear controls. | 199 | 27.46 | 762.84
13693 | TIN-INTERP | Interpolated Ground | 87506.83 | -3.83 | 746.69 | 0 | 27.46 | 0 | OK | Ground clear controls. | 199 | 27.46 | 774.15
13694 | TIN-INTERP | Interpolated Ground | 87507.48 | 6.2 | 748.69 | 0 | 25.58 | 0 | OK | Ground clear controls. | 199 | 25.58 | 774.27
13695 | TIN-INTERP | Interpolated Ground | 87507.53 | 6.62 | 748.71 | 0 | 14.27 | 0 | OK | Ground clear controls. | 199 | 19.72 | 762.98
13696 | TIN-INTERP | Interpolated Ground | 87507.63 | 8.11 | 748.78 | 0 | 19.72 | 0 | OK | Ground clear controls. | 199 | 19.72 | 768.5
13697 | TIN-INTERP | Interpolated Ground | 87511.26 | -5.73 | 746.18 | 0 | 22.59 | 0 | OK | Ground clear controls. | 200 | 33.04 | 768.77
13698 | TIN-INTERP | Interpolated Ground | 87511.26 | -4.23 | 746.67 | 0 | 16.61 | 0 | OK | Ground clear controls. | 200 | 33.04 | 763.28
13699 | TIN-INTERP | Interpolated Ground | 87511.26 | -3.83 | 746.8 | 0 | 27.77 | 0 | OK | Ground clear controls. | 200 | 33.04 | 774.57
13700 | TIN-INTERP | Interpolated Ground | 87511.73 | 6.6 | 748.24 | 0 | 15.05 | 0 | OK | Ground clear controls. | 200 | 33.04 | 763.29
13701 | TIN-INTERP | Interpolated Ground | 87511.79 | 6.17 | 748.2 | 0 | 26.39 | 0 | OK | Ground clear controls. | 200 | 33.04 | 774.59
13702 | TIN-INTERP | Interpolated Ground | 87511.83 | 8.09 | 748.31 | 0 | 20.48 | 0 | OK | Ground clear controls. | 200 | 33.04 | 768.79
13703 | TIN-INTERP | Interpolated Ground | 87550.97 | -5.86 | 739.25 | 0 | 24.33 | 0 | OK | Ground clear controls. | 200 | 33.04 | 763.58
13704 | TIN-INTERP | Interpolated Ground | 87551.11 | -3.94 | 739.38 | 0 | 29.96 | 0 | OK | Ground clear controls. | 200 | 33.04 | 769.34
13705 | TIN-INTERP | Interpolated Ground | 87551.2 | -4.36 | 739.34 | 0 | 18.83 | 0 | OK | Ground clear controls. | 200 | 33.04 | 758.17
13706 | TIN-INTERP | Interpolated Ground | 87551.73 | 6.4 | 739.64 | 0 | 18.51 | 0 | OK | Ground clear controls. | 200 | 33.04 | 758.15
13707 | TIN-INTERP | Interpolated Ground | 87551.79 | 5.96 | 739.66 | 0 | 29.7 | 0 | OK | Ground clear controls. | 200 | 33.04 | 769.36
13708 | TIN-INTERP | Interpolated Ground | 87551.83 | 7.89 | 739.37 | 0 | 24.23 | 0 | OK | Ground clear controls. | 200 | 33.04 | 763.6
13709 | TIN-INTERP | Interpolated Ground | 87590.97 | -5.99 | 735.35 | 0 | 23.93 | 0 | OK | Ground clear controls. | 200 | 33.04 | 759.28
13710 | TIN-INTERP | Interpolated Ground | 87591.11 | -4.06 | 735.07 | 0 | 29.92 | 0 | OK | Ground clear controls. | 200 | 33.04 | 764.99
13711 | TIN-INTERP | Interpolated Ground | 87591.2 | -4.49 | 735.1 | 0 | 18.82 | 0 | OK | Ground clear controls. | 200 | 33.04 | 753.92
13712 | TIN-INTERP | Interpolated Ground | 87591.73 | 6.2 | 732.25 | 0 | 21.63 | 0 | OK | Ground clear controls. | 200 | 33.04 | 753.88
13713 | TIN-INTERP | Interpolated Ground | 87591.79 | 5.76 | 732.49 | 0 | 32.53 | 0 | OK | Ground clear controls. | 200 | 33.04 | 765.02
13714 | TIN-INTERP | Interpolated Ground | 87591.83 | 7.69 | 731.69 | 0 | 27.61 | 0 | OK | Ground clear controls. | 200 | 33.04 | 759.3
13715 | TIN-INTERP | Interpolated Ground | 87630.97 | -6.11 | 732.5 | 0 | 23.36 | 0 | OK | Ground clear controls. | 200 | 33.04 | 755.86
13716 | TIN-INTERP | Interpolated Ground | 87631.11 | -4.17 | 731.74 | 0 | 29.79 | 0 | OK | Ground clear controls. | 200 | 33.04 | 761.53
13717 | TIN-INTERP | Interpolated Ground | 87631.2 | -4.62 | 731.89 | 0 | 18.63 | 0 | OK | Ground clear controls. | 200 | 33.04 | 750.52
13718 | TIN-INTERP | Interpolated Ground | 87631.73 | 6.01 | 730.68 | 0 | 19.79 | 0 | OK | Ground clear controls. | 200 | 33.04 | 750.47
13719 | TIN-INTERP | Interpolated Ground | 87631.79 | 5.55 | 730.63 | 0 | 30.94 | 0 | OK | Ground clear controls. | 200 | 33.04 | 761.57
13720 | TIN-INTERP | Interpolated Ground | 87631.83 | 7.5 | 730.8 | 0 | 25.09 | 0 | OK | Ground clear controls. | 200 | 33.04 | 755.89
13721 | TIN-INTERP | Interpolated Ground | 87670.97 | -6.24 | 732.04 | 0 | 21.29 | 0 | OK | Ground clear controls. | 200 | 33.04 | 753.33
13722 | TIN-INTERP | Interpolated Ground | 87671.11 | -4.29 | 730.98 | 0 | 27.98 | 0 | OK | Ground clear controls. | 200 | 33.04 | 758.96
13723 | TIN-INTERP | Interpolated Ground | 87671.2 | -4.74 | 731.3 | 0 | 16.7 | 0 | OK | Ground clear controls. | 200 | 33.04 | 748
13724 | TIN-INTERP | Interpolated Ground | 87671.73 | 5.81 | 725.67 | 0 | 22.27 | 0 | OK | Ground clear controls. | 200 | 33.04 | 747.94
13725 | TIN-INTERP | Interpolated Ground | 87671.79 | 5.34 | 725.95 | 0 | 33.04 | 0 | OK | Ground clear controls. | 200 | 33.04 | 758.99
13726 | TIN-INTERP | Interpolated Ground | 87671.83 | 7.3 | 724.88 | 0 | 28.48 | 0 | OK | Ground clear controls. | 200 | 30.66 | 753.36
13727 | TIN-INTERP | Interpolated Ground | 87710.97 | -6.37 | 730.48 | 0 | 21.19 | 0 | OK | Ground clear controls. | 200 | 30.66 | 751.67
13728 | TIN-INTERP | Interpolated Ground | 87711.11 | -4.41 | 730.3 | 0 | 26.97 | 0 | OK | Ground clear controls. | 200 | 30.66 | 757.27
13729 | TIN-INTERP | Interpolated Ground | 87711.2 | -4.87 | 730.32 | 0 | 16 | 0 | OK | Ground clear controls. | 200 | 30.66 | 746.32
13730 | TIN-INTERP | Interpolated Ground | 87711.73 | 5.62 | 726.89 | 0 | 19.38 | 0 | OK | Ground clear controls. | 200 | 30.66 | 746.27
13731 | TIN-INTERP | Interpolated Ground | 87711.79 | 5.14 | 727.04 | 0 | 30.25 | 0 | OK | Ground clear controls. | 200 | 30.66 | 757.29
13732 | TIN-INTERP | Interpolated Ground | 87711.83 | 7.11 | 726.32 | 0 | 25.38 | 0 | OK | Ground clear controls. | 200 | 30.66 | 751.7
13733 | TIN-INTERP | Interpolated Ground | 87750.97 | -6.5 | 727.22 | 0 | 23.68 | 0 | OK | Ground clear controls. | 200 | 30.66 | 750.9
13734 | TIN-INTERP | Interpolated Ground | 87751.11 | -4.52 | 726.95 | 0 | 29.5 | 0 | OK | Ground clear controls. | 200 | 30.66 | 756.45
13735 | TIN-INTERP | Interpolated Ground | 87751.2 | -5 | 727.01 | 0 | 18.49 | 0 | OK | Ground clear controls. | 200 | 30.66 | 745.5
13736 | TIN-INTERP | Interpolated Ground | 87751.72 | 5.42 | 725.71 | 0 | 19.76 | 0 | OK | Ground clear controls. | 200 | 30.66 | 745.47
13737 | TIN-INTERP | Interpolated Ground | 87751.79 | 4.93 | 725.81 | 0 | 30.66 | 0 | OK | Ground clear controls. | 200 | 30.66 | 756.47
13738 | TIN-INTERP | Interpolated Ground | 87751.83 | 6.91 | 725.42 | 0 | 25.5 | 0 | OK | Ground clear controls. | 200 | 27.34 | 750.92
13739 | TIN-INTERP | Interpolated Ground | 87790.97 | -6.63 | 731.54 | 0 | 19.47 | 0 | OK | Ground clear controls. | 200 | 27.34 | 751.01
13740 | TIN-INTERP | Interpolated Ground | 87791.11 | -4.64 | 731.28 | 0 | 25.24 | 0 | OK | Ground clear controls. | 200 | 27.34 | 756.52
13741 | TIN-INTERP | Interpolated Ground | 87791.2 | -5.13 | 731.35 | 0 | 14.19 | 0 | OK | Ground clear controls. | 200 | 27.34 | 745.54
13742 | TIN-INTERP | Interpolated Ground | 87791.72 | 5.22 | 729 | 0 | 16.54 | 0 | OK | Ground clear controls. | 200 | 27.34 | 745.54
13743 | TIN-INTERP | Interpolated Ground | 87791.79 | 4.72 | 729.2 | 0 | 27.34 | 0 | OK | Ground clear controls. | 200 | 27.34 | 756.54
13744 | TIN-INTERP | Interpolated Ground | 87791.83 | 6.72 | 728.66 | 0 | 22.36 | 0 | OK | Ground clear controls. | 200 | 22.36 | 751.02
13745 | TIN-INTERP | Interpolated Ground | 87806.86 | -6.68 | 730.95 | 0 | 20.35 | 0 | OK | Ground clear controls. | 201 | 51.02 | 751.3
13746 | TIN-INTERP | Interpolated Ground | 87806.88 | -4.69 | 731.15 | 0 | 25.65 | 0 | OK | Ground clear controls. | 201 | 51.02 | 756.8
13747 | TIN-INTERP | Interpolated Ground | 87806.91 | -5.18 | 731.09 | 0 | 14.7 | 0 | OK | Ground clear controls. | 201 | 51.02 | 745.79
13748 | TIN-INTERP | Interpolated Ground | 87807 | 4.65 | 731.33 | 0 | 25.46 | 0 | OK | Ground clear controls. | 201 | 51.02 | 756.79
13749 | TIN-INTERP | Interpolated Ground | 87807.05 | 5.15 | 731.33 | 0 | 14.46 | 0 | OK | Ground clear controls. | 201 | 51.02 | 745.79
13750 | TIN-INTERP | Interpolated Ground | 87807.06 | 6.64 | 731.23 | 0 | 20.06 | 0 | OK | Ground clear controls. | 201 | 51.02 | 751.29
13751 | TIN-INTERP | Interpolated Ground | 87846.85 | -7.07 | 716.26 | 0 | 28.81 | 0 | OK | Ground clear controls. | 201 | 51.02 | 745.07
13752 | TIN-INTERP | Interpolated Ground | 87846.88 | -5.06 | 716.09 | 0 | 34.58 | 0 | OK | Ground clear controls. | 201 | 51.02 | 750.67
13753 | TIN-INTERP | Interpolated Ground | 87846.9 | -5.56 | 716.09 | 0 | 23.52 | 0 | OK | Ground clear controls. | 201 | 51.02 | 739.61
13754 | TIN-INTERP | Interpolated Ground | 87847 | 4.56 | 716.44 | 0 | 34.26 | 0 | OK | Ground clear controls. | 201 | 51.02 | 750.7
13755 | TIN-INTERP | Interpolated Ground | 87847.05 | 5.09 | 716.45 | 0 | 23.16 | 0 | OK | Ground clear controls. | 201 | 51.02 | 739.61
13756 | TIN-INTERP | Interpolated Ground | 87847.06 | 6.57 | 716.54 | 0 | 28.57 | 0 | OK | Ground clear controls. | 201 | 51.02 | 745.11
13757 | TIN-INTERP | Interpolated Ground | 87886.85 | -7.45 | 706.21 | 0 | 33.53 | 0 | OK | Ground clear controls. | 201 | 51.02 | 739.74
13758 | TIN-INTERP | Interpolated Ground | 87886.87 | -5.44 | 706.3 | 0 | 39.13 | 0 | OK | Ground clear controls. | 201 | 51.02 | 745.43
13759 | TIN-INTERP | Interpolated Ground | 87886.9 | -5.93 | 706.28 | 0 | 28.03 | 0 | OK | Ground clear controls. | 201 | 51.02 | 734.31
13760 | TIN-INTERP | Interpolated Ground | 87887 | 4.48 | 706.4 | 0 | 39.1 | 0 | OK | Ground clear controls. | 201 | 51.02 | 745.5
13761 | TIN-INTERP | Interpolated Ground | 87887.05 | 5.03 | 706.42 | 0 | 27.89 | 0 | OK | Ground clear controls. | 201 | 51.02 | 734.31
13762 | TIN-INTERP | Interpolated Ground | 87887.06 | 6.49 | 706.57 | 0 | 33.24 | 0 | OK | Ground clear controls. | 201 | 51.02 | 739.81
13763 | TIN-INTERP | Interpolated Ground | 87926.85 | -7.83 | 702.52 | 0 | 32.78 | 0 | OK | Ground clear controls. | 201 | 51.02 | 735.3
13764 | TIN-INTERP | Interpolated Ground | 87926.87 | -5.82 | 702.58 | 0 | 38.5 | 0 | OK | Ground clear controls. | 201 | 51.02 | 741.08
13765 | TIN-INTERP | Interpolated Ground | 87926.9 | -6.31 | 702.5 | 0 | 27.36 | 0 | OK | Ground clear controls. | 201 | 51.02 | 729.86
13766 | TIN-INTERP | Interpolated Ground | 87927 | 4.4 | 703.92 | 0 | 37.26 | 0 | OK | Ground clear controls. | 201 | 51.02 | 741.18
13767 | TIN-INTERP | Interpolated Ground | 87927.05 | 4.96 | 704.01 | 0 | 25.87 | 0 | OK | Ground clear controls. | 201 | 51.02 | 729.88
13768 | TIN-INTERP | Interpolated Ground | 87927.06 | 6.41 | 704.21 | 0 | 31.18 | 0 | OK | Ground clear controls. | 201 | 51.02 | 735.39
13769 | TIN-INTERP | Interpolated Ground | 87966.85 | -8.22 | 692.98 | 0 | 38.76 | 0 | OK | Ground clear controls. | 201 | 51.02 | 731.74
13770 | TIN-INTERP | Interpolated Ground | 87966.87 | -6.2 | 693.12 | 0 | 44.5 | 0 | OK | Ground clear controls. | 201 | 51.02 | 737.62
13771 | TIN-INTERP | Interpolated Ground | 87966.9 | -6.68 | 693.13 | 0 | 33.14 | 0 | OK | Ground clear controls. | 201 | 51.02 | 726.27
13772 | TIN-INTERP | Interpolated Ground | 87967 | 4.32 | 694.06 | 0 | 43.69 | 0 | OK | Ground clear controls. | 201 | 51.02 | 737.75
13773 | TIN-INTERP | Interpolated Ground | 87967.05 | 4.9 | 694.15 | 0 | 32.16 | 0 | OK | Ground clear controls. | 201 | 51.02 | 726.31
13774 | TIN-INTERP | Interpolated Ground | 87967.06 | 6.33 | 694.59 | 0 | 37.26 | 0 | OK | Ground clear controls. | 201 | 51.02 | 731.85
13775 | TIN-INTERP | Interpolated Ground | 88006.85 | -8.6 | 683.83 | 0 | 45.24 | 0 | OK | Ground clear controls. | 201 | 51.02 | 729.07
13776 | TIN-INTERP | Interpolated Ground | 88006.87 | -6.58 | 684.08 | 0 | 50.97 | 0 | OK | Ground clear controls. | 201 | 51.02 | 735.05
13777 | TIN-INTERP | Interpolated Ground | 88006.9 | -7.06 | 683.91 | 0 | 39.62 | 0 | OK | Ground clear controls. | 201 | 51.02 | 723.53
13778 | TIN-INTERP | Interpolated Ground | 88007 | 4.23 | 685.48 | 0 | 49.71 | 0 | OK | Ground clear controls. | 201 | 51.02 | 735.19
13779 | TIN-INTERP | Interpolated Ground | 88007.05 | 4.84 | 685.39 | 0 | 38.22 | 0 | OK | Ground clear controls. | 201 | 51.02 | 723.61
13780 | TIN-INTERP | Interpolated Ground | 88007.06 | 6.26 | 685.32 | 0 | 43.87 | 0 | OK | Ground clear controls. | 201 | 51.02 | 729.19
13781 | TIN-INTERP | Interpolated Ground | 88046.85 | -8.98 | 686.07 | 0 | 41.22 | 0 | OK | Ground clear controls. | 201 | 51.02 | 727.29
13782 | TIN-INTERP | Interpolated Ground | 88046.87 | -6.96 | 684.85 | 0 | 48.52 | 0 | OK | Ground clear controls. | 201 | 51.02 | 733.37
13783 | TIN-INTERP | Interpolated Ground | 88046.9 | -7.43 | 685.15 | 0 | 36.52 | 0 | OK | Ground clear controls. | 201 | 51.02 | 721.67
13784 | TIN-INTERP | Interpolated Ground | 88047 | 4.15 | 682.5 | 0 | 51.02 | 0 | OK | Ground clear controls. | 201 | 51.02 | 733.52
13785 | TIN-INTERP | Interpolated Ground | 88047.05 | 4.78 | 682.44 | 0 | 39.33 | 0 | OK | Ground clear controls. | 201 | 45.15 | 721.77
13786 | TIN-INTERP | Interpolated Ground | 88047.06 | 6.18 | 682.26 | 0 | 45.15 | 0 | OK | Ground clear controls. | 201 | 45.15 | 727.41
13787 | TIN-INTERP | Interpolated Ground | 88086.84 | -9.37 | 695.96 | 0 | 30.42 | 0 | OK | Ground clear controls. | 201 | 42.47 | 726.38
13788 | TIN-INTERP | Interpolated Ground | 88086.86 | -7.34 | 695.34 | 0 | 37.23 | 0 | OK | Ground clear controls. | 201 | 42.47 | 732.57
13789 | TIN-INTERP | Interpolated Ground | 88086.89 | -7.81 | 695.45 | 0 | 25.2 | 0 | OK | Ground clear controls. | 201 | 42.47 | 720.65
13790 | TIN-INTERP | Interpolated Ground | 88087 | 4.07 | 690.25 | 0 | 42.47 | 0 | OK | Ground clear controls. | 201 | 42.47 | 732.72
13791 | TIN-INTERP | Interpolated Ground | 88087.05 | 4.72 | 690.18 | 0 | 30.62 | 0 | OK | Ground clear controls. | 201 | 36.79 | 720.8
13792 | TIN-INTERP | Interpolated Ground | 88087.06 | 6.1 | 689.72 | 0 | 36.79 | 0 | OK | Ground clear controls. | 201 | 36.79 | 726.51
13793 | TIN-INTERP | Interpolated Ground | 88124.9 | -9.73 | 687.65 | 0 | 38.69 | 0 | OK | Ground clear controls. | 202 | 44.64 | 726.34
13794 | TIN-INTERP | Interpolated Ground | 88125.07 | -8.17 | 687.94 | 0 | 32.54 | 0 | OK | Ground clear controls. | 202 | 44.64 | 720.48
13795 | TIN-INTERP | Interpolated Ground | 88125.24 | -7.7 | 688 | 0 | 44.64 | 0 | OK | Ground clear controls. | 202 | 44.64 | 732.64
13796 | TIN-INTERP | Interpolated Ground | 88126.69 | 4 | 688.41 | 0 | 44.41 | 0 | OK | Ground clear controls. | 201 | 44.41 | 732.82
13797 | TIN-INTERP | Interpolated Ground | 88126.69 | 4.03 | 688.38 | 0 | 44.43 | 0 | OK | Ground clear controls. | 202 | 44.43 | 732.81
13798 | TIN-INTERP | Interpolated Ground | 88126.69 | 4.67 | 688.33 | 0 | 32.36 | 0 | OK | Ground clear controls. | 201 | 32.36 | 720.69
13799 | TIN-INTERP | Interpolated Ground | 88126.69 | 4.71 | 688.29 | 0 | 32.41 | 0 | OK | Ground clear controls. | 202 | 32.41 | 720.7
13800 | TIN-INTERP | Interpolated Ground | 88126.69 | 6.04 | 688.15 | 0 | 38.32 | 0 | OK | Ground clear controls. | 201 | 38.32 | 726.47
13801 | TIN-INTERP | Interpolated Ground | 88126.69 | 6.1 | 688.03 | 0 | 38.45 | 0 | OK | Ground clear controls. | 202 | 51.88 | 726.48
13802 | TIN-INTERP | Interpolated Ground | 88165.57 | 6.05 | 675.41 | 0 | 38.34 | 0 | OK | Ground clear controls. | 202 | 51.88 | 713.75
13803 | TIN-INTERP | Interpolated Ground | 88165.77 | 4.66 | 675.21 | 0 | 32.81 | 0 | OK | Ground clear controls. | 202 | 51.88 | 708.02
13804 | TIN-INTERP | Interpolated Ground | 88165.93 | 4.02 | 675.01 | 0 | 44.96 | 0 | OK | Ground clear controls. | 202 | 51.88 | 719.97
13805 | TIN-INTERP | Interpolated Ground | 88167.89 | -7.93 | 673 | 0 | 34.77 | 0 | OK | Ground clear controls. | 202 | 51.88 | 707.77
13806 | TIN-INTERP | Interpolated Ground | 88167.9 | -7.43 | 672.91 | 0 | 46.83 | 0 | OK | Ground clear controls. | 202 | 51.88 | 719.74
13807 | TIN-INTERP | Interpolated Ground | 88168.26 | -9.45 | 673 | 0 | 40.55 | 0 | OK | Ground clear controls. | 202 | 51.88 | 713.55
13808 | TIN-INTERP | Interpolated Ground | 88205.57 | 6.1 | 663.41 | 0 | 38.53 | 0 | OK | Ground clear controls. | 202 | 51.88 | 701.94
13809 | TIN-INTERP | Interpolated Ground | 88205.77 | 4.7 | 664.06 | 0 | 32.2 | 0 | OK | Ground clear controls. | 202 | 51.88 | 696.26
13810 | TIN-INTERP | Interpolated Ground | 88205.93 | 4.08 | 664.34 | 0 | 43.73 | 0 | OK | Ground clear controls. | 202 | 51.88 | 708.07
13811 | TIN-INTERP | Interpolated Ground | 88207.89 | -7.62 | 666.69 | 0 | 29.3 | 0 | OK | Ground clear controls. | 202 | 51.88 | 695.99
13812 | TIN-INTERP | Interpolated Ground | 88207.9 | -7.12 | 666.57 | 0 | 41.22 | 0 | OK | Ground clear controls. | 202 | 51.88 | 707.79
13813 | TIN-INTERP | Interpolated Ground | 88208.26 | -9.14 | 666.76 | 0 | 34.92 | 0 | OK | Ground clear controls. | 202 | 51.88 | 701.68
13814 | TIN-INTERP | Interpolated Ground | 88245.57 | 6.16 | 668.42 | 0 | 22.64 | 0 | OK | Ground clear controls. | 202 | 51.88 | 691.06
13815 | TIN-INTERP | Interpolated Ground | 88245.77 | 4.74 | 668.56 | 0 | 16.86 | 0 | OK | Ground clear controls. | 202 | 51.88 | 685.42
13816 | TIN-INTERP | Interpolated Ground | 88245.93 | 4.14 | 668.58 | 0 | 28.51 | 0 | OK | Ground clear controls. | 202 | 51.88 | 697.09
13817 | TIN-INTERP | Interpolated Ground | 88247.89 | -7.31 | 670.13 | 0 | 15 | 0 | OK | Ground clear controls. | 202 | 51.88 | 685.13
13818 | TIN-INTERP | Interpolated Ground | 88247.9 | -6.81 | 670.03 | 0 | 26.75 | 0 | OK | Ground clear controls. | 202 | 51.88 | 696.78
13819 | TIN-INTERP | Interpolated Ground | 88248.26 | -8.83 | 670.43 | 0 | 20.33 | 0 | OK | Ground clear controls. | 202 | 51.88 | 690.76
13820 | TIN-INTERP | Interpolated Ground | 88285.57 | 6.21 | 652.26 | 0 | 28.84 | 0 | OK | Ground clear controls. | 202 | 51.88 | 681.1
13821 | TIN-INTERP | Interpolated Ground | 88285.77 | 4.78 | 652.1 | 0 | 23.4 | 0 | OK | Ground clear controls. | 202 | 51.88 | 675.5
13822 | TIN-INTERP | Interpolated Ground | 88285.93 | 4.19 | 652.08 | 0 | 34.96 | 0 | OK | Ground clear controls. | 202 | 51.88 | 687.04
13823 | TIN-INTERP | Interpolated Ground | 88287.89 | -6.99 | 650.55 | 0 | 24.65 | 0 | OK | Ground clear controls. | 202 | 51.88 | 675.2
13824 | TIN-INTERP | Interpolated Ground | 88287.9 | -6.5 | 650.6 | 0 | 36.12 | 0 | OK | Ground clear controls. | 202 | 51.88 | 686.72
13825 | TIN-INTERP | Interpolated Ground | 88288.25 | -8.51 | 650.09 | 0 | 30.68 | 0 | OK | Ground clear controls. | 202 | 51.88 | 680.77
13826 | TIN-INTERP | Interpolated Ground | 88325.57 | 6.27 | 630.38 | 0 | 41.68 | 0 | OK | Ground clear controls. | 202 | 51.88 | 672.06
13827 | TIN-INTERP | Interpolated Ground | 88325.77 | 4.83 | 629.79 | 0 | 36.7 | 0 | OK | Ground clear controls. | 202 | 51.88 | 666.49
13828 | TIN-INTERP | Interpolated Ground | 88325.93 | 4.25 | 629.51 | 0 | 48.4 | 0 | OK | Ground clear controls. | 202 | 51.88 | 677.91
13829 | TIN-INTERP | Interpolated Ground | 88327.89 | -6.68 | 632.21 | 0 | 33.97 | 0 | OK | Ground clear controls. | 202 | 51.88 | 666.18
13830 | TIN-INTERP | Interpolated Ground | 88327.9 | -6.19 | 631.91 | 0 | 45.66 | 0 | OK | Ground clear controls. | 202 | 51.88 | 677.57
13831 | TIN-INTERP | Interpolated Ground | 88328.25 | -8.2 | 633.13 | 0 | 38.58 | 0 | OK | Ground clear controls. | 202 | 51.88 | 671.71
13832 | TIN-INTERP | Interpolated Ground | 88365.57 | 6.32 | 634.66 | 0 | 29.27 | 0 | OK | Ground clear controls. | 202 | 51.88 | 663.93
13833 | TIN-INTERP | Interpolated Ground | 88365.77 | 4.87 | 635.07 | 0 | 23.31 | 0 | OK | Ground clear controls. | 202 | 51.88 | 658.38
13834 | TIN-INTERP | Interpolated Ground | 88365.93 | 4.31 | 635.2 | 0 | 34.48 | 0 | OK | Ground clear controls. | 202 | 51.88 | 669.68
13835 | TIN-INTERP | Interpolated Ground | 88367.89 | -6.37 | 632.72 | 0 | 25.35 | 0 | OK | Ground clear controls. | 202 | 51.88 | 658.07
13836 | TIN-INTERP | Interpolated Ground | 88367.9 | -5.88 | 633 | 0 | 36.35 | 0 | OK | Ground clear controls. | 202 | 51.88 | 669.35
13837 | TIN-INTERP | Interpolated Ground | 88368.25 | -7.88 | 631.79 | 0 | 31.78 | 0 | OK | Ground clear controls. | 202 | 51.88 | 663.57
13838 | TIN-INTERP | Interpolated Ground | 88405.57 | 6.38 | 620.76 | 0 | 35.95 | 0 | OK | Ground clear controls. | 202 | 51.88 | 656.71
13839 | TIN-INTERP | Interpolated Ground | 88405.77 | 4.91 | 620.72 | 0 | 30.46 | 0 | OK | Ground clear controls. | 202 | 51.88 | 651.18
13840 | TIN-INTERP | Interpolated Ground | 88405.93 | 4.37 | 620.67 | 0 | 41.7 | 0 | OK | Ground clear controls. | 202 | 51.88 | 662.37
13841 | TIN-INTERP | Interpolated Ground | 88407.89 | -6.06 | 618.31 | 0 | 32.57 | 0 | OK | Ground clear controls. | 202 | 51.88 | 650.88
13842 | TIN-INTERP | Interpolated Ground | 88407.9 | -5.56 | 618.54 | 0 | 43.52 | 0 | OK | Ground clear controls. | 202 | 51.88 | 662.06
13843 | TIN-INTERP | Interpolated Ground | 88408.25 | -7.57 | 617.57 | 0 | 38.78 | 0 | OK | Ground clear controls. | 202 | 51.88 | 656.35
13844 | TIN-INTERP | Interpolated Ground | 88445.57 | 6.43 | 603.91 | 0 | 46.48 | 0 | OK | Ground clear controls. | 202 | 51.88 | 650.39
13845 | TIN-INTERP | Interpolated Ground | 88445.77 | 4.95 | 604.02 | 0 | 40.85 | 0 | OK | Ground clear controls. | 202 | 51.88 | 644.87
13846 | TIN-INTERP | Interpolated Ground | 88445.93 | 4.43 | 604.09 | 0 | 51.88 | 0 | OK | Ground clear controls. | 202 | 51.88 | 655.97
13847 | TIN-INTERP | Interpolated Ground | 88447.89 | -5.75 | 606.31 | 0 | 38.29 | 0 | OK | Ground clear controls. | 202 | 49.47 | 644.6
13848 | TIN-INTERP | Interpolated Ground | 88447.9 | -5.25 | 606.22 | 0 | 49.47 | 0 | OK | Ground clear controls. | 202 | 49.47 | 655.69
13849 | TIN-INTERP | Interpolated Ground | 88448.25 | -7.25 | 607 | 0 | 43.04 | 0 | OK | Ground clear controls. | 202 | 43.04 | 650.04
13850 | TIN-INTERP | Interpolated Ground | 88485.57 | 6.49 | 613.39 | 0 | 31.58 | 0 | OK | Ground clear controls. | 202 | 37.01 | 644.97
13851 | TIN-INTERP | Interpolated Ground | 88485.77 | 5 | 613.46 | 0 | 26.01 | 0 | OK | Ground clear controls. | 202 | 37.01 | 639.47
13852 | TIN-INTERP | Interpolated Ground | 88485.93 | 4.49 | 613.45 | 0 | 37.01 | 0 | OK | Ground clear controls. | 202 | 37.01 | 650.46
13853 | TIN-INTERP | Interpolated Ground | 88487.88 | -5.44 | 617.33 | 0 | 21.88 | 0 | OK | Ground clear controls. | 202 | 32.83 | 639.21
13854 | TIN-INTERP | Interpolated Ground | 88487.89 | -4.94 | 617.4 | 0 | 32.83 | 0 | OK | Ground clear controls. | 202 | 32.83 | 650.23
13855 | TIN-INTERP | Interpolated Ground | 88488.25 | -6.94 | 617.83 | 0 | 26.83 | 0 | OK | Ground clear controls. | 202 | 26.83 | 644.66
13856 | TIN-INTERP | Interpolated Ground | 88502.01 | 6.51 | 621.7 | 0 | 21.3 | 0 | OK | Ground clear controls. | 203 | 46.53 | 643
13857 | TIN-INTERP | Interpolated Ground | 88502.05 | -6.83 | 621.77 | 0 | 21.24 | 0 | OK | Ground clear controls. | 203 | 46.53 | 643.01
13858 | TIN-INTERP | Interpolated Ground | 88502.07 | 4.51 | 621.66 | 0 | 26.84 | 0 | OK | Ground clear controls. | 203 | 46.53 | 648.5
13859 | TIN-INTERP | Interpolated Ground | 88502.07 | -4.83 | 621.9 | 0 | 26.61 | 0 | OK | Ground clear controls. | 203 | 46.53 | 648.51
13860 | TIN-INTERP | Interpolated Ground | 88502.14 | -5.33 | 621.88 | 0 | 15.63 | 0 | OK | Ground clear controls. | 203 | 46.53 | 637.51
13861 | TIN-INTERP | Interpolated Ground | 88502.16 | 5.01 | 621.68 | 0 | 15.82 | 0 | OK | Ground clear controls. | 203 | 46.53 | 637.5
13862 | TIN-INTERP | Interpolated Ground | 88542.01 | 6.52 | 607.78 | 0 | 25.37 | 0 | OK | Ground clear controls. | 203 | 46.53 | 633.15
13863 | TIN-INTERP | Interpolated Ground | 88542.05 | -6.87 | 605.78 | 0 | 27.33 | 0 | OK | Ground clear controls. | 203 | 46.53 | 633.11
13864 | TIN-INTERP | Interpolated Ground | 88542.07 | 4.54 | 607.51 | 0 | 31.17 | 0 | OK | Ground clear controls. | 203 | 46.53 | 638.68
13865 | TIN-INTERP | Interpolated Ground | 88542.07 | -4.88 | 606.27 | 0 | 32.38 | 0 | OK | Ground clear controls. | 203 | 46.53 | 638.65
13866 | TIN-INTERP | Interpolated Ground | 88542.14 | -5.37 | 606.1 | 0 | 21.57 | 0 | OK | Ground clear controls. | 203 | 46.53 | 627.67
13867 | TIN-INTERP | Interpolated Ground | 88542.16 | 5.03 | 607.54 | 0 | 20.16 | 0 | OK | Ground clear controls. | 203 | 46.53 | 627.7
13868 | TIN-INTERP | Interpolated Ground | 88582.01 | 6.54 | 591.7 | 0 | 32.52 | 0 | OK | Ground clear controls. | 203 | 46.53 | 624.22
13869 | TIN-INTERP | Interpolated Ground | 88582.05 | -6.9 | 592.56 | 0 | 31.59 | 0 | OK | Ground clear controls. | 203 | 46.53 | 624.15
13870 | TIN-INTERP | Interpolated Ground | 88582.07 | 4.56 | 591.67 | 0 | 38.12 | 0 | OK | Ground clear controls. | 203 | 46.53 | 629.79
13871 | TIN-INTERP | Interpolated Ground | 88582.07 | -4.93 | 592.82 | 0 | 36.88 | 0 | OK | Ground clear controls. | 203 | 46.53 | 629.7
13872 | TIN-INTERP | Interpolated Ground | 88582.14 | -5.4 | 592.82 | 0 | 25.93 | 0 | OK | Ground clear controls. | 203 | 46.53 | 618.75
13873 | TIN-INTERP | Interpolated Ground | 88582.16 | 5.04 | 591.59 | 0 | 27.22 | 0 | OK | Ground clear controls. | 203 | 46.53 | 618.81
13874 | TIN-INTERP | Interpolated Ground | 88622.01 | 6.56 | 579.58 | 0 | 36.63 | 0 | OK | Ground clear controls. | 203 | 46.53 | 616.21
13875 | TIN-INTERP | Interpolated Ground | 88622.05 | -6.94 | 580.4 | 0 | 35.71 | 0 | OK | Ground clear controls. | 203 | 46.53 | 616.11
13876 | TIN-INTERP | Interpolated Ground | 88622.07 | 4.59 | 579.97 | 0 | 41.84 | 0 | OK | Ground clear controls. | 203 | 46.53 | 621.81
13877 | TIN-INTERP | Interpolated Ground | 88622.07 | -4.97 | 580.8 | 0 | 40.9 | 0 | OK | Ground clear controls. | 203 | 46.53 | 621.7
13878 | TIN-INTERP | Interpolated Ground | 88622.14 | -5.44 | 580.72 | 0 | 30.03 | 0 | OK | Ground clear controls. | 203 | 46.53 | 610.75
13879 | TIN-INTERP | Interpolated Ground | 88622.16 | 5.06 | 579.83 | 0 | 30.99 | 0 | OK | Ground clear controls. | 203 | 46.53 | 610.82
13880 | TIN-INTERP | Interpolated Ground | 88662.01 | 6.57 | 573.01 | 0 | 36.1 | 0 | OK | Ground clear controls. | 203 | 46.53 | 609.11
13881 | TIN-INTERP | Interpolated Ground | 88662.05 | -6.97 | 572.43 | 0 | 36.57 | 0 | OK | Ground clear controls. | 203 | 46.53 | 609
13882 | TIN-INTERP | Interpolated Ground | 88662.07 | 4.61 | 573.32 | 0 | 41.42 | 0 | OK | Ground clear controls. | 203 | 46.53 | 614.74
13883 | TIN-INTERP | Interpolated Ground | 88662.07 | -5.02 | 573 | 0 | 41.62 | 0 | OK | Ground clear controls. | 203 | 46.53 | 614.62
13884 | TIN-INTERP | Interpolated Ground | 88662.14 | -5.48 | 572.85 | 0 | 30.8 | 0 | OK | Ground clear controls. | 203 | 46.53 | 603.65
13885 | TIN-INTERP | Interpolated Ground | 88662.16 | 5.07 | 573.23 | 0 | 30.5 | 0 | OK | Ground clear controls. | 203 | 46.53 | 603.73
13886 | TIN-INTERP | Interpolated Ground | 88702.01 | 6.59 | 564.51 | 0 | 38.41 | 0 | OK | Ground clear controls. | 203 | 46.53 | 602.92
13887 | TIN-INTERP | Interpolated Ground | 88702.05 | -7.01 | 563.98 | 0 | 38.83 | 0 | OK | Ground clear controls. | 203 | 46.53 | 602.81
13888 | TIN-INTERP | Interpolated Ground | 88702.07 | 4.64 | 563.98 | 0 | 44.6 | 0 | OK | Ground clear controls. | 203 | 46.53 | 608.58
13889 | TIN-INTERP | Interpolated Ground | 88702.07 | -5.07 | 563.96 | 0 | 44.51 | 0 | OK | Ground clear controls. | 203 | 46.53 | 608.47
13890 | TIN-INTERP | Interpolated Ground | 88702.14 | -5.51 | 563.97 | 0 | 33.49 | 0 | OK | Ground clear controls. | 203 | 46.53 | 597.46
13891 | TIN-INTERP | Interpolated Ground | 88702.16 | 5.09 | 564.07 | 0 | 33.48 | 0 | OK | Ground clear controls. | 203 | 46.53 | 597.55
13892 | TIN-INTERP | Interpolated Ground | 88742.01 | 6.6 | 561.75 | 0 | 35.89 | 0 | OK | Ground clear controls. | 203 | 46.53 | 597.64
13893 | TIN-INTERP | Interpolated Ground | 88742.05 | -7.05 | 564.58 | 0 | 32.96 | 0 | OK | Ground clear controls. | 203 | 46.53 | 597.54
13894 | TIN-INTERP | Interpolated Ground | 88742.07 | 4.66 | 562.35 | 0 | 40.99 | 0 | OK | Ground clear controls. | 203 | 46.53 | 603.34
13895 | TIN-INTERP | Interpolated Ground | 88742.07 | -5.11 | 564.67 | 0 | 38.55 | 0 | OK | Ground clear controls. | 203 | 46.53 | 603.22
13896 | TIN-INTERP | Interpolated Ground | 88742.14 | -5.55 | 564.7 | 0 | 27.47 | 0 | OK | Ground clear controls. | 203 | 46.53 | 592.17
13897 | TIN-INTERP | Interpolated Ground | 88742.16 | 5.1 | 562.15 | 0 | 30.1 | 0 | OK | Ground clear controls. | 203 | 46.53 | 592.25
13898 | TIN-INTERP | Interpolated Ground | 88782.01 | 6.62 | 552.58 | 0 | 40.68 | 0 | OK | Ground clear controls. | 203 | 46.53 | 593.26
13899 | TIN-INTERP | Interpolated Ground | 88782.05 | -7.08 | 552.37 | 0 | 40.81 | 0 | OK | Ground clear controls. | 203 | 46.53 | 593.18
13900 | TIN-INTERP | Interpolated Ground | 88782.07 | 4.69 | 552.64 | 0 | 46.35 | 0 | OK | Ground clear controls. | 203 | 46.53 | 598.99
13901 | TIN-INTERP | Interpolated Ground | 88782.07 | -5.16 | 552.38 | 0 | 46.53 | 0 | OK | Ground clear controls. | 203 | 46.53 | 598.91
13902 | TIN-INTERP | Interpolated Ground | 88782.14 | -5.59 | 552.31 | 0 | 35.48 | 0 | OK | Ground clear controls. | 203 | 39.52 | 587.79
13903 | TIN-INTERP | Interpolated Ground | 88782.16 | 5.12 | 552.56 | 0 | 35.29 | 0 | OK | Ground clear controls. | 203 | 39.52 | 587.85
13904 | TIN-INTERP | Interpolated Ground | 88822.01 | 6.63 | 557.26 | 0 | 32.53 | 0 | OK | Ground clear controls. | 203 | 39.52 | 589.79
13905 | TIN-INTERP | Interpolated Ground | 88822.05 | -7.12 | 555.69 | 0 | 34.05 | 0 | OK | Ground clear controls. | 203 | 39.52 | 589.74
13906 | TIN-INTERP | Interpolated Ground | 88822.07 | 4.71 | 557.02 | 0 | 38.53 | 0 | OK | Ground clear controls. | 203 | 39.52 | 595.55
13907 | TIN-INTERP | Interpolated Ground | 88822.07 | -5.21 | 555.97 | 0 | 39.52 | 0 | OK | Ground clear controls. | 203 | 39.52 | 595.49
13908 | TIN-INTERP | Interpolated Ground | 88822.14 | -5.63 | 555.95 | 0 | 28.35 | 0 | OK | Ground clear controls. | 203 | 36.27 | 584.3
13909 | TIN-INTERP | Interpolated Ground | 88822.16 | 5.13 | 557.09 | 0 | 27.24 | 0 | OK | Ground clear controls. | 203 | 36.27 | 584.33
13910 | TIN-INTERP | Interpolated Ground | 88862.01 | 6.65 | 559.28 | 0 | 27.94 | 0 | OK | Ground clear controls. | 203 | 36.27 | 587.22
13911 | TIN-INTERP | Interpolated Ground | 88862.05 | -7.16 | 555.89 | 0 | 31.31 | 0 | OK | Ground clear controls. | 203 | 36.27 | 587.2
13912 | TIN-INTERP | Interpolated Ground | 88862.07 | 4.74 | 559.34 | 0 | 33.67 | 0 | OK | Ground clear controls. | 203 | 36.27 | 593.01
13913 | TIN-INTERP | Interpolated Ground | 88862.07 | -5.25 | 556.72 | 0 | 36.27 | 0 | OK | Ground clear controls. | 203 | 36.27 | 592.99
13914 | TIN-INTERP | Interpolated Ground | 88862.14 | -5.66 | 556.56 | 0 | 25.14 | 0 | OK | Ground clear controls. | 203 | 25.14 | 581.7
13915 | TIN-INTERP | Interpolated Ground | 88862.16 | 5.14 | 559.34 | 0 | 22.37 | 0 | OK | Ground clear controls. | 203 | 22.37 | 581.71
13916 | TIN-INTERP | Interpolated Ground | 88863.81 | -7.16 | 556.09 | 0 | 31.02 | 0 | OK | Ground clear controls. | 204 | 57.62 | 587.11
13917 | TIN-INTERP | Interpolated Ground | 88863.85 | -5.66 | 556.82 | 0 | 24.79 | 0 | OK | Ground clear controls. | 204 | 57.62 | 581.61
13918 | TIN-INTERP | Interpolated Ground | 88864 | -5.26 | 556.97 | 0 | 35.93 | 0 | OK | Ground clear controls. | 204 | 57.62 | 592.9
13919 | TIN-INTERP | Interpolated Ground | 88864.19 | 5.15 | 559.14 | 0 | 22.46 | 0 | OK | Ground clear controls. | 204 | 57.62 | 581.6
13920 | TIN-INTERP | Interpolated Ground | 88864.21 | 6.65 | 559.15 | 0 | 27.95 | 0 | OK | Ground clear controls. | 204 | 57.62 | 587.1
13921 | TIN-INTERP | Interpolated Ground | 88864.29 | 4.74 | 559.14 | 0 | 33.76 | 0 | OK | Ground clear controls. | 204 | 57.62 | 592.9
13922 | TIN-INTERP | Interpolated Ground | 88904 | 6.79 | 542.53 | 0 | 33.06 | 0 | OK | Ground clear controls. | 204 | 57.62 | 575.59
13923 | TIN-INTERP | Interpolated Ground | 88904.02 | 5.29 | 542.78 | 0 | 27.41 | 0 | OK | Ground clear controls. | 204 | 57.62 | 570.19
13924 | TIN-INTERP | Interpolated Ground | 88904.04 | -5.66 | 546.08 | 0 | 23.96 | 0 | OK | Ground clear controls. | 204 | 57.62 | 570.04
13925 | TIN-INTERP | Interpolated Ground | 88904.04 | -7.16 | 546.49 | 0 | 28.91 | 0 | OK | Ground clear controls. | 204 | 57.62 | 575.4
13926 | TIN-INTERP | Interpolated Ground | 88904.13 | 4.87 | 542.83 | 0 | 38.68 | 0 | OK | Ground clear controls. | 204 | 57.62 | 581.51
13927 | TIN-INTERP | Interpolated Ground | 88904.17 | -5.23 | 545.93 | 0 | 35.4 | 0 | OK | Ground clear controls. | 204 | 57.62 | 581.33
13928 | TIN-INTERP | Interpolated Ground | 88944 | 6.94 | 532.04 | 0 | 32.97 | 0 | OK | Ground clear controls. | 204 | 57.62 | 565.01
13929 | TIN-INTERP | Interpolated Ground | 88944.02 | 5.44 | 532.21 | 0 | 27.5 | 0 | OK | Ground clear controls. | 204 | 57.62 | 559.71
13930 | TIN-INTERP | Interpolated Ground | 88944.04 | -5.65 | 532.94 | 0 | 26.46 | 0 | OK | Ground clear controls. | 204 | 57.62 | 559.4
13931 | TIN-INTERP | Interpolated Ground | 88944.04 | -7.14 | 533.15 | 0 | 31.51 | 0 | OK | Ground clear controls. | 204 | 57.62 | 564.66
13932 | TIN-INTERP | Interpolated Ground | 88944.13 | 5 | 532.2 | 0 | 38.84 | 0 | OK | Ground clear controls. | 204 | 57.62 | 571.04
13933 | TIN-INTERP | Interpolated Ground | 88944.17 | -5.2 | 532.82 | 0 | 37.89 | 0 | OK | Ground clear controls. | 204 | 57.62 | 570.71
13934 | TIN-INTERP | Interpolated Ground | 88984 | 7.09 | 511.69 | 0 | 43.71 | 0 | OK | Ground clear controls. | 204 | 57.62 | 555.4
13935 | TIN-INTERP | Interpolated Ground | 88984.02 | 5.59 | 510.96 | 0 | 39.21 | 0 | OK | Ground clear controls. | 204 | 57.62 | 550.17
13936 | TIN-INTERP | Interpolated Ground | 88984.04 | -5.63 | 510.25 | 0 | 39.48 | 0 | OK | Ground clear controls. | 204 | 57.62 | 549.73
13937 | TIN-INTERP | Interpolated Ground | 88984.04 | -7.13 | 510.32 | 0 | 44.58 | 0 | OK | Ground clear controls. | 204 | 57.62 | 554.9
13938 | TIN-INTERP | Interpolated Ground | 88984.13 | 5.14 | 510.84 | 0 | 50.7 | 0 | OK | Ground clear controls. | 204 | 57.62 | 561.54
13939 | TIN-INTERP | Interpolated Ground | 88984.17 | -5.17 | 510.15 | 0 | 50.91 | 0 | OK | Ground clear controls. | 204 | 57.62 | 561.06
13940 | TIN-INTERP | Interpolated Ground | 89024 | 7.24 | 507.81 | 0 | 38.91 | 0 | OK | Ground clear controls. | 204 | 57.62 | 546.72
13941 | TIN-INTERP | Interpolated Ground | 89024.02 | 5.74 | 507.04 | 0 | 34.52 | 0 | OK | Ground clear controls. | 204 | 57.62 | 541.56
13942 | TIN-INTERP | Interpolated Ground | 89024.04 | -5.62 | 500.3 | 0 | 40.69 | 0 | OK | Ground clear controls. | 204 | 57.62 | 540.99
13943 | TIN-INTERP | Interpolated Ground | 89024.04 | -7.11 | 499.52 | 0 | 46.57 | 0 | OK | Ground clear controls. | 204 | 57.62 | 546.09
13944 | TIN-INTERP | Interpolated Ground | 89024.13 | 5.27 | 506.78 | 0 | 46.17 | 0 | OK | Ground clear controls. | 204 | 57.62 | 552.95
13945 | TIN-INTERP | Interpolated Ground | 89024.17 | -5.13 | 500.54 | 0 | 51.81 | 0 | OK | Ground clear controls. | 204 | 57.62 | 552.35
13946 | TIN-INTERP | Interpolated Ground | 89064 | 7.39 | 496.24 | 0 | 42.75 | 0 | OK | Ground clear controls. | 204 | 57.62 | 538.99
13947 | TIN-INTERP | Interpolated Ground | 89064.02 | 5.89 | 495.25 | 0 | 38.63 | 0 | OK | Ground clear controls. | 204 | 57.62 | 533.88
13948 | TIN-INTERP | Interpolated Ground | 89064.04 | -5.6 | 491.46 | 0 | 41.75 | 0 | OK | Ground clear controls. | 204 | 57.62 | 533.21
13949 | TIN-INTERP | Interpolated Ground | 89064.04 | -7.1 | 490.95 | 0 | 47.3 | 0 | OK | Ground clear controls. | 204 | 57.62 | 538.25
13950 | TIN-INTERP | Interpolated Ground | 89064.13 | 5.4 | 494.96 | 0 | 50.35 | 0 | OK | Ground clear controls. | 204 | 57.62 | 545.31
13951 | TIN-INTERP | Interpolated Ground | 89064.17 | -5.1 | 491.58 | 0 | 53.01 | 0 | OK | Ground clear controls. | 204 | 57.62 | 544.59
13952 | TIN-INTERP | Interpolated Ground | 89104 | 7.54 | 483.17 | 0 | 49.03 | 0 | OK | Ground clear controls. | 204 | 57.62 | 532.2
13953 | TIN-INTERP | Interpolated Ground | 89104.02 | 6.04 | 482.67 | 0 | 44.45 | 0 | OK | Ground clear controls. | 204 | 57.62 | 527.12
13954 | TIN-INTERP | Interpolated Ground | 89104.04 | -5.59 | 480.19 | 0 | 46.17 | 0 | OK | Ground clear controls. | 204 | 57.62 | 526.36
13955 | TIN-INTERP | Interpolated Ground | 89104.04 | -7.08 | 480.2 | 0 | 51.16 | 0 | OK | Ground clear controls. | 204 | 57.62 | 531.36
13956 | TIN-INTERP | Interpolated Ground | 89104.13 | 5.54 | 482.51 | 0 | 56.07 | 0 | OK | Ground clear controls. | 204 | 57.62 | 538.58
13957 | TIN-INTERP | Interpolated Ground | 89104.17 | -5.07 | 480.15 | 0 | 57.62 | 0 | OK | Ground clear controls. | 204 | 57.62 | 537.77
13958 | TIN-INTERP | Interpolated Ground | 89143.99 | 7.69 | 480.74 | 0 | 45.6 | 0 | OK | Ground clear controls. | 204 | 51.59 | 526.34
13959 | TIN-INTERP | Interpolated Ground | 89144.02 | 6.19 | 481.1 | 0 | 40.17 | 0 | OK | Ground clear controls. | 204 | 51.59 | 521.27
13960 | TIN-INTERP | Interpolated Ground | 89144.04 | -5.57 | 482.2 | 0 | 38.22 | 0 | OK | Ground clear controls. | 204 | 51.59 | 520.42
13961 | TIN-INTERP | Interpolated Ground | 89144.04 | -7.07 | 482.34 | 0 | 43.06 | 0 | OK | Ground clear controls. | 204 | 51.59 | 525.4
13962 | TIN-INTERP | Interpolated Ground | 89144.13 | 5.67 | 481.19 | 0 | 51.59 | 0 | OK | Ground clear controls. | 204 | 51.59 | 532.78
13963 | TIN-INTERP | Interpolated Ground | 89144.17 | -5.04 | 482.13 | 0 | 49.75 | 0 | OK | Ground clear controls. | 204 | 49.75 | 531.88
13964 | TIN-INTERP | Interpolated Ground | 89183.99 | 7.84 | 483.01 | 0 | 38.41 | 0 | OK | Ground clear controls. | 204 | 44.96 | 521.42
13965 | TIN-INTERP | Interpolated Ground | 89184.02 | 6.34 | 482.96 | 0 | 33.39 | 0 | OK | Ground clear controls. | 204 | 44.96 | 516.35
13966 | TIN-INTERP | Interpolated Ground | 89184.04 | -5.55 | 482.39 | 0 | 33.06 | 0 | OK | Ground clear controls. | 204 | 44.96 | 515.45
13967 | TIN-INTERP | Interpolated Ground | 89184.04 | -7.05 | 482.26 | 0 | 38.16 | 0 | OK | Ground clear controls. | 204 | 44.96 | 520.42
13968 | TIN-INTERP | Interpolated Ground | 89184.13 | 5.8 | 482.93 | 0 | 44.96 | 0 | OK | Ground clear controls. | 204 | 44.96 | 527.89
13969 | TIN-INTERP | Interpolated Ground | 89184.17 | -5.01 | 482.37 | 0 | 44.57 | 0 | OK | Ground clear controls. | 204 | 44.57 | 526.94
13970 | TIN-INTERP | Interpolated Ground | 89223.99 | 7.99 | 481 | 0 | 36.42 | 0 | OK | Ground clear controls. | 204 | 43.81 | 517.42
13971 | TIN-INTERP | Interpolated Ground | 89224.02 | 6.48 | 481.03 | 0 | 31.31 | 0 | OK | Ground clear controls. | 204 | 43.81 | 512.34
13972 | TIN-INTERP | Interpolated Ground | 89224.04 | -5.54 | 481.3 | 0 | 30.09 | 0 | OK | Ground clear controls. | 204 | 43.81 | 511.39
13973 | TIN-INTERP | Interpolated Ground | 89224.04 | -7.04 | 481.43 | 0 | 34.94 | 0 | OK | Ground clear controls. | 204 | 43.81 | 516.37
13974 | TIN-INTERP | Interpolated Ground | 89224.13 | 5.94 | 481.06 | 0 | 42.86 | 0 | OK | Ground clear controls. | 204 | 43.81 | 523.92
13975 | TIN-INTERP | Interpolated Ground | 89224.17 | -4.97 | 481.26 | 0 | 41.67 | 0 | OK | Ground clear controls. | 204 | 43.81 | 522.93
13976 | TIN-INTERP | Interpolated Ground | 89263.99 | 8.13 | 482.28 | 0 | 32.06 | 0 | OK | Ground clear controls. | 204 | 43.81 | 514.34
13977 | TIN-INTERP | Interpolated Ground | 89264.02 | 6.63 | 482.28 | 0 | 26.95 | 0 | OK | Ground clear controls. | 204 | 43.81 | 509.23
13978 | TIN-INTERP | Interpolated Ground | 89264.04 | -5.52 | 482.95 | 0 | 25.3 | 0 | OK | Ground clear controls. | 204 | 43.81 | 508.25
13979 | TIN-INTERP | Interpolated Ground | 89264.04 | -7.02 | 483.06 | 0 | 30.21 | 0 | OK | Ground clear controls. | 204 | 43.81 | 513.27
13980 | TIN-INTERP | Interpolated Ground | 89264.13 | 6.07 | 482.35 | 0 | 38.52 | 0 | OK | Ground clear controls. | 204 | 43.81 | 520.87
13981 | TIN-INTERP | Interpolated Ground | 89264.17 | -4.94 | 482.91 | 0 | 36.93 | 0 | OK | Ground clear controls. | 204 | 43.81 | 519.84
13982 | TIN-INTERP | Interpolated Ground | 89303.99 | 8.28 | 483.7 | 0 | 28.49 | 0 | OK | Ground clear controls. | 204 | 43.81 | 512.19
13983 | TIN-INTERP | Interpolated Ground | 89304.02 | 6.78 | 483.69 | 0 | 23.36 | 0 | OK | Ground clear controls. | 204 | 43.81 | 507.05
13984 | TIN-INTERP | Interpolated Ground | 89304.04 | -5.51 | 484.04 | 0 | 22.01 | 0 | OK | Ground clear controls. | 204 | 43.81 | 506.05
13985 | TIN-INTERP | Interpolated Ground | 89304.04 | -7 | 484.1 | 0 | 27.01 | 0 | OK | Ground clear controls. | 204 | 43.81 | 511.11
13986 | TIN-INTERP | Interpolated Ground | 89304.13 | 6.2 | 483.65 | 0 | 35.08 | 0 | OK | Ground clear controls. | 204 | 43.81 | 518.73
13987 | TIN-INTERP | Interpolated Ground | 89304.17 | -4.91 | 483.96 | 0 | 33.73 | 0 | OK | Ground clear controls. | 204 | 43.81 | 517.69
13988 | TIN-INTERP | Interpolated Ground | 89343.99 | 8.43 | 484.98 | 0 | 25.98 | 0 | OK | Ground clear controls. | 204 | 43.81 | 510.96
13989 | TIN-INTERP | Interpolated Ground | 89344.02 | 6.93 | 484.98 | 0 | 20.77 | 0 | OK | Ground clear controls. | 204 | 43.81 | 505.75
13990 | TIN-INTERP | Interpolated Ground | 89344.04 | -5.49 | 484.9 | 0 | 19.85 | 0 | OK | Ground clear controls. | 204 | 43.81 | 504.75
13991 | TIN-INTERP | Interpolated Ground | 89344.04 | -6.99 | 484.97 | 0 | 24.91 | 0 | OK | Ground clear controls. | 204 | 43.81 | 509.88
13992 | TIN-INTERP | Interpolated Ground | 89344.13 | 6.34 | 484.99 | 0 | 32.5 | 0 | OK | Ground clear controls. | 204 | 43.81 | 517.49
13993 | TIN-INTERP | Interpolated Ground | 89344.17 | -4.88 | 484.91 | 0 | 31.54 | 0 | OK | Ground clear controls. | 204 | 43.81 | 516.45
13994 | TIN-INTERP | Interpolated Ground | 89383.99 | 8.58 | 485.77 | 0 | 24.89 | 0 | OK | Ground clear controls. | 204 | 43.81 | 510.66
13995 | TIN-INTERP | Interpolated Ground | 89384.02 | 7.08 | 485.69 | 0 | 19.69 | 0 | OK | Ground clear controls. | 204 | 43.81 | 505.38
13996 | TIN-INTERP | Interpolated Ground | 89384.04 | -5.48 | 485.69 | 0 | 18.7 | 0 | OK | Ground clear controls. | 204 | 43.81 | 504.39
13997 | TIN-INTERP | Interpolated Ground | 89384.04 | -6.97 | 485.73 | 0 | 23.86 | 0 | OK | Ground clear controls. | 204 | 43.81 | 509.59
13998 | TIN-INTERP | Interpolated Ground | 89384.13 | 6.47 | 485.69 | 0 | 31.48 | 0 | OK | Ground clear controls. | 204 | 43.81 | 517.17
13999 | TIN-INTERP | Interpolated Ground | 89384.17 | -4.84 | 485.72 | 0 | 30.43 | 0 | OK | Ground clear controls. | 204 | 43.81 | 516.15
14000 | TIN-INTERP | Interpolated Ground | 89423.99 | 8.73 | 486.73 | 0 | 24.56 | 0 | OK | Ground clear controls. | 204 | 43.81 | 511.29
14001 | TIN-INTERP | Interpolated Ground | 89424.02 | 7.23 | 486.93 | 0 | 18.99 | 0 | OK | Ground clear controls. | 204 | 43.81 | 505.92
14002 | TIN-INTERP | Interpolated Ground | 89424.04 | -5.46 | 487.49 | 0 | 17.46 | 0 | OK | Ground clear controls. | 204 | 43.81 | 504.95
14003 | TIN-INTERP | Interpolated Ground | 89424.04 | -6.96 | 487.49 | 0 | 22.75 | 0 | OK | Ground clear controls. | 204 | 43.81 | 510.24
14004 | TIN-INTERP | Interpolated Ground | 89424.13 | 6.61 | 486.95 | 0 | 30.82 | 0 | OK | Ground clear controls. | 204 | 43.81 | 517.77
14005 | TIN-INTERP | Interpolated Ground | 89424.17 | -4.81 | 487.46 | 0 | 29.32 | 0 | OK | Ground clear controls. | 204 | 43.81 | 516.78
14006 | TIN-INTERP | Interpolated Ground | 89463.99 | 8.88 | 485.41 | 0 | 27.41 | 0 | OK | Ground clear controls. | 204 | 43.81 | 512.82
14007 | TIN-INTERP | Interpolated Ground | 89464.02 | 7.38 | 485.34 | 0 | 22 | 0 | OK | Ground clear controls. | 204 | 43.81 | 507.34
14008 | TIN-INTERP | Interpolated Ground | 89464.04 | -5.45 | 484.33 | 0 | 22.09 | 0 | OK | Ground clear controls. | 204 | 43.81 | 506.42
14009 | TIN-INTERP | Interpolated Ground | 89464.04 | -6.94 | 484.21 | 0 | 27.63 | 0 | OK | Ground clear controls. | 204 | 43.81 | 511.84
14010 | TIN-INTERP | Interpolated Ground | 89464.13 | 6.74 | 485.27 | 0 | 33.99 | 0 | OK | Ground clear controls. | 204 | 43.81 | 519.26
14011 | TIN-INTERP | Interpolated Ground | 89464.17 | -4.78 | 484.42 | 0 | 33.9 | 0 | OK | Ground clear controls. | 204 | 43.81 | 518.32
14012 | TIN-INTERP | Interpolated Ground | 89503.99 | 9.03 | 483.68 | 0 | 31.61 | 0 | OK | Ground clear controls. | 204 | 43.81 | 515.29
14013 | TIN-INTERP | Interpolated Ground | 89504.02 | 7.53 | 483.6 | 0 | 26.1 | 0 | OK | Ground clear controls. | 204 | 43.81 | 509.7
14014 | TIN-INTERP | Interpolated Ground | 89504.04 | -5.43 | 482.93 | 0 | 25.89 | 0 | OK | Ground clear controls. | 204 | 43.81 | 508.82
14015 | TIN-INTERP | Interpolated Ground | 89504.04 | -6.93 | 483 | 0 | 31.37 | 0 | OK | Ground clear controls. | 204 | 43.81 | 514.37
14016 | TIN-INTERP | Interpolated Ground | 89504.13 | 6.87 | 483.49 | 0 | 38.2 | 0 | OK | Ground clear controls. | 204 | 43.81 | 521.69
14017 | TIN-INTERP | Interpolated Ground | 89504.17 | -4.75 | 482.93 | 0 | 37.88 | 0 | OK | Ground clear controls. | 204 | 43.81 | 520.81
14018 | TIN-INTERP | Interpolated Ground | 89543.99 | 9.18 | 481.65 | 0 | 37.04 | 0 | OK | Ground clear controls. | 204 | 43.81 | 518.69
14019 | TIN-INTERP | Interpolated Ground | 89544.02 | 7.68 | 481.48 | 0 | 31.47 | 0 | OK | Ground clear controls. | 204 | 43.81 | 512.95
14020 | TIN-INTERP | Interpolated Ground | 89544.04 | -5.42 | 480.36 | 0 | 31.79 | 0 | OK | Ground clear controls. | 204 | 43.81 | 512.15
14021 | TIN-INTERP | Interpolated Ground | 89544.04 | -6.91 | 480.31 | 0 | 37.54 | 0 | OK | Ground clear controls. | 204 | 43.81 | 517.85
14022 | TIN-INTERP | Interpolated Ground | 89544.13 | 7.01 | 481.45 | 0 | 43.56 | 0 | OK | Ground clear controls. | 204 | 43.81 | 525.01
14023 | TIN-INTERP | Interpolated Ground | 89544.17 | -4.71 | 480.4 | 0 | 43.81 | 0 | OK | Ground clear controls. | 204 | 43.81 | 524.21
14024 | TIN-INTERP | Interpolated Ground | 89558.83 | 9.23 | 481.1 | 0 | 39.07 | 0 | OK | Ground clear controls. | 205 | 45.39 | 520.17
14025 | TIN-INTERP | Interpolated Ground | 89558.87 | 7.74 | 481.19 | 0 | 33.2 | 0 | OK | Ground clear controls. | 205 | 45.39 | 514.39
14026 | TIN-INTERP | Interpolated Ground | 89559.06 | 7.06 | 481.23 | 0 | 45.24 | 0 | OK | Ground clear controls. | 205 | 45.39 | 526.47
14027 | TIN-INTERP | Interpolated Ground | 89559.97 | -6.93 | 480.71 | 0 | 38.83 | 0 | OK | Ground clear controls. | 205 | 45.39 | 519.54
14028 | TIN-INTERP | Interpolated Ground | 89559.97 | -5.42 | 480.89 | 0 | 32.87 | 0 | OK | Ground clear controls. | 205 | 45.39 | 513.76
14029 | TIN-INTERP | Interpolated Ground | 89559.97 | -4.72 | 480.94 | 0 | 44.91 | 0 | OK | Ground clear controls. | 205 | 45.39 | 525.85
14030 | TIN-INTERP | Interpolated Ground | 89599.17 | -7.11 | 478.17 | 0 | 31 | 0 | OK | Ground clear controls. | 205 | 45.39 | 509.17
14031 | TIN-INTERP | Interpolated Ground | 89599.23 | -5.6 | 478.21 | 0 | 25.22 | 0 | OK | Ground clear controls. | 205 | 45.39 | 503.43
14032 | TIN-INTERP | Interpolated Ground | 89599.42 | -4.91 | 478.22 | 0 | 37.41 | 0 | OK | Ground clear controls. | 205 | 45.39 | 515.63
14033 | TIN-INTERP | Interpolated Ground | 89600.39 | 7.56 | 477.4 | 0 | 26.7 | 0 | OK | Ground clear controls. | 205 | 45.39 | 504.1
14034 | TIN-INTERP | Interpolated Ground | 89600.45 | 6.85 | 477.41 | 0 | 38.87 | 0 | OK | Ground clear controls. | 205 | 45.39 | 516.28
14035 | TIN-INTERP | Interpolated Ground | 89600.65 | 9.04 | 477.09 | 0 | 32.81 | 0 | OK | Ground clear controls. | 205 | 45.39 | 509.9
14036 | TIN-INTERP | Interpolated Ground | 89639.17 | -7.34 | 468.73 | 0 | 31.07 | 0 | OK | Ground clear controls. | 205 | 45.39 | 499.8
14037 | TIN-INTERP | Interpolated Ground | 89639.23 | -5.82 | 468.79 | 0 | 25.29 | 0 | OK | Ground clear controls. | 205 | 45.39 | 494.08
14038 | TIN-INTERP | Interpolated Ground | 89639.42 | -5.13 | 468.82 | 0 | 37.55 | 0 | OK | Ground clear controls. | 205 | 45.39 | 506.37
14039 | TIN-INTERP | Interpolated Ground | 89640.39 | 7.32 | 469.58 | 0 | 25.21 | 0 | OK | Ground clear controls. | 205 | 45.39 | 494.79
14040 | TIN-INTERP | Interpolated Ground | 89640.45 | 6.6 | 469.52 | 0 | 37.52 | 0 | OK | Ground clear controls. | 205 | 45.39 | 507.04
14041 | TIN-INTERP | Interpolated Ground | 89640.65 | 8.8 | 469.56 | 0 | 31.04 | 0 | OK | Ground clear controls. | 205 | 45.39 | 500.6
14042 | TIN-INTERP | Interpolated Ground | 89679.17 | -7.56 | 462.47 | 0 | 28.93 | 0 | OK | Ground clear controls. | 205 | 45.39 | 491.4
14043 | TIN-INTERP | Interpolated Ground | 89679.23 | -6.05 | 462.65 | 0 | 23.06 | 0 | OK | Ground clear controls. | 205 | 45.39 | 485.71
14044 | TIN-INTERP | Interpolated Ground | 89679.42 | -5.35 | 462.74 | 0 | 35.35 | 0 | OK | Ground clear controls. | 205 | 45.39 | 498.09
14045 | TIN-INTERP | Interpolated Ground | 89680.39 | 7.08 | 464.33 | 0 | 22.11 | 0 | OK | Ground clear controls. | 205 | 45.39 | 486.44
14046 | TIN-INTERP | Interpolated Ground | 89680.45 | 6.34 | 464.24 | 0 | 34.51 | 0 | OK | Ground clear controls. | 205 | 45.39 | 498.75
14047 | TIN-INTERP | Interpolated Ground | 89680.65 | 8.56 | 464.49 | 0 | 27.77 | 0 | OK | Ground clear controls. | 205 | 45.39 | 492.26
14048 | TIN-INTERP | Interpolated Ground | 89719.17 | -7.79 | 456.4 | 0 | 27.61 | 0 | OK | Ground clear controls. | 205 | 45.39 | 484.01
14049 | TIN-INTERP | Interpolated Ground | 89719.23 | -6.28 | 456.8 | 0 | 21.53 | 0 | OK | Ground clear controls. | 205 | 45.39 | 478.33
14050 | TIN-INTERP | Interpolated Ground | 89719.42 | -5.57 | 456.96 | 0 | 33.82 | 0 | OK | Ground clear controls. | 205 | 45.39 | 490.78
14051 | TIN-INTERP | Interpolated Ground | 89720.39 | 6.84 | 458.84 | 0 | 20.23 | 0 | OK | Ground clear controls. | 205 | 45.39 | 479.07
14052 | TIN-INTERP | Interpolated Ground | 89720.45 | 6.09 | 458.72 | 0 | 32.7 | 0 | OK | Ground clear controls. | 205 | 45.39 | 491.42
14053 | TIN-INTERP | Interpolated Ground | 89720.65 | 8.32 | 459.11 | 0 | 25.79 | 0 | OK | Ground clear controls. | 205 | 45.39 | 484.9
14054 | TIN-INTERP | Interpolated Ground | 89759.17 | -8.01 | 452.95 | 0 | 24.64 | 0 | OK | Ground clear controls. | 205 | 45.39 | 477.59
14055 | TIN-INTERP | Interpolated Ground | 89759.23 | -6.5 | 452.89 | 0 | 19.02 | 0 | OK | Ground clear controls. | 205 | 45.39 | 471.91
14056 | TIN-INTERP | Interpolated Ground | 89759.42 | -5.79 | 452.85 | 0 | 31.57 | 0 | OK | Ground clear controls. | 205 | 45.39 | 484.42
14057 | TIN-INTERP | Interpolated Ground | 89760.39 | 6.6 | 454.16 | 0 | 18.49 | 0 | OK | Ground clear controls. | 205 | 45.39 | 472.65
14058 | TIN-INTERP | Interpolated Ground | 89760.45 | 5.84 | 453.98 | 0 | 31.05 | 0 | OK | Ground clear controls. | 205 | 45.39 | 485.03
14059 | TIN-INTERP | Interpolated Ground | 89760.65 | 8.09 | 454.52 | 0 | 23.97 | 0 | OK | Ground clear controls. | 205 | 45.39 | 478.49
14060 | TIN-INTERP | Interpolated Ground | 89799.16 | -8.24 | 447.34 | 0 | 24.82 | 0 | OK | Ground clear controls. | 205 | 45.39 | 472.16
14061 | TIN-INTERP | Interpolated Ground | 89799.23 | -6.73 | 447.51 | 0 | 18.98 | 0 | OK | Ground clear controls. | 205 | 45.39 | 466.49
14062 | TIN-INTERP | Interpolated Ground | 89799.42 | -6.01 | 447.54 | 0 | 31.48 | 0 | OK | Ground clear controls. | 205 | 45.39 | 479.02
14063 | TIN-INTERP | Interpolated Ground | 89800.39 | 6.36 | 448.57 | 0 | 18.64 | 0 | OK | Ground clear controls. | 205 | 45.39 | 467.21
14064 | TIN-INTERP | Interpolated Ground | 89800.45 | 5.59 | 448.45 | 0 | 31.14 | 0 | OK | Ground clear controls. | 205 | 45.39 | 479.59
14065 | TIN-INTERP | Interpolated Ground | 89800.65 | 7.85 | 448.77 | 0 | 24.28 | 0 | OK | Ground clear controls. | 205 | 45.39 | 473.05
14066 | TIN-INTERP | Interpolated Ground | 89839.16 | -8.46 | 440.98 | 0 | 26.71 | 0 | OK | Ground clear controls. | 205 | 45.39 | 467.69
14067 | TIN-INTERP | Interpolated Ground | 89839.23 | -6.96 | 440.83 | 0 | 21.18 | 0 | OK | Ground clear controls. | 205 | 45.39 | 462.01
14068 | TIN-INTERP | Interpolated Ground | 89839.42 | -6.23 | 440.74 | 0 | 33.83 | 0 | OK | Ground clear controls. | 205 | 45.39 | 474.57
14069 | TIN-INTERP | Interpolated Ground | 89840.39 | 6.12 | 441.38 | 0 | 21.34 | 0 | OK | Ground clear controls. | 205 | 45.39 | 462.72
14070 | TIN-INTERP | Interpolated Ground | 89840.45 | 5.34 | 441.29 | 0 | 33.8 | 0 | OK | Ground clear controls. | 205 | 45.39 | 475.09
14071 | TIN-INTERP | Interpolated Ground | 89840.65 | 7.61 | 441.46 | 0 | 27.08 | 0 | OK | Ground clear controls. | 205 | 45.39 | 468.54
14072 | TIN-INTERP | Interpolated Ground | 89879.16 | -8.69 | 433.7 | 0 | 30.5 | 0 | OK | Ground clear controls. | 205 | 45.39 | 464.2
14073 | TIN-INTERP | Interpolated Ground | 89879.22 | -7.18 | 433.93 | 0 | 24.58 | 0 | OK | Ground clear controls. | 205 | 45.39 | 458.51
14074 | TIN-INTERP | Interpolated Ground | 89879.42 | -6.45 | 434.12 | 0 | 36.96 | 0 | OK | Ground clear controls. | 205 | 45.39 | 471.08
14075 | TIN-INTERP | Interpolated Ground | 89880.39 | 5.88 | 435.23 | 0 | 23.95 | 0 | OK | Ground clear controls. | 205 | 45.39 | 459.18
14076 | TIN-INTERP | Interpolated Ground | 89880.45 | 5.09 | 435.28 | 0 | 36.27 | 0 | OK | Ground clear controls. | 205 | 45.39 | 471.55
14077 | TIN-INTERP | Interpolated Ground | 89880.65 | 7.37 | 435.18 | 0 | 29.82 | 0 | OK | Ground clear controls. | 205 | 45.39 | 465
14078 | TIN-INTERP | Interpolated Ground | 89919.16 | -8.92 | 427.49 | 0 | 34.19 | 0 | OK | Ground clear controls. | 205 | 45.39 | 461.68
14079 | TIN-INTERP | Interpolated Ground | 89919.22 | -7.41 | 426.91 | 0 | 29.06 | 0 | OK | Ground clear controls. | 205 | 45.39 | 455.97
14080 | TIN-INTERP | Interpolated Ground | 89919.42 | -6.67 | 426.56 | 0 | 41.97 | 0 | OK | Ground clear controls. | 205 | 45.39 | 468.53
14081 | TIN-INTERP | Interpolated Ground | 89920.39 | 5.64 | 431.58 | 0 | 25.01 | 0 | OK | Ground clear controls. | 205 | 45.39 | 456.59
14082 | TIN-INTERP | Interpolated Ground | 89920.45 | 4.84 | 430.65 | 0 | 38.27 | 0 | OK | Ground clear controls. | 205 | 45.39 | 468.92
14083 | TIN-INTERP | Interpolated Ground | 89920.65 | 7.13 | 432.4 | 0 | 29.99 | 0 | OK | Ground clear controls. | 205 | 45.39 | 462.39
14084 | TIN-INTERP | Interpolated Ground | 89959.16 | -9.14 | 423.35 | 0 | 36.78 | 0 | OK | Ground clear controls. | 205 | 45.39 | 460.13
14085 | TIN-INTERP | Interpolated Ground | 89959.22 | -7.64 | 423.95 | 0 | 30.44 | 0 | OK | Ground clear controls. | 205 | 45.39 | 454.39
14086 | TIN-INTERP | Interpolated Ground | 89959.42 | -6.89 | 424.14 | 0 | 42.79 | 0 | OK | Ground clear controls. | 205 | 45.39 | 466.93
14087 | TIN-INTERP | Interpolated Ground | 89960.39 | 5.4 | 428.85 | 0 | 26.11 | 0 | OK | Ground clear controls. | 205 | 45.39 | 454.96
14088 | TIN-INTERP | Interpolated Ground | 89960.45 | 4.59 | 428.69 | 0 | 38.55 | 0 | OK | Ground clear controls. | 205 | 45.39 | 467.24
14089 | TIN-INTERP | Interpolated Ground | 89960.65 | 6.89 | 429.65 | 0 | 31.1 | 0 | OK | Ground clear controls. | 205 | 45.39 | 460.75
14090 | TIN-INTERP | Interpolated Ground | 89999.16 | -9.37 | 420.09 | 0 | 39.46 | 0 | OK | Ground clear controls. | 205 | 45.39 | 459.55
14091 | TIN-INTERP | Interpolated Ground | 89999.22 | -7.86 | 420.92 | 0 | 32.86 | 0 | OK | Ground clear controls. | 205 | 45.39 | 453.78
14092 | TIN-INTERP | Interpolated Ground | 89999.42 | -7.12 | 421.24 | 0 | 45.04 | 0 | OK | Ground clear controls. | 205 | 45.39 | 466.28
14093 | TIN-INTERP | Interpolated Ground | 90000.39 | 5.16 | 425.93 | 0 | 28.35 | 0 | OK | Ground clear controls. | 205 | 45.39 | 454.28
14094 | TIN-INTERP | Interpolated Ground | 90000.44 | 4.34 | 425.83 | 0 | 40.65 | 0 | OK | Ground clear controls. | 205 | 45.39 | 466.48
14095 | TIN-INTERP | Interpolated Ground | 90000.64 | 6.66 | 426.09 | 0 | 33.95 | 0 | OK | Ground clear controls. | 205 | 45.39 | 460.04
14096 | TIN-INTERP | Interpolated Ground | 90039.16 | -9.59 | 420.05 | 0 | 39.89 | 0 | OK | Ground clear controls. | 205 | 45.39 | 459.94
14097 | TIN-INTERP | Interpolated Ground | 90039.22 | -8.09 | 420.57 | 0 | 33.56 | 0 | OK | Ground clear controls. | 205 | 45.39 | 454.13
14098 | TIN-INTERP | Interpolated Ground | 90039.42 | -7.34 | 421.18 | 0 | 45.39 | 0 | OK | Ground clear controls. | 205 | 45.39 | 466.57
14099 | TIN-INTERP | Interpolated Ground | 90040.38 | 4.92 | 424.06 | 0 | 30.48 | 0 | OK | Ground clear controls. | 205 | 42.56 | 454.54
14100 | TIN-INTERP | Interpolated Ground | 90040.44 | 4.09 | 424.11 | 0 | 42.56 | 0 | OK | Ground clear controls. | 205 | 42.56 | 466.67
14101 | TIN-INTERP | Interpolated Ground | 90040.64 | 6.42 | 423.97 | 0 | 36.32 | 0 | OK | Ground clear controls. | 205 | 36.32 | 460.29
14102 | TIN-INTERP | Interpolated Ground | 90075.43 | -9.8 | 421.58 | 0 | 39.54 | 0 | OK | Ground clear controls. | 206 | 48.79 | 461.12
14103 | TIN-INTERP | Interpolated Ground | 90075.68 | -8.3 | 421.66 | 0 | 33.61 | 0 | OK | Ground clear controls. | 206 | 48.79 | 455.27
14104 | TIN-INTERP | Interpolated Ground | 90075.71 | -7.54 | 421.71 | 0 | 45.95 | 0 | OK | Ground clear controls. | 206 | 48.79 | 467.66
14105 | TIN-INTERP | Interpolated Ground | 90077.06 | 3.88 | 421.7 | 0 | 45.96 | 0 | OK | Ground clear controls. | 206 | 48.79 | 467.66
14106 | TIN-INTERP | Interpolated Ground | 90077.06 | 4.74 | 421.71 | 0 | 33.94 | 0 | OK | Ground clear controls. | 206 | 48.79 | 455.65
14107 | TIN-INTERP | Interpolated Ground | 90077.06 | 6.24 | 421.83 | 0 | 39.52 | 0 | OK | Ground clear controls. | 206 | 48.79 | 461.35
14108 | TIN-INTERP | Interpolated Ground | 90116.08 | 6.37 | 419.25 | 0 | 34.54 | 0 | OK | Ground clear controls. | 206 | 48.79 | 453.79
14109 | TIN-INTERP | Interpolated Ground | 90116.36 | 4.04 | 419.38 | 0 | 40.78 | 0 | OK | Ground clear controls. | 206 | 48.79 | 460.16
14110 | TIN-INTERP | Interpolated Ground | 90116.39 | 4.9 | 419.33 | 0 | 28.85 | 0 | OK | Ground clear controls. | 206 | 48.79 | 448.18
14111 | TIN-INTERP | Interpolated Ground | 90117.83 | -7.42 | 419.65 | 0 | 40.36 | 0 | OK | Ground clear controls. | 206 | 48.79 | 460.01
14112 | TIN-INTERP | Interpolated Ground | 90118.01 | -8.16 | 419.7 | 0 | 27.95 | 0 | OK | Ground clear controls. | 206 | 48.79 | 447.65
14113 | TIN-INTERP | Interpolated Ground | 90118.18 | -9.67 | 419.82 | 0 | 33.6 | 0 | OK | Ground clear controls. | 206 | 48.79 | 453.42
14114 | TIN-INTERP | Interpolated Ground | 90156.08 | 6.58 | 418.1 | 0 | 29.1 | 0 | OK | Ground clear controls. | 206 | 48.79 | 447.2
14115 | TIN-INTERP | Interpolated Ground | 90156.36 | 4.26 | 418.09 | 0 | 35.53 | 0 | OK | Ground clear controls. | 206 | 48.79 | 453.62
14116 | TIN-INTERP | Interpolated Ground | 90156.39 | 5.11 | 418.12 | 0 | 23.57 | 0 | OK | Ground clear controls. | 206 | 48.79 | 441.69
14117 | TIN-INTERP | Interpolated Ground | 90157.83 | -7.23 | 418 | 0 | 35.36 | 0 | OK | Ground clear controls. | 206 | 48.79 | 453.36
14118 | TIN-INTERP | Interpolated Ground | 90158.01 | -7.96 | 417.97 | 0 | 23.05 | 0 | OK | Ground clear controls. | 206 | 48.79 | 441.02
14119 | TIN-INTERP | Interpolated Ground | 90158.18 | -9.47 | 417.89 | 0 | 28.84 | 0 | OK | Ground clear controls. | 206 | 48.79 | 446.73
14120 | TIN-INTERP | Interpolated Ground | 90196.08 | 6.79 | 416.46 | 0 | 25.16 | 0 | OK | Ground clear controls. | 206 | 48.79 | 441.62
14121 | TIN-INTERP | Interpolated Ground | 90196.36 | 4.48 | 416.49 | 0 | 31.59 | 0 | OK | Ground clear controls. | 206 | 48.79 | 448.08
14122 | TIN-INTERP | Interpolated Ground | 90196.39 | 5.32 | 416.54 | 0 | 19.62 | 0 | OK | Ground clear controls. | 206 | 48.79 | 436.16
14123 | TIN-INTERP | Interpolated Ground | 90197.83 | -7.03 | 415.73 | 0 | 31.98 | 0 | OK | Ground clear controls. | 206 | 48.79 | 447.71
14124 | TIN-INTERP | Interpolated Ground | 90198.01 | -7.76 | 415.72 | 0 | 19.67 | 0 | OK | Ground clear controls. | 206 | 48.79 | 435.39
14125 | TIN-INTERP | Interpolated Ground | 90198.18 | -9.28 | 415.71 | 0 | 25.33 | 0 | OK | Ground clear controls. | 206 | 48.79 | 441.04
14126 | TIN-INTERP | Interpolated Ground | 90236.08 | 7 | 414.14 | 0 | 22.89 | 0 | OK | Ground clear controls. | 206 | 48.79 | 437.03
14127 | TIN-INTERP | Interpolated Ground | 90236.36 | 4.7 | 414.31 | 0 | 29.2 | 0 | OK | Ground clear controls. | 206 | 48.79 | 443.51
14128 | TIN-INTERP | Interpolated Ground | 90236.39 | 5.53 | 414.15 | 0 | 17.46 | 0 | OK | Ground clear controls. | 206 | 48.79 | 431.61
14129 | TIN-INTERP | Interpolated Ground | 90237.83 | -6.84 | 414.06 | 0 | 28.99 | 0 | OK | Ground clear controls. | 206 | 48.79 | 443.05
14130 | TIN-INTERP | Interpolated Ground | 90238.01 | -7.57 | 414.05 | 0 | 16.71 | 0 | OK | Ground clear controls. | 206 | 48.79 | 430.76
14131 | TIN-INTERP | Interpolated Ground | 90238.18 | -9.08 | 414.02 | 0 | 22.35 | 0 | OK | Ground clear controls. | 206 | 48.79 | 436.37
14132 | TIN-INTERP | Interpolated Ground | 90276.08 | 7.21 | 412.12 | 0 | 21.28 | 0 | OK | Ground clear controls. | 206 | 48.79 | 433.4
14133 | TIN-INTERP | Interpolated Ground | 90276.36 | 4.92 | 412.09 | 0 | 27.82 | 0 | OK | Ground clear controls. | 206 | 48.79 | 439.91
14134 | TIN-INTERP | Interpolated Ground | 90276.39 | 5.74 | 412.11 | 0 | 15.91 | 0 | OK | Ground clear controls. | 206 | 48.79 | 428.02
14135 | TIN-INTERP | Interpolated Ground | 90277.83 | -6.65 | 412.07 | 0 | 27.31 | 0 | OK | Ground clear controls. | 206 | 48.79 | 439.38
14136 | TIN-INTERP | Interpolated Ground | 90278.01 | -7.37 | 412.14 | 0 | 14.96 | 0 | OK | Ground clear controls. | 206 | 48.79 | 427.1
14137 | TIN-INTERP | Interpolated Ground | 90278.18 | -8.88 | 412.12 | 0 | 20.57 | 0 | OK | Ground clear controls. | 206 | 48.79 | 432.69
14138 | TIN-INTERP | Interpolated Ground | 90316.08 | 7.42 | 409.51 | 0 | 21.27 | 0 | OK | Ground clear controls. | 206 | 48.79 | 430.78
14139 | TIN-INTERP | Interpolated Ground | 90316.36 | 5.14 | 409.38 | 0 | 27.91 | 0 | OK | Ground clear controls. | 206 | 48.79 | 437.29
14140 | TIN-INTERP | Interpolated Ground | 90316.39 | 5.95 | 409.37 | 0 | 16.04 | 0 | OK | Ground clear controls. | 206 | 48.79 | 425.41
14141 | TIN-INTERP | Interpolated Ground | 90317.83 | -6.45 | 408.93 | 0 | 27.78 | 0 | OK | Ground clear controls. | 206 | 48.79 | 436.71
14142 | TIN-INTERP | Interpolated Ground | 90318.01 | -7.17 | 408.83 | 0 | 15.62 | 0 | OK | Ground clear controls. | 206 | 48.79 | 424.45
14143 | TIN-INTERP | Interpolated Ground | 90318.18 | -8.68 | 408.65 | 0 | 21.37 | 0 | OK | Ground clear controls. | 206 | 48.79 | 430.02
14144 | TIN-INTERP | Interpolated Ground | 90356.08 | 7.63 | 407.33 | 0 | 21.79 | 0 | OK | Ground clear controls. | 206 | 48.79 | 429.12
14145 | TIN-INTERP | Interpolated Ground | 90356.36 | 5.37 | 407.22 | 0 | 28.42 | 0 | OK | Ground clear controls. | 206 | 48.79 | 435.64
14146 | TIN-INTERP | Interpolated Ground | 90356.39 | 6.16 | 407.25 | 0 | 16.5 | 0 | OK | Ground clear controls. | 206 | 48.79 | 423.75
14147 | TIN-INTERP | Interpolated Ground | 90357.83 | -6.26 | 406.75 | 0 | 28.27 | 0 | OK | Ground clear controls. | 206 | 48.79 | 435.02
14148 | TIN-INTERP | Interpolated Ground | 90358.01 | -6.97 | 406.73 | 0 | 16.04 | 0 | OK | Ground clear controls. | 206 | 48.79 | 422.77
14149 | TIN-INTERP | Interpolated Ground | 90358.18 | -8.48 | 406.56 | 0 | 21.77 | 0 | OK | Ground clear controls. | 206 | 48.79 | 428.33
14150 | TIN-INTERP | Interpolated Ground | 90396.08 | 7.84 | 405.75 | 0 | 22.69 | 0 | OK | Ground clear controls. | 206 | 48.79 | 428.44
14151 | TIN-INTERP | Interpolated Ground | 90396.36 | 5.59 | 405.68 | 0 | 29.27 | 0 | OK | Ground clear controls. | 206 | 48.79 | 434.95
14152 | TIN-INTERP | Interpolated Ground | 90396.39 | 6.37 | 405.75 | 0 | 17.31 | 0 | OK | Ground clear controls. | 206 | 48.79 | 423.06
14153 | TIN-INTERP | Interpolated Ground | 90397.82 | -6.06 | 405.13 | 0 | 29.18 | 0 | OK | Ground clear controls. | 206 | 48.79 | 434.31
14154 | TIN-INTERP | Interpolated Ground | 90398.01 | -6.78 | 405.21 | 0 | 16.88 | 0 | OK | Ground clear controls. | 206 | 48.79 | 422.09
14155 | TIN-INTERP | Interpolated Ground | 90398.18 | -8.29 | 405.16 | 0 | 22.49 | 0 | OK | Ground clear controls. | 206 | 48.79 | 427.65
14156 | TIN-INTERP | Interpolated Ground | 90436.08 | 8.05 | 404.22 | 0 | 24.53 | 0 | OK | Ground clear controls. | 206 | 48.79 | 428.75
14157 | TIN-INTERP | Interpolated Ground | 90436.36 | 5.81 | 404.03 | 0 | 31.22 | 0 | OK | Ground clear controls. | 206 | 48.79 | 435.25
14158 | TIN-INTERP | Interpolated Ground | 90436.39 | 6.58 | 404.09 | 0 | 19.24 | 0 | OK | Ground clear controls. | 206 | 48.79 | 423.33
14159 | TIN-INTERP | Interpolated Ground | 90437.82 | -5.87 | 403.77 | 0 | 30.81 | 0 | OK | Ground clear controls. | 206 | 48.79 | 434.58
14160 | TIN-INTERP | Interpolated Ground | 90438.01 | -6.58 | 403.83 | 0 | 18.56 | 0 | OK | Ground clear controls. | 206 | 48.79 | 422.39
14161 | TIN-INTERP | Interpolated Ground | 90438.18 | -8.09 | 403.84 | 0 | 24.14 | 0 | OK | Ground clear controls. | 206 | 48.79 | 427.98
14162 | TIN-INTERP | Interpolated Ground | 90476.07 | 8.26 | 402.23 | 0 | 27.81 | 0 | OK | Ground clear controls. | 206 | 48.79 | 430.04
14163 | TIN-INTERP | Interpolated Ground | 90476.36 | 6.03 | 402.04 | 0 | 34.47 | 0 | OK | Ground clear controls. | 206 | 48.79 | 436.51
14164 | TIN-INTERP | Interpolated Ground | 90476.39 | 6.79 | 402.14 | 0 | 22.42 | 0 | OK | Ground clear controls. | 206 | 48.79 | 424.56
14165 | TIN-INTERP | Interpolated Ground | 90477.82 | -5.67 | 402.08 | 0 | 33.75 | 0 | OK | Ground clear controls. | 206 | 48.79 | 435.83
14166 | TIN-INTERP | Interpolated Ground | 90478.01 | -6.38 | 401.86 | 0 | 21.8 | 0 | OK | Ground clear controls. | 206 | 48.79 | 423.66
14167 | TIN-INTERP | Interpolated Ground | 90478.17 | -7.89 | 401.52 | 0 | 27.76 | 0 | OK | Ground clear controls. | 206 | 48.79 | 429.28
14168 | TIN-INTERP | Interpolated Ground | 90516.07 | 8.47 | 400.75 | 0 | 31.55 | 0 | OK | Ground clear controls. | 206 | 48.79 | 432.3
14169 | TIN-INTERP | Interpolated Ground | 90516.36 | 6.25 | 401.14 | 0 | 37.59 | 0 | OK | Ground clear controls. | 206 | 48.79 | 438.73
14170 | TIN-INTERP | Interpolated Ground | 90516.39 | 6.99 | 400.95 | 0 | 25.81 | 0 | OK | Ground clear controls. | 206 | 48.79 | 426.76
14171 | TIN-INTERP | Interpolated Ground | 90517.82 | -5.48 | 401.69 | 0 | 36.39 | 0 | OK | Ground clear controls. | 206 | 48.79 | 438.08
14172 | TIN-INTERP | Interpolated Ground | 90518.01 | -6.18 | 401.64 | 0 | 24.31 | 0 | OK | Ground clear controls. | 206 | 48.79 | 425.95
14173 | TIN-INTERP | Interpolated Ground | 90518.17 | -7.69 | 401.6 | 0 | 30 | 0 | OK | Ground clear controls. | 206 | 48.79 | 431.6
14174 | TIN-INTERP | Interpolated Ground | 90556.07 | 8.68 | 392.19 | 0 | 43.35 | 0 | OK | Ground clear controls. | 206 | 48.79 | 435.54
14175 | TIN-INTERP | Interpolated Ground | 90556.36 | 6.47 | 393.15 | 0 | 48.79 | 0 | OK | Ground clear controls. | 206 | 48.79 | 441.94
14176 | TIN-INTERP | Interpolated Ground | 90556.39 | 7.2 | 392.84 | 0 | 37.08 | 0 | OK | Ground clear controls. | 206 | 44.42 | 429.92
14177 | TIN-INTERP | Interpolated Ground | 90557.82 | -5.29 | 398.74 | 0 | 42.58 | 0 | OK | Ground clear controls. | 206 | 44.42 | 441.32
14178 | TIN-INTERP | Interpolated Ground | 90558 | -5.99 | 398.61 | 0 | 30.59 | 0 | OK | Ground clear controls. | 206 | 44.42 | 429.2
14179 | TIN-INTERP | Interpolated Ground | 90558.17 | -7.5 | 398.92 | 0 | 35.99 | 0 | OK | Ground clear controls. | 206 | 44.42 | 434.91
14180 | TIN-INTERP | Interpolated Ground | 90596.07 | 8.89 | 401.54 | 0 | 38.23 | 0 | OK | Ground clear controls. | 206 | 44.42 | 439.77
14181 | TIN-INTERP | Interpolated Ground | 90596.36 | 6.7 | 401.69 | 0 | 44.42 | 0 | OK | Ground clear controls. | 206 | 44.42 | 446.11
14182 | TIN-INTERP | Interpolated Ground | 90596.39 | 7.41 | 401.69 | 0 | 32.36 | 0 | OK | Ground clear controls. | 206 | 43.37 | 434.05
14183 | TIN-INTERP | Interpolated Ground | 90597.82 | -5.09 | 402.17 | 0 | 43.37 | 0 | OK | Ground clear controls. | 206 | 43.37 | 445.54
14184 | TIN-INTERP | Interpolated Ground | 90598 | -5.79 | 402.03 | 0 | 31.41 | 0 | OK | Ground clear controls. | 206 | 37.54 | 433.44
14185 | TIN-INTERP | Interpolated Ground | 90598.17 | -7.3 | 401.68 | 0 | 37.54 | 0 | OK | Ground clear controls. | 206 | 37.54 | 439.22
14186 | TIN-INTERP | Interpolated Ground | 90613.31 | 8.98 | 401.6 | 0 | 40.29 | 0 | OK | Ground clear controls. | 207 | 53.86 | 441.89
14187 | TIN-INTERP | Interpolated Ground | 90613.45 | 7.5 | 401.88 | 0 | 34.22 | 0 | OK | Ground clear controls. | 207 | 53.86 | 436.1
14188 | TIN-INTERP | Interpolated Ground | 90613.47 | 6.79 | 402.01 | 0 | 46.19 | 0 | OK | Ground clear controls. | 207 | 53.86 | 448.2
14189 | TIN-INTERP | Interpolated Ground | 90613.96 | -7.23 | 404.54 | 0 | 36.72 | 0 | OK | Ground clear controls. | 207 | 53.86 | 441.26
14190 | TIN-INTERP | Interpolated Ground | 90613.96 | -5.72 | 404.14 | 0 | 31.32 | 0 | OK | Ground clear controls. | 207 | 53.86 | 435.46
14191 | TIN-INTERP | Interpolated Ground | 90613.96 | -5.02 | 403.92 | 0 | 43.64 | 0 | OK | Ground clear controls. | 207 | 53.86 | 447.56
14192 | TIN-INTERP | Interpolated Ground | 90653.6 | -7.21 | 403.03 | 0 | 31.72 | 0 | OK | Ground clear controls. | 207 | 53.86 | 434.75
14193 | TIN-INTERP | Interpolated Ground | 90653.67 | -5.7 | 402.89 | 0 | 26.17 | 0 | OK | Ground clear controls. | 207 | 53.86 | 429.06
14194 | TIN-INTERP | Interpolated Ground | 90653.73 | -5.02 | 402.82 | 0 | 38.34 | 0 | OK | Ground clear controls. | 207 | 53.86 | 441.16
14195 | TIN-INTERP | Interpolated Ground | 90654.25 | 6.7 | 400.3 | 0 | 41.5 | 0 | OK | Ground clear controls. | 207 | 53.86 | 441.8
14196 | TIN-INTERP | Interpolated Ground | 90654.31 | 7.39 | 400.18 | 0 | 29.67 | 0 | OK | Ground clear controls. | 207 | 53.86 | 429.85
14197 | TIN-INTERP | Interpolated Ground | 90654.34 | 8.87 | 399.93 | 0 | 35.5 | 0 | OK | Ground clear controls. | 207 | 53.86 | 435.43
14198 | TIN-INTERP | Interpolated Ground | 90693.6 | -7.2 | 402.01 | 0 | 27.23 | 0 | OK | Ground clear controls. | 207 | 53.86 | 429.24
14199 | TIN-INTERP | Interpolated Ground | 90693.67 | -5.69 | 401.81 | 0 | 21.84 | 0 | OK | Ground clear controls. | 207 | 53.86 | 423.65
14200 | TIN-INTERP | Interpolated Ground | 90693.73 | -5.02 | 401.67 | 0 | 34.06 | 0 | OK | Ground clear controls. | 207 | 53.86 | 435.73
14201 | TIN-INTERP | Interpolated Ground | 90694.25 | 6.6 | 400.47 | 0 | 35.92 | 0 | OK | Ground clear controls. | 207 | 53.86 | 436.39
14202 | TIN-INTERP | Interpolated Ground | 90694.31 | 7.27 | 400.43 | 0 | 24.14 | 0 | OK | Ground clear controls. | 207 | 53.86 | 424.57
14203 | TIN-INTERP | Interpolated Ground | 90694.34 | 8.75 | 400.3 | 0 | 29.67 | 0 | OK | Ground clear controls. | 207 | 53.86 | 429.97
14204 | TIN-INTERP | Interpolated Ground | 90733.6 | -7.18 | 405.35 | 0 | 19.38 | 0 | OK | Ground clear controls. | 207 | 53.86 | 424.73
14205 | TIN-INTERP | Interpolated Ground | 90733.67 | -5.67 | 405.07 | 0 | 14.16 | 0 | OK | Ground clear controls. | 207 | 53.86 | 419.23
14206 | TIN-INTERP | Interpolated Ground | 90733.73 | -5.02 | 404.95 | 0 | 26.33 | 0 | OK | Ground clear controls. | 207 | 53.86 | 431.28
14207 | TIN-INTERP | Interpolated Ground | 90734.25 | 6.5 | 402.54 | 0 | 29.4 | 0 | OK | Ground clear controls. | 207 | 53.86 | 431.94
14208 | TIN-INTERP | Interpolated Ground | 90734.31 | 7.15 | 402.34 | 0 | 17.9 | 0 | OK | Ground clear controls. | 207 | 53.86 | 420.24
14209 | TIN-INTERP | Interpolated Ground | 90734.34 | 8.64 | 402.02 | 0 | 23.47 | 0 | OK | Ground clear controls. | 207 | 53.86 | 425.49
14210 | TIN-INTERP | Interpolated Ground | 90773.6 | -7.17 | 403.67 | 0 | 17.57 | 0 | OK | Ground clear controls. | 207 | 53.86 | 421.24
14211 | TIN-INTERP | Interpolated Ground | 90773.67 | -5.66 | 403.6 | 0 | 12.21 | 0 | OK | Ground clear controls. | 207 | 53.86 | 415.81
14212 | TIN-INTERP | Interpolated Ground | 90773.73 | -5.03 | 403.38 | 0 | 24.46 | 0 | OK | Ground clear controls. | 207 | 53.86 | 427.84
14213 | TIN-INTERP | Interpolated Ground | 90774.25 | 6.39 | 400.39 | 0 | 28.1 | 0 | OK | Ground clear controls. | 207 | 53.86 | 428.49
14214 | TIN-INTERP | Interpolated Ground | 90774.31 | 7.03 | 400.28 | 0 | 16.63 | 0 | OK | Ground clear controls. | 207 | 53.86 | 416.91
14215 | TIN-INTERP | Interpolated Ground | 90774.34 | 8.52 | 400.51 | 0 | 21.5 | 0 | OK | Ground clear controls. | 207 | 53.86 | 422.01
14216 | TIN-INTERP | Interpolated Ground | 90813.6 | -7.15 | 397.03 | 0 | 21.71 | 0 | OK | Ground clear controls. | 207 | 53.86 | 418.74
14217 | TIN-INTERP | Interpolated Ground | 90813.67 | -5.64 | 396.76 | 0 | 16.62 | 0 | OK | Ground clear controls. | 207 | 53.86 | 413.38
14218 | TIN-INTERP | Interpolated Ground | 90813.73 | -5.03 | 396.72 | 0 | 28.66 | 0 | OK | Ground clear controls. | 207 | 53.86 | 425.38
14219 | TIN-INTERP | Interpolated Ground | 90814.24 | 6.29 | 394 | 0 | 32.03 | 0 | OK | Ground clear controls. | 207 | 53.86 | 426.03
14220 | TIN-INTERP | Interpolated Ground | 90814.31 | 6.91 | 393.91 | 0 | 20.63 | 0 | OK | Ground clear controls. | 207 | 53.86 | 414.54
14221 | TIN-INTERP | Interpolated Ground | 90814.34 | 8.4 | 393.79 | 0 | 25.73 | 0 | OK | Ground clear controls. | 207 | 53.86 | 419.52
14222 | TIN-INTERP | Interpolated Ground | 90853.6 | -7.14 | 388.52 | 0 | 28.71 | 0 | OK | Ground clear controls. | 207 | 53.86 | 417.23
14223 | TIN-INTERP | Interpolated Ground | 90853.67 | -5.63 | 388.52 | 0 | 23.4 | 0 | OK | Ground clear controls. | 207 | 53.86 | 411.92
14224 | TIN-INTERP | Interpolated Ground | 90853.73 | -5.03 | 388.56 | 0 | 35.33 | 0 | OK | Ground clear controls. | 207 | 53.86 | 423.89
14225 | TIN-INTERP | Interpolated Ground | 90854.24 | 6.19 | 388.94 | 0 | 35.6 | 0 | OK | Ground clear controls. | 207 | 53.86 | 424.54
14226 | TIN-INTERP | Interpolated Ground | 90854.31 | 6.8 | 388.9 | 0 | 24.22 | 0 | OK | Ground clear controls. | 207 | 53.86 | 413.12
14227 | TIN-INTERP | Interpolated Ground | 90854.34 | 8.28 | 388.8 | 0 | 29.21 | 0 | OK | Ground clear controls. | 207 | 53.86 | 418.01
14228 | TIN-INTERP | Interpolated Ground | 90893.6 | -7.12 | 382.53 | 0 | 34.18 | 0 | OK | Ground clear controls. | 207 | 53.86 | 416.71
14229 | TIN-INTERP | Interpolated Ground | 90893.67 | -5.62 | 382.05 | 0 | 29.4 | 0 | OK | Ground clear controls. | 207 | 53.86 | 411.45
14230 | TIN-INTERP | Interpolated Ground | 90893.73 | -5.03 | 381.72 | 0 | 41.66 | 0 | OK | Ground clear controls. | 207 | 53.86 | 423.38
14231 | TIN-INTERP | Interpolated Ground | 90894.24 | 6.09 | 376.25 | 0 | 47.77 | 0 | OK | Ground clear controls. | 207 | 53.86 | 424.02
14232 | TIN-INTERP | Interpolated Ground | 90894.31 | 6.68 | 376.01 | 0 | 36.67 | 0 | OK | Ground clear controls. | 207 | 53.86 | 412.68
14233 | TIN-INTERP | Interpolated Ground | 90894.34 | 8.16 | 375.41 | 0 | 42.09 | 0 | OK | Ground clear controls. | 207 | 53.86 | 417.5
14234 | TIN-INTERP | Interpolated Ground | 90933.6 | -7.11 | 377.64 | 0 | 39.57 | 0 | OK | Ground clear controls. | 207 | 53.86 | 417.21
14235 | TIN-INTERP | Interpolated Ground | 90933.67 | -5.6 | 377.55 | 0 | 34.43 | 0 | OK | Ground clear controls. | 207 | 53.86 | 411.98
14236 | TIN-INTERP | Interpolated Ground | 90933.73 | -5.04 | 377.54 | 0 | 46.34 | 0 | OK | Ground clear controls. | 207 | 53.86 | 423.88
14237 | TIN-INTERP | Interpolated Ground | 90934.24 | 5.98 | 376.49 | 0 | 48 | 0 | OK | Ground clear controls. | 207 | 53.86 | 424.49
14238 | TIN-INTERP | Interpolated Ground | 90934.31 | 6.56 | 376.38 | 0 | 36.83 | 0 | OK | Ground clear controls. | 207 | 53.86 | 413.21
14239 | TIN-INTERP | Interpolated Ground | 90934.34 | 8.04 | 376.17 | 0 | 41.81 | 0 | OK | Ground clear controls. | 207 | 53.86 | 417.98
14240 | TIN-INTERP | Interpolated Ground | 90973.6 | -7.09 | 372.5 | 0 | 46.19 | 0 | OK | Ground clear controls. | 207 | 53.86 | 418.69
14241 | TIN-INTERP | Interpolated Ground | 90973.67 | -5.59 | 372.67 | 0 | 40.81 | 0 | OK | Ground clear controls. | 207 | 53.86 | 413.48
14242 | TIN-INTERP | Interpolated Ground | 90973.73 | -5.04 | 372.64 | 0 | 52.7 | 0 | OK | Ground clear controls. | 207 | 53.86 | 425.34
14243 | TIN-INTERP | Interpolated Ground | 90974.24 | 5.88 | 373.63 | 0 | 52.29 | 0 | OK | Ground clear controls. | 207 | 53.86 | 425.92
14244 | TIN-INTERP | Interpolated Ground | 90974.31 | 6.44 | 373.89 | 0 | 40.81 | 0 | OK | Ground clear controls. | 207 | 53.86 | 414.7
14245 | TIN-INTERP | Interpolated Ground | 90974.34 | 7.93 | 373.83 | 0 | 45.61 | 0 | OK | Ground clear controls. | 207 | 53.86 | 419.44
14246 | TIN-INTERP | Interpolated Ground | 91013.6 | -7.08 | 375.2 | 0 | 45.96 | 0 | OK | Ground clear controls. | 207 | 53.86 | 421.16
14247 | TIN-INTERP | Interpolated Ground | 91013.67 | -5.57 | 375.56 | 0 | 40.42 | 0 | OK | Ground clear controls. | 207 | 53.86 | 415.98
14248 | TIN-INTERP | Interpolated Ground | 91013.73 | -5.04 | 375.62 | 0 | 52.17 | 0 | OK | Ground clear controls. | 207 | 53.86 | 427.79
14249 | TIN-INTERP | Interpolated Ground | 91014.24 | 5.78 | 377.11 | 0 | 51.22 | 0 | OK | Ground clear controls. | 207 | 53.86 | 428.33
14250 | TIN-INTERP | Interpolated Ground | 91014.31 | 6.32 | 377.13 | 0 | 40.02 | 0 | OK | Ground clear controls. | 207 | 53.86 | 417.15
14251 | TIN-INTERP | Interpolated Ground | 91014.34 | 7.81 | 377.09 | 0 | 44.8 | 0 | OK | Ground clear controls. | 207 | 53.86 | 421.89
14252 | TIN-INTERP | Interpolated Ground | 91053.6 | -7.06 | 382.03 | 0 | 42.62 | 0 | OK | Ground clear controls. | 207 | 53.86 | 424.65
14253 | TIN-INTERP | Interpolated Ground | 91053.67 | -5.56 | 382.39 | 0 | 37.07 | 0 | OK | Ground clear controls. | 207 | 53.86 | 419.46
14254 | TIN-INTERP | Interpolated Ground | 91053.73 | -5.04 | 382.53 | 0 | 48.69 | 0 | OK | Ground clear controls. | 207 | 53.86 | 431.22
14255 | TIN-INTERP | Interpolated Ground | 91054.24 | 5.68 | 384.14 | 0 | 47.6 | 0 | OK | Ground clear controls. | 207 | 53.86 | 431.74
14256 | TIN-INTERP | Interpolated Ground | 91054.31 | 6.2 | 384.17 | 0 | 36.4 | 0 | OK | Ground clear controls. | 207 | 53.86 | 420.57
14257 | TIN-INTERP | Interpolated Ground | 91054.34 | 7.69 | 384.25 | 0 | 41.09 | 0 | OK | Ground clear controls. | 207 | 53.86 | 425.34
14258 | TIN-INTERP | Interpolated Ground | 91093.6 | -7.05 | 381.25 | 0 | 47.88 | 0 | OK | Ground clear controls. | 207 | 53.86 | 429.13
14259 | TIN-INTERP | Interpolated Ground | 91093.67 | -5.54 | 381.66 | 0 | 42.27 | 0 | OK | Ground clear controls. | 207 | 53.86 | 423.93
14260 | TIN-INTERP | Interpolated Ground | 91093.73 | -5.04 | 381.79 | 0 | 53.86 | 0 | OK | Ground clear controls. | 207 | 53.86 | 435.65
14261 | TIN-INTERP | Interpolated Ground | 91094.24 | 5.57 | 387.16 | 0 | 48.95 | 0 | OK | Ground clear controls. | 207 | 52.48 | 436.11
14262 | TIN-INTERP | Interpolated Ground | 91094.31 | 6.08 | 387.72 | 0 | 37.25 | 0 | OK | Ground clear controls. | 207 | 52.48 | 424.97
14263 | TIN-INTERP | Interpolated Ground | 91094.34 | 7.57 | 388.67 | 0 | 41.1 | 0 | OK | Ground clear controls. | 207 | 52.48 | 429.77
14264 | TIN-INTERP | Interpolated Ground | 91133.6 | -7.03 | 391.86 | 0 | 42.75 | 0 | OK | Ground clear controls. | 207 | 52.48 | 434.61
14265 | TIN-INTERP | Interpolated Ground | 91133.67 | -5.53 | 391.12 | 0 | 38.27 | 0 | OK | Ground clear controls. | 207 | 52.48 | 429.39
14266 | TIN-INTERP | Interpolated Ground | 91133.73 | -5.05 | 390.9 | 0 | 50.15 | 0 | OK | Ground clear controls. | 207 | 52.48 | 441.05
14267 | TIN-INTERP | Interpolated Ground | 91134.24 | 5.47 | 389.53 | 0 | 51.94 | 0 | OK | Ground clear controls. | 207 | 52.48 | 441.47
14268 | TIN-INTERP | Interpolated Ground | 91134.31 | 5.96 | 389.35 | 0 | 40.98 | 0 | OK | Ground clear controls. | 207 | 52.48 | 430.33
14269 | TIN-INTERP | Interpolated Ground | 91134.34 | 7.45 | 389.11 | 0 | 46.09 | 0 | OK | Ground clear controls. | 207 | 52.48 | 435.2
14270 | TIN-INTERP | Interpolated Ground | 91173.6 | -7.02 | 401.44 | 0 | 39.66 | 0 | OK | Ground clear controls. | 207 | 52.48 | 441.1
14271 | TIN-INTERP | Interpolated Ground | 91173.67 | -5.52 | 400.47 | 0 | 35.38 | 0 | OK | Ground clear controls. | 207 | 52.48 | 435.85
14272 | TIN-INTERP | Interpolated Ground | 91173.73 | -5.05 | 400.25 | 0 | 47.2 | 0 | OK | Ground clear controls. | 207 | 52.48 | 447.45
14273 | TIN-INTERP | Interpolated Ground | 91174.24 | 5.37 | 395.35 | 0 | 52.48 | 0 | OK | Ground clear controls. | 207 | 52.48 | 447.83
14274 | TIN-INTERP | Interpolated Ground | 91174.31 | 5.84 | 395.3 | 0 | 41.38 | 0 | OK | Ground clear controls. | 207 | 46.64 | 436.68
14275 | TIN-INTERP | Interpolated Ground | 91174.34 | 7.33 | 395.23 | 0 | 46.39 | 0 | OK | Ground clear controls. | 207 | 46.64 | 441.62
14276 | TIN-INTERP | Interpolated Ground | 91213.6 | -7 | 407.97 | 0 | 40.65 | 0 | OK | Ground clear controls. | 207 | 46.64 | 448.62
14277 | TIN-INTERP | Interpolated Ground | 91213.67 | -5.5 | 408.17 | 0 | 35.15 | 0 | OK | Ground clear controls. | 207 | 46.64 | 443.32
14278 | TIN-INTERP | Interpolated Ground | 91213.73 | -5.05 | 408.21 | 0 | 46.64 | 0 | OK | Ground clear controls. | 207 | 46.64 | 454.85
14279 | TIN-INTERP | Interpolated Ground | 91214.24 | 5.27 | 410.44 | 0 | 44.74 | 0 | OK | Ground clear controls. | 207 | 44.74 | 455.18
14280 | TIN-INTERP | Interpolated Ground | 91214.31 | 5.72 | 410.53 | 0 | 33.47 | 0 | OK | Ground clear controls. | 207 | 40.24 | 444
14281 | TIN-INTERP | Interpolated Ground | 91214.34 | 7.22 | 410.7 | 0 | 38.36 | 0 | OK | Ground clear controls. | 207 | 40.24 | 449.06
14282 | TIN-INTERP | Interpolated Ground | 91253.6 | -6.99 | 422.58 | 0 | 34.56 | 0 | OK | Ground clear controls. | 207 | 40.24 | 457.14
14283 | TIN-INTERP | Interpolated Ground | 91253.67 | -5.49 | 422.9 | 0 | 28.89 | 0 | OK | Ground clear controls. | 207 | 40.24 | 451.79
14284 | TIN-INTERP | Interpolated Ground | 91253.73 | -5.05 | 423.01 | 0 | 40.24 | 0 | OK | Ground clear controls. | 207 | 40.24 | 463.25
14285 | TIN-INTERP | Interpolated Ground | 91254.24 | 5.16 | 425.5 | 0 | 38.01 | 0 | OK | Ground clear controls. | 207 | 38.01 | 463.51
14286 | TIN-INTERP | Interpolated Ground | 91254.31 | 5.6 | 425.51 | 0 | 26.8 | 0 | OK | Ground clear controls. | 207 | 33.56 | 452.31
14287 | TIN-INTERP | Interpolated Ground | 91254.34 | 7.1 | 425.79 | 0 | 31.71 | 0 | OK | Ground clear controls. | 207 | 33.56 | 457.5
14288 | TIN-INTERP | Interpolated Ground | 91293.6 | -6.98 | 438.3 | 0 | 28.37 | 0 | OK | Ground clear controls. | 207 | 33.56 | 466.67
14289 | TIN-INTERP | Interpolated Ground | 91293.67 | -5.47 | 439 | 0 | 22.26 | 0 | OK | Ground clear controls. | 207 | 33.56 | 461.26
14290 | TIN-INTERP | Interpolated Ground | 91293.73 | -5.06 | 439.09 | 0 | 33.56 | 0 | OK | Ground clear controls. | 207 | 33.56 | 472.65
14291 | TIN-INTERP | Interpolated Ground | 91294.24 | 5.06 | 441.23 | 0 | 31.61 | 0 | OK | Ground clear controls. | 207 | 31.61 | 472.84
14292 | TIN-INTERP | Interpolated Ground | 91294.31 | 5.48 | 441.26 | 0 | 20.35 | 0 | OK | Ground clear controls. | 207 | 25.55 | 461.61
14293 | TIN-INTERP | Interpolated Ground | 91294.34 | 6.98 | 441.4 | 0 | 25.55 | 0 | OK | Ground clear controls. | 207 | 25.55 | 466.95
14294 | TIN-INTERP | Interpolated Ground | 91327.77 | -5.06 | 438.08 | 0 | 43.36 | 0 | OK | Ground clear controls. | 208 | 80.96 | 481.44
14295 | TIN-INTERP | Interpolated Ground | 91327.77 | 4.97 | 437.72 | 0 | 43.72 | 0 | OK | Ground clear controls. | 208 | 80.96 | 481.44
14296 | TIN-INTERP | Interpolated Ground | 91327.8 | 5.38 | 437.72 | 0 | 32.42 | 0 | OK | Ground clear controls. | 208 | 80.96 | 470.14
14297 | TIN-INTERP | Interpolated Ground | 91327.82 | -5.46 | 438.13 | 0 | 32.02 | 0 | OK | Ground clear controls. | 208 | 80.96 | 470.15
14298 | TIN-INTERP | Interpolated Ground | 91327.87 | -6.96 | 437.89 | 0 | 37.76 | 0 | OK | Ground clear controls. | 208 | 80.96 | 475.65
14299 | TIN-INTERP | Interpolated Ground | 91327.87 | 6.88 | 437.67 | 0 | 37.98 | 0 | OK | Ground clear controls. | 208 | 80.96 | 475.65
14300 | TIN-INTERP | Interpolated Ground | 91367.77 | -5.23 | 430.71 | 0 | 44.86 | 0 | OK | Ground clear controls. | 208 | 80.96 | 475.57
14301 | TIN-INTERP | Interpolated Ground | 91367.77 | 4.92 | 432.63 | 0 | 42.9 | 0 | OK | Ground clear controls. | 208 | 80.96 | 475.53
14302 | TIN-INTERP | Interpolated Ground | 91367.8 | 5.35 | 432.69 | 0 | 31.58 | 0 | OK | Ground clear controls. | 208 | 80.96 | 464.27
14303 | TIN-INTERP | Interpolated Ground | 91367.82 | -5.65 | 430.55 | 0 | 33.7 | 0 | OK | Ground clear controls. | 208 | 80.96 | 464.25
14304 | TIN-INTERP | Interpolated Ground | 91367.87 | -7.15 | 430.25 | 0 | 39.52 | 0 | OK | Ground clear controls. | 208 | 80.96 | 469.77
14305 | TIN-INTERP | Interpolated Ground | 91367.87 | 6.84 | 432.84 | 0 | 36.89 | 0 | OK | Ground clear controls. | 208 | 80.96 | 469.73
14306 | TIN-INTERP | Interpolated Ground | 91407.77 | -5.4 | 429.4 | 0 | 41.25 | 0 | OK | Ground clear controls. | 208 | 80.96 | 470.65
14307 | TIN-INTERP | Interpolated Ground | 91407.77 | 4.86 | 433.61 | 0 | 36.96 | 0 | OK | Ground clear controls. | 208 | 80.96 | 470.57
14308 | TIN-INTERP | Interpolated Ground | 91407.8 | 5.31 | 433.92 | 0 | 25.42 | 0 | OK | Ground clear controls. | 208 | 80.96 | 459.34
14309 | TIN-INTERP | Interpolated Ground | 91407.82 | -5.84 | 429.38 | 0 | 29.93 | 0 | OK | Ground clear controls. | 208 | 80.96 | 459.31
14310 | TIN-INTERP | Interpolated Ground | 91407.86 | -7.35 | 429.13 | 0 | 35.7 | 0 | OK | Ground clear controls. | 208 | 80.96 | 464.83
14311 | TIN-INTERP | Interpolated Ground | 91407.87 | 6.81 | 435.01 | 0 | 29.74 | 0 | OK | Ground clear controls. | 208 | 80.96 | 464.75
14312 | TIN-INTERP | Interpolated Ground | 91447.77 | -5.58 | 438.82 | 0 | 27.87 | 0 | OK | Ground clear controls. | 208 | 80.96 | 466.69
14313 | TIN-INTERP | Interpolated Ground | 91447.77 | 4.81 | 437.37 | 0 | 29.21 | 0 | OK | Ground clear controls. | 208 | 80.96 | 466.58
14314 | TIN-INTERP | Interpolated Ground | 91447.8 | 5.27 | 437.35 | 0 | 18.01 | 0 | OK | Ground clear controls. | 208 | 80.96 | 455.36
14315 | TIN-INTERP | Interpolated Ground | 91447.82 | -6.02 | 438.75 | 0 | 16.57 | 0 | OK | Ground clear controls. | 208 | 80.96 | 455.32
14316 | TIN-INTERP | Interpolated Ground | 91447.86 | -7.54 | 438.71 | 0 | 22.13 | 0 | OK | Ground clear controls. | 208 | 80.96 | 460.84
14317 | TIN-INTERP | Interpolated Ground | 91447.87 | 6.77 | 437.33 | 0 | 23.41 | 0 | OK | Ground clear controls. | 208 | 80.96 | 460.74
14318 | TIN-INTERP | Interpolated Ground | 91487.77 | -5.75 | 423.64 | 0 | 40.06 | 0 | OK | Ground clear controls. | 208 | 80.96 | 463.7
14319 | TIN-INTERP | Interpolated Ground | 91487.77 | 4.75 | 422.45 | 0 | 41.11 | 0 | OK | Ground clear controls. | 208 | 80.96 | 463.56
14320 | TIN-INTERP | Interpolated Ground | 91487.8 | 5.24 | 422.31 | 0 | 30.01 | 0 | OK | Ground clear controls. | 208 | 80.96 | 452.32
14321 | TIN-INTERP | Interpolated Ground | 91487.82 | -6.21 | 423.85 | 0 | 28.43 | 0 | OK | Ground clear controls. | 208 | 80.96 | 452.28
14322 | TIN-INTERP | Interpolated Ground | 91487.86 | -7.73 | 424.28 | 0 | 33.54 | 0 | OK | Ground clear controls. | 208 | 80.96 | 457.82
14323 | TIN-INTERP | Interpolated Ground | 91487.87 | 6.73 | 421.7 | 0 | 35.99 | 0 | OK | Ground clear controls. | 208 | 80.96 | 457.69
14324 | TIN-INTERP | Interpolated Ground | 91527.77 | -5.92 | 404.28 | 0 | 57.37 | 0 | OK | Ground clear controls. | 208 | 80.96 | 461.65
14325 | TIN-INTERP | Interpolated Ground | 91527.77 | 4.7 | 403.99 | 0 | 57.49 | 0 | OK | Ground clear controls. | 208 | 80.96 | 461.48
14326 | TIN-INTERP | Interpolated Ground | 91527.8 | 5.2 | 403.93 | 0 | 46.3 | 0 | OK | Ground clear controls. | 208 | 80.96 | 450.23
14327 | TIN-INTERP | Interpolated Ground | 91527.82 | -6.4 | 404.3 | 0 | 45.89 | 0 | OK | Ground clear controls. | 208 | 80.96 | 450.19
14328 | TIN-INTERP | Interpolated Ground | 91527.86 | -7.92 | 404.51 | 0 | 51.23 | 0 | OK | Ground clear controls. | 208 | 80.96 | 455.74
14329 | TIN-INTERP | Interpolated Ground | 91527.87 | 6.7 | 403.36 | 0 | 52.22 | 0 | OK | Ground clear controls. | 208 | 80.96 | 455.58
14330 | TIN-INTERP | Interpolated Ground | 91567.77 | -6.09 | 389.01 | 0 | 71.54 | 0 | OK | Ground clear controls. | 208 | 80.96 | 460.55
14331 | TIN-INTERP | Interpolated Ground | 91567.77 | 4.64 | 390.85 | 0 | 69.51 | 0 | OK | Ground clear controls. | 208 | 80.96 | 460.36
14332 | TIN-INTERP | Interpolated Ground | 91567.8 | 5.17 | 390.89 | 0 | 58.18 | 0 | OK | Ground clear controls. | 208 | 80.96 | 449.07
14333 | TIN-INTERP | Interpolated Ground | 91567.82 | -6.59 | 388.95 | 0 | 60.1 | 0 | OK | Ground clear controls. | 208 | 80.96 | 449.05
14334 | TIN-INTERP | Interpolated Ground | 91567.86 | -8.11 | 388.74 | 0 | 65.87 | 0 | OK | Ground clear controls. | 208 | 80.96 | 454.61
14335 | TIN-INTERP | Interpolated Ground | 91567.87 | 6.66 | 391.02 | 0 | 63.41 | 0 | OK | Ground clear controls. | 208 | 80.96 | 454.43
14336 | TIN-INTERP | Interpolated Ground | 91607.76 | -6.27 | 379.84 | 0 | 80.59 | 0 | OK | Ground clear controls. | 208 | 80.96 | 460.43
14337 | TIN-INTERP | Interpolated Ground | 91607.77 | 4.59 | 381.27 | 0 | 78.93 | 0 | OK | Ground clear controls. | 208 | 80.96 | 460.2
14338 | TIN-INTERP | Interpolated Ground | 91607.8 | 5.13 | 381.24 | 0 | 67.62 | 0 | OK | Ground clear controls. | 208 | 80.96 | 448.86
14339 | TIN-INTERP | Interpolated Ground | 91607.82 | -6.77 | 379.84 | 0 | 69.02 | 0 | OK | Ground clear controls. | 208 | 80.96 | 448.86
14340 | TIN-INTERP | Interpolated Ground | 91607.86 | -8.3 | 379.93 | 0 | 74.51 | 0 | OK | Ground clear controls. | 208 | 80.96 | 454.44
14341 | TIN-INTERP | Interpolated Ground | 91607.87 | 6.62 | 381.27 | 0 | 72.97 | 0 | OK | Ground clear controls. | 208 | 80.96 | 454.24
14342 | TIN-INTERP | Interpolated Ground | 91647.76 | -6.44 | 380.28 | 0 | 80.96 | 0 | OK | Ground clear controls. | 208 | 80.96 | 461.24
14343 | TIN-INTERP | Interpolated Ground | 91647.77 | 4.53 | 380.09 | 0 | 80.91 | 0 | OK | Ground clear controls. | 208 | 80.91 | 461
14344 | TIN-INTERP | Interpolated Ground | 91647.8 | 5.1 | 380.09 | 0 | 69.5 | 0 | OK | Ground clear controls. | 208 | 74.86 | 449.59
14345 | TIN-INTERP | Interpolated Ground | 91647.82 | -6.96 | 380.28 | 0 | 69.34 | 0 | OK | Ground clear controls. | 208 | 74.86 | 449.62
14346 | TIN-INTERP | Interpolated Ground | 91647.86 | -8.49 | 380.51 | 0 | 74.7 | 0 | OK | Ground clear controls. | 208 | 74.86 | 455.21
14347 | TIN-INTERP | Interpolated Ground | 91647.87 | 6.59 | 380.14 | 0 | 74.86 | 0 | OK | Ground clear controls. | 208 | 74.86 | 455
14348 | TIN-INTERP | Interpolated Ground | 91687.76 | -6.61 | 392.64 | 0 | 70.37 | 0 | OK | Ground clear controls. | 208 | 70.37 | 463.01
14349 | TIN-INTERP | Interpolated Ground | 91687.77 | 4.48 | 393.08 | 0 | 69.68 | 0 | OK | Ground clear controls. | 208 | 69.68 | 462.76
14350 | TIN-INTERP | Interpolated Ground | 91687.8 | 5.06 | 393.09 | 0 | 58.17 | 0 | OK | Ground clear controls. | 208 | 64.23 | 451.26
14351 | TIN-INTERP | Interpolated Ground | 91687.82 | -7.15 | 392.68 | 0 | 58.64 | 0 | OK | Ground clear controls. | 208 | 64.23 | 451.32
14352 | TIN-INTERP | Interpolated Ground | 91687.86 | -8.68 | 392.7 | 0 | 64.23 | 0 | OK | Ground clear controls. | 208 | 64.23 | 456.93
14353 | TIN-INTERP | Interpolated Ground | 91687.87 | 6.55 | 393.09 | 0 | 63.61 | 0 | OK | Ground clear controls. | 208 | 63.61 | 456.7
14354 | TIN-INTERP | Interpolated Ground | 91727.76 | -6.78 | 403.24 | 0 | 62.5 | 0 | OK | Ground clear controls. | 208 | 62.5 | 465.74
14355 | TIN-INTERP | Interpolated Ground | 91727.77 | 4.42 | 404.03 | 0 | 61.44 | 0 | OK | Ground clear controls. | 208 | 61.44 | 465.47
14356 | TIN-INTERP | Interpolated Ground | 91727.8 | 5.03 | 404.05 | 0 | 49.83 | 0 | OK | Ground clear controls. | 208 | 56.46 | 453.88
14357 | TIN-INTERP | Interpolated Ground | 91727.82 | -7.34 | 403.23 | 0 | 50.75 | 0 | OK | Ground clear controls. | 208 | 56.46 | 453.98
14358 | TIN-INTERP | Interpolated Ground | 91727.86 | -8.87 | 403.15 | 0 | 56.46 | 0 | OK | Ground clear controls. | 208 | 56.46 | 459.61
14359 | TIN-INTERP | Interpolated Ground | 91727.87 | 6.51 | 404.07 | 0 | 55.3 | 0 | OK | Ground clear controls. | 208 | 55.3 | 459.37
14360 | TIN-INTERP | Interpolated Ground | 91767.76 | -6.96 | 415.91 | 0 | 53.51 | 0 | OK | Ground clear controls. | 208 | 53.51 | 469.42
14361 | TIN-INTERP | Interpolated Ground | 91767.77 | 4.37 | 416.83 | 0 | 52.31 | 0 | OK | Ground clear controls. | 208 | 52.31 | 469.14
14362 | TIN-INTERP | Interpolated Ground | 91767.8 | 4.99 | 416.98 | 0 | 40.45 | 0 | OK | Ground clear controls. | 208 | 47.61 | 457.43
14363 | TIN-INTERP | Interpolated Ground | 91767.81 | -7.52 | 415.89 | 0 | 41.69 | 0 | OK | Ground clear controls. | 208 | 47.61 | 457.58
14364 | TIN-INTERP | Interpolated Ground | 91767.86 | -9.06 | 415.63 | 0 | 47.61 | 0 | OK | Ground clear controls. | 208 | 47.61 | 463.24
14365 | TIN-INTERP | Interpolated Ground | 91767.87 | 6.48 | 417.14 | 0 | 45.84 | 0 | OK | Ground clear controls. | 208 | 45.84 | 462.98
14366 | TIN-INTERP | Interpolated Ground | 91807.76 | -7.13 | 433.92 | 0 | 40.13 | 0 | OK | Ground clear controls. | 208 | 40.13 | 474.05
14367 | TIN-INTERP | Interpolated Ground | 91807.77 | 4.31 | 434.34 | 0 | 39.44 | 0 | OK | Ground clear controls. | 208 | 39.44 | 473.78
14368 | TIN-INTERP | Interpolated Ground | 91807.8 | 4.96 | 434.36 | 0 | 27.58 | 0 | OK | Ground clear controls. | 208 | 34.2 | 461.94
14369 | TIN-INTERP | Interpolated Ground | 91807.81 | -7.71 | 433.74 | 0 | 28.4 | 0 | OK | Ground clear controls. | 208 | 34.2 | 462.14
14370 | TIN-INTERP | Interpolated Ground | 91807.86 | -9.26 | 433.61 | 0 | 34.2 | 0 | OK | Ground clear controls. | 208 | 34.2 | 467.81
14371 | TIN-INTERP | Interpolated Ground | 91807.87 | 6.44 | 434.16 | 0 | 33.39 | 0 | OK | Ground clear controls. | 208 | 33.62 | 467.55
14372 | TIN-INTERP | Interpolated Ground | 91847.76 | -7.3 | 447.92 | 0 | 31.74 | 0 | OK | Ground clear controls. | 208 | 33.62 | 479.66
14373 | TIN-INTERP | Interpolated Ground | 91847.77 | 4.26 | 445.75 | 0 | 33.62 | 0 | OK | Ground clear controls. | 208 | 33.62 | 479.37
14374 | TIN-INTERP | Interpolated Ground | 91847.8 | 4.92 | 445.76 | 0 | 21.63 | 0 | OK | Ground clear controls. | 208 | 27.45 | 467.39
14375 | TIN-INTERP | Interpolated Ground | 91847.81 | -7.9 | 448.12 | 0 | 19.54 | 0 | OK | Ground clear controls. | 208 | 27.45 | 467.66
14376 | TIN-INTERP | Interpolated Ground | 91847.86 | -9.45 | 448.45 | 0 | 24.9 | 0 | OK | Ground clear controls. | 208 | 27.45 | 473.35
14377 | TIN-INTERP | Interpolated Ground | 91847.87 | 6.4 | 445.63 | 0 | 27.45 | 0 | OK | Ground clear controls. | 208 | 27.45 | 473.08
14378 | TIN-INTERP | Interpolated Ground | 91873.8 | 4.29 | 444.57 | 0 | 39.09 | 0 | OK | Ground clear controls. | 209 | 59.1 | 483.66
14379 | TIN-INTERP | Interpolated Ground | 91873.8 | 4.96 | 444.43 | 0 | 27.15 | 0 | OK | Ground clear controls. | 209 | 59.1 | 471.58
14380 | TIN-INTERP | Interpolated Ground | 91873.8 | 6.47 | 444.19 | 0 | 33.18 | 0 | OK | Ground clear controls. | 209 | 59.1 | 477.37
14381 | TIN-INTERP | Interpolated Ground | 91875 | -7.39 | 446.61 | 0 | 37.03 | 0 | OK | Ground clear controls. | 209 | 59.1 | 483.64
14382 | TIN-INTERP | Interpolated Ground | 91875.04 | -8.01 | 446.67 | 0 | 24.88 | 0 | OK | Ground clear controls. | 209 | 59.1 | 471.55
14383 | TIN-INTERP | Interpolated Ground | 91875.38 | -9.53 | 446.68 | 0 | 30.55 | 0 | OK | Ground clear controls. | 209 | 59.1 | 477.23
14384 | TIN-INTERP | Interpolated Ground | 91912.96 | 6.42 | 440.28 | 0 | 29.12 | 0 | OK | Ground clear controls. | 209 | 59.1 | 469.4
14385 | TIN-INTERP | Interpolated Ground | 91913.12 | 4.92 | 440.02 | 0 | 23.59 | 0 | OK | Ground clear controls. | 209 | 59.1 | 463.61
14386 | TIN-INTERP | Interpolated Ground | 91913.25 | 4.27 | 439.93 | 0 | 35.64 | 0 | OK | Ground clear controls. | 209 | 59.1 | 475.57
14387 | TIN-INTERP | Interpolated Ground | 91914.99 | -7.19 | 437.54 | 0 | 38 | 0 | OK | Ground clear controls. | 209 | 59.1 | 475.54
14388 | TIN-INTERP | Interpolated Ground | 91915.04 | -7.8 | 437.52 | 0 | 25.98 | 0 | OK | Ground clear controls. | 209 | 59.1 | 463.5
14389 | TIN-INTERP | Interpolated Ground | 91915.38 | -9.32 | 437.48 | 0 | 31.81 | 0 | OK | Ground clear controls. | 209 | 59.1 | 469.29
14390 | TIN-INTERP | Interpolated Ground | 91952.96 | 6.43 | 431.75 | 0 | 30.61 | 0 | OK | Ground clear controls. | 209 | 59.1 | 462.36
14391 | TIN-INTERP | Interpolated Ground | 91953.12 | 4.93 | 431.22 | 0 | 25.37 | 0 | OK | Ground clear controls. | 209 | 59.1 | 456.59
14392 | TIN-INTERP | Interpolated Ground | 91953.25 | 4.29 | 431 | 0 | 37.42 | 0 | OK | Ground clear controls. | 209 | 59.1 | 468.42
14393 | TIN-INTERP | Interpolated Ground | 91954.99 | -6.99 | 428.82 | 0 | 39.56 | 0 | OK | Ground clear controls. | 209 | 59.1 | 468.38
14394 | TIN-INTERP | Interpolated Ground | 91955.04 | -7.59 | 428.73 | 0 | 27.67 | 0 | OK | Ground clear controls. | 209 | 59.1 | 456.4
14395 | TIN-INTERP | Interpolated Ground | 91955.38 | -9.1 | 428.53 | 0 | 33.75 | 0 | OK | Ground clear controls. | 209 | 59.1 | 462.28
14396 | TIN-INTERP | Interpolated Ground | 91992.96 | 6.44 | 429.24 | 0 | 27.03 | 0 | OK | Ground clear controls. | 209 | 59.1 | 456.27
14397 | TIN-INTERP | Interpolated Ground | 91993.12 | 4.93 | 428.72 | 0 | 21.78 | 0 | OK | Ground clear controls. | 209 | 59.1 | 450.5
14398 | TIN-INTERP | Interpolated Ground | 91993.25 | 4.31 | 428.56 | 0 | 33.67 | 0 | OK | Ground clear controls. | 209 | 59.1 | 462.23
14399 | TIN-INTERP | Interpolated Ground | 91994.99 | -6.78 | 424.91 | 0 | 37.28 | 0 | OK | Ground clear controls. | 209 | 59.1 | 462.19
14400 | TIN-INTERP | Interpolated Ground | 91995.04 | -7.38 | 424.81 | 0 | 25.47 | 0 | OK | Ground clear controls. | 209 | 59.1 | 450.28
14401 | TIN-INTERP | Interpolated Ground | 91995.38 | -8.89 | 424.51 | 0 | 31.71 | 0 | OK | Ground clear controls. | 209 | 59.1 | 456.22
14402 | TIN-INTERP | Interpolated Ground | 92032.96 | 6.44 | 421.75 | 0 | 29.36 | 0 | OK | Ground clear controls. | 209 | 59.1 | 451.11
14403 | TIN-INTERP | Interpolated Ground | 92033.12 | 4.94 | 421.5 | 0 | 23.86 | 0 | OK | Ground clear controls. | 209 | 59.1 | 445.36
14404 | TIN-INTERP | Interpolated Ground | 92033.25 | 4.33 | 421.42 | 0 | 35.55 | 0 | OK | Ground clear controls. | 209 | 59.1 | 456.97
14405 | TIN-INTERP | Interpolated Ground | 92034.99 | -6.58 | 420.39 | 0 | 36.55 | 0 | OK | Ground clear controls. | 209 | 59.1 | 456.94
14406 | TIN-INTERP | Interpolated Ground | 92035.03 | -7.17 | 420.31 | 0 | 24.79 | 0 | OK | Ground clear controls. | 209 | 59.1 | 445.1
14407 | TIN-INTERP | Interpolated Ground | 92035.38 | -8.68 | 420.04 | 0 | 31.05 | 0 | OK | Ground clear controls. | 209 | 59.1 | 451.09
14408 | TIN-INTERP | Interpolated Ground | 92072.96 | 6.45 | 420.4 | 0 | 26.48 | 0 | OK | Ground clear controls. | 209 | 59.1 | 446.88
14409 | TIN-INTERP | Interpolated Ground | 92073.12 | 4.95 | 420.38 | 0 | 20.78 | 0 | OK | Ground clear controls. | 209 | 59.1 | 441.16
14410 | TIN-INTERP | Interpolated Ground | 92073.25 | 4.34 | 420.34 | 0 | 32.32 | 0 | OK | Ground clear controls. | 209 | 59.1 | 452.66
14411 | TIN-INTERP | Interpolated Ground | 92074.99 | -6.38 | 421 | 0 | 31.65 | 0 | OK | Ground clear controls. | 209 | 59.1 | 452.65
14412 | TIN-INTERP | Interpolated Ground | 92075.03 | -6.96 | 421.03 | 0 | 19.85 | 0 | OK | Ground clear controls. | 209 | 59.1 | 440.88
14413 | TIN-INTERP | Interpolated Ground | 92075.38 | -8.47 | 421.12 | 0 | 25.77 | 0 | OK | Ground clear controls. | 209 | 59.1 | 446.89
14414 | TIN-INTERP | Interpolated Ground | 92112.96 | 6.46 | 418.14 | 0 | 25.44 | 0 | OK | Ground clear controls. | 209 | 59.1 | 443.58
14415 | TIN-INTERP | Interpolated Ground | 92113.12 | 4.95 | 418.63 | 0 | 19.25 | 0 | OK | Ground clear controls. | 209 | 59.1 | 437.88
14416 | TIN-INTERP | Interpolated Ground | 92113.25 | 4.36 | 418.76 | 0 | 30.54 | 0 | OK | Ground clear controls. | 209 | 59.1 | 449.3
14417 | TIN-INTERP | Interpolated Ground | 92114.99 | -6.18 | 419.21 | 0 | 30.08 | 0 | OK | Ground clear controls. | 209 | 59.1 | 449.29
14418 | TIN-INTERP | Interpolated Ground | 92115.03 | -6.74 | 419.22 | 0 | 18.37 | 0 | OK | Ground clear controls. | 209 | 59.1 | 437.59
14419 | TIN-INTERP | Interpolated Ground | 92115.38 | -8.25 | 419.2 | 0 | 24.42 | 0 | OK | Ground clear controls. | 209 | 59.1 | 443.62
14420 | TIN-INTERP | Interpolated Ground | 92152.96 | 6.46 | 406.66 | 0 | 34.57 | 0 | OK | Ground clear controls. | 209 | 59.1 | 441.23
14421 | TIN-INTERP | Interpolated Ground | 92153.12 | 4.96 | 406.27 | 0 | 29.27 | 0 | OK | Ground clear controls. | 209 | 59.1 | 435.54
14422 | TIN-INTERP | Interpolated Ground | 92153.25 | 4.38 | 406.07 | 0 | 40.81 | 0 | OK | Ground clear controls. | 209 | 59.1 | 446.88
14423 | TIN-INTERP | Interpolated Ground | 92154.99 | -5.98 | 406.14 | 0 | 40.74 | 0 | OK | Ground clear controls. | 209 | 59.1 | 446.88
14424 | TIN-INTERP | Interpolated Ground | 92155.03 | -6.53 | 406 | 0 | 29.27 | 0 | OK | Ground clear controls. | 209 | 59.1 | 435.27
14425 | TIN-INTERP | Interpolated Ground | 92155.37 | -8.04 | 405.58 | 0 | 35.71 | 0 | OK | Ground clear controls. | 209 | 59.1 | 441.29
14426 | TIN-INTERP | Interpolated Ground | 92192.96 | 6.47 | 395.86 | 0 | 43.92 | 0 | OK | Ground clear controls. | 209 | 59.1 | 439.78
14427 | TIN-INTERP | Interpolated Ground | 92193.12 | 4.97 | 395.39 | 0 | 38.74 | 0 | OK | Ground clear controls. | 209 | 59.1 | 434.13
14428 | TIN-INTERP | Interpolated Ground | 92193.25 | 4.4 | 394.88 | 0 | 50.51 | 0 | OK | Ground clear controls. | 209 | 59.1 | 445.39
14429 | TIN-INTERP | Interpolated Ground | 92194.99 | -5.77 | 392.16 | 0 | 53.25 | 0 | OK | Ground clear controls. | 209 | 59.1 | 445.41
14430 | TIN-INTERP | Interpolated Ground | 92195.03 | -6.32 | 392.08 | 0 | 41.81 | 0 | OK | Ground clear controls. | 209 | 59.1 | 433.89
14431 | TIN-INTERP | Interpolated Ground | 92195.37 | -7.83 | 391.76 | 0 | 48.12 | 0 | OK | Ground clear controls. | 209 | 59.1 | 439.88
14432 | TIN-INTERP | Interpolated Ground | 92232.96 | 6.48 | 393.52 | 0 | 45.76 | 0 | OK | Ground clear controls. | 209 | 59.1 | 439.28
14433 | TIN-INTERP | Interpolated Ground | 92233.12 | 4.97 | 393.2 | 0 | 40.45 | 0 | OK | Ground clear controls. | 209 | 59.1 | 433.65
14434 | TIN-INTERP | Interpolated Ground | 92233.25 | 4.42 | 393.06 | 0 | 51.79 | 0 | OK | Ground clear controls. | 209 | 59.1 | 444.85
14435 | TIN-INTERP | Interpolated Ground | 92234.99 | -5.57 | 389.99 | 0 | 54.91 | 0 | OK | Ground clear controls. | 209 | 59.1 | 444.9
14436 | TIN-INTERP | Interpolated Ground | 92235.03 | -6.11 | 389.78 | 0 | 43.69 | 0 | OK | Ground clear controls. | 209 | 59.1 | 433.47
14437 | TIN-INTERP | Interpolated Ground | 92235.37 | -7.62 | 389.31 | 0 | 50.09 | 0 | OK | Ground clear controls. | 209 | 59.1 | 439.4
14438 | TIN-INTERP | Interpolated Ground | 92272.96 | 6.48 | 386.58 | 0 | 53.11 | 0 | OK | Ground clear controls. | 209 | 59.1 | 439.69
14439 | TIN-INTERP | Interpolated Ground | 92273.12 | 4.98 | 386.54 | 0 | 47.55 | 0 | OK | Ground clear controls. | 209 | 59.1 | 434.09
14440 | TIN-INTERP | Interpolated Ground | 92273.25 | 4.44 | 386.51 | 0 | 58.73 | 0 | OK | Ground clear controls. | 209 | 59.1 | 445.24
14441 | TIN-INTERP | Interpolated Ground | 92274.99 | -5.37 | 386.2 | 0 | 59.1 | 0 | OK | Ground clear controls. | 209 | 59.1 | 445.3
14442 | TIN-INTERP | Interpolated Ground | 92275.03 | -5.9 | 386.14 | 0 | 47.83 | 0 | OK | Ground clear controls. | 209 | 53.92 | 433.97
14443 | TIN-INTERP | Interpolated Ground | 92275.37 | -7.4 | 385.92 | 0 | 53.92 | 0 | OK | Ground clear controls. | 209 | 53.92 | 439.84
14444 | TIN-INTERP | Interpolated Ground | 92312.96 | 6.49 | 393.08 | 0 | 47.96 | 0 | OK | Ground clear controls. | 209 | 53.44 | 441.04
14445 | TIN-INTERP | Interpolated Ground | 92313.12 | 4.99 | 393.09 | 0 | 42.39 | 0 | OK | Ground clear controls. | 209 | 53.44 | 435.48
14446 | TIN-INTERP | Interpolated Ground | 92313.25 | 4.46 | 393.13 | 0 | 53.44 | 0 | OK | Ground clear controls. | 209 | 53.44 | 446.57
14447 | TIN-INTERP | Interpolated Ground | 92314.99 | -5.17 | 393.93 | 0 | 52.73 | 0 | OK | Ground clear controls. | 209 | 52.73 | 446.66
14448 | TIN-INTERP | Interpolated Ground | 92315.03 | -5.69 | 394.02 | 0 | 41.42 | 0 | OK | Ground clear controls. | 209 | 47.12 | 435.44
14449 | TIN-INTERP | Interpolated Ground | 92315.37 | -7.19 | 394.1 | 0 | 47.12 | 0 | OK | Ground clear controls. | 209 | 47.12 | 441.22
14450 | TIN-INTERP | Interpolated Ground | 92352.96 | 6.49 | 403.93 | 0 | 39.38 | 0 | OK | Ground clear controls. | 209 | 44.69 | 443.31
14451 | TIN-INTERP | Interpolated Ground | 92353.12 | 4.99 | 404.11 | 0 | 33.67 | 0 | OK | Ground clear controls. | 209 | 44.69 | 437.78
14452 | TIN-INTERP | Interpolated Ground | 92353.25 | 4.48 | 404.14 | 0 | 44.69 | 0 | OK | Ground clear controls. | 209 | 44.69 | 448.83
14453 | TIN-INTERP | Interpolated Ground | 92354.99 | -4.97 | 404.78 | 0 | 44.18 | 0 | OK | Ground clear controls. | 209 | 44.18 | 448.96
14454 | TIN-INTERP | Interpolated Ground | 92355.03 | -5.48 | 404.82 | 0 | 33.03 | 0 | OK | Ground clear controls. | 209 | 38.58 | 437.85
14455 | TIN-INTERP | Interpolated Ground | 92355.37 | -6.98 | 404.94 | 0 | 38.58 | 0 | OK | Ground clear controls. | 209 | 38.58 | 443.52
14456 | TIN-INTERP | Interpolated Ground | 92392.96 | 6.5 | 422.23 | 0 | 24.28 | 0 | OK | Ground clear controls. | 209 | 29.72 | 446.51
14457 | TIN-INTERP | Interpolated Ground | 92393.12 | 5 | 422.3 | 0 | 18.72 | 0 | OK | Ground clear controls. | 209 | 29.72 | 441.02
14458 | TIN-INTERP | Interpolated Ground | 92393.25 | 4.5 | 422.32 | 0 | 29.72 | 0 | OK | Ground clear controls. | 209 | 29.72 | 452.04
14459 | TIN-INTERP | Interpolated Ground | 92394.99 | -4.77 | 422.9 | 0 | 29.31 | 0 | OK | Ground clear controls. | 209 | 29.31 | 452.21
14460 | TIN-INTERP | Interpolated Ground | 92395.03 | -5.27 | 422.91 | 0 | 18.29 | 0 | OK | Ground clear controls. | 209 | 23.86 | 441.2
14461 | TIN-INTERP | Interpolated Ground | 92395.37 | -6.77 | 422.88 | 0 | 23.86 | 0 | OK | Ground clear controls. | 209 | 23.86 | 446.74
14462 | TIN-INTERP | Interpolated Ground | 92397.43 | -4.75 | 422.61 | 0 | 29.82 | 0 | OK | Ground clear controls. | 210 | 54.02 | 452.43
14463 | TIN-INTERP | Interpolated Ground | 92397.47 | 6.5 | 422.4 | 0 | 24.53 | 0 | OK | Ground clear controls. | 210 | 54.02 | 446.93
14464 | TIN-INTERP | Interpolated Ground | 92397.49 | -5.25 | 422.59 | 0 | 18.84 | 0 | OK | Ground clear controls. | 210 | 54.02 | 441.43
14465 | TIN-INTERP | Interpolated Ground | 92397.5 | -6.76 | 422.56 | 0 | 24.38 | 0 | OK | Ground clear controls. | 210 | 54.02 | 446.94
14466 | TIN-INTERP | Interpolated Ground | 92397.5 | 4.5 | 422.4 | 0 | 30.03 | 0 | OK | Ground clear controls. | 210 | 54.02 | 452.43
14467 | TIN-INTERP | Interpolated Ground | 92397.51 | 5 | 422.4 | 0 | 19.04 | 0 | OK | Ground clear controls. | 210 | 54.02 | 441.44
14468 | TIN-INTERP | Interpolated Ground | 92437.43 | -4.74 | 426.26 | 0 | 21.31 | 0 | OK | Ground clear controls. | 210 | 54.02 | 447.57
14469 | TIN-INTERP | Interpolated Ground | 92437.47 | 6.52 | 425.69 | 0 | 16.42 | 0 | OK | Ground clear controls. | 210 | 54.02 | 442.11
14470 | TIN-INTERP | Interpolated Ground | 92437.49 | -5.24 | 426.25 | 0 | 10.33 | 0 | OK | Ground clear controls. | 210 | 54.02 | 436.58
14471 | TIN-INTERP | Interpolated Ground | 92437.5 | -6.74 | 426.13 | 0 | 16.05 | 0 | OK | Ground clear controls. | 210 | 54.02 | 442.18
14472 | TIN-INTERP | Interpolated Ground | 92437.5 | 4.52 | 425.65 | 0 | 21.93 | 0 | OK | Ground clear controls. | 210 | 54.02 | 447.58
14473 | TIN-INTERP | Interpolated Ground | 92437.51 | 5.02 | 425.67 | 0 | 10.96 | 0 | OK | Ground clear controls. | 210 | 54.02 | 436.63
14474 | TIN-INTERP | Interpolated Ground | 92477.43 | -4.73 | 406.85 | 0 | 36.79 | 0 | OK | Ground clear controls. | 210 | 54.02 | 443.64
14475 | TIN-INTERP | Interpolated Ground | 92477.47 | 6.54 | 404.16 | 0 | 34.06 | 0 | OK | Ground clear controls. | 210 | 54.02 | 438.22
14476 | TIN-INTERP | Interpolated Ground | 92477.49 | -5.23 | 407 | 0 | 25.65 | 0 | OK | Ground clear controls. | 210 | 54.02 | 432.65
14477 | TIN-INTERP | Interpolated Ground | 92477.5 | -6.73 | 407.38 | 0 | 30.94 | 0 | OK | Ground clear controls. | 210 | 54.02 | 438.32
14478 | TIN-INTERP | Interpolated Ground | 92477.5 | 4.53 | 404.71 | 0 | 38.95 | 0 | OK | Ground clear controls. | 210 | 54.02 | 443.66
14479 | TIN-INTERP | Interpolated Ground | 92477.51 | 5.04 | 404.51 | 0 | 28.23 | 0 | OK | Ground clear controls. | 210 | 54.02 | 432.74
14480 | TIN-INTERP | Interpolated Ground | 92517.43 | -4.71 | 400.79 | 0 | 39.86 | 0 | OK | Ground clear controls. | 210 | 54.02 | 440.65
14481 | TIN-INTERP | Interpolated Ground | 92517.47 | 6.55 | 397.33 | 0 | 37.92 | 0 | OK | Ground clear controls. | 210 | 54.02 | 435.25
14482 | TIN-INTERP | Interpolated Ground | 92517.49 | -5.21 | 400.98 | 0 | 28.68 | 0 | OK | Ground clear controls. | 210 | 54.02 | 429.66
14483 | TIN-INTERP | Interpolated Ground | 92517.5 | -6.71 | 401.54 | 0 | 33.85 | 0 | OK | Ground clear controls. | 210 | 54.02 | 435.39
14484 | TIN-INTERP | Interpolated Ground | 92517.5 | 4.55 | 397.98 | 0 | 42.7 | 0 | OK | Ground clear controls. | 210 | 54.02 | 440.68
14485 | TIN-INTERP | Interpolated Ground | 92517.51 | 5.05 | 397.81 | 0 | 31.97 | 0 | OK | Ground clear controls. | 210 | 54.02 | 429.78
14486 | TIN-INTERP | Interpolated Ground | 92557.43 | -4.7 | 396.42 | 0 | 42.17 | 0 | OK | Ground clear controls. | 210 | 54.02 | 438.59
14487 | TIN-INTERP | Interpolated Ground | 92557.47 | 6.57 | 394.16 | 0 | 39.05 | 0 | OK | Ground clear controls. | 210 | 54.02 | 433.21
14488 | TIN-INTERP | Interpolated Ground | 92557.49 | -5.2 | 396.6 | 0 | 31.01 | 0 | OK | Ground clear controls. | 210 | 54.02 | 427.61
14489 | TIN-INTERP | Interpolated Ground | 92557.5 | -6.7 | 397.1 | 0 | 36.27 | 0 | OK | Ground clear controls. | 210 | 54.02 | 433.37
14490 | TIN-INTERP | Interpolated Ground | 92557.5 | 4.56 | 394.6 | 0 | 44.03 | 0 | OK | Ground clear controls. | 210 | 54.02 | 438.63
14491 | TIN-INTERP | Interpolated Ground | 92557.51 | 5.07 | 394.49 | 0 | 33.25 | 0 | OK | Ground clear controls. | 210 | 54.02 | 427.74
14492 | TIN-INTERP | Interpolated Ground | 92597.43 | -4.68 | 385.29 | 0 | 52.17 | 0 | OK | Ground clear controls. | 210 | 54.02 | 437.46
14493 | TIN-INTERP | Interpolated Ground | 92597.47 | 6.59 | 383.12 | 0 | 48.96 | 0 | OK | Ground clear controls. | 210 | 54.02 | 432.08
14494 | TIN-INTERP | Interpolated Ground | 92597.49 | -5.19 | 385.3 | 0 | 41.17 | 0 | OK | Ground clear controls. | 210 | 54.02 | 426.47
14495 | TIN-INTERP | Interpolated Ground | 92597.5 | -6.69 | 385.42 | 0 | 46.85 | 0 | OK | Ground clear controls. | 210 | 54.02 | 432.27
14496 | TIN-INTERP | Interpolated Ground | 92597.5 | 4.58 | 383.48 | 0 | 54.02 | 0 | OK | Ground clear controls. | 210 | 54.02 | 437.5
14497 | TIN-INTERP | Interpolated Ground | 92597.51 | 5.09 | 383.4 | 0 | 43.23 | 0 | OK | Ground clear controls. | 210 | 43.23 | 426.63
14498 | TIN-INTERP | Interpolated Ground | 92637.43 | -4.67 | 395.11 | 0 | 42.15 | 0 | OK | Ground clear controls. | 210 | 42.15 | 437.26
14499 | TIN-INTERP | Interpolated Ground | 92637.47 | 6.6 | 397.03 | 0 | 34.87 | 0 | OK | Ground clear controls. | 210 | 40.61 | 431.9
14500 | TIN-INTERP | Interpolated Ground | 92637.49 | -5.17 | 395.03 | 0 | 31.26 | 0 | OK | Ground clear controls. | 210 | 40.61 | 426.29
14501 | TIN-INTERP | Interpolated Ground | 92637.5 | -6.67 | 394.87 | 0 | 37.2 | 0 | OK | Ground clear controls. | 210 | 40.61 | 432.07
14502 | TIN-INTERP | Interpolated Ground | 92637.5 | 4.6 | 396.69 | 0 | 40.61 | 0 | OK | Ground clear controls. | 210 | 40.61 | 437.3
14503 | TIN-INTERP | Interpolated Ground | 92637.51 | 5.1 | 396.78 | 0 | 29.65 | 0 | OK | Ground clear controls. | 210 | 37.31 | 426.43
14504 | TIN-INTERP | Interpolated Ground | 92677.43 | -4.66 | 401.73 | 0 | 36.27 | 0 | OK | Ground clear controls. | 210 | 37.31 | 438
14505 | TIN-INTERP | Interpolated Ground | 92677.47 | 6.62 | 400.57 | 0 | 32.05 | 0 | OK | Ground clear controls. | 210 | 37.31 | 432.62
14506 | TIN-INTERP | Interpolated Ground | 92677.49 | -5.16 | 401.8 | 0 | 25.22 | 0 | OK | Ground clear controls. | 210 | 37.31 | 427.02
14507 | TIN-INTERP | Interpolated Ground | 92677.5 | -6.66 | 401.98 | 0 | 30.81 | 0 | OK | Ground clear controls. | 210 | 37.31 | 432.79
14508 | TIN-INTERP | Interpolated Ground | 92677.5 | 4.61 | 400.72 | 0 | 37.31 | 0 | OK | Ground clear controls. | 210 | 37.31 | 438.03
14509 | TIN-INTERP | Interpolated Ground | 92677.51 | 5.12 | 400.7 | 0 | 26.46 | 0 | OK | Ground clear controls. | 210 | 33.79 | 427.16
14510 | TIN-INTERP | Interpolated Ground | 92717.43 | -4.64 | 406.71 | 0 | 32.96 | 0 | OK | Ground clear controls. | 210 | 33.79 | 439.67
14511 | TIN-INTERP | Interpolated Ground | 92717.47 | 6.64 | 405.95 | 0 | 28.32 | 0 | OK | Ground clear controls. | 210 | 33.79 | 434.27
14512 | TIN-INTERP | Interpolated Ground | 92717.49 | -5.15 | 406.76 | 0 | 21.94 | 0 | OK | Ground clear controls. | 210 | 33.79 | 428.7
14513 | TIN-INTERP | Interpolated Ground | 92717.5 | -6.65 | 406.86 | 0 | 27.56 | 0 | OK | Ground clear controls. | 210 | 33.79 | 434.42
14514 | TIN-INTERP | Interpolated Ground | 92717.5 | 4.63 | 405.92 | 0 | 33.79 | 0 | OK | Ground clear controls. | 210 | 33.79 | 439.71
14515 | TIN-INTERP | Interpolated Ground | 92717.51 | 5.14 | 405.91 | 0 | 22.9 | 0 | OK | Ground clear controls. | 210 | 30.08 | 428.81
14516 | TIN-INTERP | Interpolated Ground | 92757.43 | -4.63 | 414.45 | 0 | 27.82 | 0 | OK | Ground clear controls. | 210 | 30.08 | 442.27
14517 | TIN-INTERP | Interpolated Ground | 92757.47 | 6.65 | 413.98 | 0 | 22.86 | 0 | OK | Ground clear controls. | 210 | 30.08 | 436.84
14518 | TIN-INTERP | Interpolated Ground | 92757.49 | -5.13 | 414.48 | 0 | 16.82 | 0 | OK | Ground clear controls. | 210 | 30.08 | 431.3
14519 | TIN-INTERP | Interpolated Ground | 92757.5 | -6.63 | 414.47 | 0 | 22.49 | 0 | OK | Ground clear controls. | 210 | 30.08 | 436.96
14520 | TIN-INTERP | Interpolated Ground | 92757.5 | 4.65 | 414.09 | 0 | 28.21 | 0 | OK | Ground clear controls. | 210 | 30.08 | 442.3
14521 | TIN-INTERP | Interpolated Ground | 92757.51 | 5.15 | 414.07 | 0 | 17.31 | 0 | OK | Ground clear controls. | 210 | 30.08 | 431.38
14522 | TIN-INTERP | Interpolated Ground | 92797.43 | -4.61 | 418.04 | 0 | 27.77 | 0 | OK | Ground clear controls. | 210 | 30.08 | 445.81
14523 | TIN-INTERP | Interpolated Ground | 92797.47 | 6.67 | 415.44 | 0 | 24.91 | 0 | OK | Ground clear controls. | 210 | 30.08 | 440.35
14524 | TIN-INTERP | Interpolated Ground | 92797.49 | -5.12 | 418.23 | 0 | 16.61 | 0 | OK | Ground clear controls. | 210 | 30.08 | 434.84
14525 | TIN-INTERP | Interpolated Ground | 92797.5 | -6.62 | 418.74 | 0 | 21.67 | 0 | OK | Ground clear controls. | 210 | 30.08 | 440.41
14526 | TIN-INTERP | Interpolated Ground | 92797.5 | 4.66 | 415.75 | 0 | 30.08 | 0 | OK | Ground clear controls. | 210 | 30.08 | 445.83
14527 | TIN-INTERP | Interpolated Ground | 92797.51 | 5.17 | 415.66 | 0 | 19.21 | 0 | OK | Ground clear controls. | 210 | 19.21 | 434.87
14528 | TIN-INTERP | Interpolated Ground | 92832.14 | -5.11 | 419.24 | 0 | 19.41 | 0 | OK | Ground clear controls. | 211 | 37.89 | 438.65
14529 | TIN-INTERP | Interpolated Ground | 92832.22 | 5.19 | 416.87 | 0 | 21.79 | 0 | OK | Ground clear controls. | 211 | 37.89 | 438.66
14530 | TIN-INTERP | Interpolated Ground | 92832.24 | -6.61 | 419.38 | 0 | 24.77 | 0 | OK | Ground clear controls. | 211 | 37.89 | 444.15
14531 | TIN-INTERP | Interpolated Ground | 92832.26 | 4.68 | 417.08 | 0 | 32.57 | 0 | OK | Ground clear controls. | 211 | 37.89 | 449.65
14532 | TIN-INTERP | Interpolated Ground | 92832.28 | -4.6 | 419.16 | 0 | 30.49 | 0 | OK | Ground clear controls. | 211 | 37.89 | 449.65
14533 | TIN-INTERP | Interpolated Ground | 92832.31 | 6.69 | 416.39 | 0 | 27.76 | 0 | OK | Ground clear controls. | 211 | 37.89 | 444.15
14534 | TIN-INTERP | Interpolated Ground | 92872.14 | -5.11 | 412.11 | 0 | 19.82 | 0 | OK | Ground clear controls. | 211 | 37.89 | 431.93
14535 | TIN-INTERP | Interpolated Ground | 92872.22 | 5.62 | 410.84 | 0 | 21.13 | 0 | OK | Ground clear controls. | 211 | 37.89 | 431.97
14536 | TIN-INTERP | Interpolated Ground | 92872.24 | -6.61 | 412.18 | 0 | 25.39 | 0 | OK | Ground clear controls. | 211 | 37.89 | 437.57
14537 | TIN-INTERP | Interpolated Ground | 92872.25 | 5.08 | 410.9 | 0 | 32.22 | 0 | OK | Ground clear controls. | 211 | 37.89 | 443.12
14538 | TIN-INTERP | Interpolated Ground | 92872.28 | -4.58 | 411.97 | 0 | 31.17 | 0 | OK | Ground clear controls. | 211 | 37.89 | 443.14
14539 | TIN-INTERP | Interpolated Ground | 92872.31 | 7.12 | 410.69 | 0 | 26.85 | 0 | OK | Ground clear controls. | 211 | 37.89 | 437.54
14540 | TIN-INTERP | Interpolated Ground | 92912.14 | -5.11 | 400.56 | 0 | 25.61 | 0 | OK | Ground clear controls. | 211 | 37.89 | 426.17
14541 | TIN-INTERP | Interpolated Ground | 92912.22 | 6.06 | 399.66 | 0 | 26.57 | 0 | OK | Ground clear controls. | 211 | 37.89 | 426.23
14542 | TIN-INTERP | Interpolated Ground | 92912.24 | -6.6 | 400.64 | 0 | 31.27 | 0 | OK | Ground clear controls. | 211 | 37.89 | 431.91
14543 | TIN-INTERP | Interpolated Ground | 92912.25 | 5.48 | 399.66 | 0 | 37.89 | 0 | OK | Ground clear controls. | 211 | 37.89 | 437.55
14544 | TIN-INTERP | Interpolated Ground | 92912.28 | -4.56 | 400.5 | 0 | 37.07 | 0 | OK | Ground clear controls. | 211 | 37.07 | 437.57
14545 | TIN-INTERP | Interpolated Ground | 92912.3 | 7.56 | 399.54 | 0 | 32.31 | 0 | OK | Ground clear controls. | 211 | 37.05 | 431.85
14546 | TIN-INTERP | Interpolated Ground | 92952.14 | -5.12 | 396.4 | 0 | 24.97 | 0 | OK | Ground clear controls. | 211 | 37.05 | 421.37
14547 | TIN-INTERP | Interpolated Ground | 92952.21 | 6.5 | 395.86 | 0 | 25.58 | 0 | OK | Ground clear controls. | 211 | 37.05 | 421.44
14548 | TIN-INTERP | Interpolated Ground | 92952.24 | -6.6 | 396.43 | 0 | 30.75 | 0 | OK | Ground clear controls. | 211 | 37.05 | 427.18
14549 | TIN-INTERP | Interpolated Ground | 92952.25 | 5.88 | 395.85 | 0 | 37.05 | 0 | OK | Ground clear controls. | 211 | 37.05 | 432.9
14550 | TIN-INTERP | Interpolated Ground | 92952.28 | -4.54 | 396.38 | 0 | 36.56 | 0 | OK | Ground clear controls. | 211 | 36.56 | 432.94
14551 | TIN-INTERP | Interpolated Ground | 92952.3 | 8 | 395.83 | 0 | 31.28 | 0 | OK | Ground clear controls. | 211 | 36.4 | 427.11
14552 | TIN-INTERP | Interpolated Ground | 92992.14 | -5.12 | 395.08 | 0 | 22.44 | 0 | OK | Ground clear controls. | 211 | 36.4 | 417.52
14553 | TIN-INTERP | Interpolated Ground | 92992.21 | 6.93 | 395.37 | 0 | 22.2 | 0 | OK | Ground clear controls. | 211 | 36.4 | 417.57
14554 | TIN-INTERP | Interpolated Ground | 92992.24 | -6.6 | 394.97 | 0 | 28.42 | 0 | OK | Ground clear controls. | 211 | 36.4 | 423.39
14555 | TIN-INTERP | Interpolated Ground | 92992.25 | 6.29 | 395.33 | 0 | 33.88 | 0 | OK | Ground clear controls. | 211 | 36.4 | 429.21
14556 | TIN-INTERP | Interpolated Ground | 92992.28 | -4.52 | 395.11 | 0 | 34.15 | 0 | OK | Ground clear controls. | 211 | 36.4 | 429.26
14557 | TIN-INTERP | Interpolated Ground | 92992.3 | 8.43 | 395.32 | 0 | 27.97 | 0 | OK | Ground clear controls. | 211 | 36.4 | 423.29
14558 | TIN-INTERP | Interpolated Ground | 93032.14 | -5.12 | 394.07 | 0 | 20.56 | 0 | OK | Ground clear controls. | 211 | 36.4 | 414.63
14559 | TIN-INTERP | Interpolated Ground | 93032.21 | 7.37 | 389.71 | 0 | 24.94 | 0 | OK | Ground clear controls. | 211 | 36.4 | 414.65
14560 | TIN-INTERP | Interpolated Ground | 93032.24 | 6.69 | 390.06 | 0 | 36.4 | 0 | OK | Ground clear controls. | 211 | 36.4 | 426.46
14561 | TIN-INTERP | Interpolated Ground | 93032.24 | -6.6 | 394.44 | 0 | 26.06 | 0 | OK | Ground clear controls. | 211 | 32.48 | 420.5
14562 | TIN-INTERP | Interpolated Ground | 93032.28 | -4.5 | 394.04 | 0 | 32.48 | 0 | OK | Ground clear controls. | 211 | 32.48 | 426.52
14563 | TIN-INTERP | Interpolated Ground | 93032.3 | 8.87 | 389.26 | 0 | 31.15 | 0 | OK | Ground clear controls. | 211 | 31.77 | 420.41
14564 | TIN-INTERP | Interpolated Ground | 93072.14 | -5.12 | 393.45 | 0 | 19.24 | 0 | OK | Ground clear controls. | 211 | 31.77 | 412.69
14565 | TIN-INTERP | Interpolated Ground | 93072.21 | 7.8 | 392.91 | 0 | 19.74 | 0 | OK | Ground clear controls. | 211 | 31.77 | 412.65
14566 | TIN-INTERP | Interpolated Ground | 93072.24 | 7.09 | 392.88 | 0 | 31.77 | 0 | OK | Ground clear controls. | 211 | 31.77 | 424.65
14567 | TIN-INTERP | Interpolated Ground | 93072.24 | -6.6 | 393.56 | 0 | 24.99 | 0 | OK | Ground clear controls. | 211 | 31.35 | 418.55
14568 | TIN-INTERP | Interpolated Ground | 93072.28 | -4.47 | 393.37 | 0 | 31.35 | 0 | OK | Ground clear controls. | 211 | 31.35 | 424.72
14569 | TIN-INTERP | Interpolated Ground | 93072.29 | 9.31 | 392.95 | 0 | 25.49 | 0 | OK | Ground clear controls. | 211 | 25.49 | 418.44
14570 | TIN-INTERP | Interpolated Ground | 93093.71 | 9.54 | 390.58 | 0 | 27.18 | 0 | OK | Ground clear controls. | 212 | 41.53 | 417.76
14571 | TIN-INTERP | Interpolated Ground | 93093.82 | 7.31 | 390.5 | 0 | 33.55 | 0 | OK | Ground clear controls. | 212 | 41.53 | 424.05
14572 | TIN-INTERP | Interpolated Ground | 93093.83 | 8.04 | 390.5 | 0 | 21.47 | 0 | OK | Ground clear controls. | 212 | 41.53 | 411.97
14573 | TIN-INTERP | Interpolated Ground | 93094.48 | -6.6 | 390.31 | 0 | 27.54 | 0 | OK | Ground clear controls. | 212 | 41.53 | 417.85
14574 | TIN-INTERP | Interpolated Ground | 93094.48 | -5.14 | 390.25 | 0 | 21.78 | 0 | OK | Ground clear controls. | 212 | 41.53 | 412.03
14575 | TIN-INTERP | Interpolated Ground | 93094.48 | -4.46 | 390.12 | 0 | 34 | 0 | OK | Ground clear controls. | 212 | 41.53 | 424.12
14576 | TIN-INTERP | Interpolated Ground | 93133.91 | -6.58 | 380.7 | 0 | 29.07 | 0 | OK | Ground clear controls. | 212 | 41.53 | 409.77
14577 | TIN-INTERP | Interpolated Ground | 93134.01 | -4.45 | 380.63 | 0 | 35.2 | 0 | OK | Ground clear controls. | 212 | 41.53 | 415.83
14578 | TIN-INTERP | Interpolated Ground | 93134.15 | -5.13 | 380.57 | 0 | 23.22 | 0 | OK | Ground clear controls. | 212 | 41.53 | 403.79
14579 | TIN-INTERP | Interpolated Ground | 93134.79 | 7.17 | 382.03 | 0 | 33.75 | 0 | OK | Ground clear controls. | 212 | 41.53 | 415.78
14580 | TIN-INTERP | Interpolated Ground | 93134.89 | 7.89 | 382.14 | 0 | 21.69 | 0 | OK | Ground clear controls. | 212 | 41.53 | 403.83
14581 | TIN-INTERP | Interpolated Ground | 93134.96 | 9.39 | 382.34 | 0 | 27.33 | 0 | OK | Ground clear controls. | 212 | 41.53 | 409.67
14582 | TIN-INTERP | Interpolated Ground | 93173.91 | -6.58 | 374.5 | 0 | 28.14 | 0 | OK | Ground clear controls. | 212 | 41.53 | 402.64
14583 | TIN-INTERP | Interpolated Ground | 93174.01 | -4.46 | 374.63 | 0 | 33.85 | 0 | OK | Ground clear controls. | 212 | 41.53 | 408.48
14584 | TIN-INTERP | Interpolated Ground | 93174.15 | -5.13 | 374.56 | 0 | 21.95 | 0 | OK | Ground clear controls. | 212 | 41.53 | 396.51
14585 | TIN-INTERP | Interpolated Ground | 93174.79 | 7.02 | 375.36 | 0 | 33.09 | 0 | OK | Ground clear controls. | 212 | 41.53 | 408.45
14586 | TIN-INTERP | Interpolated Ground | 93174.89 | 7.72 | 375.37 | 0 | 21.28 | 0 | OK | Ground clear controls. | 212 | 41.53 | 396.65
14587 | TIN-INTERP | Interpolated Ground | 93174.96 | 9.22 | 375.44 | 0 | 27.06 | 0 | OK | Ground clear controls. | 212 | 41.53 | 402.5
14588 | TIN-INTERP | Interpolated Ground | 93213.91 | -6.59 | 368.15 | 0 | 28.3 | 0 | OK | Ground clear controls. | 212 | 41.53 | 396.45
14589 | TIN-INTERP | Interpolated Ground | 93214.01 | -4.47 | 368.23 | 0 | 33.89 | 0 | OK | Ground clear controls. | 212 | 41.53 | 402.12
14590 | TIN-INTERP | Interpolated Ground | 93214.15 | -5.13 | 368.18 | 0 | 22.04 | 0 | OK | Ground clear controls. | 212 | 41.53 | 390.22
14591 | TIN-INTERP | Interpolated Ground | 93214.79 | 6.86 | 368.08 | 0 | 34.03 | 0 | OK | Ground clear controls. | 212 | 41.53 | 402.11
14592 | TIN-INTERP | Interpolated Ground | 93214.89 | 7.54 | 368.07 | 0 | 22.36 | 0 | OK | Ground clear controls. | 212 | 41.53 | 390.43
14593 | TIN-INTERP | Interpolated Ground | 93214.96 | 9.05 | 368.12 | 0 | 28.18 | 0 | OK | Ground clear controls. | 212 | 41.53 | 396.3
14594 | TIN-INTERP | Interpolated Ground | 93253.91 | -6.59 | 365.14 | 0 | 26.06 | 0 | OK | Ground clear controls. | 212 | 41.53 | 391.2
14595 | TIN-INTERP | Interpolated Ground | 93254.01 | -4.48 | 365.13 | 0 | 31.58 | 0 | OK | Ground clear controls. | 212 | 41.53 | 396.71
14596 | TIN-INTERP | Interpolated Ground | 93254.15 | -5.13 | 365.1 | 0 | 19.77 | 0 | OK | Ground clear controls. | 212 | 41.53 | 384.87
14597 | TIN-INTERP | Interpolated Ground | 93254.79 | 6.7 | 365.64 | 0 | 31.08 | 0 | OK | Ground clear controls. | 212 | 41.53 | 396.72
14598 | TIN-INTERP | Interpolated Ground | 93254.89 | 7.37 | 365.63 | 0 | 19.53 | 0 | OK | Ground clear controls. | 212 | 41.53 | 385.16
14599 | TIN-INTERP | Interpolated Ground | 93254.96 | 8.88 | 365.67 | 0 | 25.37 | 0 | OK | Ground clear controls. | 212 | 41.53 | 391.04
14600 | TIN-INTERP | Interpolated Ground | 93293.91 | -6.59 | 359.9 | 0 | 26.98 | 0 | OK | Ground clear controls. | 212 | 41.53 | 386.88
14601 | TIN-INTERP | Interpolated Ground | 93294.01 | -4.49 | 360.56 | 0 | 31.69 | 0 | OK | Ground clear controls. | 212 | 41.53 | 392.25
14602 | TIN-INTERP | Interpolated Ground | 93294.15 | -5.13 | 360.31 | 0 | 20.17 | 0 | OK | Ground clear controls. | 212 | 41.53 | 380.48
14603 | TIN-INTERP | Interpolated Ground | 93294.79 | 6.54 | 361.65 | 0 | 30.63 | 0 | OK | Ground clear controls. | 212 | 41.53 | 392.28
14604 | TIN-INTERP | Interpolated Ground | 93294.89 | 7.2 | 361.69 | 0 | 19.13 | 0 | OK | Ground clear controls. | 212 | 41.53 | 380.82
14605 | TIN-INTERP | Interpolated Ground | 93294.96 | 8.7 | 361.58 | 0 | 25.14 | 0 | OK | Ground clear controls. | 212 | 41.53 | 386.72
14606 | TIN-INTERP | Interpolated Ground | 93333.91 | -6.6 | 353.68 | 0 | 29.82 | 0 | OK | Ground clear controls. | 212 | 41.53 | 383.5
14607 | TIN-INTERP | Interpolated Ground | 93334.01 | -4.5 | 354.85 | 0 | 33.92 | 0 | OK | Ground clear controls. | 212 | 41.53 | 388.77
14608 | TIN-INTERP | Interpolated Ground | 93334.15 | -5.13 | 354.53 | 0 | 22.53 | 0 | OK | Ground clear controls. | 212 | 41.53 | 377.06
14609 | TIN-INTERP | Interpolated Ground | 93334.79 | 6.38 | 357.87 | 0 | 30.95 | 0 | OK | Ground clear controls. | 212 | 41.53 | 388.82
14610 | TIN-INTERP | Interpolated Ground | 93334.89 | 7.03 | 357.96 | 0 | 19.48 | 0 | OK | Ground clear controls. | 212 | 41.53 | 377.44
14611 | TIN-INTERP | Interpolated Ground | 93334.96 | 8.53 | 358.23 | 0 | 25.11 | 0 | OK | Ground clear controls. | 212 | 41.53 | 383.34
14612 | TIN-INTERP | Interpolated Ground | 93373.91 | -6.6 | 353.11 | 0 | 27.94 | 0 | OK | Ground clear controls. | 212 | 41.53 | 381.05
14613 | TIN-INTERP | Interpolated Ground | 93374.01 | -4.52 | 353.31 | 0 | 32.92 | 0 | OK | Ground clear controls. | 212 | 41.53 | 386.23
14614 | TIN-INTERP | Interpolated Ground | 93374.15 | -5.13 | 353.2 | 0 | 21.38 | 0 | OK | Ground clear controls. | 212 | 41.53 | 374.58
14615 | TIN-INTERP | Interpolated Ground | 93374.79 | 6.23 | 353.28 | 0 | 33.01 | 0 | OK | Ground clear controls. | 212 | 41.53 | 386.29
14616 | TIN-INTERP | Interpolated Ground | 93374.89 | 6.86 | 353.28 | 0 | 21.72 | 0 | OK | Ground clear controls. | 212 | 41.53 | 375
14617 | TIN-INTERP | Interpolated Ground | 93374.96 | 8.36 | 353.27 | 0 | 27.62 | 0 | OK | Ground clear controls. | 212 | 41.53 | 380.89
14618 | TIN-INTERP | Interpolated Ground | 93413.91 | -6.6 | 348.06 | 0 | 31.48 | 0 | OK | Ground clear controls. | 212 | 41.53 | 379.54
14619 | TIN-INTERP | Interpolated Ground | 93414.01 | -4.53 | 348.12 | 0 | 36.53 | 0 | OK | Ground clear controls. | 212 | 41.53 | 384.65
14620 | TIN-INTERP | Interpolated Ground | 93414.15 | -5.13 | 348.11 | 0 | 24.96 | 0 | OK | Ground clear controls. | 212 | 41.53 | 373.07
14621 | TIN-INTERP | Interpolated Ground | 93414.79 | 6.07 | 347.73 | 0 | 36.99 | 0 | OK | Ground clear controls. | 212 | 41.53 | 384.72
14622 | TIN-INTERP | Interpolated Ground | 93414.89 | 6.69 | 347.77 | 0 | 25.74 | 0 | OK | Ground clear controls. | 212 | 41.53 | 373.51
14623 | TIN-INTERP | Interpolated Ground | 93414.96 | 8.19 | 347.67 | 0 | 31.72 | 0 | OK | Ground clear controls. | 212 | 41.53 | 379.39
14624 | TIN-INTERP | Interpolated Ground | 93453.91 | -6.61 | 342.5 | 0 | 36.46 | 0 | OK | Ground clear controls. | 212 | 41.53 | 378.96
14625 | TIN-INTERP | Interpolated Ground | 93454.01 | -4.54 | 342.49 | 0 | 41.53 | 0 | OK | Ground clear controls. | 212 | 41.53 | 384.02
14626 | TIN-INTERP | Interpolated Ground | 93454.15 | -5.13 | 342.49 | 0 | 30.01 | 0 | OK | Ground clear controls. | 212 | 39.39 | 372.5
14627 | TIN-INTERP | Interpolated Ground | 93454.79 | 5.91 | 344.72 | 0 | 39.39 | 0 | OK | Ground clear controls. | 212 | 39.39 | 384.11
14628 | TIN-INTERP | Interpolated Ground | 93454.89 | 6.52 | 344.8 | 0 | 28.15 | 0 | OK | Ground clear controls. | 212 | 39.32 | 372.95
14629 | TIN-INTERP | Interpolated Ground | 93454.96 | 8.02 | 344.92 | 0 | 33.9 | 0 | OK | Ground clear controls. | 212 | 39.32 | 378.82
14630 | TIN-INTERP | Interpolated Ground | 93493.91 | -6.61 | 346.4 | 0 | 32.9 | 0 | OK | Ground clear controls. | 212 | 39.32 | 379.3
14631 | TIN-INTERP | Interpolated Ground | 93494.01 | -4.55 | 346.18 | 0 | 38.16 | 0 | OK | Ground clear controls. | 212 | 39.32 | 384.34
14632 | TIN-INTERP | Interpolated Ground | 93494.15 | -5.13 | 346.27 | 0 | 26.62 | 0 | OK | Ground clear controls. | 212 | 39.32 | 372.89
14633 | TIN-INTERP | Interpolated Ground | 93494.79 | 5.75 | 345.12 | 0 | 39.32 | 0 | OK | Ground clear controls. | 212 | 39.32 | 384.44
14634 | TIN-INTERP | Interpolated Ground | 93494.89 | 6.35 | 345.05 | 0 | 28.29 | 0 | OK | Ground clear controls. | 212 | 34.37 | 373.34
14635 | TIN-INTERP | Interpolated Ground | 93494.96 | 7.85 | 344.82 | 0 | 34.37 | 0 | OK | Ground clear controls. | 212 | 34.37 | 379.19
14636 | TIN-INTERP | Interpolated Ground | 93533.91 | -6.61 | 353.87 | 0 | 26.71 | 0 | OK | Ground clear controls. | 212 | 32.6 | 380.58
14637 | TIN-INTERP | Interpolated Ground | 93534.01 | -4.56 | 353.87 | 0 | 31.74 | 0 | OK | Ground clear controls. | 212 | 32.6 | 385.61
14638 | TIN-INTERP | Interpolated Ground | 93534.15 | -5.13 | 353.93 | 0 | 20.3 | 0 | OK | Ground clear controls. | 212 | 32.6 | 374.23
14639 | TIN-INTERP | Interpolated Ground | 93534.79 | 5.6 | 353.12 | 0 | 32.6 | 0 | OK | Ground clear controls. | 212 | 32.6 | 385.72
14640 | TIN-INTERP | Interpolated Ground | 93534.89 | 6.18 | 353.04 | 0 | 21.63 | 0 | OK | Ground clear controls. | 212 | 30.04 | 374.67
14641 | TIN-INTERP | Interpolated Ground | 93534.96 | 7.68 | 352.85 | 0 | 27.64 | 0 | OK | Ground clear controls. | 212 | 30.04 | 380.49
14642 | TIN-INTERP | Interpolated Ground | 93573.91 | -6.61 | 361.16 | 0 | 21.63 | 0 | OK | Ground clear controls. | 212 | 30.04 | 382.79
14643 | TIN-INTERP | Interpolated Ground | 93574.01 | -4.57 | 360.79 | 0 | 27.05 | 0 | OK | Ground clear controls. | 212 | 30.04 | 387.84
14644 | TIN-INTERP | Interpolated Ground | 93574.15 | -5.13 | 360.92 | 0 | 15.6 | 0 | OK | Ground clear controls. | 212 | 30.04 | 376.52
14645 | TIN-INTERP | Interpolated Ground | 93574.79 | 5.44 | 359.26 | 0 | 28.7 | 0 | OK | Ground clear controls. | 212 | 30.04 | 387.96
14646 | TIN-INTERP | Interpolated Ground | 93574.89 | 6.01 | 359.18 | 0 | 17.76 | 0 | OK | Ground clear controls. | 212 | 30.04 | 376.94
14647 | TIN-INTERP | Interpolated Ground | 93574.96 | 7.51 | 358.96 | 0 | 23.77 | 0 | OK | Ground clear controls. | 212 | 30.04 | 382.73
14648 | TIN-INTERP | Interpolated Ground | 93613.91 | -6.62 | 364.58 | 0 | 21.34 | 0 | OK | Ground clear controls. | 212 | 30.04 | 385.92
14649 | TIN-INTERP | Interpolated Ground | 93614.01 | -4.58 | 364.42 | 0 | 26.6 | 0 | OK | Ground clear controls. | 212 | 30.04 | 391.02
14650 | TIN-INTERP | Interpolated Ground | 93614.15 | -5.13 | 364.49 | 0 | 15.27 | 0 | OK | Ground clear controls. | 212 | 30.04 | 379.76
14651 | TIN-INTERP | Interpolated Ground | 93614.79 | 5.28 | 363.22 | 0 | 27.92 | 0 | OK | Ground clear controls. | 212 | 30.04 | 391.14
14652 | TIN-INTERP | Interpolated Ground | 93614.89 | 5.84 | 363.19 | 0 | 16.96 | 0 | OK | Ground clear controls. | 212 | 30.04 | 380.15
14653 | TIN-INTERP | Interpolated Ground | 93614.96 | 7.34 | 363.02 | 0 | 22.88 | 0 | OK | Ground clear controls. | 212 | 30.04 | 385.9
14654 | TIN-INTERP | Interpolated Ground | 93653.91 | -6.62 | 369.46 | 0 | 20.54 | 0 | OK | Ground clear controls. | 212 | 30.04 | 390
14655 | TIN-INTERP | Interpolated Ground | 93654.01 | -4.59 | 369.15 | 0 | 26.01 | 0 | OK | Ground clear controls. | 212 | 30.04 | 395.16
14656 | TIN-INTERP | Interpolated Ground | 93654.15 | -5.13 | 369.27 | 0 | 14.7 | 0 | OK | Ground clear controls. | 212 | 30.04 | 383.97
14657 | TIN-INTERP | Interpolated Ground | 93654.79 | 5.12 | 367.9 | 0 | 27.39 | 0 | OK | Ground clear controls. | 212 | 30.04 | 395.29
14658 | TIN-INTERP | Interpolated Ground | 93654.89 | 5.67 | 367.91 | 0 | 16.41 | 0 | OK | Ground clear controls. | 212 | 30.04 | 384.32
14659 | TIN-INTERP | Interpolated Ground | 93654.96 | 7.17 | 367.76 | 0 | 22.27 | 0 | OK | Ground clear controls. | 212 | 30.04 | 390.03
14660 | TIN-INTERP | Interpolated Ground | 93693.91 | -6.62 | 374.78 | 0 | 20.23 | 0 | OK | Ground clear controls. | 212 | 30.04 | 395.01
14661 | TIN-INTERP | Interpolated Ground | 93694.01 | -4.6 | 374.63 | 0 | 25.62 | 0 | OK | Ground clear controls. | 212 | 30.04 | 400.25
14662 | TIN-INTERP | Interpolated Ground | 93694.15 | -5.13 | 374.68 | 0 | 14.44 | 0 | OK | Ground clear controls. | 212 | 30.04 | 389.12
14663 | TIN-INTERP | Interpolated Ground | 93694.78 | 4.97 | 373.03 | 0 | 27.36 | 0 | OK | Ground clear controls. | 212 | 30.04 | 400.39
14664 | TIN-INTERP | Interpolated Ground | 93694.89 | 5.5 | 372.93 | 0 | 16.49 | 0 | OK | Ground clear controls. | 212 | 30.04 | 389.42
14665 | TIN-INTERP | Interpolated Ground | 93694.96 | 7 | 372.77 | 0 | 22.31 | 0 | OK | Ground clear controls. | 212 | 30.04 | 395.08
14666 | TIN-INTERP | Interpolated Ground | 93733.91 | -6.63 | 378.17 | 0 | 22.79 | 0 | OK | Ground clear controls. | 212 | 30.04 | 400.96
14667 | TIN-INTERP | Interpolated Ground | 93734.01 | -4.61 | 377.98 | 0 | 28.33 | 0 | OK | Ground clear controls. | 212 | 30.04 | 406.31
14668 | TIN-INTERP | Interpolated Ground | 93734.15 | -5.13 | 378.07 | 0 | 17.17 | 0 | OK | Ground clear controls. | 212 | 30.04 | 395.24
14669 | TIN-INTERP | Interpolated Ground | 93734.78 | 4.81 | 377.69 | 0 | 28.76 | 0 | OK | Ground clear controls. | 212 | 30.04 | 406.45
14670 | TIN-INTERP | Interpolated Ground | 93734.89 | 5.33 | 377.7 | 0 | 17.78 | 0 | OK | Ground clear controls. | 212 | 30.04 | 395.48
14671 | TIN-INTERP | Interpolated Ground | 93734.96 | 6.83 | 377.67 | 0 | 23.42 | 0 | OK | Ground clear controls. | 212 | 30.04 | 401.09
14672 | TIN-INTERP | Interpolated Ground | 93773.91 | -6.63 | 383.18 | 0 | 24.68 | 0 | OK | Ground clear controls. | 212 | 30.04 | 407.86
14673 | TIN-INTERP | Interpolated Ground | 93774.01 | -4.62 | 383.3 | 0 | 30.04 | 0 | OK | Ground clear controls. | 212 | 30.04 | 413.34
14674 | TIN-INTERP | Interpolated Ground | 93774.15 | -5.13 | 383.25 | 0 | 19.08 | 0 | OK | Ground clear controls. | 212 | 29.09 | 402.33
14675 | TIN-INTERP | Interpolated Ground | 93774.78 | 4.65 | 384.39 | 0 | 29.09 | 0 | OK | Ground clear controls. | 212 | 29.09 | 413.48
14676 | TIN-INTERP | Interpolated Ground | 93774.88 | 5.16 | 384.5 | 0 | 17.99 | 0 | OK | Ground clear controls. | 212 | 23.33 | 402.49
14677 | TIN-INTERP | Interpolated Ground | 93774.96 | 6.66 | 384.71 | 0 | 23.33 | 0 | OK | Ground clear controls. | 212 | 23.33 | 408.04
14678 | TIN-INTERP | Interpolated Ground | 93789.39 | -4.63 | 383.16 | 0 | 33.12 | 0 | OK | Ground clear controls. | 213 | 49.9 | 416.28
14679 | TIN-INTERP | Interpolated Ground | 93789.4 | -5.13 | 383.06 | 0 | 22.22 | 0 | OK | Ground clear controls. | 213 | 49.9 | 405.28
14680 | TIN-INTERP | Interpolated Ground | 93789.41 | -6.63 | 382.74 | 0 | 28.04 | 0 | OK | Ground clear controls. | 213 | 49.9 | 410.78
14681 | TIN-INTERP | Interpolated Ground | 93789.42 | 4.59 | 384.66 | 0 | 31.62 | 0 | OK | Ground clear controls. | 213 | 49.9 | 416.28
14682 | TIN-INTERP | Interpolated Ground | 93789.43 | 6.59 | 384.95 | 0 | 25.83 | 0 | OK | Ground clear controls. | 213 | 49.9 | 410.78
14683 | TIN-INTERP | Interpolated Ground | 93789.46 | 5.09 | 384.74 | 0 | 20.54 | 0 | OK | Ground clear controls. | 213 | 49.9 | 405.28
14684 | TIN-INTERP | Interpolated Ground | 93829.39 | -4.63 | 377.62 | 0 | 29.6 | 0 | OK | Ground clear controls. | 213 | 49.9 | 407.22
14685 | TIN-INTERP | Interpolated Ground | 93829.4 | -5.13 | 377.44 | 0 | 18.79 | 0 | OK | Ground clear controls. | 213 | 49.9 | 396.23
14686 | TIN-INTERP | Interpolated Ground | 93829.41 | -6.63 | 376.9 | 0 | 24.95 | 0 | OK | Ground clear controls. | 213 | 49.9 | 401.85
14687 | TIN-INTERP | Interpolated Ground | 93829.42 | 4.59 | 380.17 | 0 | 27.07 | 0 | OK | Ground clear controls. | 213 | 49.9 | 407.24
14688 | TIN-INTERP | Interpolated Ground | 93829.42 | 6.59 | 380.64 | 0 | 21.19 | 0 | OK | Ground clear controls. | 213 | 49.9 | 401.83
14689 | TIN-INTERP | Interpolated Ground | 93829.46 | 5.09 | 380.24 | 0 | 16.08 | 0 | OK | Ground clear controls. | 213 | 49.9 | 396.32
14690 | TIN-INTERP | Interpolated Ground | 93869.39 | -4.62 | 367.15 | 0 | 31.99 | 0 | OK | Ground clear controls. | 213 | 49.9 | 399.14
14691 | TIN-INTERP | Interpolated Ground | 93869.4 | -5.12 | 367.02 | 0 | 21.14 | 0 | OK | Ground clear controls. | 213 | 49.9 | 388.16
14692 | TIN-INTERP | Interpolated Ground | 93869.41 | -6.62 | 366.67 | 0 | 27.2 | 0 | OK | Ground clear controls. | 213 | 49.9 | 393.87
14693 | TIN-INTERP | Interpolated Ground | 93869.42 | 4.59 | 369.61 | 0 | 29.58 | 0 | OK | Ground clear controls. | 213 | 49.9 | 399.19
14694 | TIN-INTERP | Interpolated Ground | 93869.42 | 6.59 | 370.09 | 0 | 23.74 | 0 | OK | Ground clear controls. | 213 | 49.9 | 393.83
14695 | TIN-INTERP | Interpolated Ground | 93869.46 | 5.09 | 369.72 | 0 | 18.61 | 0 | OK | Ground clear controls. | 213 | 49.9 | 388.33
14696 | TIN-INTERP | Interpolated Ground | 93909.39 | -4.62 | 358.06 | 0 | 34 | 0 | OK | Ground clear controls. | 213 | 49.9 | 392.06
14697 | TIN-INTERP | Interpolated Ground | 93909.4 | -5.12 | 357.94 | 0 | 23.13 | 0 | OK | Ground clear controls. | 213 | 49.9 | 381.07
14698 | TIN-INTERP | Interpolated Ground | 93909.41 | -6.62 | 357.61 | 0 | 29.25 | 0 | OK | Ground clear controls. | 213 | 49.9 | 386.86
14699 | TIN-INTERP | Interpolated Ground | 93909.42 | 4.59 | 360.1 | 0 | 32.03 | 0 | OK | Ground clear controls. | 213 | 49.9 | 392.13
14700 | TIN-INTERP | Interpolated Ground | 93909.42 | 6.59 | 360.44 | 0 | 26.37 | 0 | OK | Ground clear controls. | 213 | 49.9 | 386.81
14701 | TIN-INTERP | Interpolated Ground | 93909.46 | 5.09 | 360.18 | 0 | 21.13 | 0 | OK | Ground clear controls. | 213 | 49.9 | 381.31
14702 | TIN-INTERP | Interpolated Ground | 93949.39 | -4.62 | 347.03 | 0 | 38.92 | 0 | OK | Ground clear controls. | 213 | 49.9 | 385.95
14703 | TIN-INTERP | Interpolated Ground | 93949.4 | -5.12 | 346.91 | 0 | 28.06 | 0 | OK | Ground clear controls. | 213 | 49.9 | 374.97
14704 | TIN-INTERP | Interpolated Ground | 93949.41 | -6.62 | 346.65 | 0 | 34.14 | 0 | OK | Ground clear controls. | 213 | 49.9 | 380.79
14705 | TIN-INTERP | Interpolated Ground | 93949.42 | 4.59 | 349.16 | 0 | 36.88 | 0 | OK | Ground clear controls. | 213 | 49.9 | 386.04
14706 | TIN-INTERP | Interpolated Ground | 93949.42 | 6.59 | 349.91 | 0 | 30.84 | 0 | OK | Ground clear controls. | 213 | 49.9 | 380.75
14707 | TIN-INTERP | Interpolated Ground | 93949.46 | 5.09 | 349.32 | 0 | 25.92 | 0 | OK | Ground clear controls. | 213 | 49.9 | 375.24
14708 | TIN-INTERP | Interpolated Ground | 93989.39 | -4.61 | 337.45 | 0 | 43.37 | 0 | OK | Ground clear controls. | 213 | 49.9 | 380.82
14709 | TIN-INTERP | Interpolated Ground | 93989.4 | -5.11 | 337.37 | 0 | 32.47 | 0 | OK | Ground clear controls. | 213 | 49.9 | 369.84
14710 | TIN-INTERP | Interpolated Ground | 93989.41 | -6.61 | 337.1 | 0 | 38.59 | 0 | OK | Ground clear controls. | 213 | 49.9 | 375.69
14711 | TIN-INTERP | Interpolated Ground | 93989.42 | 4.59 | 339.28 | 0 | 41.63 | 0 | OK | Ground clear controls. | 213 | 49.9 | 380.91
14712 | TIN-INTERP | Interpolated Ground | 93989.42 | 6.58 | 339.71 | 0 | 35.92 | 0 | OK | Ground clear controls. | 213 | 49.9 | 375.63
14713 | TIN-INTERP | Interpolated Ground | 93989.46 | 5.09 | 339.33 | 0 | 30.8 | 0 | OK | Ground clear controls. | 213 | 49.9 | 370.13
14714 | TIN-INTERP | Interpolated Ground | 94029.39 | -4.61 | 332.25 | 0 | 44.42 | 0 | OK | Ground clear controls. | 213 | 49.9 | 376.67
14715 | TIN-INTERP | Interpolated Ground | 94029.4 | -5.11 | 332.22 | 0 | 33.47 | 0 | OK | Ground clear controls. | 213 | 49.9 | 365.69
14716 | TIN-INTERP | Interpolated Ground | 94029.41 | -6.61 | 332.14 | 0 | 39.4 | 0 | OK | Ground clear controls. | 213 | 49.9 | 371.54
14717 | TIN-INTERP | Interpolated Ground | 94029.42 | 4.58 | 333.03 | 0 | 43.73 | 0 | OK | Ground clear controls. | 213 | 49.9 | 376.76
14718 | TIN-INTERP | Interpolated Ground | 94029.42 | 6.58 | 333.26 | 0 | 38.22 | 0 | OK | Ground clear controls. | 213 | 49.9 | 371.48
14719 | TIN-INTERP | Interpolated Ground | 94029.46 | 5.08 | 333.05 | 0 | 32.92 | 0 | OK | Ground clear controls. | 213 | 49.9 | 365.97
14720 | TIN-INTERP | Interpolated Ground | 94069.39 | -4.6 | 328.05 | 0 | 45.44 | 0 | OK | Ground clear controls. | 213 | 49.9 | 373.49
14721 | TIN-INTERP | Interpolated Ground | 94069.4 | -5.11 | 328.06 | 0 | 34.45 | 0 | OK | Ground clear controls. | 213 | 49.9 | 362.51
14722 | TIN-INTERP | Interpolated Ground | 94069.41 | -6.6 | 328.1 | 0 | 40.23 | 0 | OK | Ground clear controls. | 213 | 49.9 | 368.33
14723 | TIN-INTERP | Interpolated Ground | 94069.42 | 4.58 | 327.91 | 0 | 45.67 | 0 | OK | Ground clear controls. | 213 | 49.9 | 373.58
14724 | TIN-INTERP | Interpolated Ground | 94069.42 | 6.58 | 328.1 | 0 | 40.18 | 0 | OK | Ground clear controls. | 213 | 49.9 | 368.28
14725 | TIN-INTERP | Interpolated Ground | 94069.46 | 5.08 | 327.95 | 0 | 34.81 | 0 | OK | Ground clear controls. | 213 | 49.9 | 362.76
14726 | TIN-INTERP | Interpolated Ground | 94109.39 | -4.6 | 321.86 | 0 | 49.43 | 0 | OK | Ground clear controls. | 213 | 49.9 | 371.29
14727 | TIN-INTERP | Interpolated Ground | 94109.4 | -5.1 | 321.88 | 0 | 38.42 | 0 | OK | Ground clear controls. | 213 | 49.9 | 360.3
14728 | TIN-INTERP | Interpolated Ground | 94109.41 | -6.6 | 322.13 | 0 | 43.93 | 0 | OK | Ground clear controls. | 213 | 49.9 | 366.06
14729 | TIN-INTERP | Interpolated Ground | 94109.42 | 4.58 | 321.46 | 0 | 49.9 | 0 | OK | Ground clear controls. | 213 | 49.9 | 371.36
14730 | TIN-INTERP | Interpolated Ground | 94109.42 | 6.58 | 321.28 | 0 | 44.74 | 0 | OK | Ground clear controls. | 213 | 44.74 | 366.02
14731 | TIN-INTERP | Interpolated Ground | 94109.46 | 5.08 | 321.43 | 0 | 39.09 | 0 | OK | Ground clear controls. | 213 | 40.36 | 360.52
14732 | TIN-INTERP | Interpolated Ground | 94149.39 | -4.6 | 331.5 | 0 | 38.54 | 0 | OK | Ground clear controls. | 213 | 40.36 | 370.04
14733 | TIN-INTERP | Interpolated Ground | 94149.4 | -5.1 | 331.62 | 0 | 27.45 | 0 | OK | Ground clear controls. | 213 | 40.36 | 359.07
14734 | TIN-INTERP | Interpolated Ground | 94149.41 | -6.6 | 331.95 | 0 | 32.79 | 0 | OK | Ground clear controls. | 213 | 40.36 | 364.74
14735 | TIN-INTERP | Interpolated Ground | 94149.42 | 4.58 | 329.75 | 0 | 40.36 | 0 | OK | Ground clear controls. | 213 | 40.36 | 370.11
14736 | TIN-INTERP | Interpolated Ground | 94149.42 | 6.58 | 329.31 | 0 | 35.39 | 0 | OK | Ground clear controls. | 213 | 35.39 | 364.7
14737 | TIN-INTERP | Interpolated Ground | 94149.46 | 5.08 | 329.68 | 0 | 29.53 | 0 | OK | Ground clear controls. | 213 | 29.63 | 359.21
14738 | TIN-INTERP | Interpolated Ground | 94189.39 | -4.59 | 341.19 | 0 | 28.6 | 0 | OK | Ground clear controls. | 213 | 29.63 | 369.79
14739 | TIN-INTERP | Interpolated Ground | 94189.4 | -5.1 | 341.18 | 0 | 17.61 | 0 | OK | Ground clear controls. | 213 | 29.63 | 358.79
14740 | TIN-INTERP | Interpolated Ground | 94189.41 | -6.59 | 341.32 | 0 | 23.05 | 0 | OK | Ground clear controls. | 213 | 29.63 | 364.37
14741 | TIN-INTERP | Interpolated Ground | 94189.42 | 4.58 | 340.19 | 0 | 29.63 | 0 | OK | Ground clear controls. | 213 | 29.63 | 369.82
14742 | TIN-INTERP | Interpolated Ground | 94189.42 | 6.57 | 340.02 | 0 | 24.33 | 0 | OK | Ground clear controls. | 213 | 24.33 | 364.35
14743 | TIN-INTERP | Interpolated Ground | 94189.46 | 5.08 | 340.14 | 0 | 18.71 | 0 | OK | Ground clear controls. | 213 | 18.71 | 358.85
14744 | TIN-INTERP | Interpolated Ground | 94214.64 | 4.58 | 344.35 | 0 | 25.79 | 0 | OK | Ground clear controls. | 214 | 38.2 | 370.14
14745 | TIN-INTERP | Interpolated Ground | 94214.7 | -6.59 | 345.06 | 0 | 19.56 | 0 | OK | Ground clear controls. | 214 | 38.2 | 364.62
14746 | TIN-INTERP | Interpolated Ground | 94214.71 | -5.09 | 344.89 | 0 | 14.22 | 0 | OK | Ground clear controls. | 214 | 38.2 | 359.11
14747 | TIN-INTERP | Interpolated Ground | 94214.71 | -4.59 | 344.85 | 0 | 25.27 | 0 | OK | Ground clear controls. | 214 | 38.2 | 370.12
14748 | TIN-INTERP | Interpolated Ground | 94214.86 | 5.08 | 344.33 | 0 | 14.78 | 0 | OK | Ground clear controls. | 214 | 38.2 | 359.11
14749 | TIN-INTERP | Interpolated Ground | 94214.9 | 6.57 | 344.15 | 0 | 20.46 | 0 | OK | Ground clear controls. | 214 | 38.2 | 364.61
14750 | TIN-INTERP | Interpolated Ground | 94254.64 | 4.5 | 339.03 | 0 | 23.78 | 0 | OK | Ground clear controls. | 214 | 38.2 | 362.81
14751 | TIN-INTERP | Interpolated Ground | 94254.7 | -6.56 | 338.97 | 0 | 18.47 | 0 | OK | Ground clear controls. | 214 | 38.2 | 357.44
14752 | TIN-INTERP | Interpolated Ground | 94254.71 | -5.07 | 339.03 | 0 | 12.79 | 0 | OK | Ground clear controls. | 214 | 38.2 | 351.82
14753 | TIN-INTERP | Interpolated Ground | 94254.71 | -4.56 | 339.05 | 0 | 23.76 | 0 | OK | Ground clear controls. | 214 | 38.2 | 362.81
14754 | TIN-INTERP | Interpolated Ground | 94254.86 | 4.99 | 338.95 | 0 | 13.03 | 0 | OK | Ground clear controls. | 214 | 38.2 | 351.98
14755 | TIN-INTERP | Interpolated Ground | 94254.9 | 6.49 | 338.91 | 0 | 18.58 | 0 | OK | Ground clear controls. | 214 | 38.2 | 357.49
14756 | TIN-INTERP | Interpolated Ground | 94294.64 | 4.42 | 329.3 | 0 | 27.2 | 0 | OK | Ground clear controls. | 214 | 38.2 | 356.5
14757 | TIN-INTERP | Interpolated Ground | 94294.7 | -6.53 | 328.69 | 0 | 22.55 | 0 | OK | Ground clear controls. | 214 | 38.2 | 351.24
14758 | TIN-INTERP | Interpolated Ground | 94294.71 | -5.05 | 328.77 | 0 | 16.75 | 0 | OK | Ground clear controls. | 214 | 38.2 | 345.52
14759 | TIN-INTERP | Interpolated Ground | 94294.71 | -4.52 | 328.8 | 0 | 27.71 | 0 | OK | Ground clear controls. | 214 | 38.2 | 356.51
14760 | TIN-INTERP | Interpolated Ground | 94294.86 | 4.91 | 329.25 | 0 | 16.56 | 0 | OK | Ground clear controls. | 214 | 38.2 | 345.81
14761 | TIN-INTERP | Interpolated Ground | 94294.9 | 6.4 | 329.3 | 0 | 22.03 | 0 | OK | Ground clear controls. | 214 | 38.2 | 351.33
14762 | TIN-INTERP | Interpolated Ground | 94334.64 | 4.35 | 320.85 | 0 | 30.34 | 0 | OK | Ground clear controls. | 214 | 38.2 | 351.19
14763 | TIN-INTERP | Interpolated Ground | 94334.7 | -6.49 | 320.14 | 0 | 25.88 | 0 | OK | Ground clear controls. | 214 | 38.2 | 346.02
14764 | TIN-INTERP | Interpolated Ground | 94334.71 | -5.02 | 320.13 | 0 | 20.1 | 0 | OK | Ground clear controls. | 214 | 38.2 | 340.23
14765 | TIN-INTERP | Interpolated Ground | 94334.71 | -4.49 | 320.19 | 0 | 31.02 | 0 | OK | Ground clear controls. | 214 | 38.2 | 351.21
14766 | TIN-INTERP | Interpolated Ground | 94334.86 | 4.83 | 320.86 | 0 | 19.77 | 0 | OK | Ground clear controls. | 214 | 38.2 | 340.63
14767 | TIN-INTERP | Interpolated Ground | 94334.9 | 6.32 | 321.18 | 0 | 24.98 | 0 | OK | Ground clear controls. | 214 | 38.2 | 346.16
14768 | TIN-INTERP | Interpolated Ground | 94374.64 | 4.27 | 310.19 | 0 | 36.71 | 0 | OK | Ground clear controls. | 214 | 38.2 | 346.9
14769 | TIN-INTERP | Interpolated Ground | 94374.7 | -6.46 | 310.06 | 0 | 31.71 | 0 | OK | Ground clear controls. | 214 | 38.2 | 341.77
14770 | TIN-INTERP | Interpolated Ground | 94374.71 | -5 | 309.99 | 0 | 25.94 | 0 | OK | Ground clear controls. | 214 | 38.2 | 335.93
14771 | TIN-INTERP | Interpolated Ground | 94374.71 | -4.46 | 310 | 0 | 36.9 | 0 | OK | Ground clear controls. | 214 | 38.2 | 346.9
14772 | TIN-INTERP | Interpolated Ground | 94374.86 | 4.75 | 310.15 | 0 | 26.25 | 0 | OK | Ground clear controls. | 214 | 38.2 | 336.4
14773 | TIN-INTERP | Interpolated Ground | 94374.9 | 6.23 | 310.25 | 0 | 31.69 | 0 | OK | Ground clear controls. | 214 | 38.2 | 341.94
14774 | TIN-INTERP | Interpolated Ground | 94414.64 | 4.19 | 309.46 | 0 | 34.14 | 0 | OK | Ground clear controls. | 214 | 38.2 | 343.6
14775 | TIN-INTERP | Interpolated Ground | 94414.7 | -6.43 | 310.2 | 0 | 28.29 | 0 | OK | Ground clear controls. | 214 | 38.2 | 338.49
14776 | TIN-INTERP | Interpolated Ground | 94414.71 | -4.97 | 310.07 | 0 | 22.56 | 0 | OK | Ground clear controls. | 214 | 38.2 | 332.63
14777 | TIN-INTERP | Interpolated Ground | 94414.71 | -4.42 | 310.04 | 0 | 33.56 | 0 | OK | Ground clear controls. | 214 | 38.2 | 343.6
14778 | TIN-INTERP | Interpolated Ground | 94414.86 | 4.67 | 309.43 | 0 | 23.72 | 0 | OK | Ground clear controls. | 214 | 38.2 | 333.15
14779 | TIN-INTERP | Interpolated Ground | 94414.9 | 6.15 | 309.39 | 0 | 29.31 | 0 | OK | Ground clear controls. | 214 | 38.2 | 338.7
14780 | TIN-INTERP | Interpolated Ground | 94454.64 | 4.11 | 306.84 | 0 | 34.46 | 0 | OK | Ground clear controls. | 214 | 38.2 | 341.3
14781 | TIN-INTERP | Interpolated Ground | 94454.7 | -6.39 | 307.64 | 0 | 28.54 | 0 | OK | Ground clear controls. | 214 | 38.2 | 336.18
14782 | TIN-INTERP | Interpolated Ground | 94454.71 | -4.95 | 307.65 | 0 | 22.67 | 0 | OK | Ground clear controls. | 214 | 38.2 | 330.32
14783 | TIN-INTERP | Interpolated Ground | 94454.71 | -4.39 | 307.64 | 0 | 33.65 | 0 | OK | Ground clear controls. | 214 | 38.2 | 341.29
14784 | TIN-INTERP | Interpolated Ground | 94454.86 | 4.59 | 306.74 | 0 | 24.12 | 0 | OK | Ground clear controls. | 214 | 38.2 | 330.86
14785 | TIN-INTERP | Interpolated Ground | 94454.9 | 6.06 | 306.56 | 0 | 29.86 | 0 | OK | Ground clear controls. | 214 | 38.2 | 336.42
14786 | TIN-INTERP | Interpolated Ground | 94494.64 | 4.04 | 301.81 | 0 | 38.2 | 0 | OK | Ground clear controls. | 214 | 38.2 | 340.01
14787 | TIN-INTERP | Interpolated Ground | 94494.7 | -6.36 | 307.11 | 0 | 27.72 | 0 | OK | Ground clear controls. | 214 | 37.98 | 334.83
14788 | TIN-INTERP | Interpolated Ground | 94494.71 | -4.93 | 306.37 | 0 | 22.64 | 0 | OK | Ground clear controls. | 214 | 37.98 | 329.01
14789 | TIN-INTERP | Interpolated Ground | 94494.71 | -4.35 | 306.07 | 0 | 33.9 | 0 | OK | Ground clear controls. | 214 | 37.98 | 339.97
14790 | TIN-INTERP | Interpolated Ground | 94494.86 | 4.51 | 301.58 | 0 | 27.96 | 0 | OK | Ground clear controls. | 214 | 37.98 | 329.54
14791 | TIN-INTERP | Interpolated Ground | 94494.9 | 5.98 | 301.16 | 0 | 33.93 | 0 | OK | Ground clear controls. | 214 | 37.98 | 335.09
14792 | TIN-INTERP | Interpolated Ground | 94534.64 | 3.96 | 301.73 | 0 | 37.98 | 0 | OK | Ground clear controls. | 214 | 37.98 | 339.71
14793 | TIN-INTERP | Interpolated Ground | 94534.7 | -6.33 | 302.35 | 0 | 32.1 | 0 | OK | Ground clear controls. | 214 | 37.8 | 334.45
14794 | TIN-INTERP | Interpolated Ground | 94534.71 | -4.9 | 302.21 | 0 | 26.47 | 0 | OK | Ground clear controls. | 214 | 37.8 | 328.68
14795 | TIN-INTERP | Interpolated Ground | 94534.71 | -4.32 | 302.19 | 0 | 37.46 | 0 | OK | Ground clear controls. | 214 | 37.8 | 339.65
14796 | TIN-INTERP | Interpolated Ground | 94534.86 | 4.43 | 301.62 | 0 | 27.56 | 0 | OK | Ground clear controls. | 214 | 37.8 | 329.18
14797 | TIN-INTERP | Interpolated Ground | 94534.9 | 5.89 | 301.64 | 0 | 33.08 | 0 | OK | Ground clear controls. | 214 | 37.8 | 334.72
14798 | TIN-INTERP | Interpolated Ground | 94574.64 | 3.88 | 302.62 | 0 | 37.8 | 0 | OK | Ground clear controls. | 214 | 37.8 | 340.42
14799 | TIN-INTERP | Interpolated Ground | 94574.7 | -6.29 | 304.52 | 0 | 30.52 | 0 | OK | Ground clear controls. | 214 | 36.2 | 335.04
14800 | TIN-INTERP | Interpolated Ground | 94574.71 | -4.88 | 304.25 | 0 | 25.1 | 0 | OK | Ground clear controls. | 214 | 36.2 | 329.35
14801 | TIN-INTERP | Interpolated Ground | 94574.71 | -4.29 | 304.12 | 0 | 36.2 | 0 | OK | Ground clear controls. | 214 | 36.2 | 340.32
14802 | TIN-INTERP | Interpolated Ground | 94574.86 | 4.35 | 302.56 | 0 | 27.22 | 0 | OK | Ground clear controls. | 214 | 33 | 329.78
14803 | TIN-INTERP | Interpolated Ground | 94574.9 | 5.81 | 302.32 | 0 | 33 | 0 | OK | Ground clear controls. | 214 | 33 | 335.32
14804 | TIN-INTERP | Interpolated Ground | 94614.64 | 3.81 | 310.67 | 0 | 31.45 | 0 | OK | Ground clear controls. | 214 | 31.45 | 342.12
14805 | TIN-INTERP | Interpolated Ground | 94614.7 | -6.26 | 311.42 | 0 | 25.18 | 0 | OK | Ground clear controls. | 214 | 30.83 | 336.6
14806 | TIN-INTERP | Interpolated Ground | 94614.71 | -4.85 | 311.2 | 0 | 19.8 | 0 | OK | Ground clear controls. | 214 | 30.83 | 331
14807 | TIN-INTERP | Interpolated Ground | 94614.71 | -4.25 | 311.15 | 0 | 30.83 | 0 | OK | Ground clear controls. | 214 | 30.83 | 341.98
14808 | TIN-INTERP | Interpolated Ground | 94614.86 | 4.27 | 310.64 | 0 | 20.69 | 0 | OK | Ground clear controls. | 214 | 26.45 | 331.33
14809 | TIN-INTERP | Interpolated Ground | 94614.9 | 5.72 | 310.43 | 0 | 26.45 | 0 | OK | Ground clear controls. | 214 | 26.45 | 336.88
14810 | TIN-INTERP | Interpolated Ground | 94658.49 | -6.29 | 317.28 | 0 | 21.75 | 0 | OK | Ground clear controls. | 215 | 95.8 | 339.03
14811 | TIN-INTERP | Interpolated Ground | 94658.98 | -4.29 | 316.96 | 0 | 27.57 | 0 | OK | Ground clear controls. | 215 | 95.8 | 344.53
14812 | TIN-INTERP | Interpolated Ground | 94659.01 | -4.88 | 316.95 | 0 | 16.59 | 0 | OK | Ground clear controls. | 215 | 95.8 | 333.54
14813 | TIN-INTERP | Interpolated Ground | 94661.28 | 3.7 | 315.59 | 0 | 28.93 | 0 | OK | Ground clear controls. | 215 | 95.8 | 344.52
14814 | TIN-INTERP | Interpolated Ground | 94661.75 | 4.13 | 315.58 | 0 | 17.96 | 0 | OK | Ground clear controls. | 215 | 95.8 | 333.54
14815 | TIN-INTERP | Interpolated Ground | 94662.05 | 5.6 | 315.46 | 0 | 23.56 | 0 | OK | Ground clear controls. | 215 | 95.8 | 339.02
14816 | TIN-INTERP | Interpolated Ground | 94698.49 | -6.36 | 304.59 | 0 | 30.76 | 0 | OK | Ground clear controls. | 215 | 95.8 | 335.35
14817 | TIN-INTERP | Interpolated Ground | 94698.97 | -4.38 | 304.39 | 0 | 36.41 | 0 | OK | Ground clear controls. | 215 | 95.8 | 340.8
14818 | TIN-INTERP | Interpolated Ground | 94699.01 | -4.94 | 304.37 | 0 | 25.62 | 0 | OK | Ground clear controls. | 215 | 95.8 | 329.99
14819 | TIN-INTERP | Interpolated Ground | 94701.28 | 3.82 | 303.72 | 0 | 37.05 | 0 | OK | Ground clear controls. | 215 | 95.8 | 340.77
14820 | TIN-INTERP | Interpolated Ground | 94701.75 | 4.25 | 303.51 | 0 | 26.49 | 0 | OK | Ground clear controls. | 215 | 95.8 | 330
14821 | TIN-INTERP | Interpolated Ground | 94702.05 | 5.73 | 303.27 | 0 | 32.01 | 0 | OK | Ground clear controls. | 215 | 95.8 | 335.28
14822 | TIN-INTERP | Interpolated Ground | 94738.49 | -6.44 | 293.77 | 0 | 38.83 | 0 | OK | Ground clear controls. | 215 | 95.8 | 332.6
14823 | TIN-INTERP | Interpolated Ground | 94738.97 | -4.46 | 293.59 | 0 | 44.45 | 0 | OK | Ground clear controls. | 215 | 95.8 | 338.04
14824 | TIN-INTERP | Interpolated Ground | 94739.01 | -5.01 | 293.58 | 0 | 33.79 | 0 | OK | Ground clear controls. | 215 | 95.8 | 327.37
14825 | TIN-INTERP | Interpolated Ground | 94741.28 | 3.94 | 292.94 | 0 | 45.04 | 0 | OK | Ground clear controls. | 215 | 95.8 | 337.98
14826 | TIN-INTERP | Interpolated Ground | 94741.75 | 4.37 | 292.87 | 0 | 34.5 | 0 | OK | Ground clear controls. | 215 | 95.8 | 327.37
14827 | TIN-INTERP | Interpolated Ground | 94742.05 | 5.85 | 292.88 | 0 | 39.61 | 0 | OK | Ground clear controls. | 215 | 95.8 | 332.49
14828 | TIN-INTERP | Interpolated Ground | 94778.49 | -6.51 | 283.97 | 0 | 46.84 | 0 | OK | Ground clear controls. | 215 | 95.8 | 330.81
14829 | TIN-INTERP | Interpolated Ground | 94778.97 | -4.54 | 284.24 | 0 | 51.99 | 0 | OK | Ground clear controls. | 215 | 95.8 | 336.23
14830 | TIN-INTERP | Interpolated Ground | 94779.01 | -5.08 | 284.19 | 0 | 41.46 | 0 | OK | Ground clear controls. | 215 | 95.8 | 325.65
14831 | TIN-INTERP | Interpolated Ground | 94781.28 | 4.07 | 284.05 | 0 | 52.12 | 0 | OK | Ground clear controls. | 215 | 95.8 | 336.17
14832 | TIN-INTERP | Interpolated Ground | 94781.75 | 4.49 | 283.91 | 0 | 41.75 | 0 | OK | Ground clear controls. | 215 | 95.8 | 325.66
14833 | TIN-INTERP | Interpolated Ground | 94782.05 | 5.97 | 283.62 | 0 | 47.07 | 0 | OK | Ground clear controls. | 215 | 95.8 | 330.69
14834 | TIN-INTERP | Interpolated Ground | 94818.49 | -6.59 | 286.47 | 0 | 43.48 | 0 | OK | Ground clear controls. | 215 | 95.8 | 329.95
14835 | TIN-INTERP | Interpolated Ground | 94818.97 | -4.63 | 285.96 | 0 | 49.42 | 0 | OK | Ground clear controls. | 215 | 95.8 | 335.38
14836 | TIN-INTERP | Interpolated Ground | 94819.01 | -5.14 | 286.16 | 0 | 38.67 | 0 | OK | Ground clear controls. | 215 | 95.8 | 324.83
14837 | TIN-INTERP | Interpolated Ground | 94821.28 | 4.19 | 283.16 | 0 | 52.18 | 0 | OK | Ground clear controls. | 215 | 95.8 | 335.34
14838 | TIN-INTERP | Interpolated Ground | 94821.75 | 4.61 | 283.26 | 0 | 41.61 | 0 | OK | Ground clear controls. | 215 | 95.8 | 324.87
14839 | TIN-INTERP | Interpolated Ground | 94822.05 | 6.1 | 279.98 | 0 | 49.86 | 0 | OK | Ground clear controls. | 215 | 95.8 | 329.84
14840 | TIN-INTERP | Interpolated Ground | 94858.49 | -6.66 | 291.85 | 0 | 38.18 | 0 | OK | Ground clear controls. | 215 | 95.8 | 330.03
14841 | TIN-INTERP | Interpolated Ground | 94858.97 | -4.71 | 291.65 | 0 | 43.85 | 0 | OK | Ground clear controls. | 215 | 95.8 | 335.5
14842 | TIN-INTERP | Interpolated Ground | 94859.01 | -5.21 | 291.72 | 0 | 33.21 | 0 | OK | Ground clear controls. | 215 | 95.8 | 324.93
14843 | TIN-INTERP | Interpolated Ground | 94861.28 | 4.31 | 290.7 | 0 | 44.78 | 0 | OK | Ground clear controls. | 215 | 95.8 | 335.48
14844 | TIN-INTERP | Interpolated Ground | 94861.75 | 4.73 | 290.68 | 0 | 34.32 | 0 | OK | Ground clear controls. | 215 | 95.8 | 325
14845 | TIN-INTERP | Interpolated Ground | 94862.05 | 6.22 | 290.31 | 0 | 39.65 | 0 | OK | Ground clear controls. | 215 | 95.8 | 329.96
14846 | TIN-INTERP | Interpolated Ground | 94898.49 | -6.74 | 293.86 | 0 | 37.2 | 0 | OK | Ground clear controls. | 215 | 95.8 | 331.06
14847 | TIN-INTERP | Interpolated Ground | 94898.97 | -4.8 | 292.99 | 0 | 43.59 | 0 | OK | Ground clear controls. | 215 | 95.8 | 336.58
14848 | TIN-INTERP | Interpolated Ground | 94899.01 | -5.28 | 293.17 | 0 | 32.78 | 0 | OK | Ground clear controls. | 215 | 95.8 | 325.95
14849 | TIN-INTERP | Interpolated Ground | 94901.28 | 4.44 | 281.46 | 0 | 55.14 | 0 | OK | Ground clear controls. | 215 | 95.8 | 336.6
14850 | TIN-INTERP | Interpolated Ground | 94901.75 | 4.85 | 280.63 | 0 | 45.42 | 0 | OK | Ground clear controls. | 215 | 95.8 | 326.05
14851 | TIN-INTERP | Interpolated Ground | 94902.05 | 6.35 | 278.26 | 0 | 52.8 | 0 | OK | Ground clear controls. | 215 | 95.8 | 331.06
14852 | TIN-INTERP | Interpolated Ground | 94938.49 | -6.81 | 258.07 | 0 | 74.97 | 0 | OK | Ground clear controls. | 215 | 95.8 | 333.04
14853 | TIN-INTERP | Interpolated Ground | 94938.97 | -4.88 | 254.99 | 0 | 83.63 | 0 | OK | Ground clear controls. | 215 | 95.8 | 338.62
14854 | TIN-INTERP | Interpolated Ground | 94939.01 | -5.34 | 255.31 | 0 | 72.56 | 0 | OK | Ground clear controls. | 215 | 95.8 | 327.87
14855 | TIN-INTERP | Interpolated Ground | 94941.28 | 4.56 | 242.9 | 0 | 95.8 | 0 | OK | Ground clear controls. | 215 | 95.8 | 338.7
14856 | TIN-INTERP | Interpolated Ground | 94941.75 | 4.97 | 242.06 | 0 | 85.96 | 0 | OK | Ground clear controls. | 215 | 92.85 | 328.02
14857 | TIN-INTERP | Interpolated Ground | 94942.05 | 6.47 | 240.27 | 0 | 92.85 | 0 | OK | Ground clear controls. | 215 | 92.85 | 333.12
14858 | TIN-INTERP | Interpolated Ground | 94978.49 | -6.89 | 268.5 | 0 | 67.45 | 0 | OK | Ground clear controls. | 215 | 72.02 | 335.95
14859 | TIN-INTERP | Interpolated Ground | 94978.97 | -4.97 | 269.61 | 0 | 72.02 | 0 | OK | Ground clear controls. | 215 | 72.02 | 341.63
14860 | TIN-INTERP | Interpolated Ground | 94979.01 | -5.41 | 269.42 | 0 | 61.29 | 0 | OK | Ground clear controls. | 215 | 67.09 | 330.71
14861 | TIN-INTERP | Interpolated Ground | 94981.28 | 4.68 | 274.68 | 0 | 67.09 | 0 | OK | Ground clear controls. | 215 | 67.09 | 341.77
14862 | TIN-INTERP | Interpolated Ground | 94981.75 | 5.09 | 275.24 | 0 | 55.68 | 0 | OK | Ground clear controls. | 215 | 60.09 | 330.92
14863 | TIN-INTERP | Interpolated Ground | 94982.05 | 6.59 | 276.06 | 0 | 60.09 | 0 | OK | Ground clear controls. | 215 | 60.09 | 336.15
14864 | TIN-INTERP | Interpolated Ground | 95018.49 | -6.96 | 304.9 | 0 | 34.91 | 0 | OK | Ground clear controls. | 215 | 39.33 | 339.81
14865 | TIN-INTERP | Interpolated Ground | 95018.97 | -5.05 | 306.26 | 0 | 39.33 | 0 | OK | Ground clear controls. | 215 | 39.33 | 345.59
14866 | TIN-INTERP | Interpolated Ground | 95019.01 | -5.48 | 305.9 | 0 | 28.56 | 0 | OK | Ground clear controls. | 215 | 34.05 | 334.46
14867 | TIN-INTERP | Interpolated Ground | 95021.28 | 4.81 | 311.77 | 0 | 34.05 | 0 | OK | Ground clear controls. | 215 | 34.05 | 345.82
14868 | TIN-INTERP | Interpolated Ground | 95021.75 | 5.21 | 311.87 | 0 | 22.86 | 0 | OK | Ground clear controls. | 215 | 27.95 | 334.73
14869 | TIN-INTERP | Interpolated Ground | 95022.05 | 6.72 | 312.2 | 0 | 27.95 | 0 | OK | Ground clear controls. | 215 | 27.95 | 340.15
14870 | TIN-INTERP | Interpolated Ground | 95041.63 | -5.51 | 308.74 | 0 | 28.24 | 0 | OK | Ground clear controls. | 216 | 78.01 | 336.98
14871 | TIN-INTERP | Interpolated Ground | 95041.73 | -7.01 | 308.11 | 0 | 34.37 | 0 | OK | Ground clear controls. | 216 | 78.01 | 342.48
14872 | TIN-INTERP | Interpolated Ground | 95041.85 | 5.27 | 312.24 | 0 | 24.75 | 0 | OK | Ground clear controls. | 216 | 78.01 | 336.99
14873 | TIN-INTERP | Interpolated Ground | 95041.92 | -5.1 | 308.98 | 0 | 39.31 | 0 | OK | Ground clear controls. | 216 | 78.01 | 348.29
14874 | TIN-INTERP | Interpolated Ground | 95041.92 | 4.87 | 312.26 | 0 | 36.03 | 0 | OK | Ground clear controls. | 216 | 78.01 | 348.29
14875 | TIN-INTERP | Interpolated Ground | 95042.2 | 6.78 | 312.16 | 0 | 30.37 | 0 | OK | Ground clear controls. | 216 | 78.01 | 342.53
14876 | TIN-INTERP | Interpolated Ground | 95081.62 | -5.67 | 307.54 | 0 | 28.56 | 0 | OK | Ground clear controls. | 216 | 78.01 | 336.1
14877 | TIN-INTERP | Interpolated Ground | 95081.73 | -7.17 | 307.18 | 0 | 34.27 | 0 | OK | Ground clear controls. | 216 | 78.01 | 341.45
14878 | TIN-INTERP | Interpolated Ground | 95081.85 | 5.27 | 311.63 | 0 | 24.46 | 0 | OK | Ground clear controls. | 216 | 78.01 | 336.09
14879 | TIN-INTERP | Interpolated Ground | 95081.91 | -5.24 | 307.66 | 0 | 39.58 | 0 | OK | Ground clear controls. | 216 | 78.01 | 347.24
14880 | TIN-INTERP | Interpolated Ground | 95081.92 | 4.85 | 311.42 | 0 | 35.67 | 0 | OK | Ground clear controls. | 216 | 78.01 | 347.09
14881 | TIN-INTERP | Interpolated Ground | 95082.2 | 6.78 | 312.34 | 0 | 29.13 | 0 | OK | Ground clear controls. | 216 | 78.01 | 341.47
14882 | TIN-INTERP | Interpolated Ground | 95121.62 | -5.83 | 302.41 | 0 | 33.72 | 0 | OK | Ground clear controls. | 216 | 78.01 | 336.13
14883 | TIN-INTERP | Interpolated Ground | 95121.73 | -7.32 | 301.85 | 0 | 39.51 | 0 | OK | Ground clear controls. | 216 | 78.01 | 341.36
14884 | TIN-INTERP | Interpolated Ground | 95121.85 | 5.27 | 306.87 | 0 | 29.24 | 0 | OK | Ground clear controls. | 216 | 78.01 | 336.11
14885 | TIN-INTERP | Interpolated Ground | 95121.91 | -5.38 | 302.43 | 0 | 44.7 | 0 | OK | Ground clear controls. | 216 | 78.01 | 347.13
14886 | TIN-INTERP | Interpolated Ground | 95121.92 | 4.83 | 306.62 | 0 | 40.23 | 0 | OK | Ground clear controls. | 216 | 78.01 | 346.85
14887 | TIN-INTERP | Interpolated Ground | 95122.2 | 6.77 | 307.58 | 0 | 33.77 | 0 | OK | Ground clear controls. | 216 | 78.01 | 341.35
14888 | TIN-INTERP | Interpolated Ground | 95161.62 | -5.99 | 275 | 0 | 62.07 | 0 | OK | Ground clear controls. | 216 | 78.01 | 337.07
14889 | TIN-INTERP | Interpolated Ground | 95161.73 | -7.48 | 275.42 | 0 | 66.78 | 0 | OK | Ground clear controls. | 216 | 78.01 | 342.2
14890 | TIN-INTERP | Interpolated Ground | 95161.85 | 5.27 | 268.75 | 0 | 68.27 | 0 | OK | Ground clear controls. | 216 | 78.01 | 337.02
14891 | TIN-INTERP | Interpolated Ground | 95161.91 | -5.52 | 275.51 | 0 | 72.46 | 0 | OK | Ground clear controls. | 216 | 78.01 | 347.97
14892 | TIN-INTERP | Interpolated Ground | 95161.92 | 4.81 | 269.55 | 0 | 78.01 | 0 | OK | Ground clear controls. | 216 | 78.01 | 347.56
14893 | TIN-INTERP | Interpolated Ground | 95162.2 | 6.77 | 268.47 | 0 | 73.69 | 0 | OK | Ground clear controls. | 216 | 73.69 | 342.16
14894 | TIN-INTERP | Interpolated Ground | 95201.62 | -6.16 | 300.46 | 0 | 38.45 | 0 | OK | Ground clear controls. | 216 | 50.73 | 338.91
14895 | TIN-INTERP | Interpolated Ground | 95201.73 | -7.64 | 301 | 0 | 42.97 | 0 | OK | Ground clear controls. | 216 | 50.73 | 343.97
14896 | TIN-INTERP | Interpolated Ground | 95201.85 | 5.26 | 300.16 | 0 | 38.69 | 0 | OK | Ground clear controls. | 216 | 50.73 | 338.85
14897 | TIN-INTERP | Interpolated Ground | 95201.91 | -5.66 | 300.4 | 0 | 49.34 | 0 | OK | Ground clear controls. | 216 | 50.73 | 349.74
14898 | TIN-INTERP | Interpolated Ground | 95201.92 | 4.79 | 300.21 | 0 | 49.03 | 0 | OK | Ground clear controls. | 216 | 50.73 | 349.24
14899 | TIN-INTERP | Interpolated Ground | 95202.2 | 6.77 | 300.21 | 0 | 43.7 | 0 | OK | Ground clear controls. | 216 | 50.73 | 343.91
14900 | TIN-INTERP | Interpolated Ground | 95241.62 | -6.32 | 307.73 | 0 | 33.94 | 0 | OK | Ground clear controls. | 216 | 50.73 | 341.67
14901 | TIN-INTERP | Interpolated Ground | 95241.73 | -7.8 | 308.07 | 0 | 38.61 | 0 | OK | Ground clear controls. | 216 | 50.73 | 346.68
14902 | TIN-INTERP | Interpolated Ground | 95241.85 | 5.26 | 307.54 | 0 | 34.05 | 0 | OK | Ground clear controls. | 216 | 50.73 | 341.59
14903 | TIN-INTERP | Interpolated Ground | 95241.91 | -5.8 | 307.65 | 0 | 44.8 | 0 | OK | Ground clear controls. | 216 | 50.73 | 352.45
14904 | TIN-INTERP | Interpolated Ground | 95241.92 | 4.77 | 307.59 | 0 | 44.28 | 0 | OK | Ground clear controls. | 216 | 50.73 | 351.87
14905 | TIN-INTERP | Interpolated Ground | 95242.2 | 6.77 | 307.53 | 0 | 39.05 | 0 | OK | Ground clear controls. | 216 | 50.73 | 346.58
14906 | TIN-INTERP | Interpolated Ground | 95281.62 | -6.48 | 314.38 | 0 | 30.96 | 0 | OK | Ground clear controls. | 216 | 50.73 | 345.34
14907 | TIN-INTERP | Interpolated Ground | 95281.73 | -7.96 | 314.2 | 0 | 36.12 | 0 | OK | Ground clear controls. | 216 | 50.73 | 350.32
14908 | TIN-INTERP | Interpolated Ground | 95281.85 | 5.26 | 319.55 | 0 | 25.69 | 0 | OK | Ground clear controls. | 216 | 50.73 | 345.24
14909 | TIN-INTERP | Interpolated Ground | 95281.91 | -5.94 | 314.76 | 0 | 41.34 | 0 | OK | Ground clear controls. | 216 | 50.73 | 356.1
14910 | TIN-INTERP | Interpolated Ground | 95281.92 | 4.75 | 319.39 | 0 | 36.07 | 0 | OK | Ground clear controls. | 216 | 50.73 | 355.46
14911 | TIN-INTERP | Interpolated Ground | 95282.2 | 6.77 | 320.3 | 0 | 29.9 | 0 | OK | Ground clear controls. | 216 | 50.73 | 350.2
14912 | TIN-INTERP | Interpolated Ground | 95321.62 | -6.64 | 318.8 | 0 | 31.12 | 0 | OK | Ground clear controls. | 216 | 50.73 | 349.92
14913 | TIN-INTERP | Interpolated Ground | 95321.73 | -8.12 | 318.61 | 0 | 36.3 | 0 | OK | Ground clear controls. | 216 | 50.73 | 354.91
14914 | TIN-INTERP | Interpolated Ground | 95321.85 | 5.26 | 319.82 | 0 | 29.98 | 0 | OK | Ground clear controls. | 216 | 50.73 | 349.8
14915 | TIN-INTERP | Interpolated Ground | 95321.91 | -6.08 | 318.75 | 0 | 41.95 | 0 | OK | Ground clear controls. | 216 | 50.73 | 360.7
14916 | TIN-INTERP | Interpolated Ground | 95321.92 | 4.73 | 319.75 | 0 | 40.27 | 0 | OK | Ground clear controls. | 216 | 50.73 | 360.02
14917 | TIN-INTERP | Interpolated Ground | 95322.2 | 6.77 | 320.01 | 0 | 34.74 | 0 | OK | Ground clear controls. | 216 | 50.73 | 354.75
14918 | TIN-INTERP | Interpolated Ground | 95361.62 | -6.8 | 315.24 | 0 | 40.19 | 0 | OK | Ground clear controls. | 216 | 50.73 | 355.43
14919 | TIN-INTERP | Interpolated Ground | 95361.73 | -8.27 | 315.26 | 0 | 45.17 | 0 | OK | Ground clear controls. | 216 | 50.73 | 360.43
14920 | TIN-INTERP | Interpolated Ground | 95361.85 | 5.25 | 319.07 | 0 | 36.21 | 0 | OK | Ground clear controls. | 216 | 50.73 | 355.28
14921 | TIN-INTERP | Interpolated Ground | 95361.91 | -6.22 | 315.54 | 0 | 50.73 | 0 | OK | Ground clear controls. | 216 | 50.73 | 366.27
14922 | TIN-INTERP | Interpolated Ground | 95361.92 | 4.71 | 318.94 | 0 | 46.61 | 0 | OK | Ground clear controls. | 216 | 50.24 | 365.55
14923 | TIN-INTERP | Interpolated Ground | 95362.2 | 6.76 | 319.46 | 0 | 40.79 | 0 | OK | Ground clear controls. | 216 | 50.24 | 360.25
14924 | TIN-INTERP | Interpolated Ground | 95401.62 | -6.96 | 322.49 | 0 | 39.36 | 0 | OK | Ground clear controls. | 216 | 50.24 | 361.85
14925 | TIN-INTERP | Interpolated Ground | 95401.73 | -8.43 | 322.55 | 0 | 44.36 | 0 | OK | Ground clear controls. | 216 | 50.24 | 366.91
14926 | TIN-INTERP | Interpolated Ground | 95401.85 | 5.25 | 323.42 | 0 | 38.27 | 0 | OK | Ground clear controls. | 216 | 50.24 | 361.69
14927 | TIN-INTERP | Interpolated Ground | 95401.91 | -6.36 | 322.53 | 0 | 50.24 | 0 | OK | Ground clear controls. | 216 | 50.24 | 372.77
14928 | TIN-INTERP | Interpolated Ground | 95401.92 | 4.69 | 323.23 | 0 | 48.81 | 0 | OK | Ground clear controls. | 216 | 49.91 | 372.04
14929 | TIN-INTERP | Interpolated Ground | 95402.2 | 6.76 | 323.75 | 0 | 42.94 | 0 | OK | Ground clear controls. | 216 | 49.91 | 366.69
14930 | TIN-INTERP | Interpolated Ground | 95441.62 | -7.12 | 330.13 | 0 | 39.07 | 0 | OK | Ground clear controls. | 216 | 49.91 | 369.2
14931 | TIN-INTERP | Interpolated Ground | 95441.73 | -8.59 | 330.05 | 0 | 44.28 | 0 | OK | Ground clear controls. | 216 | 49.91 | 374.33
14932 | TIN-INTERP | Interpolated Ground | 95441.85 | 5.25 | 330.92 | 0 | 38.09 | 0 | OK | Ground clear controls. | 216 | 49.91 | 369.01
14933 | TIN-INTERP | Interpolated Ground | 95441.91 | -6.5 | 330.33 | 0 | 49.91 | 0 | OK | Ground clear controls. | 216 | 49.91 | 380.24
14934 | TIN-INTERP | Interpolated Ground | 95441.92 | 4.67 | 330.9 | 0 | 48.62 | 0 | OK | Ground clear controls. | 216 | 48.62 | 379.52
14935 | TIN-INTERP | Interpolated Ground | 95442.2 | 6.76 | 331.04 | 0 | 43.05 | 0 | OK | Ground clear controls. | 216 | 48.52 | 374.09
14936 | TIN-INTERP | Interpolated Ground | 95481.62 | -7.28 | 340.04 | 0 | 37.43 | 0 | OK | Ground clear controls. | 216 | 48.52 | 377.47
14937 | TIN-INTERP | Interpolated Ground | 95481.73 | -8.75 | 339.84 | 0 | 42.85 | 0 | OK | Ground clear controls. | 216 | 48.52 | 382.69
14938 | TIN-INTERP | Interpolated Ground | 95481.85 | 5.24 | 340.63 | 0 | 36.63 | 0 | OK | Ground clear controls. | 216 | 48.52 | 377.26
14939 | TIN-INTERP | Interpolated Ground | 95481.91 | -6.64 | 340.14 | 0 | 48.52 | 0 | OK | Ground clear controls. | 216 | 48.52 | 388.66
14940 | TIN-INTERP | Interpolated Ground | 95481.92 | 4.65 | 340.56 | 0 | 47.41 | 0 | OK | Ground clear controls. | 216 | 47.41 | 387.97
14941 | TIN-INTERP | Interpolated Ground | 95482.2 | 6.76 | 340.93 | 0 | 41.5 | 0 | OK | Ground clear controls. | 216 | 46.62 | 382.43
14942 | TIN-INTERP | Interpolated Ground | 95521.62 | -7.44 | 351.06 | 0 | 35.62 | 0 | OK | Ground clear controls. | 216 | 46.62 | 386.68
14943 | TIN-INTERP | Interpolated Ground | 95521.73 | -8.91 | 350.86 | 0 | 41.16 | 0 | OK | Ground clear controls. | 216 | 46.62 | 392.02
14944 | TIN-INTERP | Interpolated Ground | 95521.85 | 5.24 | 353.34 | 0 | 33.09 | 0 | OK | Ground clear controls. | 216 | 46.62 | 386.43
14945 | TIN-INTERP | Interpolated Ground | 95521.91 | -6.78 | 351.43 | 0 | 46.62 | 0 | OK | Ground clear controls. | 216 | 46.62 | 398.05
14946 | TIN-INTERP | Interpolated Ground | 95521.92 | 4.63 | 353.31 | 0 | 44.09 | 0 | OK | Ground clear controls. | 216 | 44.19 | 397.4
14947 | TIN-INTERP | Interpolated Ground | 95522.2 | 6.76 | 353.65 | 0 | 38.08 | 0 | OK | Ground clear controls. | 216 | 44.19 | 391.73
14948 | TIN-INTERP | Interpolated Ground | 95561.62 | -7.6 | 364.05 | 0 | 32.77 | 0 | OK | Ground clear controls. | 216 | 44.19 | 396.82
14949 | TIN-INTERP | Interpolated Ground | 95561.73 | -9.06 | 363.9 | 0 | 38.41 | 0 | OK | Ground clear controls. | 216 | 44.19 | 402.31
14950 | TIN-INTERP | Interpolated Ground | 95561.85 | 5.24 | 366.51 | 0 | 30.04 | 0 | OK | Ground clear controls. | 216 | 44.19 | 396.55
14951 | TIN-INTERP | Interpolated Ground | 95561.91 | -6.92 | 364.22 | 0 | 44.19 | 0 | OK | Ground clear controls. | 216 | 44.19 | 408.41
14952 | TIN-INTERP | Interpolated Ground | 95561.92 | 4.61 | 366.37 | 0 | 41.45 | 0 | OK | Ground clear controls. | 216 | 41.45 | 407.82
14953 | TIN-INTERP | Interpolated Ground | 95562.2 | 6.75 | 366.93 | 0 | 35.06 | 0 | OK | Ground clear controls. | 216 | 39.66 | 401.99
14954 | TIN-INTERP | Interpolated Ground | 95601.62 | -7.76 | 380.12 | 0 | 27.77 | 0 | OK | Ground clear controls. | 216 | 39.66 | 407.89
14955 | TIN-INTERP | Interpolated Ground | 95601.73 | -9.22 | 380.32 | 0 | 33.24 | 0 | OK | Ground clear controls. | 216 | 39.66 | 413.56
14956 | TIN-INTERP | Interpolated Ground | 95601.85 | 5.24 | 381.2 | 0 | 26.4 | 0 | OK | Ground clear controls. | 216 | 39.66 | 407.6
14957 | TIN-INTERP | Interpolated Ground | 95601.91 | -7.06 | 380.08 | 0 | 39.66 | 0 | OK | Ground clear controls. | 216 | 39.66 | 419.74
14958 | TIN-INTERP | Interpolated Ground | 95601.92 | 4.59 | 381.31 | 0 | 37.92 | 0 | OK | Ground clear controls. | 216 | 37.92 | 419.23
14959 | TIN-INTERP | Interpolated Ground | 95602.2 | 6.75 | 381.42 | 0 | 31.8 | 0 | OK | Ground clear controls. | 216 | 35.36 | 413.22
14960 | TIN-INTERP | Interpolated Ground | 95641.62 | -7.92 | 396.81 | 0 | 23.12 | 0 | OK | Ground clear controls. | 216 | 35.36 | 419.93
14961 | TIN-INTERP | Interpolated Ground | 95641.73 | -9.38 | 396.3 | 0 | 29.49 | 0 | OK | Ground clear controls. | 216 | 35.36 | 425.79
14962 | TIN-INTERP | Interpolated Ground | 95641.85 | 5.23 | 400.33 | 0 | 19.27 | 0 | OK | Ground clear controls. | 216 | 35.36 | 419.6
14963 | TIN-INTERP | Interpolated Ground | 95641.91 | -7.2 | 396.7 | 0 | 35.36 | 0 | OK | Ground clear controls. | 216 | 35.36 | 432.06
14964 | TIN-INTERP | Interpolated Ground | 95641.92 | 4.57 | 400.18 | 0 | 31.46 | 0 | OK | Ground clear controls. | 216 | 31.46 | 431.64
14965 | TIN-INTERP | Interpolated Ground | 95642.2 | 6.75 | 401.19 | 0 | 24.23 | 0 | OK | Ground clear controls. | 216 | 24.23 | 425.42
14966 | TIN-INTERP | Interpolated Ground | 95647.53 | 4.63 | 401.65 | 0 | 32.05 | 0 | OK | Ground clear controls. | 217 | 135.15 | 433.7
14967 | TIN-INTERP | Interpolated Ground | 95647.53 | 5.29 | 402.26 | 0 | 19.37 | 0 | OK | Ground clear controls. | 217 | 135.15 | 421.63
14968 | TIN-INTERP | Interpolated Ground | 95647.53 | 6.81 | 403.65 | 0 | 23.75 | 0 | OK | Ground clear controls. | 217 | 135.15 | 427.4
14969 | TIN-INTERP | Interpolated Ground | 95648.5 | -7.2 | 396.87 | 0 | 36.69 | 0 | OK | Ground clear controls. | 217 | 135.15 | 433.56
14970 | TIN-INTERP | Interpolated Ground | 95648.63 | -7.92 | 396.79 | 0 | 24.68 | 0 | OK | Ground clear controls. | 217 | 135.15 | 421.47
14971 | TIN-INTERP | Interpolated Ground | 95648.78 | -9.39 | 396.64 | 0 | 30.62 | 0 | OK | Ground clear controls. | 217 | 135.15 | 427.26
14972 | TIN-INTERP | Interpolated Ground | 95686.71 | 6.81 | 401.2 | 0 | 20.14 | 0 | OK | Ground clear controls. | 217 | 135.15 | 421.34
14973 | TIN-INTERP | Interpolated Ground | 95686.95 | 5.31 | 400.45 | 0 | 15.32 | 0 | OK | Ground clear controls. | 217 | 135.15 | 415.77
14974 | TIN-INTERP | Interpolated Ground | 95687.1 | 4.66 | 400.28 | 0 | 27.36 | 0 | OK | Ground clear controls. | 217 | 135.15 | 427.64
14975 | TIN-INTERP | Interpolated Ground | 95688.5 | -7.16 | 395.78 | 0 | 31.7 | 0 | OK | Ground clear controls. | 217 | 135.15 | 427.48
14976 | TIN-INTERP | Interpolated Ground | 95688.63 | -7.87 | 395.47 | 0 | 20.15 | 0 | OK | Ground clear controls. | 217 | 135.15 | 415.62
14977 | TIN-INTERP | Interpolated Ground | 95688.78 | -9.35 | 394.84 | 0 | 26.37 | 0 | OK | Ground clear controls. | 217 | 135.15 | 421.21
14978 | TIN-INTERP | Interpolated Ground | 95726.71 | 6.86 | 393 | 0 | 23.19 | 0 | OK | Ground clear controls. | 217 | 135.15 | 416.19
14979 | TIN-INTERP | Interpolated Ground | 95726.95 | 5.36 | 392.42 | 0 | 18.39 | 0 | OK | Ground clear controls. | 217 | 135.15 | 410.81
14980 | TIN-INTERP | Interpolated Ground | 95727.1 | 4.7 | 392.14 | 0 | 30.35 | 0 | OK | Ground clear controls. | 217 | 135.15 | 422.49
14981 | TIN-INTERP | Interpolated Ground | 95728.5 | -7.11 | 389.07 | 0 | 33.25 | 0 | OK | Ground clear controls. | 217 | 135.15 | 422.32
14982 | TIN-INTERP | Interpolated Ground | 95728.63 | -7.83 | 388.25 | 0 | 22.42 | 0 | OK | Ground clear controls. | 217 | 135.15 | 410.67
14983 | TIN-INTERP | Interpolated Ground | 95728.78 | -9.3 | 387 | 0 | 29.09 | 0 | OK | Ground clear controls. | 217 | 135.15 | 416.09
14984 | TIN-INTERP | Interpolated Ground | 95766.71 | 6.91 | 380.7 | 0 | 31.28 | 0 | OK | Ground clear controls. | 217 | 135.15 | 411.98
14985 | TIN-INTERP | Interpolated Ground | 95766.95 | 5.41 | 379.81 | 0 | 26.94 | 0 | OK | Ground clear controls. | 217 | 135.15 | 406.75
14986 | TIN-INTERP | Interpolated Ground | 95767.1 | 4.75 | 379.36 | 0 | 38.92 | 0 | OK | Ground clear controls. | 217 | 135.15 | 418.28
14987 | TIN-INTERP | Interpolated Ground | 95768.5 | -7.07 | 370.47 | 0 | 47.63 | 0 | OK | Ground clear controls. | 217 | 135.15 | 418.1
14988 | TIN-INTERP | Interpolated Ground | 95768.63 | -7.78 | 370.09 | 0 | 36.53 | 0 | OK | Ground clear controls. | 217 | 135.15 | 406.62
14989 | TIN-INTERP | Interpolated Ground | 95768.78 | -9.26 | 369.24 | 0 | 42.67 | 0 | OK | Ground clear controls. | 217 | 135.15 | 411.91
14990 | TIN-INTERP | Interpolated Ground | 95806.71 | 6.96 | 368.07 | 0 | 40.63 | 0 | OK | Ground clear controls. | 217 | 135.15 | 408.7
14991 | TIN-INTERP | Interpolated Ground | 95806.95 | 5.46 | 368.04 | 0 | 35.54 | 0 | OK | Ground clear controls. | 217 | 135.15 | 403.58
14992 | TIN-INTERP | Interpolated Ground | 95807.1 | 4.8 | 368.04 | 0 | 46.97 | 0 | OK | Ground clear controls. | 217 | 135.15 | 415.01
14993 | TIN-INTERP | Interpolated Ground | 95808.5 | -7.02 | 366.56 | 0 | 48.27 | 0 | OK | Ground clear controls. | 217 | 135.15 | 414.83
14994 | TIN-INTERP | Interpolated Ground | 95808.63 | -7.74 | 366.32 | 0 | 37.15 | 0 | OK | Ground clear controls. | 217 | 135.15 | 403.47
14995 | TIN-INTERP | Interpolated Ground | 95808.78 | -9.21 | 365.86 | 0 | 42.81 | 0 | OK | Ground clear controls. | 217 | 135.15 | 408.67
14996 | TIN-INTERP | Interpolated Ground | 95846.71 | 7.01 | 359.65 | 0 | 46.69 | 0 | OK | Ground clear controls. | 217 | 135.15 | 406.34
14997 | TIN-INTERP | Interpolated Ground | 95846.95 | 5.51 | 359.29 | 0 | 42.02 | 0 | OK | Ground clear controls. | 217 | 135.15 | 401.31
14998 | TIN-INTERP | Interpolated Ground | 95847.1 | 4.85 | 359.11 | 0 | 53.54 | 0 | OK | Ground clear controls. | 217 | 135.15 | 412.65
14999 | TIN-INTERP | Interpolated Ground | 95848.5 | -6.98 | 355.54 | 0 | 56.94 | 0 | OK | Ground clear controls. | 217 | 135.15 | 412.48
15000 | TIN-INTERP | Interpolated Ground | 95848.63 | -7.69 | 355.44 | 0 | 45.77 | 0 | OK | Ground clear controls. | 217 | 135.15 | 401.21
15001 | TIN-INTERP | Interpolated Ground | 95848.78 | -9.17 | 355.39 | 0 | 50.95 | 0 | OK | Ground clear controls. | 217 | 135.15 | 406.34
15002 | TIN-INTERP | Interpolated Ground | 95886.71 | 7.06 | 346.5 | 0 | 58.4 | 0 | OK | Ground clear controls. | 217 | 135.15 | 404.9
15003 | TIN-INTERP | Interpolated Ground | 95886.95 | 5.56 | 345.46 | 0 | 54.46 | 0 | OK | Ground clear controls. | 217 | 135.15 | 399.92
15004 | TIN-INTERP | Interpolated Ground | 95887.1 | 4.89 | 344.99 | 0 | 66.23 | 0 | OK | Ground clear controls. | 217 | 135.15 | 411.22
15005 | TIN-INTERP | Interpolated Ground | 95888.5 | -6.93 | 346 | 0 | 65.07 | 0 | OK | Ground clear controls. | 217 | 135.15 | 411.07
15006 | TIN-INTERP | Interpolated Ground | 95888.63 | -7.65 | 346 | 0 | 53.85 | 0 | OK | Ground clear controls. | 217 | 135.15 | 399.85
15007 | TIN-INTERP | Interpolated Ground | 95888.78 | -9.13 | 345.84 | 0 | 59.1 | 0 | OK | Ground clear controls. | 217 | 135.15 | 404.94
15008 | TIN-INTERP | Interpolated Ground | 95926.71 | 7.11 | 327.11 | 0 | 77.29 | 0 | OK | Ground clear controls. | 217 | 135.15 | 404.4
15009 | TIN-INTERP | Interpolated Ground | 95926.95 | 5.61 | 326.55 | 0 | 72.87 | 0 | OK | Ground clear controls. | 217 | 135.15 | 399.42
15010 | TIN-INTERP | Interpolated Ground | 95927.1 | 4.94 | 326.29 | 0 | 84.43 | 0 | OK | Ground clear controls. | 217 | 135.15 | 410.72
15011 | TIN-INTERP | Interpolated Ground | 95928.5 | -6.89 | 320.82 | 0 | 89.78 | 0 | OK | Ground clear controls. | 217 | 135.15 | 410.6
15012 | TIN-INTERP | Interpolated Ground | 95928.63 | -7.6 | 320.52 | 0 | 78.87 | 0 | OK | Ground clear controls. | 217 | 135.15 | 399.39
15013 | TIN-INTERP | Interpolated Ground | 95928.78 | -9.08 | 319.89 | 0 | 84.59 | 0 | OK | Ground clear controls. | 217 | 135.15 | 404.48
15014 | TIN-INTERP | Interpolated Ground | 95966.71 | 7.16 | 305.52 | 0 | 99.29 | 0 | OK | Ground clear controls. | 217 | 135.15 | 404.81
15015 | TIN-INTERP | Interpolated Ground | 95966.95 | 5.65 | 305.63 | 0 | 94.18 | 0 | OK | Ground clear controls. | 217 | 135.15 | 399.81
15016 | TIN-INTERP | Interpolated Ground | 95967.1 | 4.99 | 305.65 | 0 | 105.49 | 0 | OK | Ground clear controls. | 217 | 135.15 | 411.14
15017 | TIN-INTERP | Interpolated Ground | 95968.5 | -6.84 | 303.34 | 0 | 107.72 | 0 | OK | Ground clear controls. | 217 | 135.15 | 411.06
15018 | TIN-INTERP | Interpolated Ground | 95968.63 | -7.56 | 302.89 | 0 | 96.93 | 0 | OK | Ground clear controls. | 217 | 135.15 | 399.82
15019 | TIN-INTERP | Interpolated Ground | 95968.78 | -9.04 | 302.58 | 0 | 102.35 | 0 | OK | Ground clear controls. | 217 | 135.15 | 404.93
15020 | TIN-INTERP | Interpolated Ground | 96006.71 | 7.21 | 285.58 | 0 | 120.56 | 0 | OK | Ground clear controls. | 217 | 135.15 | 406.14
15021 | TIN-INTERP | Interpolated Ground | 96006.95 | 5.7 | 284.65 | 0 | 116.44 | 0 | OK | Ground clear controls. | 217 | 135.15 | 401.09
15022 | TIN-INTERP | Interpolated Ground | 96007.1 | 5.03 | 284.38 | 0 | 128.09 | 0 | OK | Ground clear controls. | 217 | 135.15 | 412.47
15023 | TIN-INTERP | Interpolated Ground | 96008.5 | -6.8 | 277.3 | 0 | 135.15 | 0 | OK | Ground clear controls. | 217 | 135.15 | 412.45
15024 | TIN-INTERP | Interpolated Ground | 96008.63 | -7.52 | 277.01 | 0 | 124.14 | 0 | OK | Ground clear controls. | 217 | 129.95 | 401.15
15025 | TIN-INTERP | Interpolated Ground | 96008.78 | -9 | 276.37 | 0 | 129.95 | 0 | OK | Ground clear controls. | 217 | 129.95 | 406.32
15026 | TIN-INTERP | Interpolated Ground | 96046.71 | 7.26 | 326.54 | 0 | 81.87 | 0 | OK | Ground clear controls. | 217 | 91.01 | 408.41
15027 | TIN-INTERP | Interpolated Ground | 96046.95 | 5.75 | 326.47 | 0 | 76.8 | 0 | OK | Ground clear controls. | 217 | 91.01 | 403.27
15028 | TIN-INTERP | Interpolated Ground | 96047.1 | 5.08 | 326.32 | 0 | 88.43 | 0 | OK | Ground clear controls. | 217 | 91.01 | 414.75
15029 | TIN-INTERP | Interpolated Ground | 96048.5 | -6.75 | 323.77 | 0 | 91.01 | 0 | OK | Ground clear controls. | 217 | 91.01 | 414.78
15030 | TIN-INTERP | Interpolated Ground | 96048.63 | -7.47 | 323.73 | 0 | 79.64 | 0 | OK | Ground clear controls. | 217 | 85.4 | 403.37
15031 | TIN-INTERP | Interpolated Ground | 96048.78 | -8.95 | 323.23 | 0 | 85.4 | 0 | OK | Ground clear controls. | 217 | 85.4 | 408.63
15032 | TIN-INTERP | Interpolated Ground | 96086.71 | 7.31 | 365.04 | 0 | 46.56 | 0 | OK | Ground clear controls. | 217 | 54.25 | 411.6
15033 | TIN-INTERP | Interpolated Ground | 96086.95 | 5.8 | 364.45 | 0 | 41.88 | 0 | OK | Ground clear controls. | 217 | 54.25 | 406.33
15034 | TIN-INTERP | Interpolated Ground | 96087.1 | 5.13 | 364.22 | 0 | 53.72 | 0 | OK | Ground clear controls. | 217 | 54.25 | 417.94
15035 | TIN-INTERP | Interpolated Ground | 96088.5 | -6.71 | 363.78 | 0 | 54.25 | 0 | OK | Ground clear controls. | 217 | 54.25 | 418.03
15036 | TIN-INTERP | Interpolated Ground | 96088.63 | -7.43 | 363.98 | 0 | 42.5 | 0 | OK | Ground clear controls. | 217 | 47.49 | 406.48
15037 | TIN-INTERP | Interpolated Ground | 96088.78 | -8.91 | 364.38 | 0 | 47.49 | 0 | OK | Ground clear controls. | 217 | 47.49 | 411.87
15038 | TIN-INTERP | Interpolated Ground | 96126.71 | 7.36 | 390.98 | 0 | 24.73 | 0 | OK | Ground clear controls. | 217 | 37.73 | 415.71
15039 | TIN-INTERP | Interpolated Ground | 96126.95 | 5.85 | 391 | 0 | 19.29 | 0 | OK | Ground clear controls. | 217 | 37.73 | 410.29
15040 | TIN-INTERP | Interpolated Ground | 96127.1 | 5.18 | 390.99 | 0 | 31.08 | 0 | OK | Ground clear controls. | 217 | 37.73 | 422.07
15041 | TIN-INTERP | Interpolated Ground | 96128.5 | -6.66 | 390.66 | 0 | 31.58 | 0 | OK | Ground clear controls. | 217 | 37.73 | 422.24
15042 | TIN-INTERP | Interpolated Ground | 96128.63 | -7.38 | 390.75 | 0 | 19.76 | 0 | OK | Ground clear controls. | 217 | 37.73 | 410.51
15043 | TIN-INTERP | Interpolated Ground | 96128.78 | -8.86 | 390.84 | 0 | 25.2 | 0 | OK | Ground clear controls. | 217 | 37.73 | 416.04
15044 | TIN-INTERP | Interpolated Ground | 96166.71 | 7.41 | 389.51 | 0 | 31.25 | 0 | OK | Ground clear controls. | 217 | 37.73 | 420.76
15045 | TIN-INTERP | Interpolated Ground | 96166.95 | 5.9 | 389.58 | 0 | 25.56 | 0 | OK | Ground clear controls. | 217 | 37.73 | 415.14
15046 | TIN-INTERP | Interpolated Ground | 96167.1 | 5.22 | 389.6 | 0 | 37.53 | 0 | OK | Ground clear controls. | 217 | 37.73 | 427.13
15047 | TIN-INTERP | Interpolated Ground | 96168.5 | -6.62 | 389.65 | 0 | 37.73 | 0 | OK | Ground clear controls. | 217 | 37.73 | 427.38
15048 | TIN-INTERP | Interpolated Ground | 96168.63 | -7.34 | 389.61 | 0 | 25.81 | 0 | OK | Ground clear controls. | 217 | 31.52 | 415.42
15049 | TIN-INTERP | Interpolated Ground | 96168.78 | -8.82 | 389.62 | 0 | 31.52 | 0 | OK | Ground clear controls. | 217 | 31.52 | 421.14
15050 | TIN-INTERP | Interpolated Ground | 96189.35 | -8.8 | 391.89 | 0 | 32.24 | 0 | OK | Ground clear controls. | 218 | 49.63 | 424.13
15051 | TIN-INTERP | Interpolated Ground | 96189.4 | -6.59 | 392.08 | 0 | 38.35 | 0 | OK | Ground clear controls. | 218 | 49.63 | 430.43
15052 | TIN-INTERP | Interpolated Ground | 96189.41 | -7.31 | 392.01 | 0 | 26.32 | 0 | OK | Ground clear controls. | 218 | 49.63 | 418.33
15053 | TIN-INTERP | Interpolated Ground | 96189.8 | 5.25 | 391.72 | 0 | 38.72 | 0 | OK | Ground clear controls. | 218 | 49.63 | 430.44
15054 | TIN-INTERP | Interpolated Ground | 96189.8 | 5.93 | 391.57 | 0 | 26.77 | 0 | OK | Ground clear controls. | 218 | 49.63 | 418.34
15055 | TIN-INTERP | Interpolated Ground | 96189.8 | 7.45 | 391.37 | 0 | 32.77 | 0 | OK | Ground clear controls. | 218 | 49.63 | 424.14
15056 | TIN-INTERP | Interpolated Ground | 96229.43 | 7.36 | 382.02 | 0 | 32.55 | 0 | OK | Ground clear controls. | 218 | 49.63 | 414.57
15057 | TIN-INTERP | Interpolated Ground | 96229.44 | 5.84 | 382.01 | 0 | 26.92 | 0 | OK | Ground clear controls. | 218 | 49.63 | 408.93
15058 | TIN-INTERP | Interpolated Ground | 96229.5 | 5.18 | 381.99 | 0 | 38.77 | 0 | OK | Ground clear controls. | 218 | 49.63 | 420.76
15059 | TIN-INTERP | Interpolated Ground | 96230.02 | -6.42 | 381.84 | 0 | 38.85 | 0 | OK | Ground clear controls. | 218 | 49.63 | 420.69
15060 | TIN-INTERP | Interpolated Ground | 96230.1 | -7.11 | 381.83 | 0 | 27.08 | 0 | OK | Ground clear controls. | 218 | 49.63 | 408.91
15061 | TIN-INTERP | Interpolated Ground | 96230.17 | -8.6 | 381.82 | 0 | 32.72 | 0 | OK | Ground clear controls. | 218 | 49.63 | 414.54
15062 | TIN-INTERP | Interpolated Ground | 96269.42 | 7.28 | 373.08 | 0 | 32.86 | 0 | OK | Ground clear controls. | 218 | 49.63 | 405.94
15063 | TIN-INTERP | Interpolated Ground | 96269.44 | 5.76 | 372.75 | 0 | 27.68 | 0 | OK | Ground clear controls. | 218 | 49.63 | 400.43
15064 | TIN-INTERP | Interpolated Ground | 96269.5 | 5.12 | 372.61 | 0 | 39.44 | 0 | OK | Ground clear controls. | 218 | 49.63 | 412.05
15065 | TIN-INTERP | Interpolated Ground | 96270.01 | -6.23 | 373.85 | 0 | 38.06 | 0 | OK | Ground clear controls. | 218 | 49.63 | 411.91
15066 | TIN-INTERP | Interpolated Ground | 96270.1 | -6.9 | 374.05 | 0 | 26.37 | 0 | OK | Ground clear controls. | 218 | 49.63 | 400.42
15067 | TIN-INTERP | Interpolated Ground | 96270.17 | -8.39 | 374.36 | 0 | 31.53 | 0 | OK | Ground clear controls. | 218 | 49.63 | 405.89
15068 | TIN-INTERP | Interpolated Ground | 96309.42 | 7.19 | 375.66 | 0 | 22.61 | 0 | OK | Ground clear controls. | 218 | 49.63 | 398.27
15069 | TIN-INTERP | Interpolated Ground | 96309.44 | 5.68 | 376.18 | 0 | 16.67 | 0 | OK | Ground clear controls. | 218 | 49.63 | 392.85
15070 | TIN-INTERP | Interpolated Ground | 96309.5 | 5.06 | 376.38 | 0 | 27.91 | 0 | OK | Ground clear controls. | 218 | 49.63 | 404.29
15071 | TIN-INTERP | Interpolated Ground | 96310.01 | -6.04 | 377.8 | 0 | 26.3 | 0 | OK | Ground clear controls. | 218 | 49.63 | 404.1
15072 | TIN-INTERP | Interpolated Ground | 96310.1 | -6.7 | 377.84 | 0 | 15 | 0 | OK | Ground clear controls. | 218 | 49.63 | 392.84
15073 | TIN-INTERP | Interpolated Ground | 96310.17 | -8.18 | 377.94 | 0 | 20.26 | 0 | OK | Ground clear controls. | 218 | 49.63 | 398.2
15074 | TIN-INTERP | Interpolated Ground | 96349.42 | 7.11 | 371.39 | 0 | 20.14 | 0 | OK | Ground clear controls. | 218 | 49.63 | 391.53
15075 | TIN-INTERP | Interpolated Ground | 96349.44 | 5.6 | 370.62 | 0 | 15.57 | 0 | OK | Ground clear controls. | 218 | 49.63 | 386.19
15076 | TIN-INTERP | Interpolated Ground | 96349.5 | 4.99 | 370.59 | 0 | 26.87 | 0 | OK | Ground clear controls. | 218 | 49.63 | 397.46
15077 | TIN-INTERP | Interpolated Ground | 96350.01 | -5.86 | 367.25 | 0 | 30 | 0 | OK | Ground clear controls. | 218 | 49.63 | 397.25
15078 | TIN-INTERP | Interpolated Ground | 96350.1 | -6.49 | 366.84 | 0 | 19.33 | 0 | OK | Ground clear controls. | 218 | 49.63 | 386.17
15079 | TIN-INTERP | Interpolated Ground | 96350.17 | -7.98 | 366.13 | 0 | 25.33 | 0 | OK | Ground clear controls. | 218 | 49.63 | 391.46
15080 | TIN-INTERP | Interpolated Ground | 96389.42 | 7.03 | 350.27 | 0 | 35.47 | 0 | OK | Ground clear controls. | 218 | 49.63 | 385.74
15081 | TIN-INTERP | Interpolated Ground | 96389.44 | 5.52 | 349.47 | 0 | 30.98 | 0 | OK | Ground clear controls. | 218 | 49.63 | 380.45
15082 | TIN-INTERP | Interpolated Ground | 96389.5 | 4.93 | 348.95 | 0 | 42.64 | 0 | OK | Ground clear controls. | 218 | 49.63 | 391.59
15083 | TIN-INTERP | Interpolated Ground | 96390.01 | -5.67 | 347.54 | 0 | 43.82 | 0 | OK | Ground clear controls. | 218 | 49.63 | 391.36
15084 | TIN-INTERP | Interpolated Ground | 96390.1 | -6.28 | 347.61 | 0 | 32.82 | 0 | OK | Ground clear controls. | 218 | 49.63 | 380.43
15085 | TIN-INTERP | Interpolated Ground | 96390.17 | -7.77 | 347.95 | 0 | 37.71 | 0 | OK | Ground clear controls. | 218 | 49.63 | 385.66
15086 | TIN-INTERP | Interpolated Ground | 96429.42 | 6.95 | 337.75 | 0 | 43.13 | 0 | OK | Ground clear controls. | 218 | 49.63 | 380.88
15087 | TIN-INTERP | Interpolated Ground | 96429.44 | 5.44 | 338.09 | 0 | 37.52 | 0 | OK | Ground clear controls. | 218 | 49.63 | 375.61
15088 | TIN-INTERP | Interpolated Ground | 96429.5 | 4.87 | 338.26 | 0 | 48.4 | 0 | OK | Ground clear controls. | 218 | 49.63 | 386.66
15089 | TIN-INTERP | Interpolated Ground | 96430.01 | -5.48 | 341.15 | 0 | 45.3 | 0 | OK | Ground clear controls. | 218 | 49.63 | 386.45
15090 | TIN-INTERP | Interpolated Ground | 96430.1 | -6.08 | 341.39 | 0 | 34.2 | 0 | OK | Ground clear controls. | 218 | 49.63 | 375.59
15091 | TIN-INTERP | Interpolated Ground | 96430.17 | -7.57 | 342.16 | 0 | 38.64 | 0 | OK | Ground clear controls. | 218 | 49.63 | 380.8
15092 | TIN-INTERP | Interpolated Ground | 96469.42 | 6.87 | 336.55 | 0 | 40.41 | 0 | OK | Ground clear controls. | 218 | 49.63 | 376.96
15093 | TIN-INTERP | Interpolated Ground | 96469.44 | 5.36 | 337.5 | 0 | 34.18 | 0 | OK | Ground clear controls. | 218 | 49.63 | 371.68
15094 | TIN-INTERP | Interpolated Ground | 96469.5 | 4.8 | 337.82 | 0 | 44.85 | 0 | OK | Ground clear controls. | 218 | 49.63 | 382.67
15095 | TIN-INTERP | Interpolated Ground | 96470.01 | -5.3 | 342.55 | 0 | 39.92 | 0 | OK | Ground clear controls. | 218 | 49.63 | 382.47
15096 | TIN-INTERP | Interpolated Ground | 96470.1 | -5.87 | 342.81 | 0 | 28.84 | 0 | OK | Ground clear controls. | 218 | 49.63 | 371.65
15097 | TIN-INTERP | Interpolated Ground | 96470.17 | -7.36 | 343.35 | 0 | 33.54 | 0 | OK | Ground clear controls. | 218 | 49.63 | 376.89
15098 | TIN-INTERP | Interpolated Ground | 96509.42 | 6.79 | 335.28 | 0 | 38.68 | 0 | OK | Ground clear controls. | 218 | 49.63 | 373.96
15099 | TIN-INTERP | Interpolated Ground | 96509.44 | 5.28 | 336.28 | 0 | 32.37 | 0 | OK | Ground clear controls. | 218 | 49.63 | 368.65
15100 | TIN-INTERP | Interpolated Ground | 96509.5 | 4.74 | 336.53 | 0 | 43.08 | 0 | OK | Ground clear controls. | 218 | 49.63 | 379.61
15101 | TIN-INTERP | Interpolated Ground | 96510.01 | -5.11 | 342.82 | 0 | 36.62 | 0 | OK | Ground clear controls. | 218 | 49.63 | 379.44
15102 | TIN-INTERP | Interpolated Ground | 96510.1 | -5.66 | 343.36 | 0 | 25.27 | 0 | OK | Ground clear controls. | 218 | 49.63 | 368.63
15103 | TIN-INTERP | Interpolated Ground | 96510.17 | -7.16 | 344.29 | 0 | 29.61 | 0 | OK | Ground clear controls. | 218 | 49.63 | 373.9
15104 | TIN-INTERP | Interpolated Ground | 96549.42 | 6.7 | 327.35 | 0 | 44.56 | 0 | OK | Ground clear controls. | 218 | 49.63 | 371.91
15105 | TIN-INTERP | Interpolated Ground | 96549.44 | 5.2 | 327.77 | 0 | 38.76 | 0 | OK | Ground clear controls. | 218 | 49.63 | 366.53
15106 | TIN-INTERP | Interpolated Ground | 96549.5 | 4.68 | 327.86 | 0 | 49.63 | 0 | OK | Ground clear controls. | 218 | 49.63 | 377.49
15107 | TIN-INTERP | Interpolated Ground | 96550.01 | -4.92 | 331.47 | 0 | 45.91 | 0 | OK | Ground clear controls. | 218 | 45.91 | 377.38
15108 | TIN-INTERP | Interpolated Ground | 96550.1 | -5.46 | 331.93 | 0 | 34.58 | 0 | OK | Ground clear controls. | 218 | 42.68 | 366.51
15109 | TIN-INTERP | Interpolated Ground | 96550.17 | -6.95 | 332.4 | 0 | 39.46 | 0 | OK | Ground clear controls. | 218 | 42.68 | 371.86
15110 | TIN-INTERP | Interpolated Ground | 96589.42 | 6.62 | 332.59 | 0 | 38.18 | 0 | OK | Ground clear controls. | 218 | 42.68 | 370.77
15111 | TIN-INTERP | Interpolated Ground | 96589.44 | 5.12 | 333.37 | 0 | 31.93 | 0 | OK | Ground clear controls. | 218 | 42.68 | 365.3
15112 | TIN-INTERP | Interpolated Ground | 96589.5 | 4.61 | 333.61 | 0 | 42.68 | 0 | OK | Ground clear controls. | 218 | 42.68 | 376.29
15113 | TIN-INTERP | Interpolated Ground | 96590.01 | -4.74 | 333.7 | 0 | 42.55 | 0 | OK | Ground clear controls. | 218 | 42.55 | 376.25
15114 | TIN-INTERP | Interpolated Ground | 96590.09 | -5.25 | 333.72 | 0 | 31.57 | 0 | OK | Ground clear controls. | 218 | 36.95 | 365.29
15115 | TIN-INTERP | Interpolated Ground | 96590.17 | -6.75 | 333.8 | 0 | 36.95 | 0 | OK | Ground clear controls. | 218 | 36.95 | 370.75
15116 | TIN-INTERP | Interpolated Ground | 96601.57 | -4.68 | 334.17 | 0 | 41.94 | 0 | OK | Ground clear controls. | 219 | 65.61 | 376.11
15117 | TIN-INTERP | Interpolated Ground | 96601.57 | -5.19 | 334.38 | 0 | 30.72 | 0 | OK | Ground clear controls. | 219 | 65.61 | 365.1
15118 | TIN-INTERP | Interpolated Ground | 96601.63 | -6.69 | 334.8 | 0 | 35.8 | 0 | OK | Ground clear controls. | 219 | 65.61 | 370.6
15119 | TIN-INTERP | Interpolated Ground | 96601.68 | 4.59 | 333.52 | 0 | 42.59 | 0 | OK | Ground clear controls. | 219 | 65.61 | 376.11
15120 | TIN-INTERP | Interpolated Ground | 96601.76 | 5.1 | 333.3 | 0 | 31.81 | 0 | OK | Ground clear controls. | 219 | 65.61 | 365.11
15121 | TIN-INTERP | Interpolated Ground | 96601.82 | 6.6 | 332.62 | 0 | 37.98 | 0 | OK | Ground clear controls. | 219 | 65.61 | 370.6
15122 | TIN-INTERP | Interpolated Ground | 96641.57 | -4.68 | 331.76 | 0 | 36.54 | 0 | OK | Ground clear controls. | 219 | 65.61 | 368.3
15123 | TIN-INTERP | Interpolated Ground | 96641.57 | -5.18 | 331.84 | 0 | 25.7 | 0 | OK | Ground clear controls. | 219 | 65.61 | 357.54
15124 | TIN-INTERP | Interpolated Ground | 96641.62 | -6.68 | 331.94 | 0 | 30.97 | 0 | OK | Ground clear controls. | 219 | 65.61 | 362.91
15125 | TIN-INTERP | Interpolated Ground | 96641.68 | 4.59 | 327.88 | 0 | 40.46 | 0 | OK | Ground clear controls. | 219 | 65.61 | 368.34
15126 | TIN-INTERP | Interpolated Ground | 96641.76 | 5.1 | 327.69 | 0 | 29.82 | 0 | OK | Ground clear controls. | 219 | 65.61 | 357.51
15127 | TIN-INTERP | Interpolated Ground | 96641.82 | 6.6 | 327.16 | 0 | 35.73 | 0 | OK | Ground clear controls. | 219 | 65.61 | 362.89
15128 | TIN-INTERP | Interpolated Ground | 96681.57 | -4.67 | 313.41 | 0 | 48.06 | 0 | OK | Ground clear controls. | 219 | 65.61 | 361.47
15129 | TIN-INTERP | Interpolated Ground | 96681.57 | -5.18 | 313.2 | 0 | 37.69 | 0 | OK | Ground clear controls. | 219 | 65.61 | 350.89
15130 | TIN-INTERP | Interpolated Ground | 96681.62 | -6.67 | 312.1 | 0 | 44.06 | 0 | OK | Ground clear controls. | 219 | 65.61 | 356.16
15131 | TIN-INTERP | Interpolated Ground | 96681.68 | 4.59 | 317.03 | 0 | 44.5 | 0 | OK | Ground clear controls. | 219 | 65.61 | 361.53
15132 | TIN-INTERP | Interpolated Ground | 96681.76 | 5.1 | 317.16 | 0 | 33.69 | 0 | OK | Ground clear controls. | 219 | 65.61 | 350.85
15133 | TIN-INTERP | Interpolated Ground | 96681.82 | 6.6 | 316.85 | 0 | 39.28 | 0 | OK | Ground clear controls. | 219 | 65.61 | 356.13
15134 | TIN-INTERP | Interpolated Ground | 96721.57 | -4.66 | 296.14 | 0 | 59.47 | 0 | OK | Ground clear controls. | 219 | 65.61 | 355.61
15135 | TIN-INTERP | Interpolated Ground | 96721.57 | -5.17 | 296.09 | 0 | 49.06 | 0 | OK | Ground clear controls. | 219 | 65.61 | 345.15
15136 | TIN-INTERP | Interpolated Ground | 96721.62 | -6.66 | 295.58 | 0 | 54.78 | 0 | OK | Ground clear controls. | 219 | 65.61 | 350.36
15137 | TIN-INTERP | Interpolated Ground | 96721.68 | 4.59 | 295.8 | 0 | 59.89 | 0 | OK | Ground clear controls. | 219 | 65.61 | 355.69
15138 | TIN-INTERP | Interpolated Ground | 96721.76 | 5.1 | 295.47 | 0 | 49.63 | 0 | OK | Ground clear controls. | 219 | 65.61 | 345.1
15139 | TIN-INTERP | Interpolated Ground | 96721.82 | 6.6 | 293.88 | 0 | 56.43 | 0 | OK | Ground clear controls. | 219 | 65.61 | 350.31
15140 | TIN-INTERP | Interpolated Ground | 96761.57 | -4.65 | 297.1 | 0 | 53.62 | 0 | OK | Ground clear controls. | 219 | 65.61 | 350.72
15141 | TIN-INTERP | Interpolated Ground | 96761.57 | -5.16 | 297.07 | 0 | 43.27 | 0 | OK | Ground clear controls. | 219 | 65.61 | 340.34
15142 | TIN-INTERP | Interpolated Ground | 96761.62 | -6.66 | 297.09 | 0 | 48.42 | 0 | OK | Ground clear controls. | 219 | 65.61 | 345.51
15143 | TIN-INTERP | Interpolated Ground | 96761.68 | 4.59 | 290.29 | 0 | 60.51 | 0 | OK | Ground clear controls. | 219 | 65.61 | 350.8
15144 | TIN-INTERP | Interpolated Ground | 96761.76 | 5.1 | 289.7 | 0 | 50.58 | 0 | OK | Ground clear controls. | 219 | 65.61 | 340.28
15145 | TIN-INTERP | Interpolated Ground | 96761.82 | 6.6 | 287.9 | 0 | 57.54 | 0 | OK | Ground clear controls. | 219 | 65.61 | 345.44
15146 | TIN-INTERP | Interpolated Ground | 96801.57 | -4.65 | 306.37 | 0 | 40.41 | 0 | OK | Ground clear controls. | 219 | 65.61 | 346.78
15147 | TIN-INTERP | Interpolated Ground | 96801.57 | -5.15 | 306.65 | 0 | 29.79 | 0 | OK | Ground clear controls. | 219 | 65.61 | 336.44
15148 | TIN-INTERP | Interpolated Ground | 96801.62 | -6.65 | 307.1 | 0 | 34.5 | 0 | OK | Ground clear controls. | 219 | 65.61 | 341.6
15149 | TIN-INTERP | Interpolated Ground | 96801.68 | 4.59 | 296.42 | 0 | 50.45 | 0 | OK | Ground clear controls. | 219 | 65.61 | 346.87
15150 | TIN-INTERP | Interpolated Ground | 96801.76 | 5.1 | 295.58 | 0 | 40.8 | 0 | OK | Ground clear controls. | 219 | 65.61 | 336.38
15151 | TIN-INTERP | Interpolated Ground | 96801.82 | 6.6 | 294 | 0 | 47.53 | 0 | OK | Ground clear controls. | 219 | 65.61 | 341.53
15152 | TIN-INTERP | Interpolated Ground | 96841.57 | -4.64 | 285.68 | 0 | 58.13 | 0 | OK | Ground clear controls. | 219 | 65.61 | 343.81
15153 | TIN-INTERP | Interpolated Ground | 96841.57 | -5.14 | 286.13 | 0 | 47.32 | 0 | OK | Ground clear controls. | 219 | 65.61 | 333.45
15154 | TIN-INTERP | Interpolated Ground | 96841.62 | -6.64 | 287.32 | 0 | 51.29 | 0 | OK | Ground clear controls. | 219 | 65.61 | 338.61
15155 | TIN-INTERP | Interpolated Ground | 96841.68 | 4.59 | 278.28 | 0 | 65.61 | 0 | OK | Ground clear controls. | 219 | 65.61 | 343.89
15156 | TIN-INTERP | Interpolated Ground | 96841.76 | 5.1 | 277.7 | 0 | 55.69 | 0 | OK | Ground clear controls. | 219 | 62.28 | 333.39
15157 | TIN-INTERP | Interpolated Ground | 96841.82 | 6.6 | 276.27 | 0 | 62.28 | 0 | OK | Ground clear controls. | 219 | 62.28 | 338.55
15158 | TIN-INTERP | Interpolated Ground | 96881.57 | -4.63 | 303.23 | 0 | 38.57 | 0 | OK | Ground clear controls. | 219 | 41.98 | 341.8
15159 | TIN-INTERP | Interpolated Ground | 96881.57 | -5.13 | 303.3 | 0 | 28.09 | 0 | OK | Ground clear controls. | 219 | 41.98 | 331.39
15160 | TIN-INTERP | Interpolated Ground | 96881.62 | -6.63 | 303.58 | 0 | 32.99 | 0 | OK | Ground clear controls. | 219 | 41.98 | 336.57
15161 | TIN-INTERP | Interpolated Ground | 96881.68 | 4.6 | 299.89 | 0 | 41.98 | 0 | OK | Ground clear controls. | 219 | 41.98 | 341.87
15162 | TIN-INTERP | Interpolated Ground | 96881.76 | 5.1 | 299.64 | 0 | 31.68 | 0 | OK | Ground clear controls. | 219 | 37.68 | 331.32
15163 | TIN-INTERP | Interpolated Ground | 96881.82 | 6.6 | 299.48 | 0 | 37.03 | 0 | OK | Ground clear controls. | 219 | 37.68 | 336.51
15164 | TIN-INTERP | Interpolated Ground | 96921.57 | -4.62 | 304.61 | 0 | 36.13 | 0 | OK | Ground clear controls. | 219 | 37.68 | 340.74
15165 | TIN-INTERP | Interpolated Ground | 96921.57 | -5.13 | 304.66 | 0 | 25.56 | 0 | OK | Ground clear controls. | 219 | 37.68 | 330.22
15166 | TIN-INTERP | Interpolated Ground | 96921.62 | -6.62 | 304.9 | 0 | 30.57 | 0 | OK | Ground clear controls. | 219 | 37.68 | 335.47
15167 | TIN-INTERP | Interpolated Ground | 96921.68 | 4.6 | 303.12 | 0 | 37.68 | 0 | OK | Ground clear controls. | 219 | 37.68 | 340.8
15168 | TIN-INTERP | Interpolated Ground | 96921.76 | 5.1 | 303.06 | 0 | 27.11 | 0 | OK | Ground clear controls. | 219 | 35.99 | 330.17
15169 | TIN-INTERP | Interpolated Ground | 96921.82 | 6.6 | 302.87 | 0 | 32.55 | 0 | OK | Ground clear controls. | 219 | 35.99 | 335.42
15170 | TIN-INTERP | Interpolated Ground | 96961.57 | -4.62 | 306.63 | 0 | 34.01 | 0 | OK | Ground clear controls. | 219 | 35.99 | 340.64
15171 | TIN-INTERP | Interpolated Ground | 96961.57 | -5.12 | 306.67 | 0 | 23.29 | 0 | OK | Ground clear controls. | 219 | 35.99 | 329.96
15172 | TIN-INTERP | Interpolated Ground | 96961.62 | -6.62 | 306.87 | 0 | 28.43 | 0 | OK | Ground clear controls. | 219 | 35.99 | 335.3
15173 | TIN-INTERP | Interpolated Ground | 96961.68 | 4.6 | 306.19 | 0 | 34.49 | 0 | OK | Ground clear controls. | 219 | 35.99 | 340.68
15174 | TIN-INTERP | Interpolated Ground | 96961.76 | 5.1 | 306.06 | 0 | 23.87 | 0 | OK | Ground clear controls. | 219 | 35.99 | 329.93
15175 | TIN-INTERP | Interpolated Ground | 96961.82 | 6.6 | 305.75 | 0 | 29.51 | 0 | OK | Ground clear controls. | 219 | 35.99 | 335.26
15176 | TIN-INTERP | Interpolated Ground | 97001.57 | -4.61 | 306.05 | 0 | 35.45 | 0 | OK | Ground clear controls. | 219 | 35.99 | 341.5
15177 | TIN-INTERP | Interpolated Ground | 97001.57 | -5.11 | 306.05 | 0 | 24.56 | 0 | OK | Ground clear controls. | 219 | 35.99 | 330.61
15178 | TIN-INTERP | Interpolated Ground | 97001.62 | -6.61 | 306.16 | 0 | 29.9 | 0 | OK | Ground clear controls. | 219 | 35.99 | 336.06
15179 | TIN-INTERP | Interpolated Ground | 97001.68 | 4.6 | 305.53 | 0 | 35.99 | 0 | OK | Ground clear controls. | 219 | 35.99 | 341.52
15180 | TIN-INTERP | Interpolated Ground | 97001.76 | 5.1 | 305.61 | 0 | 24.99 | 0 | OK | Ground clear controls. | 219 | 30.28 | 330.6
15181 | TIN-INTERP | Interpolated Ground | 97001.82 | 6.6 | 305.77 | 0 | 30.28 | 0 | OK | Ground clear controls. | 219 | 30.28 | 336.05
15182 | TIN-INTERP | Interpolated Ground | 97017.6 | -5.11 | 308.34 | 0 | 22.79 | 0 | OK | Ground clear controls. | 220 | 85.04 | 331.13
15183 | TIN-INTERP | Interpolated Ground | 97017.64 | -6.6 | 308.26 | 0 | 28.37 | 0 | OK | Ground clear controls. | 220 | 85.04 | 336.63
15184 | TIN-INTERP | Interpolated Ground | 97017.68 | -4.6 | 308.41 | 0 | 33.71 | 0 | OK | Ground clear controls. | 220 | 85.04 | 342.12
15185 | TIN-INTERP | Interpolated Ground | 97017.7 | 5.1 | 307.83 | 0 | 23.3 | 0 | OK | Ground clear controls. | 220 | 85.04 | 331.13
15186 | TIN-INTERP | Interpolated Ground | 97017.77 | 6.6 | 307.3 | 0 | 29.33 | 0 | OK | Ground clear controls. | 220 | 85.04 | 336.63
15187 | TIN-INTERP | Interpolated Ground | 97017.82 | 4.6 | 307.94 | 0 | 34.18 | 0 | OK | Ground clear controls. | 220 | 85.04 | 342.12
15188 | TIN-INTERP | Interpolated Ground | 97057.6 | -5.11 | 301.87 | 0 | 21.13 | 0 | OK | Ground clear controls. | 220 | 85.04 | 323
15189 | TIN-INTERP | Interpolated Ground | 97057.64 | -6.61 | 301.88 | 0 | 26.45 | 0 | OK | Ground clear controls. | 220 | 85.04 | 328.33
15190 | TIN-INTERP | Interpolated Ground | 97057.69 | -4.6 | 301.84 | 0 | 31.84 | 0 | OK | Ground clear controls. | 220 | 85.04 | 333.68
15191 | TIN-INTERP | Interpolated Ground | 97057.7 | 5.1 | 298.75 | 0 | 24.22 | 0 | OK | Ground clear controls. | 220 | 85.04 | 322.97
15192 | TIN-INTERP | Interpolated Ground | 97057.77 | 6.6 | 298.45 | 0 | 29.86 | 0 | OK | Ground clear controls. | 220 | 85.04 | 328.31
15193 | TIN-INTERP | Interpolated Ground | 97057.82 | 4.6 | 298.91 | 0 | 34.87 | 0 | OK | Ground clear controls. | 220 | 85.04 | 333.78
15194 | TIN-INTERP | Interpolated Ground | 97097.6 | -5.11 | 301.73 | 0 | 14.09 | 0 | OK | Ground clear controls. | 220 | 85.04 | 315.82
15195 | TIN-INTERP | Interpolated Ground | 97097.64 | -6.61 | 302.09 | 0 | 18.93 | 0 | OK | Ground clear controls. | 220 | 85.04 | 321.02
15196 | TIN-INTERP | Interpolated Ground | 97097.69 | -4.6 | 301.5 | 0 | 24.75 | 0 | OK | Ground clear controls. | 220 | 85.04 | 326.25
15197 | TIN-INTERP | Interpolated Ground | 97097.7 | 5.1 | 299.72 | 0 | 16.04 | 0 | OK | Ground clear controls. | 220 | 85.04 | 315.76
15198 | TIN-INTERP | Interpolated Ground | 97097.77 | 6.6 | 299.67 | 0 | 21.31 | 0 | OK | Ground clear controls. | 220 | 85.04 | 320.98
15199 | TIN-INTERP | Interpolated Ground | 97097.82 | 4.6 | 299.7 | 0 | 26.7 | 0 | OK | Ground clear controls. | 220 | 85.04 | 326.4
15200 | TIN-INTERP | Interpolated Ground | 97137.6 | -5.11 | 289.32 | 0 | 20.27 | 0 | OK | Ground clear controls. | 220 | 85.04 | 309.59
15201 | TIN-INTERP | Interpolated Ground | 97137.64 | -6.61 | 289.65 | 0 | 25.02 | 0 | OK | Ground clear controls. | 220 | 85.04 | 314.67
15202 | TIN-INTERP | Interpolated Ground | 97137.69 | -4.6 | 289.18 | 0 | 30.61 | 0 | OK | Ground clear controls. | 220 | 85.04 | 319.79
15203 | TIN-INTERP | Interpolated Ground | 97137.7 | 5.1 | 290.02 | 0 | 19.49 | 0 | OK | Ground clear controls. | 220 | 85.04 | 309.51
15204 | TIN-INTERP | Interpolated Ground | 97137.77 | 6.6 | 289.95 | 0 | 24.65 | 0 | OK | Ground clear controls. | 220 | 85.04 | 314.6
15205 | TIN-INTERP | Interpolated Ground | 97137.82 | 4.6 | 290 | 0 | 30 | 0 | OK | Ground clear controls. | 220 | 85.04 | 320
15206 | TIN-INTERP | Interpolated Ground | 97177.6 | -5.11 | 283.01 | 0 | 21.28 | 0 | OK | Ground clear controls. | 220 | 85.04 | 304.29
15207 | TIN-INTERP | Interpolated Ground | 97177.64 | -6.61 | 283.63 | 0 | 25.64 | 0 | OK | Ground clear controls. | 220 | 85.04 | 309.27
15208 | TIN-INTERP | Interpolated Ground | 97177.69 | -4.6 | 282.67 | 0 | 31.65 | 0 | OK | Ground clear controls. | 220 | 85.04 | 314.32
15209 | TIN-INTERP | Interpolated Ground | 97177.7 | 5.1 | 279.14 | 0 | 25.05 | 0 | OK | Ground clear controls. | 220 | 85.04 | 304.19
15210 | TIN-INTERP | Interpolated Ground | 97177.77 | 6.6 | 278.75 | 0 | 30.45 | 0 | OK | Ground clear controls. | 220 | 85.04 | 309.2
15211 | TIN-INTERP | Interpolated Ground | 97177.82 | 4.6 | 279.43 | 0 | 35.14 | 0 | OK | Ground clear controls. | 220 | 85.04 | 314.57
15212 | TIN-INTERP | Interpolated Ground | 97217.6 | -5.11 | 270.23 | 0 | 29.69 | 0 | OK | Ground clear controls. | 220 | 85.04 | 299.92
15213 | TIN-INTERP | Interpolated Ground | 97217.64 | -6.61 | 270.36 | 0 | 34.48 | 0 | OK | Ground clear controls. | 220 | 85.04 | 304.84
15214 | TIN-INTERP | Interpolated Ground | 97217.69 | -4.6 | 270.1 | 0 | 39.71 | 0 | OK | Ground clear controls. | 220 | 85.04 | 309.81
15215 | TIN-INTERP | Interpolated Ground | 97217.7 | 5.1 | 263.54 | 0 | 36.28 | 0 | OK | Ground clear controls. | 220 | 85.04 | 299.82
15216 | TIN-INTERP | Interpolated Ground | 97217.77 | 6.6 | 261.27 | 0 | 43.49 | 0 | OK | Ground clear controls. | 220 | 85.04 | 304.76
15217 | TIN-INTERP | Interpolated Ground | 97217.82 | 4.6 | 264 | 0 | 46.11 | 0 | OK | Ground clear controls. | 220 | 85.04 | 310.11
15218 | TIN-INTERP | Interpolated Ground | 97257.6 | -5.11 | 251.14 | 0 | 45.35 | 0 | OK | Ground clear controls. | 220 | 85.04 | 296.49
15219 | TIN-INTERP | Interpolated Ground | 97257.64 | -6.61 | 251.46 | 0 | 49.91 | 0 | OK | Ground clear controls. | 220 | 85.04 | 301.37
15220 | TIN-INTERP | Interpolated Ground | 97257.69 | -4.6 | 250.98 | 0 | 55.32 | 0 | OK | Ground clear controls. | 220 | 85.04 | 306.3
15221 | TIN-INTERP | Interpolated Ground | 97257.7 | 5.1 | 248.57 | 0 | 47.8 | 0 | OK | Ground clear controls. | 220 | 85.04 | 296.37
15222 | TIN-INTERP | Interpolated Ground | 97257.77 | 6.6 | 248.33 | 0 | 52.94 | 0 | OK | Ground clear controls. | 220 | 85.04 | 301.27
15223 | TIN-INTERP | Interpolated Ground | 97257.82 | 4.6 | 248.66 | 0 | 57.95 | 0 | OK | Ground clear controls. | 220 | 85.04 | 306.61
15224 | TIN-INTERP | Interpolated Ground | 97297.6 | -5.11 | 224.44 | 0 | 69.55 | 0 | OK | Ground clear controls. | 220 | 85.04 | 293.99
15225 | TIN-INTERP | Interpolated Ground | 97297.64 | -6.61 | 224.32 | 0 | 74.52 | 0 | OK | Ground clear controls. | 220 | 85.04 | 298.84
15226 | TIN-INTERP | Interpolated Ground | 97297.69 | -4.6 | 224.36 | 0 | 79.39 | 0 | OK | Ground clear controls. | 220 | 85.04 | 303.75
15227 | TIN-INTERP | Interpolated Ground | 97297.7 | 5.1 | 218.8 | 0 | 75.07 | 0 | OK | Ground clear controls. | 220 | 85.04 | 293.87
15228 | TIN-INTERP | Interpolated Ground | 97297.77 | 6.6 | 217.18 | 0 | 81.56 | 0 | OK | Ground clear controls. | 220 | 85.04 | 298.74
15229 | TIN-INTERP | Interpolated Ground | 97297.82 | 4.6 | 219.05 | 0 | 85.04 | 0 | OK | Ground clear controls. | 220 | 85.04 | 304.09
15230 | TIN-INTERP | Interpolated Ground | 97337.6 | -5.11 | 234.16 | 0 | 58.26 | 0 | OK | Ground clear controls. | 220 | 67.41 | 292.42
15231 | TIN-INTERP | Interpolated Ground | 97337.64 | -6.61 | 232.63 | 0 | 64.63 | 0 | OK | Ground clear controls. | 220 | 67.41 | 297.26
15232 | TIN-INTERP | Interpolated Ground | 97337.69 | -4.6 | 234.76 | 0 | 67.41 | 0 | OK | Ground clear controls. | 220 | 67.41 | 302.17
15233 | TIN-INTERP | Interpolated Ground | 97337.7 | 5.1 | 242.55 | 0 | 49.74 | 0 | OK | Ground clear controls. | 220 | 60.19 | 292.29
15234 | TIN-INTERP | Interpolated Ground | 97337.77 | 6.6 | 243.33 | 0 | 53.84 | 0 | OK | Ground clear controls. | 220 | 60.19 | 297.17
15235 | TIN-INTERP | Interpolated Ground | 97337.82 | 4.6 | 242.32 | 0 | 60.19 | 0 | OK | Ground clear controls. | 220 | 60.19 | 302.51
15236 | TIN-INTERP | Interpolated Ground | 97377.6 | -5.11 | 262.97 | 0 | 28.8 | 0 | OK | Ground clear controls. | 220 | 51.91 | 291.77
15237 | TIN-INTERP | Interpolated Ground | 97377.64 | -6.61 | 261.6 | 0 | 35.04 | 0 | OK | Ground clear controls. | 220 | 51.91 | 296.64
15238 | TIN-INTERP | Interpolated Ground | 97377.69 | -4.6 | 263.33 | 0 | 38.24 | 0 | OK | Ground clear controls. | 220 | 51.91 | 301.57
15239 | TIN-INTERP | Interpolated Ground | 97377.7 | 5.1 | 268.03 | 0 | 23.63 | 0 | OK | Ground clear controls. | 220 | 51.91 | 291.66
15240 | TIN-INTERP | Interpolated Ground | 97377.77 | 6.6 | 268.31 | 0 | 28.24 | 0 | OK | Ground clear controls. | 220 | 51.91 | 296.55
15241 | TIN-INTERP | Interpolated Ground | 97377.82 | 4.6 | 267.97 | 0 | 33.93 | 0 | OK | Ground clear controls. | 220 | 51.91 | 301.9
15242 | TIN-INTERP | Interpolated Ground | 97417.6 | -5.11 | 261.04 | 0 | 31.02 | 0 | OK | Ground clear controls. | 220 | 51.91 | 292.06
15243 | TIN-INTERP | Interpolated Ground | 97417.64 | -6.61 | 261.13 | 0 | 35.84 | 0 | OK | Ground clear controls. | 220 | 51.91 | 296.97
15244 | TIN-INTERP | Interpolated Ground | 97417.69 | -4.61 | 260.93 | 0 | 41 | 0 | OK | Ground clear controls. | 220 | 51.91 | 301.93
15245 | TIN-INTERP | Interpolated Ground | 97417.7 | 5.1 | 258.98 | 0 | 32.97 | 0 | OK | Ground clear controls. | 220 | 51.91 | 291.95
15246 | TIN-INTERP | Interpolated Ground | 97417.77 | 6.6 | 258.69 | 0 | 38.19 | 0 | OK | Ground clear controls. | 220 | 51.91 | 296.88
15247 | TIN-INTERP | Interpolated Ground | 97417.82 | 4.6 | 259.01 | 0 | 43.23 | 0 | OK | Ground clear controls. | 220 | 51.91 | 302.24
15248 | TIN-INTERP | Interpolated Ground | 97457.6 | -5.11 | 250.58 | 0 | 42.69 | 0 | OK | Ground clear controls. | 220 | 51.91 | 293.27
15249 | TIN-INTERP | Interpolated Ground | 97457.64 | -6.61 | 249.22 | 0 | 49.03 | 0 | OK | Ground clear controls. | 220 | 51.91 | 298.25
15250 | TIN-INTERP | Interpolated Ground | 97457.69 | -4.61 | 251.37 | 0 | 51.91 | 0 | OK | Ground clear controls. | 220 | 51.91 | 303.28
15251 | TIN-INTERP | Interpolated Ground | 97457.7 | 5.1 | 257.41 | 0 | 35.78 | 0 | OK | Ground clear controls. | 220 | 46.26 | 293.19
15252 | TIN-INTERP | Interpolated Ground | 97457.77 | 6.6 | 258.06 | 0 | 40.11 | 0 | OK | Ground clear controls. | 220 | 46.26 | 298.17
15253 | TIN-INTERP | Interpolated Ground | 97457.82 | 4.6 | 257.29 | 0 | 46.26 | 0 | OK | Ground clear controls. | 220 | 46.26 | 303.55
15254 | TIN-INTERP | Interpolated Ground | 97497.6 | -5.11 | 266.59 | 0 | 28.84 | 0 | OK | Ground clear controls. | 220 | 38.87 | 295.43
15255 | TIN-INTERP | Interpolated Ground | 97497.64 | -6.61 | 266.33 | 0 | 34.15 | 0 | OK | Ground clear controls. | 220 | 38.87 | 300.48
15256 | TIN-INTERP | Interpolated Ground | 97497.69 | -4.61 | 266.73 | 0 | 38.87 | 0 | OK | Ground clear controls. | 220 | 38.87 | 305.6
15257 | TIN-INTERP | Interpolated Ground | 97497.7 | 5.1 | 268.09 | 0 | 27.26 | 0 | OK | Ground clear controls. | 220 | 37.74 | 295.35
15258 | TIN-INTERP | Interpolated Ground | 97497.77 | 6.6 | 268.48 | 0 | 31.95 | 0 | OK | Ground clear controls. | 220 | 37.74 | 300.43
15259 | TIN-INTERP | Interpolated Ground | 97497.82 | 4.6 | 268.09 | 0 | 37.74 | 0 | OK | Ground clear controls. | 220 | 37.74 | 305.83
15260 | TIN-INTERP | Interpolated Ground | 97537.6 | -5.11 | 271.35 | 0 | 27.15 | 0 | OK | Ground clear controls. | 220 | 37.31 | 298.5
15261 | TIN-INTERP | Interpolated Ground | 97537.64 | -6.61 | 270.46 | 0 | 33.22 | 0 | OK | Ground clear controls. | 220 | 37.31 | 303.68
15262 | TIN-INTERP | Interpolated Ground | 97537.69 | -4.61 | 271.58 | 0 | 37.31 | 0 | OK | Ground clear controls. | 220 | 37.31 | 308.89
15263 | TIN-INTERP | Interpolated Ground | 97537.7 | 5.09 | 275.19 | 0 | 23.26 | 0 | OK | Ground clear controls. | 220 | 34.08 | 298.45
15264 | TIN-INTERP | Interpolated Ground | 97537.77 | 6.59 | 275.86 | 0 | 27.77 | 0 | OK | Ground clear controls. | 220 | 34.08 | 303.63
15265 | TIN-INTERP | Interpolated Ground | 97537.82 | 4.6 | 274.98 | 0 | 34.08 | 0 | OK | Ground clear controls. | 220 | 34.08 | 309.06
15266 | TIN-INTERP | Interpolated Ground | 97577.6 | -5.11 | 279.89 | 0 | 22.63 | 0 | OK | Ground clear controls. | 220 | 32.79 | 302.52
15267 | TIN-INTERP | Interpolated Ground | 97577.64 | -6.61 | 278.78 | 0 | 29.04 | 0 | OK | Ground clear controls. | 220 | 32.79 | 307.82
15268 | TIN-INTERP | Interpolated Ground | 97577.69 | -4.61 | 280.36 | 0 | 32.79 | 0 | OK | Ground clear controls. | 220 | 32.79 | 313.15
15269 | TIN-INTERP | Interpolated Ground | 97577.7 | 5.09 | 286.59 | 0 | 15.9 | 0 | OK | Ground clear controls. | 220 | 30.07 | 302.49
15270 | TIN-INTERP | Interpolated Ground | 97577.77 | 6.59 | 287.31 | 0 | 20.48 | 0 | OK | Ground clear controls. | 220 | 30.07 | 307.79
15271 | TIN-INTERP | Interpolated Ground | 97577.82 | 4.6 | 286.36 | 0 | 26.9 | 0 | OK | Ground clear controls. | 220 | 30.07 | 313.26
15272 | TIN-INTERP | Interpolated Ground | 97617.6 | -5.11 | 288.14 | 0 | 19.32 | 0 | OK | Ground clear controls. | 220 | 30.07 | 307.46
15273 | TIN-INTERP | Interpolated Ground | 97617.64 | -6.61 | 287.73 | 0 | 25.18 | 0 | OK | Ground clear controls. | 220 | 30.07 | 312.91
15274 | TIN-INTERP | Interpolated Ground | 97617.69 | -4.61 | 288.33 | 0 | 30.07 | 0 | OK | Ground clear controls. | 220 | 30.07 | 318.4
15275 | TIN-INTERP | Interpolated Ground | 97617.7 | 5.09 | 290.79 | 0 | 16.68 | 0 | OK | Ground clear controls. | 220 | 27.78 | 307.47
15276 | TIN-INTERP | Interpolated Ground | 97617.77 | 6.59 | 291.28 | 0 | 21.64 | 0 | OK | Ground clear controls. | 220 | 27.78 | 312.92
15277 | TIN-INTERP | Interpolated Ground | 97617.82 | 4.6 | 290.64 | 0 | 27.78 | 0 | OK | Ground clear controls. | 220 | 27.78 | 318.42
15278 | TIN-INTERP | Interpolated Ground | 97623.28 | -5.11 | 288.83 | 0 | 19.4 | 0 | OK | Ground clear controls. | 221 | 43.8 | 308.23
15279 | TIN-INTERP | Interpolated Ground | 97623.34 | 5.09 | 291.38 | 0 | 16.85 | 0 | OK | Ground clear controls. | 221 | 43.8 | 308.23
15280 | TIN-INTERP | Interpolated Ground | 97623.39 | -6.61 | 288.24 | 0 | 25.48 | 0 | OK | Ground clear controls. | 221 | 43.8 | 313.72
15281 | TIN-INTERP | Interpolated Ground | 97623.42 | -4.61 | 289.06 | 0 | 30.16 | 0 | OK | Ground clear controls. | 221 | 43.8 | 319.22
15282 | TIN-INTERP | Interpolated Ground | 97623.48 | 4.6 | 291.39 | 0 | 27.84 | 0 | OK | Ground clear controls. | 221 | 43.8 | 319.23
15283 | TIN-INTERP | Interpolated Ground | 97623.51 | 6.59 | 291.35 | 0 | 22.37 | 0 | OK | Ground clear controls. | 221 | 43.8 | 313.72
15284 | TIN-INTERP | Interpolated Ground | 97663.28 | -5.15 | 271.72 | 0 | 32.93 | 0 | OK | Ground clear controls. | 221 | 43.8 | 304.65
15285 | TIN-INTERP | Interpolated Ground | 97663.34 | 5.06 | 278.36 | 0 | 26.28 | 0 | OK | Ground clear controls. | 221 | 43.8 | 304.64
15286 | TIN-INTERP | Interpolated Ground | 97663.39 | -6.65 | 271.09 | 0 | 39.04 | 0 | OK | Ground clear controls. | 221 | 43.8 | 310.13
15287 | TIN-INTERP | Interpolated Ground | 97663.42 | -4.65 | 271.79 | 0 | 43.8 | 0 | OK | Ground clear controls. | 221 | 43.8 | 315.59
15288 | TIN-INTERP | Interpolated Ground | 97663.48 | 4.56 | 278.22 | 0 | 37.38 | 0 | OK | Ground clear controls. | 221 | 40.8 | 315.6
15289 | TIN-INTERP | Interpolated Ground | 97663.51 | 6.56 | 278.49 | 0 | 31.62 | 0 | OK | Ground clear controls. | 221 | 40.8 | 310.11
15290 | TIN-INTERP | Interpolated Ground | 97703.28 | -5.19 | 274.14 | 0 | 27.9 | 0 | OK | Ground clear controls. | 221 | 40.8 | 302.04
15291 | TIN-INTERP | Interpolated Ground | 97703.34 | 5.02 | 272.15 | 0 | 29.85 | 0 | OK | Ground clear controls. | 221 | 40.8 | 302
15292 | TIN-INTERP | Interpolated Ground | 97703.39 | -6.69 | 274.03 | 0 | 33.47 | 0 | OK | Ground clear controls. | 221 | 40.8 | 307.5
15293 | TIN-INTERP | Interpolated Ground | 97703.42 | -4.69 | 274.14 | 0 | 38.78 | 0 | OK | Ground clear controls. | 221 | 40.8 | 312.92
15294 | TIN-INTERP | Interpolated Ground | 97703.48 | 4.52 | 272.15 | 0 | 40.8 | 0 | OK | Ground clear controls. | 221 | 40.8 | 312.95
15295 | TIN-INTERP | Interpolated Ground | 97703.51 | 6.52 | 272.15 | 0 | 35.32 | 0 | OK | Ground clear controls. | 221 | 39.12 | 307.47
15296 | TIN-INTERP | Interpolated Ground | 97743.28 | -5.23 | 272.16 | 0 | 28.21 | 0 | OK | Ground clear controls. | 221 | 39.12 | 300.37
15297 | TIN-INTERP | Interpolated Ground | 97743.34 | 4.98 | 272.16 | 0 | 28.17 | 0 | OK | Ground clear controls. | 221 | 39.12 | 300.33
15298 | TIN-INTERP | Interpolated Ground | 97743.39 | -6.73 | 272.18 | 0 | 33.64 | 0 | OK | Ground clear controls. | 221 | 39.12 | 305.82
15299 | TIN-INTERP | Interpolated Ground | 97743.42 | -4.73 | 272.16 | 0 | 39.09 | 0 | OK | Ground clear controls. | 221 | 39.12 | 311.25
15300 | TIN-INTERP | Interpolated Ground | 97743.48 | 4.48 | 272.16 | 0 | 39.12 | 0 | OK | Ground clear controls. | 221 | 39.12 | 311.28
15301 | TIN-INTERP | Interpolated Ground | 97743.51 | 6.48 | 272.16 | 0 | 33.64 | 0 | OK | Ground clear controls. | 221 | 33.64 | 305.8
15302 | TIN-INTERP | Interpolated Ground | 97783.28 | -5.27 | 282.58 | 0 | 17.07 | 0 | OK | Ground clear controls. | 221 | 27.92 | 299.65
15303 | TIN-INTERP | Interpolated Ground | 97783.34 | 4.94 | 283.46 | 0 | 16.15 | 0 | OK | Ground clear controls. | 221 | 27.92 | 299.61
15304 | TIN-INTERP | Interpolated Ground | 97783.39 | -6.77 | 282.36 | 0 | 22.76 | 0 | OK | Ground clear controls. | 221 | 27.92 | 305.12
15305 | TIN-INTERP | Interpolated Ground | 97783.42 | -4.77 | 282.64 | 0 | 27.92 | 0 | OK | Ground clear controls. | 221 | 27.92 | 310.56
15306 | TIN-INTERP | Interpolated Ground | 97783.48 | 4.45 | 283.41 | 0 | 27.17 | 0 | OK | Ground clear controls. | 221 | 27.17 | 310.58
15307 | TIN-INTERP | Interpolated Ground | 97783.51 | 6.44 | 283.55 | 0 | 21.54 | 0 | OK | Ground clear controls. | 221 | 26.04 | 305.09
15308 | TIN-INTERP | Interpolated Ground | 97823.28 | -5.31 | 284.59 | 0 | 15.28 | 0 | OK | Ground clear controls. | 221 | 26.04 | 299.87
15309 | TIN-INTERP | Interpolated Ground | 97823.34 | 4.9 | 287.26 | 0 | 12.59 | 0 | OK | Ground clear controls. | 221 | 26.04 | 299.85
15310 | TIN-INTERP | Interpolated Ground | 97823.39 | -6.81 | 283.97 | 0 | 21.39 | 0 | OK | Ground clear controls. | 221 | 26.04 | 305.36
15311 | TIN-INTERP | Interpolated Ground | 97823.42 | -4.81 | 284.8 | 0 | 26.04 | 0 | OK | Ground clear controls. | 221 | 26.04 | 310.84
15312 | TIN-INTERP | Interpolated Ground | 97823.48 | 4.41 | 286.98 | 0 | 23.87 | 0 | OK | Ground clear controls. | 221 | 23.87 | 310.85
15313 | TIN-INTERP | Interpolated Ground | 97823.51 | 6.41 | 287.9 | 0 | 17.45 | 0 | OK | Ground clear controls. | 221 | 17.45 | 305.35
15314 | TIN-INTERP | Interpolated Ground | 97836.12 | -5.32 | 285.17 | 0 | 14.98 | 0 | OK | Ground clear controls. | 222 | 123.4 | 300.15
15315 | TIN-INTERP | Interpolated Ground | 97836.15 | -6.82 | 284.72 | 0 | 20.92 | 0 | OK | Ground clear controls. | 222 | 123.4 | 305.64
15316 | TIN-INTERP | Interpolated Ground | 97836.23 | -4.82 | 285.25 | 0 | 25.89 | 0 | OK | Ground clear controls. | 222 | 123.4 | 311.14
15317 | TIN-INTERP | Interpolated Ground | 97836.33 | 4.4 | 286.09 | 0 | 25.05 | 0 | OK | Ground clear controls. | 222 | 123.4 | 311.14
15318 | TIN-INTERP | Interpolated Ground | 97836.37 | 6.39 | 286.18 | 0 | 19.46 | 0 | OK | Ground clear controls. | 222 | 123.4 | 305.64
15319 | TIN-INTERP | Interpolated Ground | 97836.41 | 4.89 | 286.13 | 0 | 14.01 | 0 | OK | Ground clear controls. | 222 | 123.4 | 300.14
15320 | TIN-INTERP | Interpolated Ground | 97876.22 | 6.43 | 272.43 | 0 | 26.53 | 0 | OK | Ground clear controls. | 222 | 123.4 | 298.96
15321 | TIN-INTERP | Interpolated Ground | 97876.23 | 4.44 | 272.31 | 0 | 32.14 | 0 | OK | Ground clear controls. | 222 | 123.4 | 304.45
15322 | TIN-INTERP | Interpolated Ground | 97876.24 | -5.34 | 272.24 | 0 | 21.28 | 0 | OK | Ground clear controls. | 222 | 123.4 | 293.52
15323 | TIN-INTERP | Interpolated Ground | 97876.3 | 4.93 | 272.34 | 0 | 21.19 | 0 | OK | Ground clear controls. | 222 | 123.4 | 293.53
15324 | TIN-INTERP | Interpolated Ground | 97876.3 | -6.84 | 272.4 | 0 | 26.58 | 0 | OK | Ground clear controls. | 222 | 123.4 | 298.98
15325 | TIN-INTERP | Interpolated Ground | 97876.34 | -4.84 | 272.21 | 0 | 32.21 | 0 | OK | Ground clear controls. | 222 | 123.4 | 304.42
15326 | TIN-INTERP | Interpolated Ground | 97916.22 | 6.47 | 266.17 | 0 | 27.1 | 0 | OK | Ground clear controls. | 222 | 123.4 | 293.27
15327 | TIN-INTERP | Interpolated Ground | 97916.23 | 4.49 | 265.84 | 0 | 32.93 | 0 | OK | Ground clear controls. | 222 | 123.4 | 298.77
15328 | TIN-INTERP | Interpolated Ground | 97916.24 | -5.35 | 265.12 | 0 | 22.75 | 0 | OK | Ground clear controls. | 222 | 123.4 | 287.87
15329 | TIN-INTERP | Interpolated Ground | 97916.3 | 4.97 | 265.95 | 0 | 21.94 | 0 | OK | Ground clear controls. | 222 | 123.4 | 287.89
15330 | TIN-INTERP | Interpolated Ground | 97916.3 | -6.85 | 264.85 | 0 | 28.45 | 0 | OK | Ground clear controls. | 222 | 123.4 | 293.3
15331 | TIN-INTERP | Interpolated Ground | 97916.34 | -4.87 | 265.21 | 0 | 33.5 | 0 | OK | Ground clear controls. | 222 | 123.4 | 298.71
15332 | TIN-INTERP | Interpolated Ground | 97956.22 | 6.51 | 235.8 | 0 | 52.78 | 0 | OK | Ground clear controls. | 222 | 123.4 | 288.58
15333 | TIN-INTERP | Interpolated Ground | 97956.23 | 4.54 | 236.04 | 0 | 58.03 | 0 | OK | Ground clear controls. | 222 | 123.4 | 294.07
15334 | TIN-INTERP | Interpolated Ground | 97956.24 | -5.36 | 235.63 | 0 | 47.56 | 0 | OK | Ground clear controls. | 222 | 123.4 | 283.19
15335 | TIN-INTERP | Interpolated Ground | 97956.3 | 5.01 | 235.96 | 0 | 47.27 | 0 | OK | Ground clear controls. | 222 | 123.4 | 283.23
15336 | TIN-INTERP | Interpolated Ground | 97956.3 | -6.86 | 235.4 | 0 | 53.21 | 0 | OK | Ground clear controls. | 222 | 123.4 | 288.61
15337 | TIN-INTERP | Interpolated Ground | 97956.34 | -4.89 | 235.64 | 0 | 58.36 | 0 | OK | Ground clear controls. | 222 | 123.4 | 294
15338 | TIN-INTERP | Interpolated Ground | 97996.22 | 6.55 | 216.65 | 0 | 68.2 | 0 | OK | Ground clear controls. | 222 | 123.4 | 284.85
15339 | TIN-INTERP | Interpolated Ground | 97996.23 | 4.58 | 216.58 | 0 | 73.79 | 0 | OK | Ground clear controls. | 222 | 123.4 | 290.37
15340 | TIN-INTERP | Interpolated Ground | 97996.24 | -5.38 | 216.8 | 0 | 62.7 | 0 | OK | Ground clear controls. | 222 | 123.4 | 279.5
15341 | TIN-INTERP | Interpolated Ground | 97996.3 | 5.05 | 216.58 | 0 | 62.95 | 0 | OK | Ground clear controls. | 222 | 123.4 | 279.53
15342 | TIN-INTERP | Interpolated Ground | 97996.3 | -6.87 | 216.69 | 0 | 68.2 | 0 | OK | Ground clear controls. | 222 | 123.4 | 284.89
15343 | TIN-INTERP | Interpolated Ground | 97996.34 | -4.91 | 216.86 | 0 | 73.42 | 0 | OK | Ground clear controls. | 222 | 123.4 | 290.28
15344 | TIN-INTERP | Interpolated Ground | 98036.22 | 6.59 | 200.45 | 0 | 81.67 | 0 | OK | Ground clear controls. | 222 | 123.4 | 282.12
15345 | TIN-INTERP | Interpolated Ground | 98036.23 | 4.63 | 199.41 | 0 | 88.24 | 0 | OK | Ground clear controls. | 222 | 123.4 | 287.65
15346 | TIN-INTERP | Interpolated Ground | 98036.24 | -5.39 | 196.1 | 0 | 80.66 | 0 | OK | Ground clear controls. | 222 | 123.4 | 276.76
15347 | TIN-INTERP | Interpolated Ground | 98036.3 | 5.08 | 199.61 | 0 | 77.2 | 0 | OK | Ground clear controls. | 222 | 123.4 | 276.81
15348 | TIN-INTERP | Interpolated Ground | 98036.3 | -6.89 | 196.7 | 0 | 85.46 | 0 | OK | Ground clear controls. | 222 | 123.4 | 282.16
15349 | TIN-INTERP | Interpolated Ground | 98036.34 | -4.93 | 195.9 | 0 | 91.66 | 0 | OK | Ground clear controls. | 222 | 123.4 | 287.56
15350 | TIN-INTERP | Interpolated Ground | 98076.22 | 6.62 | 166.57 | 0 | 113.79 | 0 | OK | Ground clear controls. | 222 | 123.4 | 280.36
15351 | TIN-INTERP | Interpolated Ground | 98076.23 | 4.68 | 165.85 | 0 | 120.07 | 0 | OK | Ground clear controls. | 222 | 123.4 | 285.92
15352 | TIN-INTERP | Interpolated Ground | 98076.24 | -5.4 | 161.83 | 0 | 113.17 | 0 | OK | Ground clear controls. | 222 | 123.4 | 275
15353 | TIN-INTERP | Interpolated Ground | 98076.3 | 5.12 | 166.17 | 0 | 108.88 | 0 | OK | Ground clear controls. | 222 | 123.4 | 275.05
15354 | TIN-INTERP | Interpolated Ground | 98076.3 | -6.9 | 161.21 | 0 | 119.18 | 0 | OK | Ground clear controls. | 222 | 123.4 | 280.39
15355 | TIN-INTERP | Interpolated Ground | 98076.34 | -4.95 | 162.44 | 0 | 123.4 | 0 | OK | Ground clear controls. | 222 | 123.4 | 285.84
15356 | TIN-INTERP | Interpolated Ground | 98116.22 | 6.66 | 190.5 | 0 | 89.08 | 0 | OK | Ground clear controls. | 222 | 94.51 | 279.58
15357 | TIN-INTERP | Interpolated Ground | 98116.23 | 4.73 | 190.67 | 0 | 94.51 | 0 | OK | Ground clear controls. | 222 | 94.51 | 285.18
15358 | TIN-INTERP | Interpolated Ground | 98116.24 | -5.41 | 195.82 | 0 | 78.38 | 0 | OK | Ground clear controls. | 222 | 89.49 | 274.2
15359 | TIN-INTERP | Interpolated Ground | 98116.3 | 5.16 | 190.67 | 0 | 83.58 | 0 | OK | Ground clear controls. | 222 | 89.49 | 274.25
15360 | TIN-INTERP | Interpolated Ground | 98116.3 | -6.91 | 196.66 | 0 | 82.95 | 0 | OK | Ground clear controls. | 222 | 89.49 | 279.61
15361 | TIN-INTERP | Interpolated Ground | 98116.34 | -4.97 | 195.61 | 0 | 89.49 | 0 | OK | Ground clear controls. | 222 | 89.49 | 285.1
15362 | TIN-INTERP | Interpolated Ground | 98156.22 | 6.7 | 235.92 | 0 | 43.86 | 0 | OK | Ground clear controls. | 222 | 49.57 | 279.78
15363 | TIN-INTERP | Interpolated Ground | 98156.23 | 4.77 | 235.86 | 0 | 49.57 | 0 | OK | Ground clear controls. | 222 | 49.57 | 285.43
15364 | TIN-INTERP | Interpolated Ground | 98156.24 | -5.43 | 236.01 | 0 | 38.38 | 0 | OK | Ground clear controls. | 222 | 49.33 | 274.39
15365 | TIN-INTERP | Interpolated Ground | 98156.3 | 5.2 | 235.89 | 0 | 38.53 | 0 | OK | Ground clear controls. | 222 | 49.33 | 274.42
15366 | TIN-INTERP | Interpolated Ground | 98156.3 | -6.92 | 236.04 | 0 | 43.77 | 0 | OK | Ground clear controls. | 222 | 49.33 | 279.81
15367 | TIN-INTERP | Interpolated Ground | 98156.34 | -5 | 236.03 | 0 | 49.33 | 0 | OK | Ground clear controls. | 222 | 49.33 | 285.36
15368 | TIN-INTERP | Interpolated Ground | 98196.22 | 6.74 | 247.16 | 0 | 33.8 | 0 | OK | Ground clear controls. | 222 | 39.46 | 280.96
15369 | TIN-INTERP | Interpolated Ground | 98196.23 | 4.82 | 247.19 | 0 | 39.46 | 0 | OK | Ground clear controls. | 222 | 39.46 | 286.65
15370 | TIN-INTERP | Interpolated Ground | 98196.24 | -5.44 | 247.4 | 0 | 28.12 | 0 | OK | Ground clear controls. | 222 | 39.19 | 275.52
15371 | TIN-INTERP | Interpolated Ground | 98196.3 | 5.24 | 247.19 | 0 | 28.36 | 0 | OK | Ground clear controls. | 222 | 39.19 | 275.55
15372 | TIN-INTERP | Interpolated Ground | 98196.3 | -6.94 | 247.47 | 0 | 33.5 | 0 | OK | Ground clear controls. | 222 | 39.19 | 280.97
15373 | TIN-INTERP | Interpolated Ground | 98196.34 | -5.02 | 247.41 | 0 | 39.19 | 0 | OK | Ground clear controls. | 222 | 39.19 | 286.6
15374 | TIN-INTERP | Interpolated Ground | 98236.22 | 6.78 | 251.73 | 0 | 31.38 | 0 | OK | Ground clear controls. | 222 | 37.95 | 283.11
15375 | TIN-INTERP | Interpolated Ground | 98236.23 | 4.87 | 251.6 | 0 | 37.27 | 0 | OK | Ground clear controls. | 222 | 37.95 | 288.87
15376 | TIN-INTERP | Interpolated Ground | 98236.24 | -5.45 | 250.85 | 0 | 26.79 | 0 | OK | Ground clear controls. | 222 | 37.95 | 277.64
15377 | TIN-INTERP | Interpolated Ground | 98236.3 | 5.28 | 251.62 | 0 | 26.04 | 0 | OK | Ground clear controls. | 222 | 37.95 | 277.66
15378 | TIN-INTERP | Interpolated Ground | 98236.3 | -6.95 | 250.68 | 0 | 32.43 | 0 | OK | Ground clear controls. | 222 | 37.95 | 283.11
15379 | TIN-INTERP | Interpolated Ground | 98236.34 | -5.04 | 250.9 | 0 | 37.95 | 0 | OK | Ground clear controls. | 222 | 37.95 | 288.85
15380 | TIN-INTERP | Interpolated Ground | 98261.92 | 4.9 | 253.32 | 0 | 37.49 | 0 | OK | Ground clear controls. | 223 | 42.88 | 290.81
15381 | TIN-INTERP | Interpolated Ground | 98261.95 | 6.8 | 253.41 | 0 | 31.61 | 0 | OK | Ground clear controls. | 223 | 42.88 | 285.02
15382 | TIN-INTERP | Interpolated Ground | 98261.97 | -5.05 | 252.29 | 0 | 38.52 | 0 | OK | Ground clear controls. | 223 | 42.88 | 290.81
15383 | TIN-INTERP | Interpolated Ground | 98261.99 | 5.3 | 253.34 | 0 | 26.17 | 0 | OK | Ground clear controls. | 223 | 42.88 | 279.51
15384 | TIN-INTERP | Interpolated Ground | 98262.02 | -5.46 | 252.28 | 0 | 27.23 | 0 | OK | Ground clear controls. | 223 | 42.88 | 279.51
15385 | TIN-INTERP | Interpolated Ground | 98262.03 | -6.96 | 252.14 | 0 | 32.87 | 0 | OK | Ground clear controls. | 223 | 42.88 | 285.01
15386 | TIN-INTERP | Interpolated Ground | 98301.92 | 4.86 | 250.05 | 0 | 38.16 | 0 | OK | Ground clear controls. | 223 | 42.88 | 288.21
15387 | TIN-INTERP | Interpolated Ground | 98301.95 | 6.77 | 250.23 | 0 | 32.26 | 0 | OK | Ground clear controls. | 223 | 42.88 | 282.49
15388 | TIN-INTERP | Interpolated Ground | 98301.97 | -5.02 | 248.75 | 0 | 39.45 | 0 | OK | Ground clear controls. | 223 | 42.88 | 288.2
15389 | TIN-INTERP | Interpolated Ground | 98301.99 | 5.27 | 250.1 | 0 | 26.96 | 0 | OK | Ground clear controls. | 223 | 42.88 | 277.06
15390 | TIN-INTERP | Interpolated Ground | 98302.02 | -5.44 | 248.66 | 0 | 28.4 | 0 | OK | Ground clear controls. | 223 | 42.88 | 277.06
15391 | TIN-INTERP | Interpolated Ground | 98302.03 | -6.94 | 248.3 | 0 | 34.23 | 0 | OK | Ground clear controls. | 223 | 42.88 | 282.53
15392 | TIN-INTERP | Interpolated Ground | 98341.92 | 4.82 | 249.77 | 0 | 36.83 | 0 | OK | Ground clear controls. | 223 | 42.88 | 286.6
15393 | TIN-INTERP | Interpolated Ground | 98341.95 | 6.74 | 249.9 | 0 | 31.04 | 0 | OK | Ground clear controls. | 223 | 42.88 | 280.94
15394 | TIN-INTERP | Interpolated Ground | 98341.97 | -4.99 | 249.03 | 0 | 37.55 | 0 | OK | Ground clear controls. | 223 | 42.88 | 286.58
15395 | TIN-INTERP | Interpolated Ground | 98341.99 | 5.24 | 249.8 | 0 | 25.78 | 0 | OK | Ground clear controls. | 223 | 42.88 | 275.58
15396 | TIN-INTERP | Interpolated Ground | 98342.02 | -5.42 | 248.99 | 0 | 26.58 | 0 | OK | Ground clear controls. | 223 | 42.88 | 275.57
15397 | TIN-INTERP | Interpolated Ground | 98342.03 | -6.92 | 248.86 | 0 | 32.15 | 0 | OK | Ground clear controls. | 223 | 42.88 | 281.01
15398 | TIN-INTERP | Interpolated Ground | 98381.92 | 4.78 | 250.42 | 0 | 35.57 | 0 | OK | Ground clear controls. | 223 | 42.88 | 285.99
15399 | TIN-INTERP | Interpolated Ground | 98381.95 | 6.71 | 250.47 | 0 | 29.92 | 0 | OK | Ground clear controls. | 223 | 42.88 | 280.39
15400 | TIN-INTERP | Interpolated Ground | 98381.97 | -4.97 | 249.67 | 0 | 36.29 | 0 | OK | Ground clear controls. | 223 | 42.88 | 285.96
15401 | TIN-INTERP | Interpolated Ground | 98381.99 | 5.21 | 250.41 | 0 | 24.65 | 0 | OK | Ground clear controls. | 223 | 42.88 | 275.06
15402 | TIN-INTERP | Interpolated Ground | 98382.02 | -5.4 | 249.63 | 0 | 25.43 | 0 | OK | Ground clear controls. | 223 | 42.88 | 275.06
15403 | TIN-INTERP | Interpolated Ground | 98382.03 | -6.9 | 249.51 | 0 | 30.97 | 0 | OK | Ground clear controls. | 223 | 42.88 | 280.48
15404 | TIN-INTERP | Interpolated Ground | 98421.92 | 4.73 | 250.7 | 0 | 35.67 | 0 | OK | Ground clear controls. | 223 | 42.88 | 286.37
15405 | TIN-INTERP | Interpolated Ground | 98421.95 | 6.67 | 250.86 | 0 | 29.96 | 0 | OK | Ground clear controls. | 223 | 42.88 | 280.82
15406 | TIN-INTERP | Interpolated Ground | 98421.97 | -4.94 | 250.4 | 0 | 35.93 | 0 | OK | Ground clear controls. | 223 | 42.88 | 286.33
15407 | TIN-INTERP | Interpolated Ground | 98421.99 | 5.17 | 250.74 | 0 | 24.78 | 0 | OK | Ground clear controls. | 223 | 42.88 | 275.52
15408 | TIN-INTERP | Interpolated Ground | 98422.02 | -5.38 | 250.43 | 0 | 25.08 | 0 | OK | Ground clear controls. | 223 | 42.88 | 275.51
15409 | TIN-INTERP | Interpolated Ground | 98422.03 | -6.88 | 250.44 | 0 | 30.48 | 0 | OK | Ground clear controls. | 223 | 42.88 | 280.92
15410 | TIN-INTERP | Interpolated Ground | 98461.92 | 4.69 | 250.81 | 0 | 36.92 | 0 | OK | Ground clear controls. | 223 | 42.88 | 287.73
15411 | TIN-INTERP | Interpolated Ground | 98461.95 | 6.64 | 250.84 | 0 | 31.37 | 0 | OK | Ground clear controls. | 223 | 42.88 | 282.21
15412 | TIN-INTERP | Interpolated Ground | 98461.97 | -4.91 | 250 | 0 | 37.7 | 0 | OK | Ground clear controls. | 223 | 42.88 | 287.7
15413 | TIN-INTERP | Interpolated Ground | 98461.99 | 5.14 | 250.82 | 0 | 26.12 | 0 | OK | Ground clear controls. | 223 | 42.88 | 276.94
15414 | TIN-INTERP | Interpolated Ground | 98462.02 | -5.36 | 249.98 | 0 | 26.95 | 0 | OK | Ground clear controls. | 223 | 42.88 | 276.93
15415 | TIN-INTERP | Interpolated Ground | 98462.03 | -6.86 | 249.63 | 0 | 32.71 | 0 | OK | Ground clear controls. | 223 | 42.88 | 282.34
15416 | TIN-INTERP | Interpolated Ground | 98501.92 | 4.65 | 249.53 | 0 | 40.57 | 0 | OK | Ground clear controls. | 223 | 42.88 | 290.1
15417 | TIN-INTERP | Interpolated Ground | 98501.95 | 6.61 | 250.19 | 0 | 34.42 | 0 | OK | Ground clear controls. | 223 | 42.88 | 284.61
15418 | TIN-INTERP | Interpolated Ground | 98501.97 | -4.88 | 247.19 | 0 | 42.88 | 0 | OK | Ground clear controls. | 223 | 42.88 | 290.07
15419 | TIN-INTERP | Interpolated Ground | 98501.99 | 5.11 | 249.65 | 0 | 29.68 | 0 | OK | Ground clear controls. | 223 | 42 | 279.33
15420 | TIN-INTERP | Interpolated Ground | 98502.02 | -5.34 | 247.18 | 0 | 32.14 | 0 | OK | Ground clear controls. | 223 | 42 | 279.32
15421 | TIN-INTERP | Interpolated Ground | 98502.03 | -6.84 | 247.3 | 0 | 37.44 | 0 | OK | Ground clear controls. | 223 | 42 | 284.74
15422 | TIN-INTERP | Interpolated Ground | 98541.92 | 4.61 | 252.57 | 0 | 40.88 | 0 | OK | Ground clear controls. | 223 | 42 | 293.45
15423 | TIN-INTERP | Interpolated Ground | 98541.95 | 6.58 | 252.91 | 0 | 35.07 | 0 | OK | Ground clear controls. | 223 | 42 | 287.98
15424 | TIN-INTERP | Interpolated Ground | 98541.97 | -4.85 | 251.43 | 0 | 42 | 0 | OK | Ground clear controls. | 223 | 42 | 293.43
15425 | TIN-INTERP | Interpolated Ground | 98541.99 | 5.08 | 252.67 | 0 | 30.01 | 0 | OK | Ground clear controls. | 223 | 40.47 | 282.68
15426 | TIN-INTERP | Interpolated Ground | 98542.02 | -5.32 | 251.37 | 0 | 31.31 | 0 | OK | Ground clear controls. | 223 | 40.47 | 282.68
15427 | TIN-INTERP | Interpolated Ground | 98542.03 | -6.82 | 251.06 | 0 | 37.03 | 0 | OK | Ground clear controls. | 223 | 40.47 | 288.09
15428 | TIN-INTERP | Interpolated Ground | 98581.92 | 4.57 | 260.34 | 0 | 37.47 | 0 | OK | Ground clear controls. | 223 | 40.47 | 297.81
15429 | TIN-INTERP | Interpolated Ground | 98581.95 | 6.55 | 260.75 | 0 | 31.59 | 0 | OK | Ground clear controls. | 223 | 40.47 | 292.34
15430 | TIN-INTERP | Interpolated Ground | 98581.97 | -4.82 | 257.32 | 0 | 40.47 | 0 | OK | Ground clear controls. | 223 | 40.47 | 297.79
15431 | TIN-INTERP | Interpolated Ground | 98581.99 | 5.05 | 260.5 | 0 | 26.51 | 0 | OK | Ground clear controls. | 223 | 35.44 | 287.01
15432 | TIN-INTERP | Interpolated Ground | 98582.02 | -5.3 | 257.25 | 0 | 29.76 | 0 | OK | Ground clear controls. | 223 | 35.44 | 287.01
15433 | TIN-INTERP | Interpolated Ground | 98582.03 | -6.8 | 257.01 | 0 | 35.44 | 0 | OK | Ground clear controls. | 223 | 35.44 | 292.45
15434 | TIN-INTERP | Interpolated Ground | 98621.92 | 4.53 | 274.72 | 0 | 28.43 | 0 | OK | Ground clear controls. | 223 | 32.58 | 303.15
15435 | TIN-INTERP | Interpolated Ground | 98621.95 | 6.51 | 275.77 | 0 | 21.92 | 0 | OK | Ground clear controls. | 223 | 32.58 | 297.69
15436 | TIN-INTERP | Interpolated Ground | 98621.97 | -4.79 | 270.58 | 0 | 32.58 | 0 | OK | Ground clear controls. | 223 | 32.58 | 303.16
15437 | TIN-INTERP | Interpolated Ground | 98621.99 | 5.01 | 274.95 | 0 | 17.36 | 0 | OK | Ground clear controls. | 223 | 27.44 | 292.31
15438 | TIN-INTERP | Interpolated Ground | 98622.02 | -5.28 | 270.51 | 0 | 21.81 | 0 | OK | Ground clear controls. | 223 | 27.44 | 292.32
15439 | TIN-INTERP | Interpolated Ground | 98622.03 | -6.78 | 270.48 | 0 | 27.3 | 0 | OK | Ground clear controls. | 223 | 27.44 | 297.78
15440 | TIN-INTERP | Interpolated Ground | 98661.92 | 4.49 | 285.27 | 0 | 24.24 | 0 | OK | Ground clear controls. | 223 | 27.44 | 309.51
15441 | TIN-INTERP | Interpolated Ground | 98661.95 | 6.48 | 285.76 | 0 | 18.26 | 0 | OK | Ground clear controls. | 223 | 27.44 | 304.02
15442 | TIN-INTERP | Interpolated Ground | 98661.97 | -4.76 | 282.09 | 0 | 27.44 | 0 | OK | Ground clear controls. | 223 | 27.44 | 309.53
15443 | TIN-INTERP | Interpolated Ground | 98661.99 | 4.98 | 285.37 | 0 | 13.21 | 0 | OK | Ground clear controls. | 223 | 22.72 | 298.58
15444 | TIN-INTERP | Interpolated Ground | 98662.02 | -5.26 | 281.95 | 0 | 16.66 | 0 | OK | Ground clear controls. | 223 | 22.72 | 298.61
15445 | TIN-INTERP | Interpolated Ground | 98662.03 | -6.76 | 281.37 | 0 | 22.72 | 0 | OK | Ground clear controls. | 223 | 22.72 | 304.09
15446 | TIN-INTERP | Interpolated Ground | 98684.7 | -6.75 | 280.27 | 0 | 27.84 | 0 | OK | Ground clear controls. | 224 | 39.66 | 308.11
15447 | TIN-INTERP | Interpolated Ground | 98684.72 | -5.25 | 280.91 | 0 | 21.7 | 0 | OK | Ground clear controls. | 224 | 39.66 | 302.61
15448 | TIN-INTERP | Interpolated Ground | 98684.76 | -4.75 | 280.96 | 0 | 32.65 | 0 | OK | Ground clear controls. | 224 | 39.66 | 313.61
15449 | TIN-INTERP | Interpolated Ground | 98684.82 | 4.96 | 282.07 | 0 | 20.54 | 0 | OK | Ground clear controls. | 224 | 39.66 | 302.61
15450 | TIN-INTERP | Interpolated Ground | 98684.87 | 6.46 | 282.39 | 0 | 25.72 | 0 | OK | Ground clear controls. | 224 | 39.66 | 308.11
15451 | TIN-INTERP | Interpolated Ground | 98684.87 | 4.47 | 281.95 | 0 | 31.66 | 0 | OK | Ground clear controls. | 224 | 39.66 | 313.61
15452 | TIN-INTERP | Interpolated Ground | 98724.73 | -6.73 | 266.66 | 0 | 35.58 | 0 | OK | Ground clear controls. | 224 | 39.66 | 302.24
15453 | TIN-INTERP | Interpolated Ground | 98724.75 | -5.23 | 267.71 | 0 | 29.08 | 0 | OK | Ground clear controls. | 224 | 39.66 | 296.79
15454 | TIN-INTERP | Interpolated Ground | 98724.78 | -4.73 | 268.02 | 0 | 39.66 | 0 | OK | Ground clear controls. | 224 | 39.66 | 307.68
15455 | TIN-INTERP | Interpolated Ground | 98724.82 | 4.98 | 273.33 | 0 | 23.47 | 0 | OK | Ground clear controls. | 224 | 37.56 | 296.8
15456 | TIN-INTERP | Interpolated Ground | 98724.87 | 6.48 | 274.01 | 0 | 28.24 | 0 | OK | Ground clear controls. | 224 | 37.56 | 302.25
15457 | TIN-INTERP | Interpolated Ground | 98724.87 | 4.48 | 273.1 | 0 | 34.61 | 0 | OK | Ground clear controls. | 224 | 37.56 | 307.71
15458 | TIN-INTERP | Interpolated Ground | 98764.73 | -6.72 | 271.19 | 0 | 26.17 | 0 | OK | Ground clear controls. | 224 | 37.56 | 297.36
15459 | TIN-INTERP | Interpolated Ground | 98764.75 | -5.22 | 271.89 | 0 | 20.05 | 0 | OK | Ground clear controls. | 224 | 37.56 | 291.94
15460 | TIN-INTERP | Interpolated Ground | 98764.78 | -4.72 | 272.14 | 0 | 30.59 | 0 | OK | Ground clear controls. | 224 | 37.56 | 302.73
15461 | TIN-INTERP | Interpolated Ground | 98764.82 | 4.99 | 276.88 | 0 | 15.08 | 0 | OK | Ground clear controls. | 224 | 37.56 | 291.96
15462 | TIN-INTERP | Interpolated Ground | 98764.87 | 6.49 | 277.26 | 0 | 20.1 | 0 | OK | Ground clear controls. | 224 | 37.56 | 297.36
15463 | TIN-INTERP | Interpolated Ground | 98764.87 | 4.49 | 276.63 | 0 | 26.16 | 0 | OK | Ground clear controls. | 224 | 37.56 | 302.79
15464 | TIN-INTERP | Interpolated Ground | 98804.73 | -6.71 | 268.81 | 0 | 24.66 | 0 | OK | Ground clear controls. | 224 | 37.56 | 293.47
15465 | TIN-INTERP | Interpolated Ground | 98804.75 | -5.21 | 269.22 | 0 | 18.85 | 0 | OK | Ground clear controls. | 224 | 37.56 | 288.07
15466 | TIN-INTERP | Interpolated Ground | 98804.78 | -4.71 | 269.35 | 0 | 29.44 | 0 | OK | Ground clear controls. | 224 | 37.56 | 298.79
15467 | TIN-INTERP | Interpolated Ground | 98804.82 | 5 | 273.29 | 0 | 14.81 | 0 | OK | Ground clear controls. | 224 | 37.56 | 288.1
15468 | TIN-INTERP | Interpolated Ground | 98804.87 | 6.5 | 273.82 | 0 | 19.66 | 0 | OK | Ground clear controls. | 224 | 37.56 | 293.48
15469 | TIN-INTERP | Interpolated Ground | 98804.87 | 4.5 | 273.1 | 0 | 25.78 | 0 | OK | Ground clear controls. | 224 | 37.56 | 298.88
15470 | TIN-INTERP | Interpolated Ground | 98844.73 | -6.69 | 270.4 | 0 | 20.16 | 0 | OK | Ground clear controls. | 224 | 37.56 | 290.56
15471 | TIN-INTERP | Interpolated Ground | 98844.75 | -5.19 | 270.52 | 0 | 14.65 | 0 | OK | Ground clear controls. | 224 | 37.56 | 285.17
15472 | TIN-INTERP | Interpolated Ground | 98844.78 | -4.69 | 270.51 | 0 | 25.34 | 0 | OK | Ground clear controls. | 224 | 37.56 | 295.85
15473 | TIN-INTERP | Interpolated Ground | 98844.82 | 5.01 | 271.37 | 0 | 13.83 | 0 | OK | Ground clear controls. | 224 | 37.56 | 285.2
15474 | TIN-INTERP | Interpolated Ground | 98844.87 | 6.51 | 271.67 | 0 | 18.88 | 0 | OK | Ground clear controls. | 224 | 37.56 | 290.55
15475 | TIN-INTERP | Interpolated Ground | 98844.87 | 4.52 | 271.33 | 0 | 24.61 | 0 | OK | Ground clear controls. | 224 | 37.56 | 295.94
15476 | TIN-INTERP | Interpolated Ground | 98884.73 | -6.68 | 272.64 | 0 | 15.98 | 0 | OK | Ground clear controls. | 224 | 37.56 | 288.62
15477 | TIN-INTERP | Interpolated Ground | 98884.75 | -5.18 | 272.27 | 0 | 10.97 | 0 | OK | Ground clear controls. | 224 | 37.56 | 283.24
15478 | TIN-INTERP | Interpolated Ground | 98884.78 | -4.68 | 272.13 | 0 | 21.77 | 0 | OK | Ground clear controls. | 224 | 37.56 | 293.9
15479 | TIN-INTERP | Interpolated Ground | 98884.82 | 5.03 | 268.56 | 0 | 14.72 | 0 | OK | Ground clear controls. | 224 | 37.56 | 283.28
15480 | TIN-INTERP | Interpolated Ground | 98884.87 | 6.53 | 268.01 | 0 | 20.62 | 0 | OK | Ground clear controls. | 224 | 37.56 | 288.63
15481 | TIN-INTERP | Interpolated Ground | 98884.87 | 4.53 | 268.73 | 0 | 25.27 | 0 | OK | Ground clear controls. | 224 | 37.56 | 294
15482 | TIN-INTERP | Interpolated Ground | 98924.73 | -6.67 | 268.49 | 0 | 19.17 | 0 | OK | Ground clear controls. | 224 | 37.56 | 287.66
15483 | TIN-INTERP | Interpolated Ground | 98924.75 | -5.17 | 267.53 | 0 | 14.75 | 0 | OK | Ground clear controls. | 224 | 37.56 | 282.28
15484 | TIN-INTERP | Interpolated Ground | 98924.78 | -4.67 | 267.23 | 0 | 25.72 | 0 | OK | Ground clear controls. | 224 | 37.56 | 292.95
15485 | TIN-INTERP | Interpolated Ground | 98924.82 | 5.04 | 263.95 | 0 | 18.37 | 0 | OK | Ground clear controls. | 224 | 37.56 | 282.32
15486 | TIN-INTERP | Interpolated Ground | 98924.87 | 6.54 | 263.42 | 0 | 24.25 | 0 | OK | Ground clear controls. | 224 | 37.56 | 287.67
15487 | TIN-INTERP | Interpolated Ground | 98924.87 | 4.54 | 264.12 | 0 | 28.92 | 0 | OK | Ground clear controls. | 224 | 37.56 | 293.04
15488 | TIN-INTERP | Interpolated Ground | 98964.73 | -6.65 | 262.2 | 0 | 25.49 | 0 | OK | Ground clear controls. | 224 | 37.56 | 287.69
15489 | TIN-INTERP | Interpolated Ground | 98964.75 | -5.15 | 261.64 | 0 | 20.66 | 0 | OK | Ground clear controls. | 224 | 37.56 | 282.3
15490 | TIN-INTERP | Interpolated Ground | 98964.78 | -4.65 | 261.46 | 0 | 31.53 | 0 | OK | Ground clear controls. | 224 | 37.56 | 292.99
15491 | TIN-INTERP | Interpolated Ground | 98964.82 | 5.05 | 258.22 | 0 | 24.11 | 0 | OK | Ground clear controls. | 224 | 37.56 | 282.33
15492 | TIN-INTERP | Interpolated Ground | 98964.87 | 6.55 | 257.82 | 0 | 29.87 | 0 | OK | Ground clear controls. | 224 | 37.56 | 287.69
15493 | TIN-INTERP | Interpolated Ground | 98964.87 | 4.55 | 258.34 | 0 | 34.75 | 0 | OK | Ground clear controls. | 224 | 37.56 | 293.09
15494 | TIN-INTERP | Interpolated Ground | 99004.73 | -6.64 | 263.94 | 0 | 24.74 | 0 | OK | Ground clear controls. | 224 | 37.56 | 288.68
15495 | TIN-INTERP | Interpolated Ground | 99004.75 | -5.14 | 263.4 | 0 | 19.87 | 0 | OK | Ground clear controls. | 224 | 37.56 | 283.27
15496 | TIN-INTERP | Interpolated Ground | 99004.78 | -4.64 | 263.19 | 0 | 30.83 | 0 | OK | Ground clear controls. | 224 | 37.56 | 294.02
15497 | TIN-INTERP | Interpolated Ground | 99004.82 | 5.07 | 258.9 | 0 | 24.4 | 0 | OK | Ground clear controls. | 224 | 37.56 | 283.3
15498 | TIN-INTERP | Interpolated Ground | 99004.87 | 6.57 | 258.23 | 0 | 30.46 | 0 | OK | Ground clear controls. | 224 | 37.56 | 288.69
15499 | TIN-INTERP | Interpolated Ground | 99004.87 | 4.57 | 259.12 | 0 | 34.97 | 0 | OK | Ground clear controls. | 224 | 37.56 | 294.09
15500 | TIN-INTERP | Interpolated Ground | 99044.73 | -6.62 | 265.44 | 0 | 25.22 | 0 | OK | Ground clear controls. | 224 | 37.56 | 290.66
15501 | TIN-INTERP | Interpolated Ground | 99044.75 | -5.12 | 264.85 | 0 | 20.38 | 0 | OK | Ground clear controls. | 224 | 37.56 | 285.23
15502 | TIN-INTERP | Interpolated Ground | 99044.78 | -4.62 | 264.72 | 0 | 31.32 | 0 | OK | Ground clear controls. | 224 | 37.56 | 296.04
15503 | TIN-INTERP | Interpolated Ground | 99044.82 | 5.08 | 260.96 | 0 | 24.29 | 0 | OK | Ground clear controls. | 224 | 37.56 | 285.25
15504 | TIN-INTERP | Interpolated Ground | 99044.87 | 6.58 | 260.41 | 0 | 30.26 | 0 | OK | Ground clear controls. | 224 | 37.56 | 290.67
15505 | TIN-INTERP | Interpolated Ground | 99044.87 | 4.58 | 261.12 | 0 | 34.98 | 0 | OK | Ground clear controls. | 224 | 37.56 | 296.1
15506 | TIN-INTERP | Interpolated Ground | 99084.73 | -6.61 | 263.82 | 0 | 29.8 | 0 | OK | Ground clear controls. | 224 | 37.56 | 293.62
15507 | TIN-INTERP | Interpolated Ground | 99084.75 | -5.11 | 263.53 | 0 | 24.62 | 0 | OK | Ground clear controls. | 224 | 37.56 | 288.15
15508 | TIN-INTERP | Interpolated Ground | 99084.78 | -4.61 | 263.44 | 0 | 35.62 | 0 | OK | Ground clear controls. | 224 | 37.56 | 299.06
15509 | TIN-INTERP | Interpolated Ground | 99084.82 | 5.09 | 261.47 | 0 | 26.69 | 0 | OK | Ground clear controls. | 224 | 37.56 | 288.16
15510 | TIN-INTERP | Interpolated Ground | 99084.87 | 6.59 | 261.07 | 0 | 32.55 | 0 | OK | Ground clear controls. | 224 | 37.56 | 293.62
15511 | TIN-INTERP | Interpolated Ground | 99084.87 | 4.59 | 261.53 | 0 | 37.56 | 0 | OK | Ground clear controls. | 224 | 37.56 | 299.09
15512 | TIN-INTERP | Interpolated Ground | 99112.88 | -5.1 | 260.16 | 0 | 30.64 | 0 | OK | Ground clear controls. | 225 | 47.68 | 290.8
15513 | TIN-INTERP | Interpolated Ground | 99112.98 | -6.6 | 260.29 | 0 | 36 | 0 | OK | Ground clear controls. | 225 | 47.68 | 296.29
15514 | TIN-INTERP | Interpolated Ground | 99112.98 | 5.1 | 258.79 | 0 | 32 | 0 | OK | Ground clear controls. | 225 | 47.68 | 290.79
15515 | TIN-INTERP | Interpolated Ground | 99113.03 | -4.6 | 260.04 | 0 | 41.75 | 0 | OK | Ground clear controls. | 225 | 47.68 | 301.79
15516 | TIN-INTERP | Interpolated Ground | 99113.04 | 6.6 | 258.7 | 0 | 37.59 | 0 | OK | Ground clear controls. | 225 | 47.68 | 296.29
15517 | TIN-INTERP | Interpolated Ground | 99113.05 | 4.6 | 258.78 | 0 | 43.01 | 0 | OK | Ground clear controls. | 225 | 47.68 | 301.79
15518 | TIN-INTERP | Interpolated Ground | 99152.88 | -5.11 | 254.91 | 0 | 29.2 | 0 | OK | Ground clear controls. | 225 | 47.68 | 284.11
15519 | TIN-INTERP | Interpolated Ground | 99152.98 | -6.61 | 255.02 | 0 | 34.6 | 0 | OK | Ground clear controls. | 225 | 47.68 | 289.62
15520 | TIN-INTERP | Interpolated Ground | 99152.99 | 5.1 | 253.65 | 0 | 30.5 | 0 | OK | Ground clear controls. | 225 | 47.68 | 284.15
15521 | TIN-INTERP | Interpolated Ground | 99153.03 | -4.61 | 254.85 | 0 | 40.24 | 0 | OK | Ground clear controls. | 225 | 47.68 | 295.09
15522 | TIN-INTERP | Interpolated Ground | 99153.04 | 6.6 | 253.56 | 0 | 36.07 | 0 | OK | Ground clear controls. | 225 | 47.68 | 289.63
15523 | TIN-INTERP | Interpolated Ground | 99153.05 | 4.6 | 253.73 | 0 | 41.38 | 0 | OK | Ground clear controls. | 225 | 47.68 | 295.11
15524 | TIN-INTERP | Interpolated Ground | 99192.88 | -5.12 | 250.79 | 0 | 27.63 | 0 | OK | Ground clear controls. | 225 | 47.68 | 278.42
15525 | TIN-INTERP | Interpolated Ground | 99192.98 | -6.62 | 250.99 | 0 | 32.93 | 0 | OK | Ground clear controls. | 225 | 47.68 | 283.92
15526 | TIN-INTERP | Interpolated Ground | 99192.99 | 5.09 | 249.5 | 0 | 28.98 | 0 | OK | Ground clear controls. | 225 | 47.68 | 278.48
15527 | TIN-INTERP | Interpolated Ground | 99193.03 | -4.62 | 250.66 | 0 | 38.73 | 0 | OK | Ground clear controls. | 225 | 47.68 | 289.39
15528 | TIN-INTERP | Interpolated Ground | 99193.04 | 6.59 | 249.24 | 0 | 34.72 | 0 | OK | Ground clear controls. | 225 | 47.68 | 283.96
15529 | TIN-INTERP | Interpolated Ground | 99193.05 | 4.59 | 249.56 | 0 | 39.87 | 0 | OK | Ground clear controls. | 225 | 47.68 | 289.43
15530 | TIN-INTERP | Interpolated Ground | 99232.88 | -5.13 | 247.02 | 0 | 26.71 | 0 | OK | Ground clear controls. | 225 | 47.68 | 273.73
15531 | TIN-INTERP | Interpolated Ground | 99232.98 | -6.63 | 247.47 | 0 | 31.76 | 0 | OK | Ground clear controls. | 225 | 47.68 | 279.23
15532 | TIN-INTERP | Interpolated Ground | 99232.99 | 5.09 | 244.46 | 0 | 29.33 | 0 | OK | Ground clear controls. | 225 | 47.68 | 273.79
15533 | TIN-INTERP | Interpolated Ground | 99233.03 | -4.63 | 246.87 | 0 | 37.82 | 0 | OK | Ground clear controls. | 225 | 47.68 | 284.69
15534 | TIN-INTERP | Interpolated Ground | 99233.04 | 6.59 | 244.1 | 0 | 35.16 | 0 | OK | Ground clear controls. | 225 | 47.68 | 279.26
15535 | TIN-INTERP | Interpolated Ground | 99233.05 | 4.59 | 244.54 | 0 | 40.19 | 0 | OK | Ground clear controls. | 225 | 47.68 | 284.73
15536 | TIN-INTERP | Interpolated Ground | 99272.88 | -5.14 | 238.39 | 0 | 31.62 | 0 | OK | Ground clear controls. | 225 | 47.68 | 270.01
15537 | TIN-INTERP | Interpolated Ground | 99272.98 | -6.64 | 238.66 | 0 | 36.86 | 0 | OK | Ground clear controls. | 225 | 47.68 | 275.52
15538 | TIN-INTERP | Interpolated Ground | 99272.99 | 5.09 | 236.38 | 0 | 33.69 | 0 | OK | Ground clear controls. | 225 | 47.68 | 270.07
15539 | TIN-INTERP | Interpolated Ground | 99273.03 | -4.63 | 238.21 | 0 | 42.78 | 0 | OK | Ground clear controls. | 225 | 47.68 | 280.99
15540 | TIN-INTERP | Interpolated Ground | 99273.04 | 6.59 | 236.06 | 0 | 39.5 | 0 | OK | Ground clear controls. | 225 | 47.68 | 275.56
15541 | TIN-INTERP | Interpolated Ground | 99273.05 | 4.59 | 236.47 | 0 | 44.55 | 0 | OK | Ground clear controls. | 225 | 47.68 | 281.02
15542 | TIN-INTERP | Interpolated Ground | 99312.88 | -5.14 | 230.38 | 0 | 36.91 | 0 | OK | Ground clear controls. | 225 | 47.68 | 267.29
15543 | TIN-INTERP | Interpolated Ground | 99312.98 | -6.64 | 229.82 | 0 | 42.98 | 0 | OK | Ground clear controls. | 225 | 47.68 | 272.8
15544 | TIN-INTERP | Interpolated Ground | 99312.99 | 5.09 | 233.74 | 0 | 33.59 | 0 | OK | Ground clear controls. | 225 | 47.68 | 267.33
15545 | TIN-INTERP | Interpolated Ground | 99313.03 | -4.64 | 230.6 | 0 | 47.68 | 0 | OK | Ground clear controls. | 225 | 47.68 | 278.28
15546 | TIN-INTERP | Interpolated Ground | 99313.04 | 6.59 | 234.26 | 0 | 38.55 | 0 | OK | Ground clear controls. | 225 | 44.76 | 272.81
15547 | TIN-INTERP | Interpolated Ground | 99313.05 | 4.58 | 233.54 | 0 | 44.76 | 0 | OK | Ground clear controls. | 225 | 44.76 | 278.3
15548 | TIN-INTERP | Interpolated Ground | 99350.02 | -6.65 | 233.31 | 0 | 37.84 | 0 | OK | Ground clear controls. | 226 | 110.14 | 271.15
15549 | TIN-INTERP | Interpolated Ground | 99350.05 | 6.58 | 234.87 | 0 | 36.28 | 0 | OK | Ground clear controls. | 226 | 110.14 | 271.15
15550 | TIN-INTERP | Interpolated Ground | 99350.08 | 5.08 | 234.83 | 0 | 30.82 | 0 | OK | Ground clear controls. | 226 | 110.14 | 265.65
15551 | TIN-INTERP | Interpolated Ground | 99350.11 | -5.15 | 233.74 | 0 | 31.91 | 0 | OK | Ground clear controls. | 226 | 110.14 | 265.65
15552 | TIN-INTERP | Interpolated Ground | 99350.13 | 4.58 | 234.79 | 0 | 41.86 | 0 | OK | Ground clear controls. | 226 | 110.14 | 276.65
15553 | TIN-INTERP | Interpolated Ground | 99350.14 | -4.65 | 233.79 | 0 | 42.86 | 0 | OK | Ground clear controls. | 226 | 110.14 | 276.65
15554 | TIN-INTERP | Interpolated Ground | 99390.02 | -6.7 | 226.58 | 0 | 34.26 | 0 | OK | Ground clear controls. | 226 | 110.14 | 260.84
15555 | TIN-INTERP | Interpolated Ground | 99390.04 | 6.67 | 221.4 | 0 | 39.56 | 0 | OK | Ground clear controls. | 226 | 110.14 | 260.96
15556 | TIN-INTERP | Interpolated Ground | 99390.08 | 5.17 | 221.98 | 0 | 33.56 | 0 | OK | Ground clear controls. | 226 | 110.14 | 255.54
15557 | TIN-INTERP | Interpolated Ground | 99390.11 | -5.2 | 225.87 | 0 | 29.53 | 0 | OK | Ground clear controls. | 226 | 110.14 | 255.4
15558 | TIN-INTERP | Interpolated Ground | 99390.13 | 4.66 | 222.11 | 0 | 44.38 | 0 | OK | Ground clear controls. | 226 | 110.14 | 266.49
15559 | TIN-INTERP | Interpolated Ground | 99390.14 | -4.69 | 225.68 | 0 | 40.73 | 0 | OK | Ground clear controls. | 226 | 110.14 | 266.41
15560 | TIN-INTERP | Interpolated Ground | 99430.02 | -6.75 | 211.2 | 0 | 40.35 | 0 | OK | Ground clear controls. | 226 | 110.14 | 251.55
15561 | TIN-INTERP | Interpolated Ground | 99430.04 | 6.76 | 210.4 | 0 | 41.37 | 0 | OK | Ground clear controls. | 226 | 110.14 | 251.77
15562 | TIN-INTERP | Interpolated Ground | 99430.08 | 5.26 | 210.48 | 0 | 35.93 | 0 | OK | Ground clear controls. | 226 | 110.14 | 246.41
15563 | TIN-INTERP | Interpolated Ground | 99430.11 | -5.25 | 210.8 | 0 | 35.35 | 0 | OK | Ground clear controls. | 226 | 110.14 | 246.15
15564 | TIN-INTERP | Interpolated Ground | 99430.13 | 4.74 | 210.5 | 0 | 46.84 | 0 | OK | Ground clear controls. | 226 | 110.14 | 257.34
15565 | TIN-INTERP | Interpolated Ground | 99430.14 | -4.73 | 210.71 | 0 | 46.46 | 0 | OK | Ground clear controls. | 226 | 110.14 | 257.17
15566 | TIN-INTERP | Interpolated Ground | 99470.02 | -6.8 | 203.11 | 0 | 40.16 | 0 | OK | Ground clear controls. | 226 | 110.14 | 243.27
15567 | TIN-INTERP | Interpolated Ground | 99470.04 | 6.85 | 204.27 | 0 | 39.31 | 0 | OK | Ground clear controls. | 226 | 110.14 | 243.58
15568 | TIN-INTERP | Interpolated Ground | 99470.08 | 5.35 | 203.83 | 0 | 34.44 | 0 | OK | Ground clear controls. | 226 | 110.14 | 238.27
15569 | TIN-INTERP | Interpolated Ground | 99470.11 | -5.3 | 203.13 | 0 | 34.78 | 0 | OK | Ground clear controls. | 226 | 110.14 | 237.91
15570 | TIN-INTERP | Interpolated Ground | 99470.13 | 4.82 | 203.74 | 0 | 45.44 | 0 | OK | Ground clear controls. | 226 | 110.14 | 249.18
15571 | TIN-INTERP | Interpolated Ground | 99470.14 | -4.77 | 203.15 | 0 | 45.8 | 0 | OK | Ground clear controls. | 226 | 110.14 | 248.95
15572 | TIN-INTERP | Interpolated Ground | 99510.02 | -6.85 | 207.9 | 0 | 28.09 | 0 | OK | Ground clear controls. | 226 | 110.14 | 235.99
15573 | TIN-INTERP | Interpolated Ground | 99510.04 | 6.94 | 211.96 | 0 | 24.43 | 0 | OK | Ground clear controls. | 226 | 110.14 | 236.39
15574 | TIN-INTERP | Interpolated Ground | 99510.08 | 5.44 | 211.47 | 0 | 19.67 | 0 | OK | Ground clear controls. | 226 | 110.14 | 231.14
15575 | TIN-INTERP | Interpolated Ground | 99510.11 | -5.35 | 208.61 | 0 | 22.05 | 0 | OK | Ground clear controls. | 226 | 110.14 | 230.66
15576 | TIN-INTERP | Interpolated Ground | 99510.13 | 4.9 | 211.32 | 0 | 30.71 | 0 | OK | Ground clear controls. | 226 | 110.14 | 242.03
15577 | TIN-INTERP | Interpolated Ground | 99510.14 | -4.81 | 208.87 | 0 | 32.87 | 0 | OK | Ground clear controls. | 226 | 110.14 | 241.74
15578 | TIN-INTERP | Interpolated Ground | 99550.02 | -6.9 | 203.82 | 0 | 25.93 | 0 | OK | Ground clear controls. | 226 | 110.14 | 229.75
15579 | TIN-INTERP | Interpolated Ground | 99550.04 | 7.03 | 203.8 | 0 | 26.42 | 0 | OK | Ground clear controls. | 226 | 110.14 | 230.22
15580 | TIN-INTERP | Interpolated Ground | 99550.08 | 5.53 | 203.55 | 0 | 21.46 | 0 | OK | Ground clear controls. | 226 | 110.14 | 225.01
15581 | TIN-INTERP | Interpolated Ground | 99550.11 | -5.4 | 203.56 | 0 | 20.89 | 0 | OK | Ground clear controls. | 226 | 110.14 | 224.45
15582 | TIN-INTERP | Interpolated Ground | 99550.13 | 4.98 | 203.55 | 0 | 32.34 | 0 | OK | Ground clear controls. | 226 | 110.14 | 235.89
15583 | TIN-INTERP | Interpolated Ground | 99550.14 | -4.85 | 203.53 | 0 | 32.02 | 0 | OK | Ground clear controls. | 226 | 110.14 | 235.55
15584 | TIN-INTERP | Interpolated Ground | 99590.02 | -6.95 | 195.28 | 0 | 29.21 | 0 | OK | Ground clear controls. | 226 | 110.14 | 224.49
15585 | TIN-INTERP | Interpolated Ground | 99590.04 | 7.12 | 192.23 | 0 | 32.8 | 0 | OK | Ground clear controls. | 226 | 110.14 | 225.03
15586 | TIN-INTERP | Interpolated Ground | 99590.08 | 5.62 | 192.44 | 0 | 27.41 | 0 | OK | Ground clear controls. | 226 | 110.14 | 219.85
15587 | TIN-INTERP | Interpolated Ground | 99590.11 | -5.44 | 194.85 | 0 | 24.37 | 0 | OK | Ground clear controls. | 226 | 110.14 | 219.22
15588 | TIN-INTERP | Interpolated Ground | 99590.13 | 5.06 | 192.45 | 0 | 38.28 | 0 | OK | Ground clear controls. | 226 | 110.14 | 230.73
15589 | TIN-INTERP | Interpolated Ground | 99590.14 | -4.89 | 194.71 | 0 | 35.64 | 0 | OK | Ground clear controls. | 226 | 110.14 | 230.35
15590 | TIN-INTERP | Interpolated Ground | 99630.02 | -6.99 | 170.87 | 0 | 49.37 | 0 | OK | Ground clear controls. | 226 | 110.14 | 220.24
15591 | TIN-INTERP | Interpolated Ground | 99630.04 | 7.2 | 168.41 | 0 | 52.42 | 0 | OK | Ground clear controls. | 226 | 110.14 | 220.83
15592 | TIN-INTERP | Interpolated Ground | 99630.08 | 5.71 | 168.43 | 0 | 47.23 | 0 | OK | Ground clear controls. | 226 | 110.14 | 215.66
15593 | TIN-INTERP | Interpolated Ground | 99630.11 | -5.49 | 170.48 | 0 | 44.49 | 0 | OK | Ground clear controls. | 226 | 110.14 | 214.97
15594 | TIN-INTERP | Interpolated Ground | 99630.13 | 5.14 | 168.58 | 0 | 57.98 | 0 | OK | Ground clear controls. | 226 | 110.14 | 226.56
15595 | TIN-INTERP | Interpolated Ground | 99630.14 | -4.93 | 170.32 | 0 | 55.82 | 0 | OK | Ground clear controls. | 226 | 110.14 | 226.14
15596 | TIN-INTERP | Interpolated Ground | 99670.02 | -7.04 | 141.47 | 0 | 75.52 | 0 | OK | Ground clear controls. | 226 | 110.14 | 216.99
15597 | TIN-INTERP | Interpolated Ground | 99670.04 | 7.29 | 138.96 | 0 | 78.67 | 0 | OK | Ground clear controls. | 226 | 110.14 | 217.63
15598 | TIN-INTERP | Interpolated Ground | 99670.08 | 5.79 | 139.23 | 0 | 73.25 | 0 | OK | Ground clear controls. | 226 | 110.14 | 212.48
15599 | TIN-INTERP | Interpolated Ground | 99670.11 | -5.54 | 140.76 | 0 | 70.98 | 0 | OK | Ground clear controls. | 226 | 110.14 | 211.74
15600 | TIN-INTERP | Interpolated Ground | 99670.13 | 5.22 | 139.27 | 0 | 84.13 | 0 | OK | Ground clear controls. | 226 | 110.14 | 223.4
15601 | TIN-INTERP | Interpolated Ground | 99670.14 | -4.97 | 140.53 | 0 | 82.42 | 0 | OK | Ground clear controls. | 226 | 110.14 | 222.95
15602 | TIN-INTERP | Interpolated Ground | 99710.02 | -7.09 | 110.63 | 0 | 104.11 | 0 | OK | Ground clear controls. | 226 | 110.14 | 214.74
15603 | TIN-INTERP | Interpolated Ground | 99710.04 | 7.38 | 111.43 | 0 | 103.97 | 0 | OK | Ground clear controls. | 226 | 110.14 | 215.4
15604 | TIN-INTERP | Interpolated Ground | 99710.08 | 5.88 | 111.22 | 0 | 99.04 | 0 | OK | Ground clear controls. | 226 | 110.14 | 210.26
15605 | TIN-INTERP | Interpolated Ground | 99710.11 | -5.59 | 110.53 | 0 | 98.96 | 0 | OK | Ground clear controls. | 226 | 110.14 | 209.49
15606 | TIN-INTERP | Interpolated Ground | 99710.13 | 5.3 | 111.23 | 0 | 109.99 | 0 | OK | Ground clear controls. | 226 | 110.14 | 221.22
15607 | TIN-INTERP | Interpolated Ground | 99710.14 | -5.01 | 110.59 | 0 | 110.14 | 0 | OK | Ground clear controls. | 226 | 110.14 | 220.73
15608 | TIN-INTERP | Interpolated Ground | 99750.02 | -7.14 | 127.06 | 0 | 86.41 | 0 | OK | Ground clear controls. | 226 | 91.29 | 213.47
15609 | TIN-INTERP | Interpolated Ground | 99750.04 | 7.47 | 135.44 | 0 | 78.72 | 0 | OK | Ground clear controls. | 226 | 91.29 | 214.16
15610 | TIN-INTERP | Interpolated Ground | 99750.08 | 5.97 | 134.94 | 0 | 74.08 | 0 | OK | Ground clear controls. | 226 | 91.29 | 209.02
15611 | TIN-INTERP | Interpolated Ground | 99750.11 | -5.64 | 127.79 | 0 | 80.43 | 0 | OK | Ground clear controls. | 226 | 91.29 | 208.22
15612 | TIN-INTERP | Interpolated Ground | 99750.13 | 5.38 | 134.81 | 0 | 85.2 | 0 | OK | Ground clear controls. | 226 | 91.29 | 220.01
15613 | TIN-INTERP | Interpolated Ground | 99750.14 | -5.05 | 128.22 | 0 | 91.29 | 0 | OK | Ground clear controls. | 226 | 91.29 | 219.51
15614 | TIN-INTERP | Interpolated Ground | 99790.02 | -7.19 | 145.65 | 0 | 67.57 | 0 | OK | Ground clear controls. | 226 | 91.28 | 213.22
15615 | TIN-INTERP | Interpolated Ground | 99790.04 | 7.56 | 153.17 | 0 | 60.75 | 0 | OK | Ground clear controls. | 226 | 91.28 | 213.92
15616 | TIN-INTERP | Interpolated Ground | 99790.08 | 6.06 | 152.26 | 0 | 56.51 | 0 | OK | Ground clear controls. | 226 | 91.28 | 208.77
15617 | TIN-INTERP | Interpolated Ground | 99790.11 | -5.69 | 145.95 | 0 | 62.01 | 0 | OK | Ground clear controls. | 226 | 91.28 | 207.96
15618 | TIN-INTERP | Interpolated Ground | 99790.13 | 5.46 | 151.95 | 0 | 67.86 | 0 | OK | Ground clear controls. | 226 | 91.28 | 219.81
15619 | TIN-INTERP | Interpolated Ground | 99790.14 | -5.09 | 146.05 | 0 | 73.24 | 0 | OK | Ground clear controls. | 226 | 91.28 | 219.29
15620 | TIN-INTERP | Interpolated Ground | 99830.02 | -7.24 | 146.74 | 0 | 67.2 | 0 | OK | Ground clear controls. | 226 | 91.28 | 213.94
15621 | TIN-INTERP | Interpolated Ground | 99830.04 | 7.65 | 155.64 | 0 | 59 | 0 | OK | Ground clear controls. | 226 | 91.28 | 214.64
15622 | TIN-INTERP | Interpolated Ground | 99830.08 | 6.15 | 154.87 | 0 | 54.61 | 0 | OK | Ground clear controls. | 226 | 91.28 | 209.48
15623 | TIN-INTERP | Interpolated Ground | 99830.11 | -5.74 | 147.66 | 0 | 61.01 | 0 | OK | Ground clear controls. | 226 | 91.28 | 208.67
15624 | TIN-INTERP | Interpolated Ground | 99830.13 | 5.54 | 154.66 | 0 | 65.91 | 0 | OK | Ground clear controls. | 226 | 91.28 | 220.57
15625 | TIN-INTERP | Interpolated Ground | 99830.14 | -5.13 | 148.03 | 0 | 72.03 | 0 | OK | Ground clear controls. | 226 | 91.28 | 220.06
15626 | TIN-INTERP | Interpolated Ground | 99870.02 | -7.29 | 154.46 | 0 | 61.21 | 0 | OK | Ground clear controls. | 226 | 91.28 | 215.67
15627 | TIN-INTERP | Interpolated Ground | 99870.04 | 7.74 | 161.04 | 0 | 55.32 | 0 | OK | Ground clear controls. | 226 | 91.28 | 216.36
15628 | TIN-INTERP | Interpolated Ground | 99870.08 | 6.24 | 159.88 | 0 | 51.28 | 0 | OK | Ground clear controls. | 226 | 91.28 | 211.16
15629 | TIN-INTERP | Interpolated Ground | 99870.11 | -5.79 | 154.91 | 0 | 55.46 | 0 | OK | Ground clear controls. | 226 | 91.28 | 210.37
15630 | TIN-INTERP | Interpolated Ground | 99870.13 | 5.62 | 159.58 | 0 | 62.73 | 0 | OK | Ground clear controls. | 226 | 91.28 | 222.31
15631 | TIN-INTERP | Interpolated Ground | 99870.14 | -5.17 | 155.15 | 0 | 66.66 | 0 | OK | Ground clear controls. | 226 | 91.28 | 221.81
15632 | TIN-INTERP | Interpolated Ground | 99910.02 | -7.34 | 154.53 | 0 | 63.86 | 0 | OK | Ground clear controls. | 226 | 91.28 | 218.39
15633 | TIN-INTERP | Interpolated Ground | 99910.04 | 7.82 | 166.19 | 0 | 52.89 | 0 | OK | Ground clear controls. | 226 | 91.28 | 219.08
15634 | TIN-INTERP | Interpolated Ground | 99910.08 | 6.33 | 165.06 | 0 | 48.79 | 0 | OK | Ground clear controls. | 226 | 91.28 | 213.85
15635 | TIN-INTERP | Interpolated Ground | 99910.11 | -5.83 | 155.6 | 0 | 57.47 | 0 | OK | Ground clear controls. | 226 | 91.28 | 213.07
15636 | TIN-INTERP | Interpolated Ground | 99910.13 | 5.7 | 164.57 | 0 | 60.5 | 0 | OK | Ground clear controls. | 226 | 91.28 | 225.07
15637 | TIN-INTERP | Interpolated Ground | 99910.14 | -5.21 | 156.17 | 0 | 68.41 | 0 | OK | Ground clear controls. | 226 | 91.28 | 224.58
15638 | TIN-INTERP | Interpolated Ground | 99950.02 | -7.38 | 135.81 | 0 | 86.3 | 0 | OK | Ground clear controls. | 226 | 91.28 | 222.11
15639 | TIN-INTERP | Interpolated Ground | 99950.04 | 7.91 | 148.19 | 0 | 74.58 | 0 | OK | Ground clear controls. | 226 | 91.28 | 222.77
15640 | TIN-INTERP | Interpolated Ground | 99950.08 | 6.42 | 146.72 | 0 | 70.77 | 0 | OK | Ground clear controls. | 226 | 91.28 | 217.49
15641 | TIN-INTERP | Interpolated Ground | 99950.11 | -5.88 | 136.71 | 0 | 80.05 | 0 | OK | Ground clear controls. | 226 | 91.28 | 216.76
15642 | TIN-INTERP | Interpolated Ground | 99950.13 | 5.78 | 145.91 | 0 | 82.88 | 0 | OK | Ground clear controls. | 226 | 91.28 | 228.79
15643 | TIN-INTERP | Interpolated Ground | 99950.14 | -5.25 | 137.04 | 0 | 91.28 | 0 | OK | Ground clear controls. | 226 | 91.28 | 228.32
15644 | TIN-INTERP | Interpolated Ground | 99990.02 | -7.43 | 161.31 | 0 | 65.51 | 0 | OK | Ground clear controls. | 226 | 77.17 | 226.82
15645 | TIN-INTERP | Interpolated Ground | 99990.04 | 8 | 155.43 | 0 | 72.02 | 0 | OK | Ground clear controls. | 226 | 77.17 | 227.45
15646 | TIN-INTERP | Interpolated Ground | 99990.08 | 6.51 | 156.01 | 0 | 66.11 | 0 | OK | Ground clear controls. | 226 | 77.17 | 222.12
15647 | TIN-INTERP | Interpolated Ground | 99990.11 | -5.93 | 161.03 | 0 | 60.41 | 0 | OK | Ground clear controls. | 226 | 77.17 | 221.44
15648 | TIN-INTERP | Interpolated Ground | 99990.13 | 5.86 | 156.34 | 0 | 77.17 | 0 | OK | Ground clear controls. | 226 | 77.17 | 233.51
15649 | TIN-INTERP | Interpolated Ground | 99990.14 | -5.29 | 160.76 | 0 | 72.31 | 0 | OK | Ground clear controls. | 226 | 72.31 | 233.07
15650 | TIN-INTERP | Interpolated Ground | 100030.02 | -7.48 | 211.39 | 0 | 21.16 | 0 | OK | Ground clear controls. | 226 | 47.27 | 232.55
15651 | TIN-INTERP | Interpolated Ground | 100030.04 | 8.09 | 210.2 | 0 | 22.93 | 0 | OK | Ground clear controls. | 226 | 47.27 | 233.13
15652 | TIN-INTERP | Interpolated Ground | 100030.08 | 6.6 | 210.9 | 0 | 16.85 | 0 | OK | Ground clear controls. | 226 | 47.27 | 227.75
15653 | TIN-INTERP | Interpolated Ground | 100030.11 | -5.98 | 211.98 | 0 | 15.14 | 0 | OK | Ground clear controls. | 226 | 47.27 | 227.12
15654 | TIN-INTERP | Interpolated Ground | 100030.13 | 5.94 | 211.27 | 0 | 27.96 | 0 | OK | Ground clear controls. | 226 | 47.27 | 239.23
15655 | TIN-INTERP | Interpolated Ground | 100030.14 | -5.33 | 212.36 | 0 | 26.47 | 0 | OK | Ground clear controls. | 226 | 47.27 | 238.83
15656 | TIN-INTERP | Interpolated Ground | 100070.02 | -7.53 | 210.15 | 0 | 29.13 | 0 | OK | Ground clear controls. | 226 | 47.27 | 239.28
15657 | TIN-INTERP | Interpolated Ground | 100070.04 | 8.18 | 202.62 | 0 | 37.18 | 0 | OK | Ground clear controls. | 226 | 47.27 | 239.8
15658 | TIN-INTERP | Interpolated Ground | 100070.08 | 6.68 | 203.3 | 0 | 31.04 | 0 | OK | Ground clear controls. | 226 | 47.27 | 234.34
15659 | TIN-INTERP | Interpolated Ground | 100070.11 | -6.03 | 209.9 | 0 | 23.89 | 0 | OK | Ground clear controls. | 226 | 47.27 | 233.79
15660 | TIN-INTERP | Interpolated Ground | 100070.13 | 6.02 | 203.72 | 0 | 42.22 | 0 | OK | Ground clear controls. | 226 | 47.27 | 245.94
15661 | TIN-INTERP | Interpolated Ground | 100070.14 | -5.37 | 209.72 | 0 | 35.85 | 0 | OK | Ground clear controls. | 226 | 47.27 | 245.57
15662 | TIN-INTERP | Interpolated Ground | 100110.02 | -7.58 | 216.14 | 0 | 30.87 | 0 | OK | Ground clear controls. | 226 | 47.27 | 247.01
15663 | TIN-INTERP | Interpolated Ground | 100110.04 | 8.27 | 209.83 | 0 | 37.63 | 0 | OK | Ground clear controls. | 226 | 47.27 | 247.46
15664 | TIN-INTERP | Interpolated Ground | 100110.08 | 6.77 | 209.9 | 0 | 32.03 | 0 | OK | Ground clear controls. | 226 | 47.27 | 241.93
15665 | TIN-INTERP | Interpolated Ground | 100110.11 | -6.08 | 215.1 | 0 | 26.37 | 0 | OK | Ground clear controls. | 226 | 47.27 | 241.47
15666 | TIN-INTERP | Interpolated Ground | 100110.13 | 6.1 | 210.02 | 0 | 43.61 | 0 | OK | Ground clear controls. | 226 | 47.27 | 253.63
15667 | TIN-INTERP | Interpolated Ground | 100110.14 | -5.41 | 214.55 | 0 | 38.78 | 0 | OK | Ground clear controls. | 226 | 47.27 | 253.33
15668 | TIN-INTERP | Interpolated Ground | 100150.02 | -7.63 | 219.04 | 0 | 36.74 | 0 | OK | Ground clear controls. | 226 | 47.27 | 255.78
15669 | TIN-INTERP | Interpolated Ground | 100150.04 | 8.36 | 217.5 | 0 | 38.65 | 0 | OK | Ground clear controls. | 226 | 47.27 | 256.15
15670 | TIN-INTERP | Interpolated Ground | 100150.08 | 6.86 | 216.89 | 0 | 33.65 | 0 | OK | Ground clear controls. | 226 | 47.27 | 250.54
15671 | TIN-INTERP | Interpolated Ground | 100150.11 | -6.13 | 218.47 | 0 | 31.7 | 0 | OK | Ground clear controls. | 226 | 47.27 | 250.17
15672 | TIN-INTERP | Interpolated Ground | 100150.13 | 6.18 | 216.62 | 0 | 45.74 | 0 | OK | Ground clear controls. | 226 | 47.27 | 262.36
15673 | TIN-INTERP | Interpolated Ground | 100150.14 | -5.45 | 218.15 | 0 | 43.96 | 0 | OK | Ground clear controls. | 226 | 47.27 | 262.11
15674 | TIN-INTERP | Interpolated Ground | 100190.02 | -7.68 | 224.58 | 0 | 40.98 | 0 | OK | Ground clear controls. | 226 | 47.27 | 265.56
15675 | TIN-INTERP | Interpolated Ground | 100190.04 | 8.45 | 226.57 | 0 | 39.27 | 0 | OK | Ground clear controls. | 226 | 47.27 | 265.84
15676 | TIN-INTERP | Interpolated Ground | 100190.08 | 6.95 | 226.44 | 0 | 33.69 | 0 | OK | Ground clear controls. | 226 | 47.27 | 260.13
15677 | TIN-INTERP | Interpolated Ground | 100190.11 | -6.18 | 224.58 | 0 | 35.29 | 0 | OK | Ground clear controls. | 226 | 47.27 | 259.87
15678 | TIN-INTERP | Interpolated Ground | 100190.13 | 6.26 | 226.47 | 0 | 45.62 | 0 | OK | Ground clear controls. | 226 | 47.27 | 272.09
15679 | TIN-INTERP | Interpolated Ground | 100190.14 | -5.49 | 224.63 | 0 | 47.27 | 0 | OK | Ground clear controls. | 226 | 47.27 | 271.9
15680 | TIN-INTERP | Interpolated Ground | 100227.65 | -7.73 | 239.07 | 0 | 36.72 | 0 | OK | Ground clear controls. | 227 | 64.6 | 275.79
15681 | TIN-INTERP | Interpolated Ground | 100227.65 | -6.23 | 239.06 | 0 | 30.93 | 0 | OK | Ground clear controls. | 227 | 64.6 | 269.99
15682 | TIN-INTERP | Interpolated Ground | 100227.65 | -5.54 | 238.92 | 0 | 43.17 | 0 | OK | Ground clear controls. | 227 | 64.6 | 282.09
15683 | TIN-INTERP | Interpolated Ground | 100227.99 | 7.03 | 237.84 | 0 | 32.15 | 0 | OK | Ground clear controls. | 227 | 64.6 | 269.99
15684 | TIN-INTERP | Interpolated Ground | 100228.02 | 6.33 | 237.84 | 0 | 44.25 | 0 | OK | Ground clear controls. | 227 | 64.6 | 282.09
15685 | TIN-INTERP | Interpolated Ground | 100228.05 | 8.52 | 237.72 | 0 | 38.07 | 0 | OK | Ground clear controls. | 227 | 64.6 | 275.79
15686 | TIN-INTERP | Interpolated Ground | 100267.46 | -7.69 | 229.51 | 0 | 40.5 | 0 | OK | Ground clear controls. | 227 | 64.6 | 270.01
15687 | TIN-INTERP | Interpolated Ground | 100267.5 | -6.19 | 229.75 | 0 | 34.5 | 0 | OK | Ground clear controls. | 227 | 64.6 | 264.25
15688 | TIN-INTERP | Interpolated Ground | 100267.53 | -5.51 | 229.78 | 0 | 46.51 | 0 | OK | Ground clear controls. | 227 | 64.6 | 276.29
15689 | TIN-INTERP | Interpolated Ground | 100267.99 | 6.94 | 227.87 | 0 | 36.45 | 0 | OK | Ground clear controls. | 227 | 64.6 | 264.32
15690 | TIN-INTERP | Interpolated Ground | 100268.02 | 6.25 | 228.08 | 0 | 48.31 | 0 | OK | Ground clear controls. | 227 | 64.6 | 276.39
15691 | TIN-INTERP | Interpolated Ground | 100268.05 | 8.43 | 227.58 | 0 | 42.45 | 0 | OK | Ground clear controls. | 227 | 64.6 | 270.03
15692 | TIN-INTERP | Interpolated Ground | 100307.46 | -7.65 | 219.13 | 0 | 46.08 | 0 | OK | Ground clear controls. | 227 | 64.6 | 265.21
15693 | TIN-INTERP | Interpolated Ground | 100307.5 | -6.15 | 218.66 | 0 | 40.83 | 0 | OK | Ground clear controls. | 227 | 64.6 | 259.49
15694 | TIN-INTERP | Interpolated Ground | 100307.53 | -5.49 | 218.45 | 0 | 53.01 | 0 | OK | Ground clear controls. | 227 | 64.6 | 271.46
15695 | TIN-INTERP | Interpolated Ground | 100307.99 | 6.85 | 216.64 | 0 | 42.98 | 0 | OK | Ground clear controls. | 227 | 64.6 | 259.62
15696 | TIN-INTERP | Interpolated Ground | 100308.02 | 6.18 | 216.64 | 0 | 55.02 | 0 | OK | Ground clear controls. | 227 | 64.6 | 271.66
15697 | TIN-INTERP | Interpolated Ground | 100308.05 | 8.34 | 216.46 | 0 | 48.8 | 0 | OK | Ground clear controls. | 227 | 64.6 | 265.26
15698 | TIN-INTERP | Interpolated Ground | 100347.46 | -7.61 | 205.98 | 0 | 55.42 | 0 | OK | Ground clear controls. | 227 | 64.6 | 261.4
15699 | TIN-INTERP | Interpolated Ground | 100347.5 | -6.11 | 206.14 | 0 | 49.57 | 0 | OK | Ground clear controls. | 227 | 64.6 | 255.71
15700 | TIN-INTERP | Interpolated Ground | 100347.53 | -5.47 | 206.32 | 0 | 61.29 | 0 | OK | Ground clear controls. | 227 | 64.6 | 267.61
15701 | TIN-INTERP | Interpolated Ground | 100347.99 | 6.76 | 209.15 | 0 | 46.74 | 0 | OK | Ground clear controls. | 227 | 64.6 | 255.89
15702 | TIN-INTERP | Interpolated Ground | 100348.02 | 6.1 | 208.94 | 0 | 58.95 | 0 | OK | Ground clear controls. | 227 | 64.6 | 267.89
15703 | TIN-INTERP | Interpolated Ground | 100348.05 | 8.25 | 209.6 | 0 | 51.86 | 0 | OK | Ground clear controls. | 227 | 64.6 | 261.46
15704 | TIN-INTERP | Interpolated Ground | 100387.46 | -7.58 | 207.16 | 0 | 51.38 | 0 | OK | Ground clear controls. | 227 | 64.6 | 258.54
15705 | TIN-INTERP | Interpolated Ground | 100387.5 | -6.07 | 207.61 | 0 | 45.29 | 0 | OK | Ground clear controls. | 227 | 64.6 | 252.9
15706 | TIN-INTERP | Interpolated Ground | 100387.53 | -5.44 | 207.83 | 0 | 56.91 | 0 | OK | Ground clear controls. | 227 | 64.6 | 264.74
15707 | TIN-INTERP | Interpolated Ground | 100387.99 | 6.66 | 212.06 | 0 | 41.07 | 0 | OK | Ground clear controls. | 227 | 64.6 | 253.13
15708 | TIN-INTERP | Interpolated Ground | 100388.02 | 6.03 | 211.8 | 0 | 53.29 | 0 | OK | Ground clear controls. | 227 | 64.6 | 265.09
15709 | TIN-INTERP | Interpolated Ground | 100388.05 | 8.16 | 212.85 | 0 | 45.79 | 0 | OK | Ground clear controls. | 227 | 64.6 | 258.64
15710 | TIN-INTERP | Interpolated Ground | 100427.46 | -7.54 | 212.49 | 0 | 44.19 | 0 | OK | Ground clear controls. | 227 | 64.6 | 256.68
15711 | TIN-INTERP | Interpolated Ground | 100427.5 | -6.03 | 212.84 | 0 | 38.22 | 0 | OK | Ground clear controls. | 227 | 64.6 | 251.06
15712 | TIN-INTERP | Interpolated Ground | 100427.53 | -5.42 | 212.99 | 0 | 49.86 | 0 | OK | Ground clear controls. | 227 | 64.6 | 262.85
15713 | TIN-INTERP | Interpolated Ground | 100427.99 | 6.57 | 212.85 | 0 | 38.49 | 0 | OK | Ground clear controls. | 227 | 64.6 | 251.34
15714 | TIN-INTERP | Interpolated Ground | 100428.02 | 5.95 | 212.89 | 0 | 50.37 | 0 | OK | Ground clear controls. | 227 | 64.6 | 263.26
15715 | TIN-INTERP | Interpolated Ground | 100428.05 | 8.07 | 212.67 | 0 | 44.12 | 0 | OK | Ground clear controls. | 227 | 64.6 | 256.79
15716 | TIN-INTERP | Interpolated Ground | 100467.46 | -7.5 | 196.96 | 0 | 58.82 | 0 | OK | Ground clear controls. | 227 | 64.6 | 255.78
15717 | TIN-INTERP | Interpolated Ground | 100467.5 | -5.99 | 197.1 | 0 | 53.1 | 0 | OK | Ground clear controls. | 227 | 64.6 | 250.2
15718 | TIN-INTERP | Interpolated Ground | 100467.53 | -5.4 | 197.33 | 0 | 64.6 | 0 | OK | Ground clear controls. | 227 | 64.6 | 261.93
15719 | TIN-INTERP | Interpolated Ground | 100467.99 | 6.48 | 199.05 | 0 | 51.46 | 0 | OK | Ground clear controls. | 227 | 64.25 | 250.51
15720 | TIN-INTERP | Interpolated Ground | 100468.02 | 5.88 | 199.04 | 0 | 63.35 | 0 | OK | Ground clear controls. | 227 | 64.25 | 262.39
15721 | TIN-INTERP | Interpolated Ground | 100468.05 | 7.98 | 199.08 | 0 | 56.82 | 0 | OK | Ground clear controls. | 227 | 64.25 | 255.9
15722 | TIN-INTERP | Interpolated Ground | 100507.46 | -7.46 | 199.75 | 0 | 56.12 | 0 | OK | Ground clear controls. | 227 | 64.25 | 255.87
15723 | TIN-INTERP | Interpolated Ground | 100507.5 | -5.96 | 199.73 | 0 | 50.59 | 0 | OK | Ground clear controls. | 227 | 64.25 | 250.32
15724 | TIN-INTERP | Interpolated Ground | 100507.53 | -5.37 | 199.7 | 0 | 62.3 | 0 | OK | Ground clear controls. | 227 | 64.25 | 262
15725 | TIN-INTERP | Interpolated Ground | 100507.99 | 6.39 | 198.18 | 0 | 52.47 | 0 | OK | Ground clear controls. | 227 | 64.25 | 250.65
15726 | TIN-INTERP | Interpolated Ground | 100508.02 | 5.8 | 198.24 | 0 | 64.25 | 0 | OK | Ground clear controls. | 227 | 64.25 | 262.49
15727 | TIN-INTERP | Interpolated Ground | 100508.05 | 7.89 | 198.11 | 0 | 57.91 | 0 | OK | Ground clear controls. | 227 | 58.99 | 256.02
15728 | TIN-INTERP | Interpolated Ground | 100547.46 | -7.42 | 204.04 | 0 | 52.91 | 0 | OK | Ground clear controls. | 227 | 58.99 | 256.95
15729 | TIN-INTERP | Interpolated Ground | 100547.5 | -5.92 | 204.04 | 0 | 47.37 | 0 | OK | Ground clear controls. | 227 | 58.99 | 251.41
15730 | TIN-INTERP | Interpolated Ground | 100547.53 | -5.35 | 204.06 | 0 | 58.98 | 0 | OK | Ground clear controls. | 227 | 58.99 | 263.04
15731 | TIN-INTERP | Interpolated Ground | 100547.99 | 6.3 | 205.01 | 0 | 46.75 | 0 | OK | Ground clear controls. | 227 | 58.99 | 251.76
15732 | TIN-INTERP | Interpolated Ground | 100548.02 | 5.73 | 204.97 | 0 | 58.6 | 0 | OK | Ground clear controls. | 227 | 58.99 | 263.57
15733 | TIN-INTERP | Interpolated Ground | 100548.05 | 7.8 | 205.04 | 0 | 52.05 | 0 | OK | Ground clear controls. | 227 | 58.99 | 257.09
15734 | TIN-INTERP | Interpolated Ground | 100587.46 | -7.38 | 205.6 | 0 | 53.38 | 0 | OK | Ground clear controls. | 227 | 58.99 | 258.98
15735 | TIN-INTERP | Interpolated Ground | 100587.5 | -5.88 | 205.95 | 0 | 47.52 | 0 | OK | Ground clear controls. | 227 | 58.99 | 253.47
15736 | TIN-INTERP | Interpolated Ground | 100587.53 | -5.32 | 206.06 | 0 | 58.99 | 0 | OK | Ground clear controls. | 227 | 58.99 | 265.05
15737 | TIN-INTERP | Interpolated Ground | 100587.99 | 6.21 | 208.03 | 0 | 45.81 | 0 | OK | Ground clear controls. | 227 | 58.54 | 253.84
15738 | TIN-INTERP | Interpolated Ground | 100588.02 | 5.65 | 207.95 | 0 | 57.65 | 0 | OK | Ground clear controls. | 227 | 58.54 | 265.6
15739 | TIN-INTERP | Interpolated Ground | 100588.05 | 7.71 | 208.28 | 0 | 50.87 | 0 | OK | Ground clear controls. | 227 | 58.54 | 259.15
15740 | TIN-INTERP | Interpolated Ground | 100627.46 | -7.34 | 214.18 | 0 | 47.82 | 0 | OK | Ground clear controls. | 227 | 58.54 | 262
15741 | TIN-INTERP | Interpolated Ground | 100627.5 | -5.84 | 214.27 | 0 | 42.23 | 0 | OK | Ground clear controls. | 227 | 58.54 | 256.5
15742 | TIN-INTERP | Interpolated Ground | 100627.53 | -5.3 | 214.3 | 0 | 53.74 | 0 | OK | Ground clear controls. | 227 | 58.54 | 268.04
15743 | TIN-INTERP | Interpolated Ground | 100627.99 | 6.12 | 216.22 | 0 | 40.66 | 0 | OK | Ground clear controls. | 227 | 58.54 | 256.88
15744 | TIN-INTERP | Interpolated Ground | 100628.02 | 5.58 | 216.14 | 0 | 52.46 | 0 | OK | Ground clear controls. | 227 | 58.54 | 268.6
15745 | TIN-INTERP | Interpolated Ground | 100628.05 | 7.61 | 216.55 | 0 | 45.63 | 0 | OK | Ground clear controls. | 227 | 58.54 | 262.18
15746 | TIN-INTERP | Interpolated Ground | 100667.46 | -7.3 | 224.74 | 0 | 41.26 | 0 | OK | Ground clear controls. | 227 | 58.54 | 266
15747 | TIN-INTERP | Interpolated Ground | 100667.5 | -5.8 | 224.34 | 0 | 36.16 | 0 | OK | Ground clear controls. | 227 | 58.54 | 260.5
15748 | TIN-INTERP | Interpolated Ground | 100667.53 | -5.28 | 224.25 | 0 | 47.76 | 0 | OK | Ground clear controls. | 227 | 58.54 | 272.01
15749 | TIN-INTERP | Interpolated Ground | 100667.99 | 6.03 | 226.64 | 0 | 34.25 | 0 | OK | Ground clear controls. | 227 | 58.54 | 260.89
15750 | TIN-INTERP | Interpolated Ground | 100668.02 | 5.5 | 226.55 | 0 | 46.02 | 0 | OK | Ground clear controls. | 227 | 58.54 | 272.57
15751 | TIN-INTERP | Interpolated Ground | 100668.05 | 7.52 | 226.98 | 0 | 39.21 | 0 | OK | Ground clear controls. | 227 | 58.54 | 266.19
15752 | TIN-INTERP | Interpolated Ground | 100707.46 | -7.26 | 242.49 | 0 | 28.48 | 0 | OK | Ground clear controls. | 227 | 58.54 | 270.97
15753 | TIN-INTERP | Interpolated Ground | 100707.5 | -5.76 | 242.54 | 0 | 22.96 | 0 | OK | Ground clear controls. | 227 | 58.54 | 265.5
15754 | TIN-INTERP | Interpolated Ground | 100707.53 | -5.25 | 242.64 | 0 | 34.33 | 0 | OK | Ground clear controls. | 227 | 58.54 | 276.97
15755 | TIN-INTERP | Interpolated Ground | 100707.99 | 5.93 | 245.2 | 0 | 20.67 | 0 | OK | Ground clear controls. | 227 | 58.54 | 265.87
15756 | TIN-INTERP | Interpolated Ground | 100708.02 | 5.42 | 245.15 | 0 | 32.35 | 0 | OK | Ground clear controls. | 227 | 58.54 | 277.5
15757 | TIN-INTERP | Interpolated Ground | 100708.05 | 7.43 | 245.6 | 0 | 25.57 | 0 | OK | Ground clear controls. | 227 | 58.54 | 271.17
15758 | TIN-INTERP | Interpolated Ground | 100747.46 | -7.22 | 235.7 | 0 | 41.24 | 0 | OK | Ground clear controls. | 227 | 58.54 | 276.94
15759 | TIN-INTERP | Interpolated Ground | 100747.5 | -5.72 | 236.15 | 0 | 35.31 | 0 | OK | Ground clear controls. | 227 | 58.54 | 271.46
15760 | TIN-INTERP | Interpolated Ground | 100747.53 | -5.23 | 236.29 | 0 | 46.61 | 0 | OK | Ground clear controls. | 227 | 58.54 | 282.9
15761 | TIN-INTERP | Interpolated Ground | 100747.99 | 5.84 | 238.67 | 0 | 33.17 | 0 | OK | Ground clear controls. | 227 | 58.54 | 271.84
15762 | TIN-INTERP | Interpolated Ground | 100748.02 | 5.35 | 238.54 | 0 | 44.88 | 0 | OK | Ground clear controls. | 227 | 58.54 | 283.42
15763 | TIN-INTERP | Interpolated Ground | 100748.05 | 7.34 | 238.98 | 0 | 38.16 | 0 | OK | Ground clear controls. | 227 | 58.54 | 277.14
15764 | TIN-INTERP | Interpolated Ground | 100787.46 | -7.18 | 230.26 | 0 | 53.63 | 0 | OK | Ground clear controls. | 227 | 58.54 | 283.89
15765 | TIN-INTERP | Interpolated Ground | 100787.5 | -5.68 | 231.03 | 0 | 47.4 | 0 | OK | Ground clear controls. | 227 | 58.54 | 278.43
15766 | TIN-INTERP | Interpolated Ground | 100787.53 | -5.21 | 231.29 | 0 | 58.54 | 0 | OK | Ground clear controls. | 227 | 58.54 | 289.83
15767 | TIN-INTERP | Interpolated Ground | 100787.99 | 5.75 | 236.93 | 0 | 41.84 | 0 | OK | Ground clear controls. | 227 | 57.82 | 278.77
15768 | TIN-INTERP | Interpolated Ground | 100788.02 | 5.27 | 236.65 | 0 | 53.66 | 0 | OK | Ground clear controls. | 227 | 57.82 | 290.31
15769 | TIN-INTERP | Interpolated Ground | 100788.05 | 7.25 | 237.59 | 0 | 46.51 | 0 | OK | Ground clear controls. | 227 | 57.82 | 284.1
15770 | TIN-INTERP | Interpolated Ground | 100827.46 | -7.14 | 239.66 | 0 | 52.18 | 0 | OK | Ground clear controls. | 227 | 57.82 | 291.84
15771 | TIN-INTERP | Interpolated Ground | 100827.5 | -5.64 | 239.87 | 0 | 46.51 | 0 | OK | Ground clear controls. | 227 | 57.82 | 286.38
15772 | TIN-INTERP | Interpolated Ground | 100827.53 | -5.18 | 239.93 | 0 | 57.82 | 0 | OK | Ground clear controls. | 227 | 57.82 | 297.75
15773 | TIN-INTERP | Interpolated Ground | 100827.99 | 5.66 | 243.73 | 0 | 42.97 | 0 | OK | Ground clear controls. | 227 | 54.75 | 286.7
15774 | TIN-INTERP | Interpolated Ground | 100828.02 | 5.2 | 243.43 | 0 | 54.75 | 0 | OK | Ground clear controls. | 227 | 54.75 | 298.18
15775 | TIN-INTERP | Interpolated Ground | 100828.05 | 7.16 | 244.77 | 0 | 47.29 | 0 | OK | Ground clear controls. | 227 | 53.72 | 292.06
15776 | TIN-INTERP | Interpolated Ground | 100867.46 | -7.1 | 252.44 | 0 | 48.34 | 0 | OK | Ground clear controls. | 227 | 53.72 | 300.78
15777 | TIN-INTERP | Interpolated Ground | 100867.5 | -5.6 | 252.74 | 0 | 42.58 | 0 | OK | Ground clear controls. | 227 | 53.72 | 295.32
15778 | TIN-INTERP | Interpolated Ground | 100867.53 | -5.16 | 252.94 | 0 | 53.72 | 0 | OK | Ground clear controls. | 227 | 53.72 | 306.66
15779 | TIN-INTERP | Interpolated Ground | 100867.99 | 5.57 | 260.35 | 0 | 35.26 | 0 | OK | Ground clear controls. | 227 | 47.02 | 295.61
15780 | TIN-INTERP | Interpolated Ground | 100868.02 | 5.12 | 260.02 | 0 | 47.02 | 0 | OK | Ground clear controls. | 227 | 47.02 | 307.04
15781 | TIN-INTERP | Interpolated Ground | 100868.05 | 7.07 | 261.53 | 0 | 39.47 | 0 | OK | Ground clear controls. | 227 | 45.39 | 301
15782 | TIN-INTERP | Interpolated Ground | 100907.46 | -7.06 | 271.42 | 0 | 39.3 | 0 | OK | Ground clear controls. | 227 | 45.39 | 310.72
15783 | TIN-INTERP | Interpolated Ground | 100907.5 | -5.56 | 271.33 | 0 | 33.93 | 0 | OK | Ground clear controls. | 227 | 45.39 | 305.26
15784 | TIN-INTERP | Interpolated Ground | 100907.53 | -5.14 | 271.18 | 0 | 45.39 | 0 | OK | Ground clear controls. | 227 | 45.39 | 316.57
15785 | TIN-INTERP | Interpolated Ground | 100907.99 | 5.48 | 271.84 | 0 | 33.66 | 0 | OK | Ground clear controls. | 227 | 45.04 | 305.5
15786 | TIN-INTERP | Interpolated Ground | 100908.02 | 5.05 | 271.85 | 0 | 45.04 | 0 | OK | Ground clear controls. | 227 | 45.04 | 316.89
15787 | TIN-INTERP | Interpolated Ground | 100908.05 | 6.98 | 271.87 | 0 | 39.07 | 0 | OK | Ground clear controls. | 227 | 43.88 | 310.94
15788 | TIN-INTERP | Interpolated Ground | 100947.46 | -7.03 | 284.2 | 0 | 37.47 | 0 | OK | Ground clear controls. | 227 | 43.88 | 321.67
15789 | TIN-INTERP | Interpolated Ground | 100947.5 | -5.53 | 284.14 | 0 | 32.06 | 0 | OK | Ground clear controls. | 227 | 43.88 | 316.2
15790 | TIN-INTERP | Interpolated Ground | 100947.53 | -5.11 | 284.08 | 0 | 43.42 | 0 | OK | Ground clear controls. | 227 | 43.88 | 327.5
15791 | TIN-INTERP | Interpolated Ground | 100947.99 | 5.39 | 283.83 | 0 | 32.58 | 0 | OK | Ground clear controls. | 227 | 43.88 | 316.41
15792 | TIN-INTERP | Interpolated Ground | 100948.02 | 4.97 | 283.85 | 0 | 43.88 | 0 | OK | Ground clear controls. | 227 | 43.88 | 327.73
15793 | TIN-INTERP | Interpolated Ground | 100948.05 | 6.89 | 284.02 | 0 | 37.87 | 0 | OK | Ground clear controls. | 227 | 37.87 | 321.89
15794 | TIN-INTERP | Interpolated Ground | 100969.76 | 5.34 | 290.53 | 0 | 32.23 | 0 | OK | Ground clear controls. | 228 | 45.57 | 322.76
15795 | TIN-INTERP | Interpolated Ground | 100969.77 | 6.84 | 290.67 | 0 | 37.59 | 0 | OK | Ground clear controls. | 228 | 45.57 | 328.26
15796 | TIN-INTERP | Interpolated Ground | 100969.82 | 4.93 | 290.44 | 0 | 43.63 | 0 | OK | Ground clear controls. | 228 | 45.57 | 334.07
15797 | TIN-INTERP | Interpolated Ground | 100969.87 | -5.5 | 289.79 | 0 | 32.97 | 0 | OK | Ground clear controls. | 228 | 45.57 | 322.76
15798 | TIN-INTERP | Interpolated Ground | 100969.91 | -7 | 289.73 | 0 | 38.53 | 0 | OK | Ground clear controls. | 228 | 45.57 | 328.26
15799 | TIN-INTERP | Interpolated Ground | 100969.94 | -5.1 | 289.81 | 0 | 44.25 | 0 | OK | Ground clear controls. | 228 | 45.57 | 334.06
15800 | TIN-INTERP | Interpolated Ground | 101009.76 | 5.41 | 291.02 | 0 | 22.89 | 0 | OK | Ground clear controls. | 228 | 45.57 | 313.91
15801 | TIN-INTERP | Interpolated Ground | 101009.77 | 6.91 | 291.02 | 0 | 28.4 | 0 | OK | Ground clear controls. | 228 | 45.57 | 319.42
15802 | TIN-INTERP | Interpolated Ground | 101009.82 | 4.98 | 291.01 | 0 | 34.34 | 0 | OK | Ground clear controls. | 228 | 45.57 | 325.35
15803 | TIN-INTERP | Interpolated Ground | 101009.87 | -5.64 | 290.9 | 0 | 22.99 | 0 | OK | Ground clear controls. | 228 | 45.57 | 313.89
15804 | TIN-INTERP | Interpolated Ground | 101009.9 | -7.14 | 290.83 | 0 | 28.6 | 0 | OK | Ground clear controls. | 228 | 45.57 | 319.43
15805 | TIN-INTERP | Interpolated Ground | 101009.94 | -5.21 | 290.91 | 0 | 34.42 | 0 | OK | Ground clear controls. | 228 | 45.57 | 325.33
15806 | TIN-INTERP | Interpolated Ground | 101049.76 | 5.49 | 284.64 | 0 | 21.39 | 0 | OK | Ground clear controls. | 228 | 45.57 | 306.03
15807 | TIN-INTERP | Interpolated Ground | 101049.77 | 6.99 | 284.26 | 0 | 27.29 | 0 | OK | Ground clear controls. | 228 | 45.57 | 311.55
15808 | TIN-INTERP | Interpolated Ground | 101049.82 | 5.03 | 284.72 | 0 | 32.87 | 0 | OK | Ground clear controls. | 228 | 45.57 | 317.59
15809 | TIN-INTERP | Interpolated Ground | 101049.87 | -5.78 | 286.22 | 0 | 19.76 | 0 | OK | Ground clear controls. | 228 | 45.57 | 305.98
15810 | TIN-INTERP | Interpolated Ground | 101049.9 | -7.28 | 286.43 | 0 | 25.13 | 0 | OK | Ground clear controls. | 228 | 45.57 | 311.56
15811 | TIN-INTERP | Interpolated Ground | 101049.94 | -5.33 | 286.14 | 0 | 31.41 | 0 | OK | Ground clear controls. | 228 | 45.57 | 317.55
15812 | TIN-INTERP | Interpolated Ground | 101089.76 | 5.57 | 278.85 | 0 | 20.27 | 0 | OK | Ground clear controls. | 228 | 45.57 | 299.12
15813 | TIN-INTERP | Interpolated Ground | 101089.77 | 7.07 | 278.88 | 0 | 25.79 | 0 | OK | Ground clear controls. | 228 | 45.57 | 304.67
15814 | TIN-INTERP | Interpolated Ground | 101089.82 | 5.08 | 278.83 | 0 | 31.97 | 0 | OK | Ground clear controls. | 228 | 45.57 | 310.8
15815 | TIN-INTERP | Interpolated Ground | 101089.87 | -5.92 | 277.92 | 0 | 21.15 | 0 | OK | Ground clear controls. | 228 | 45.57 | 299.07
15816 | TIN-INTERP | Interpolated Ground | 101089.9 | -7.42 | 277.66 | 0 | 27.01 | 0 | OK | Ground clear controls. | 228 | 45.57 | 304.67
15817 | TIN-INTERP | Interpolated Ground | 101089.94 | -5.44 | 277.98 | 0 | 32.76 | 0 | OK | Ground clear controls. | 228 | 45.57 | 310.74
15818 | TIN-INTERP | Interpolated Ground | 101129.76 | 5.64 | 268.24 | 0 | 24.94 | 0 | OK | Ground clear controls. | 228 | 45.57 | 293.18
15819 | TIN-INTERP | Interpolated Ground | 101129.77 | 7.14 | 268.34 | 0 | 30.41 | 0 | OK | Ground clear controls. | 228 | 45.57 | 298.75
15820 | TIN-INTERP | Interpolated Ground | 101129.82 | 5.13 | 268.14 | 0 | 36.82 | 0 | OK | Ground clear controls. | 228 | 45.57 | 304.96
15821 | TIN-INTERP | Interpolated Ground | 101129.87 | -6.06 | 266.59 | 0 | 26.54 | 0 | OK | Ground clear controls. | 228 | 45.57 | 293.13
15822 | TIN-INTERP | Interpolated Ground | 101129.9 | -7.56 | 266.81 | 0 | 31.94 | 0 | OK | Ground clear controls. | 228 | 45.57 | 298.75
15823 | TIN-INTERP | Interpolated Ground | 101129.94 | -5.56 | 266.55 | 0 | 38.34 | 0 | OK | Ground clear controls. | 228 | 45.57 | 304.89
15824 | TIN-INTERP | Interpolated Ground | 101169.76 | 5.72 | 262.6 | 0 | 25.61 | 0 | OK | Ground clear controls. | 228 | 45.57 | 288.21
15825 | TIN-INTERP | Interpolated Ground | 101169.77 | 7.22 | 262.44 | 0 | 31.35 | 0 | OK | Ground clear controls. | 228 | 45.57 | 293.79
15826 | TIN-INTERP | Interpolated Ground | 101169.82 | 5.18 | 262.6 | 0 | 37.46 | 0 | OK | Ground clear controls. | 228 | 45.57 | 300.06
15827 | TIN-INTERP | Interpolated Ground | 101169.87 | -6.2 | 259.62 | 0 | 28.52 | 0 | OK | Ground clear controls. | 228 | 45.57 | 288.14
15828 | TIN-INTERP | Interpolated Ground | 101169.9 | -7.7 | 259.46 | 0 | 34.34 | 0 | OK | Ground clear controls. | 228 | 45.57 | 293.8
15829 | TIN-INTERP | Interpolated Ground | 101169.94 | -5.67 | 259.66 | 0 | 40.33 | 0 | OK | Ground clear controls. | 228 | 45.57 | 299.99
15830 | TIN-INTERP | Interpolated Ground | 101209.76 | 5.79 | 251.4 | 0 | 32.8 | 0 | OK | Ground clear controls. | 228 | 45.57 | 284.2
15831 | TIN-INTERP | Interpolated Ground | 101209.77 | 7.29 | 250.68 | 0 | 39.13 | 0 | OK | Ground clear controls. | 228 | 45.57 | 289.81
15832 | TIN-INTERP | Interpolated Ground | 101209.82 | 5.23 | 251.4 | 0 | 44.73 | 0 | OK | Ground clear controls. | 228 | 45.57 | 296.13
15833 | TIN-INTERP | Interpolated Ground | 101209.87 | -6.34 | 250.79 | 0 | 33.34 | 0 | OK | Ground clear controls. | 228 | 45.57 | 284.13
15834 | TIN-INTERP | Interpolated Ground | 101209.9 | -7.84 | 251.36 | 0 | 38.45 | 0 | OK | Ground clear controls. | 228 | 45.57 | 289.81
15835 | TIN-INTERP | Interpolated Ground | 101209.94 | -5.78 | 250.48 | 0 | 45.57 | 0 | OK | Ground clear controls. | 228 | 45.57 | 296.05
15836 | TIN-INTERP | Interpolated Ground | 101249.76 | 5.87 | 253.79 | 0 | 27.36 | 0 | OK | Ground clear controls. | 228 | 44.66 | 281.15
15837 | TIN-INTERP | Interpolated Ground | 101249.77 | 7.37 | 253.76 | 0 | 33.03 | 0 | OK | Ground clear controls. | 228 | 44.66 | 286.79
15838 | TIN-INTERP | Interpolated Ground | 101249.82 | 5.28 | 253.82 | 0 | 39.32 | 0 | OK | Ground clear controls. | 228 | 44.66 | 293.14
15839 | TIN-INTERP | Interpolated Ground | 101249.87 | -6.48 | 255.61 | 0 | 25.47 | 0 | OK | Ground clear controls. | 228 | 44.66 | 281.08
15840 | TIN-INTERP | Interpolated Ground | 101249.9 | -7.98 | 255.92 | 0 | 30.87 | 0 | OK | Ground clear controls. | 228 | 44.66 | 286.79
15841 | TIN-INTERP | Interpolated Ground | 101249.94 | -5.9 | 255.47 | 0 | 37.6 | 0 | OK | Ground clear controls. | 228 | 44.66 | 293.07
15842 | TIN-INTERP | Interpolated Ground | 101289.76 | 5.94 | 252.48 | 0 | 26.57 | 0 | OK | Ground clear controls. | 228 | 44.66 | 279.05
15843 | TIN-INTERP | Interpolated Ground | 101289.77 | 7.45 | 252.67 | 0 | 32.05 | 0 | OK | Ground clear controls. | 228 | 44.66 | 284.72
15844 | TIN-INTERP | Interpolated Ground | 101289.82 | 5.33 | 252.28 | 0 | 38.8 | 0 | OK | Ground clear controls. | 228 | 44.66 | 291.08
15845 | TIN-INTERP | Interpolated Ground | 101289.87 | -6.62 | 250.31 | 0 | 28.68 | 0 | OK | Ground clear controls. | 228 | 44.66 | 278.99
15846 | TIN-INTERP | Interpolated Ground | 101289.9 | -8.12 | 250.08 | 0 | 34.65 | 0 | OK | Ground clear controls. | 228 | 44.66 | 284.73
15847 | TIN-INTERP | Interpolated Ground | 101289.94 | -6.01 | 250.42 | 0 | 40.6 | 0 | OK | Ground clear controls. | 228 | 44.66 | 291.02
15848 | TIN-INTERP | Interpolated Ground | 101329.76 | 6.02 | 256.67 | 0 | 21.23 | 0 | OK | Ground clear controls. | 228 | 44.66 | 277.9
15849 | TIN-INTERP | Interpolated Ground | 101329.77 | 7.52 | 257.14 | 0 | 26.48 | 0 | OK | Ground clear controls. | 228 | 44.66 | 283.62
15850 | TIN-INTERP | Interpolated Ground | 101329.82 | 5.38 | 256.53 | 0 | 33.45 | 0 | OK | Ground clear controls. | 228 | 44.66 | 289.98
15851 | TIN-INTERP | Interpolated Ground | 101329.87 | -6.76 | 253.26 | 0 | 24.6 | 0 | OK | Ground clear controls. | 228 | 44.66 | 277.86
15852 | TIN-INTERP | Interpolated Ground | 101329.9 | -8.26 | 253.16 | 0 | 30.46 | 0 | OK | Ground clear controls. | 228 | 44.66 | 283.62
15853 | TIN-INTERP | Interpolated Ground | 101329.94 | -6.13 | 253.39 | 0 | 36.55 | 0 | OK | Ground clear controls. | 228 | 44.66 | 289.94
15854 | TIN-INTERP | Interpolated Ground | 101369.76 | 6.1 | 252.65 | 0 | 25.07 | 0 | OK | Ground clear controls. | 228 | 44.66 | 277.72
15855 | TIN-INTERP | Interpolated Ground | 101369.77 | 7.6 | 253.33 | 0 | 30.14 | 0 | OK | Ground clear controls. | 228 | 44.66 | 283.47
15856 | TIN-INTERP | Interpolated Ground | 101369.82 | 5.43 | 252.39 | 0 | 37.43 | 0 | OK | Ground clear controls. | 228 | 44.66 | 289.82
15857 | TIN-INTERP | Interpolated Ground | 101369.87 | -6.9 | 249.94 | 0 | 27.76 | 0 | OK | Ground clear controls. | 228 | 44.66 | 277.7
15858 | TIN-INTERP | Interpolated Ground | 101369.9 | -8.4 | 249.73 | 0 | 33.75 | 0 | OK | Ground clear controls. | 228 | 44.66 | 283.48
15859 | TIN-INTERP | Interpolated Ground | 101369.94 | -6.24 | 250.04 | 0 | 39.75 | 0 | OK | Ground clear controls. | 228 | 44.66 | 289.79
15860 | TIN-INTERP | Interpolated Ground | 101409.76 | 6.17 | 247.78 | 0 | 30.72 | 0 | OK | Ground clear controls. | 228 | 44.66 | 278.5
15861 | TIN-INTERP | Interpolated Ground | 101409.77 | 7.68 | 248.16 | 0 | 36.13 | 0 | OK | Ground clear controls. | 228 | 44.66 | 284.29
15862 | TIN-INTERP | Interpolated Ground | 101409.82 | 5.48 | 247.59 | 0 | 43.02 | 0 | OK | Ground clear controls. | 228 | 44.66 | 290.61
15863 | TIN-INTERP | Interpolated Ground | 101409.87 | -7.04 | 245.86 | 0 | 32.62 | 0 | OK | Ground clear controls. | 228 | 44.66 | 278.48
15864 | TIN-INTERP | Interpolated Ground | 101409.9 | -8.54 | 245.67 | 0 | 38.62 | 0 | OK | Ground clear controls. | 228 | 44.66 | 284.29
15865 | TIN-INTERP | Interpolated Ground | 101409.94 | -6.35 | 245.94 | 0 | 44.66 | 0 | OK | Ground clear controls. | 228 | 44.66 | 290.6
15866 | TIN-INTERP | Interpolated Ground | 101410.03 | -6.35 | 245.92 | 0 | 44.67 | 0 | OK | Ground clear controls. | 229 | 77.39 | 290.59
15867 | TIN-INTERP | Interpolated Ground | 101410.03 | -8.54 | 245.65 | 0 | 38.64 | 0 | OK | Ground clear controls. | 229 | 77.39 | 284.29
15868 | TIN-INTERP | Interpolated Ground | 101410.06 | -7.05 | 245.84 | 0 | 32.66 | 0 | OK | Ground clear controls. | 229 | 77.39 | 278.5
15869 | TIN-INTERP | Interpolated Ground | 101410.22 | 5.49 | 247.55 | 0 | 43.06 | 0 | OK | Ground clear controls. | 229 | 77.39 | 290.61
15870 | TIN-INTERP | Interpolated Ground | 101410.33 | 6.17 | 247.69 | 0 | 30.82 | 0 | OK | Ground clear controls. | 229 | 77.39 | 278.51
15871 | TIN-INTERP | Interpolated Ground | 101410.36 | 7.68 | 248.08 | 0 | 36.23 | 0 | OK | Ground clear controls. | 229 | 77.39 | 284.31
15872 | TIN-INTERP | Interpolated Ground | 101449.94 | 5.45 | 238.99 | 0 | 43.17 | 0 | OK | Ground clear controls. | 229 | 77.39 | 282.16
15873 | TIN-INTERP | Interpolated Ground | 101449.98 | 7.63 | 239.27 | 0 | 36.54 | 0 | OK | Ground clear controls. | 229 | 77.39 | 275.81
15874 | TIN-INTERP | Interpolated Ground | 101450.01 | 6.13 | 239.05 | 0 | 31.01 | 0 | OK | Ground clear controls. | 229 | 77.39 | 270.06
15875 | TIN-INTERP | Interpolated Ground | 101450.35 | -6.3 | 241 | 0 | 41.2 | 0 | OK | Ground clear controls. | 229 | 77.39 | 282.2
15876 | TIN-INTERP | Interpolated Ground | 101450.42 | -6.97 | 241.06 | 0 | 29.02 | 0 | OK | Ground clear controls. | 229 | 77.39 | 270.08
15877 | TIN-INTERP | Interpolated Ground | 101450.46 | -8.47 | 241.33 | 0 | 34.55 | 0 | OK | Ground clear controls. | 229 | 77.39 | 275.88
15878 | TIN-INTERP | Interpolated Ground | 101489.94 | 5.43 | 231.12 | 0 | 43.57 | 0 | OK | Ground clear controls. | 229 | 77.39 | 274.69
15879 | TIN-INTERP | Interpolated Ground | 101489.98 | 7.59 | 229.64 | 0 | 38.67 | 0 | OK | Ground clear controls. | 229 | 77.39 | 268.31
15880 | TIN-INTERP | Interpolated Ground | 101490.01 | 6.09 | 230.69 | 0 | 31.91 | 0 | OK | Ground clear controls. | 229 | 77.39 | 262.6
15881 | TIN-INTERP | Interpolated Ground | 101490.35 | -6.23 | 237.71 | 0 | 37.08 | 0 | OK | Ground clear controls. | 229 | 77.39 | 274.79
15882 | TIN-INTERP | Interpolated Ground | 101490.42 | -6.89 | 237.87 | 0 | 24.78 | 0 | OK | Ground clear controls. | 229 | 77.39 | 262.65
15883 | TIN-INTERP | Interpolated Ground | 101490.46 | -8.39 | 238.17 | 0 | 30.28 | 0 | OK | Ground clear controls. | 229 | 77.39 | 268.45
15884 | TIN-INTERP | Interpolated Ground | 101529.94 | 5.4 | 229 | 0 | 39.21 | 0 | OK | Ground clear controls. | 229 | 77.39 | 268.21
15885 | TIN-INTERP | Interpolated Ground | 101529.98 | 7.56 | 228.26 | 0 | 33.54 | 0 | OK | Ground clear controls. | 229 | 77.39 | 261.8
15886 | TIN-INTERP | Interpolated Ground | 101530.01 | 6.05 | 228.83 | 0 | 27.29 | 0 | OK | Ground clear controls. | 229 | 77.39 | 256.12
15887 | TIN-INTERP | Interpolated Ground | 101530.35 | -6.16 | 232.93 | 0 | 35.42 | 0 | OK | Ground clear controls. | 229 | 77.39 | 268.35
15888 | TIN-INTERP | Interpolated Ground | 101530.42 | -6.81 | 233.2 | 0 | 23 | 0 | OK | Ground clear controls. | 229 | 77.39 | 256.2
15889 | TIN-INTERP | Interpolated Ground | 101530.46 | -8.31 | 233.78 | 0 | 28.22 | 0 | OK | Ground clear controls. | 229 | 77.39 | 262
15890 | TIN-INTERP | Interpolated Ground | 101569.94 | 5.38 | 232.71 | 0 | 29.99 | 0 | OK | Ground clear controls. | 229 | 77.39 | 262.7
15891 | TIN-INTERP | Interpolated Ground | 101569.98 | 7.52 | 232.75 | 0 | 23.52 | 0 | OK | Ground clear controls. | 229 | 77.39 | 256.27
15892 | TIN-INTERP | Interpolated Ground | 101570.01 | 6.02 | 232.7 | 0 | 17.93 | 0 | OK | Ground clear controls. | 229 | 77.39 | 250.63
15893 | TIN-INTERP | Interpolated Ground | 101570.35 | -6.1 | 232.06 | 0 | 30.83 | 0 | OK | Ground clear controls. | 229 | 77.39 | 262.89
15894 | TIN-INTERP | Interpolated Ground | 101570.42 | -6.73 | 231.95 | 0 | 18.79 | 0 | OK | Ground clear controls. | 229 | 77.39 | 250.74
15895 | TIN-INTERP | Interpolated Ground | 101570.46 | -8.23 | 231.7 | 0 | 24.83 | 0 | OK | Ground clear controls. | 229 | 77.39 | 256.53
15896 | TIN-INTERP | Interpolated Ground | 101609.94 | 5.36 | 226.73 | 0 | 31.45 | 0 | OK | Ground clear controls. | 229 | 77.39 | 258.18
15897 | TIN-INTERP | Interpolated Ground | 101609.98 | 7.48 | 227.31 | 0 | 24.42 | 0 | OK | Ground clear controls. | 229 | 77.39 | 251.73
15898 | TIN-INTERP | Interpolated Ground | 101610.01 | 5.98 | 226.91 | 0 | 19.22 | 0 | OK | Ground clear controls. | 229 | 77.39 | 246.13
15899 | TIN-INTERP | Interpolated Ground | 101610.35 | -6.03 | 219.63 | 0 | 38.77 | 0 | OK | Ground clear controls. | 229 | 77.39 | 258.4
15900 | TIN-INTERP | Interpolated Ground | 101610.42 | -6.65 | 219.07 | 0 | 27.19 | 0 | OK | Ground clear controls. | 229 | 77.39 | 246.26
15901 | TIN-INTERP | Interpolated Ground | 101610.46 | -8.15 | 217.75 | 0 | 34.3 | 0 | OK | Ground clear controls. | 229 | 77.39 | 252.05
15902 | TIN-INTERP | Interpolated Ground | 101649.94 | 5.33 | 221.94 | 0 | 32.68 | 0 | OK | Ground clear controls. | 229 | 77.39 | 254.62
15903 | TIN-INTERP | Interpolated Ground | 101649.98 | 7.44 | 222.3 | 0 | 25.87 | 0 | OK | Ground clear controls. | 229 | 77.39 | 248.17
15904 | TIN-INTERP | Interpolated Ground | 101650.01 | 5.94 | 222.03 | 0 | 20.56 | 0 | OK | Ground clear controls. | 229 | 77.39 | 242.59
15905 | TIN-INTERP | Interpolated Ground | 101650.35 | -5.96 | 216.12 | 0 | 38.76 | 0 | OK | Ground clear controls. | 229 | 77.39 | 254.88
15906 | TIN-INTERP | Interpolated Ground | 101650.42 | -6.57 | 215.77 | 0 | 26.98 | 0 | OK | Ground clear controls. | 229 | 77.39 | 242.75
15907 | TIN-INTERP | Interpolated Ground | 101650.46 | -8.07 | 214.78 | 0 | 33.74 | 0 | OK | Ground clear controls. | 229 | 77.39 | 248.52
15908 | TIN-INTERP | Interpolated Ground | 101689.94 | 5.31 | 218.49 | 0 | 33.55 | 0 | OK | Ground clear controls. | 229 | 77.39 | 252.04
15909 | TIN-INTERP | Interpolated Ground | 101689.98 | 7.41 | 219.31 | 0 | 26.29 | 0 | OK | Ground clear controls. | 229 | 77.39 | 245.6
15910 | TIN-INTERP | Interpolated Ground | 101690.01 | 5.9 | 218.68 | 0 | 21.37 | 0 | OK | Ground clear controls. | 229 | 77.39 | 240.05
15911 | TIN-INTERP | Interpolated Ground | 101690.35 | -5.9 | 212.11 | 0 | 40.22 | 0 | OK | Ground clear controls. | 229 | 77.39 | 252.33
15912 | TIN-INTERP | Interpolated Ground | 101690.42 | -6.49 | 211.58 | 0 | 28.64 | 0 | OK | Ground clear controls. | 229 | 77.39 | 240.22
15913 | TIN-INTERP | Interpolated Ground | 101690.46 | -7.99 | 210.32 | 0 | 35.66 | 0 | OK | Ground clear controls. | 229 | 77.39 | 245.98
15914 | TIN-INTERP | Interpolated Ground | 101729.94 | 5.29 | 214.4 | 0 | 36.03 | 0 | OK | Ground clear controls. | 229 | 77.39 | 250.43
15915 | TIN-INTERP | Interpolated Ground | 101729.98 | 7.37 | 215.27 | 0 | 28.73 | 0 | OK | Ground clear controls. | 229 | 77.39 | 244
15916 | TIN-INTERP | Interpolated Ground | 101730.01 | 5.87 | 214.57 | 0 | 23.9 | 0 | OK | Ground clear controls. | 229 | 77.39 | 238.47
15917 | TIN-INTERP | Interpolated Ground | 101730.35 | -5.83 | 210.13 | 0 | 40.62 | 0 | OK | Ground clear controls. | 229 | 77.39 | 250.75
15918 | TIN-INTERP | Interpolated Ground | 101730.42 | -6.41 | 210.01 | 0 | 28.65 | 0 | OK | Ground clear controls. | 229 | 77.39 | 238.66
15919 | TIN-INTERP | Interpolated Ground | 101730.46 | -7.91 | 209.75 | 0 | 34.67 | 0 | OK | Ground clear controls. | 229 | 77.39 | 244.42
15920 | TIN-INTERP | Interpolated Ground | 101769.94 | 5.27 | 207.39 | 0 | 42.41 | 0 | OK | Ground clear controls. | 229 | 77.39 | 249.8
15921 | TIN-INTERP | Interpolated Ground | 101769.98 | 7.33 | 206.66 | 0 | 36.72 | 0 | OK | Ground clear controls. | 229 | 77.39 | 243.38
15922 | TIN-INTERP | Interpolated Ground | 101770.01 | 5.83 | 207.19 | 0 | 30.68 | 0 | OK | Ground clear controls. | 229 | 77.39 | 237.87
15923 | TIN-INTERP | Interpolated Ground | 101770.35 | -5.76 | 206.22 | 0 | 43.9 | 0 | OK | Ground clear controls. | 229 | 77.39 | 250.12
15924 | TIN-INTERP | Interpolated Ground | 101770.42 | -6.33 | 206.15 | 0 | 31.92 | 0 | OK | Ground clear controls. | 229 | 77.39 | 238.07
15925 | TIN-INTERP | Interpolated Ground | 101770.46 | -7.82 | 206.01 | 0 | 37.8 | 0 | OK | Ground clear controls. | 229 | 77.39 | 243.81
15926 | TIN-INTERP | Interpolated Ground | 101809.94 | 5.24 | 172.75 | 0 | 77.39 | 0 | OK | Ground clear controls. | 229 | 77.39 | 250.14
15927 | TIN-INTERP | Interpolated Ground | 101809.98 | 7.29 | 171.48 | 0 | 72.26 | 0 | OK | Ground clear controls. | 229 | 72.26 | 243.74
15928 | TIN-INTERP | Interpolated Ground | 101810.01 | 5.79 | 172.26 | 0 | 65.98 | 0 | OK | Ground clear controls. | 229 | 70.34 | 238.24
15929 | TIN-INTERP | Interpolated Ground | 101810.35 | -5.7 | 184.12 | 0 | 66.34 | 0 | OK | Ground clear controls. | 229 | 70.34 | 250.46
15930 | TIN-INTERP | Interpolated Ground | 101810.42 | -6.24 | 184.35 | 0 | 54.09 | 0 | OK | Ground clear controls. | 229 | 70.34 | 238.44
15931 | TIN-INTERP | Interpolated Ground | 101810.46 | -7.74 | 185.65 | 0 | 58.53 | 0 | OK | Ground clear controls. | 229 | 70.34 | 244.18
15932 | TIN-INTERP | Interpolated Ground | 101849.94 | 5.22 | 186.36 | 0 | 65.08 | 0 | OK | Ground clear controls. | 229 | 70.34 | 251.44
15933 | TIN-INTERP | Interpolated Ground | 101849.98 | 7.26 | 187.57 | 0 | 57.5 | 0 | OK | Ground clear controls. | 229 | 70.34 | 245.07
15934 | TIN-INTERP | Interpolated Ground | 101850.01 | 5.76 | 186.62 | 0 | 52.97 | 0 | OK | Ground clear controls. | 229 | 70.34 | 239.59
15935 | TIN-INTERP | Interpolated Ground | 101850.35 | -5.63 | 181.43 | 0 | 70.34 | 0 | OK | Ground clear controls. | 229 | 70.34 | 251.77
15936 | TIN-INTERP | Interpolated Ground | 101850.42 | -6.16 | 181.23 | 0 | 58.57 | 0 | OK | Ground clear controls. | 229 | 64.99 | 239.8
15937 | TIN-INTERP | Interpolated Ground | 101850.46 | -7.66 | 180.53 | 0 | 64.99 | 0 | OK | Ground clear controls. | 229 | 64.99 | 245.52
15938 | TIN-INTERP | Interpolated Ground | 101889.94 | 5.2 | 214.3 | 0 | 39.41 | 0 | OK | Ground clear controls. | 229 | 49.31 | 253.71
15939 | TIN-INTERP | Interpolated Ground | 101889.98 | 7.22 | 215.14 | 0 | 32.25 | 0 | OK | Ground clear controls. | 229 | 49.31 | 247.39
15940 | TIN-INTERP | Interpolated Ground | 101890.01 | 5.72 | 214.47 | 0 | 27.45 | 0 | OK | Ground clear controls. | 229 | 49.31 | 241.92
15941 | TIN-INTERP | Interpolated Ground | 101890.35 | -5.56 | 209.45 | 0 | 44.59 | 0 | OK | Ground clear controls. | 229 | 49.31 | 254.04
15942 | TIN-INTERP | Interpolated Ground | 101890.42 | -6.08 | 209.38 | 0 | 32.74 | 0 | OK | Ground clear controls. | 229 | 49.31 | 242.12
15943 | TIN-INTERP | Interpolated Ground | 101890.46 | -7.58 | 208.99 | 0 | 38.83 | 0 | OK | Ground clear controls. | 229 | 49.31 | 247.82
15944 | TIN-INTERP | Interpolated Ground | 101929.94 | 5.17 | 214.59 | 0 | 42.37 | 0 | OK | Ground clear controls. | 229 | 49.31 | 256.96
15945 | TIN-INTERP | Interpolated Ground | 101929.98 | 7.18 | 215.21 | 0 | 35.47 | 0 | OK | Ground clear controls. | 229 | 49.31 | 250.68
15946 | TIN-INTERP | Interpolated Ground | 101930.01 | 5.68 | 214.83 | 0 | 30.38 | 0 | OK | Ground clear controls. | 229 | 49.31 | 245.21
15947 | TIN-INTERP | Interpolated Ground | 101930.35 | -5.5 | 211.73 | 0 | 45.54 | 0 | OK | Ground clear controls. | 229 | 49.31 | 257.27
15948 | TIN-INTERP | Interpolated Ground | 101930.42 | -6 | 211.68 | 0 | 33.74 | 0 | OK | Ground clear controls. | 229 | 49.31 | 245.42
15949 | TIN-INTERP | Interpolated Ground | 101930.46 | -7.5 | 211.52 | 0 | 39.58 | 0 | OK | Ground clear controls. | 229 | 49.31 | 251.1
15950 | TIN-INTERP | Interpolated Ground | 101969.94 | 5.15 | 211.87 | 0 | 49.31 | 0 | OK | Ground clear controls. | 229 | 49.31 | 261.18
15951 | TIN-INTERP | Interpolated Ground | 101969.98 | 7.15 | 211.41 | 0 | 43.54 | 0 | OK | Ground clear controls. | 229 | 49.2 | 254.95
15952 | TIN-INTERP | Interpolated Ground | 101970.01 | 5.64 | 211.83 | 0 | 37.66 | 0 | OK | Ground clear controls. | 229 | 49.2 | 249.49
15953 | TIN-INTERP | Interpolated Ground | 101970.35 | -5.43 | 212.29 | 0 | 49.2 | 0 | OK | Ground clear controls. | 229 | 49.2 | 261.49
15954 | TIN-INTERP | Interpolated Ground | 101970.42 | -5.92 | 212.13 | 0 | 37.56 | 0 | OK | Ground clear controls. | 229 | 46.16 | 249.69
15955 | TIN-INTERP | Interpolated Ground | 101970.46 | -7.42 | 211.56 | 0 | 43.79 | 0 | OK | Ground clear controls. | 229 | 46.16 | 255.35
15956 | TIN-INTERP | Interpolated Ground | 102009.94 | 5.13 | 227.78 | 0 | 38.59 | 0 | OK | Ground clear controls. | 229 | 46.16 | 266.37
15957 | TIN-INTERP | Interpolated Ground | 102009.98 | 7.11 | 228.48 | 0 | 31.73 | 0 | OK | Ground clear controls. | 229 | 46.16 | 260.21
15958 | TIN-INTERP | Interpolated Ground | 102010.01 | 5.61 | 228.07 | 0 | 26.68 | 0 | OK | Ground clear controls. | 229 | 46.16 | 254.75
15959 | TIN-INTERP | Interpolated Ground | 102010.35 | -5.37 | 224.08 | 0 | 42.58 | 0 | OK | Ground clear controls. | 229 | 46.16 | 266.66
15960 | TIN-INTERP | Interpolated Ground | 102010.42 | -5.84 | 223.97 | 0 | 30.97 | 0 | OK | Ground clear controls. | 229 | 46.16 | 254.94
15961 | TIN-INTERP | Interpolated Ground | 102010.46 | -7.34 | 223.54 | 0 | 37.05 | 0 | OK | Ground clear controls. | 229 | 46.16 | 260.59
15962 | TIN-INTERP | Interpolated Ground | 102049.94 | 5.11 | 230.16 | 0 | 42.4 | 0 | OK | Ground clear controls. | 229 | 46.16 | 272.56
15963 | TIN-INTERP | Interpolated Ground | 102049.98 | 7.07 | 230.97 | 0 | 35.47 | 0 | OK | Ground clear controls. | 229 | 46.16 | 266.44
15964 | TIN-INTERP | Interpolated Ground | 102050.01 | 5.57 | 230.41 | 0 | 30.57 | 0 | OK | Ground clear controls. | 229 | 46.16 | 260.98
15965 | TIN-INTERP | Interpolated Ground | 102050.35 | -5.3 | 226.65 | 0 | 46.16 | 0 | OK | Ground clear controls. | 229 | 46.16 | 272.81
15966 | TIN-INTERP | Interpolated Ground | 102050.42 | -5.76 | 227.04 | 0 | 34.13 | 0 | OK | Ground clear controls. | 229 | 39.39 | 261.17
15967 | TIN-INTERP | Interpolated Ground | 102050.46 | -7.26 | 227.39 | 0 | 39.39 | 0 | OK | Ground clear controls. | 229 | 39.39 | 266.78
15968 | TIN-INTERP | Interpolated Ground | 102089.94 | 5.08 | 243.49 | 0 | 36.22 | 0 | OK | Ground clear controls. | 229 | 36.22 | 279.71
15969 | TIN-INTERP | Interpolated Ground | 102089.98 | 7.03 | 243.16 | 0 | 30.52 | 0 | OK | Ground clear controls. | 229 | 35.86 | 273.68
15970 | TIN-INTERP | Interpolated Ground | 102090.01 | 5.53 | 243.44 | 0 | 24.77 | 0 | OK | Ground clear controls. | 229 | 35.86 | 268.21
15971 | TIN-INTERP | Interpolated Ground | 102090.35 | -5.23 | 245.37 | 0 | 34.57 | 0 | OK | Ground clear controls. | 229 | 35.86 | 279.94
15972 | TIN-INTERP | Interpolated Ground | 102090.42 | -5.68 | 245.49 | 0 | 22.89 | 0 | OK | Ground clear controls. | 229 | 35.86 | 268.38
15973 | TIN-INTERP | Interpolated Ground | 102090.46 | -7.18 | 245.39 | 0 | 28.58 | 0 | OK | Ground clear controls. | 229 | 35.86 | 273.97
15974 | TIN-INTERP | Interpolated Ground | 102129.94 | 5.06 | 260.2 | 0 | 27.66 | 0 | OK | Ground clear controls. | 229 | 35.86 | 287.86
15975 | TIN-INTERP | Interpolated Ground | 102129.98 | 7 | 261.42 | 0 | 20.48 | 0 | OK | Ground clear controls. | 229 | 35.86 | 281.9
15976 | TIN-INTERP | Interpolated Ground | 102130.01 | 5.5 | 260.51 | 0 | 15.93 | 0 | OK | Ground clear controls. | 229 | 35.86 | 276.44
15977 | TIN-INTERP | Interpolated Ground | 102130.35 | -5.17 | 254.13 | 0 | 33.92 | 0 | OK | Ground clear controls. | 229 | 35.86 | 288.05
15978 | TIN-INTERP | Interpolated Ground | 102130.42 | -5.6 | 253.87 | 0 | 22.72 | 0 | OK | Ground clear controls. | 229 | 35.86 | 276.59
15979 | TIN-INTERP | Interpolated Ground | 102130.46 | -7.1 | 253.19 | 0 | 28.96 | 0 | OK | Ground clear controls. | 229 | 35.86 | 282.15
15980 | TIN-INTERP | Interpolated Ground | 102169.94 | 5.04 | 262.93 | 0 | 34.07 | 0 | OK | Ground clear controls. | 229 | 35.86 | 297
15981 | TIN-INTERP | Interpolated Ground | 102169.98 | 6.96 | 263.77 | 0 | 27.37 | 0 | OK | Ground clear controls. | 229 | 35.86 | 291.14
15982 | TIN-INTERP | Interpolated Ground | 102170.01 | 5.46 | 263.13 | 0 | 22.52 | 0 | OK | Ground clear controls. | 229 | 35.86 | 285.65
15983 | TIN-INTERP | Interpolated Ground | 102170.35 | -5.1 | 261.27 | 0 | 35.86 | 0 | OK | Ground clear controls. | 229 | 35.86 | 297.13
15984 | TIN-INTERP | Interpolated Ground | 102170.42 | -5.52 | 261.33 | 0 | 24.45 | 0 | OK | Ground clear controls. | 229 | 29.95 | 285.78
15985 | TIN-INTERP | Interpolated Ground | 102170.46 | -7.02 | 261.37 | 0 | 29.95 | 0 | OK | Ground clear controls. | 229 | 29.95 | 291.32
15986 | TIN-INTERP | Interpolated Ground | 102199.47 | -6.96 | 270.61 | 0 | 27.97 | 0 | OK | Ground clear controls. | 230 | 44.27 | 298.58
15987 | TIN-INTERP | Interpolated Ground | 102199.48 | 6.93 | 274.2 | 0 | 24.38 | 0 | OK | Ground clear controls. | 230 | 44.27 | 298.58
15988 | TIN-INTERP | Interpolated Ground | 102199.49 | 5.02 | 274.16 | 0 | 30.22 | 0 | OK | Ground clear controls. | 230 | 44.27 | 304.38
15989 | TIN-INTERP | Interpolated Ground | 102199.51 | -5.05 | 271.34 | 0 | 33.04 | 0 | OK | Ground clear controls. | 230 | 44.27 | 304.38
15990 | TIN-INTERP | Interpolated Ground | 102199.52 | 5.43 | 274.17 | 0 | 18.91 | 0 | OK | Ground clear controls. | 230 | 44.27 | 293.08
15991 | TIN-INTERP | Interpolated Ground | 102199.52 | -5.46 | 271.18 | 0 | 21.9 | 0 | OK | Ground clear controls. | 230 | 44.27 | 293.08
15992 | TIN-INTERP | Interpolated Ground | 102239.47 | -7.33 | 257.45 | 0 | 39.18 | 0 | OK | Ground clear controls. | 230 | 44.27 | 296.63
15993 | TIN-INTERP | Interpolated Ground | 102239.48 | 6.91 | 263.05 | 0 | 33.51 | 0 | OK | Ground clear controls. | 230 | 44.27 | 296.56
15994 | TIN-INTERP | Interpolated Ground | 102239.49 | 4.96 | 262.07 | 0 | 40.39 | 0 | OK | Ground clear controls. | 230 | 44.27 | 302.46
15995 | TIN-INTERP | Interpolated Ground | 102239.51 | -5.37 | 258.25 | 0 | 44.27 | 0 | OK | Ground clear controls. | 230 | 44.27 | 302.52
15996 | TIN-INTERP | Interpolated Ground | 102239.52 | 5.4 | 262.28 | 0 | 28.76 | 0 | OK | Ground clear controls. | 230 | 39.48 | 291.04
15997 | TIN-INTERP | Interpolated Ground | 102239.52 | -5.83 | 258.1 | 0 | 32.99 | 0 | OK | Ground clear controls. | 230 | 39.48 | 291.09
15998 | TIN-INTERP | Interpolated Ground | 102279.47 | -7.69 | 260.87 | 0 | 34.76 | 0 | OK | Ground clear controls. | 230 | 39.48 | 295.63
15999 | TIN-INTERP | Interpolated Ground | 102279.48 | 6.88 | 269.87 | 0 | 25.64 | 0 | OK | Ground clear controls. | 230 | 39.48 | 295.51
16000 | TIN-INTERP | Interpolated Ground | 102279.49 | 4.89 | 268.79 | 0 | 32.72 | 0 | OK | Ground clear controls. | 230 | 39.48 | 301.51
16001 | TIN-INTERP | Interpolated Ground | 102279.5 | -5.7 | 262.14 | 0 | 39.48 | 0 | OK | Ground clear controls. | 230 | 39.48 | 301.62
16002 | TIN-INTERP | Interpolated Ground | 102279.52 | 5.38 | 269.12 | 0 | 20.85 | 0 | OK | Ground clear controls. | 230 | 29.44 | 289.97
16003 | TIN-INTERP | Interpolated Ground | 102279.52 | -6.2 | 261.84 | 0 | 28.22 | 0 | OK | Ground clear controls. | 230 | 29.44 | 290.06
16004 | TIN-INTERP | Interpolated Ground | 102319.47 | -8.06 | 274.06 | 0 | 21.54 | 0 | OK | Ground clear controls. | 230 | 29.44 | 295.6
16005 | TIN-INTERP | Interpolated Ground | 102319.48 | 6.86 | 273.71 | 0 | 21.75 | 0 | OK | Ground clear controls. | 230 | 29.44 | 295.46
16006 | TIN-INTERP | Interpolated Ground | 102319.49 | 4.83 | 273.92 | 0 | 27.62 | 0 | OK | Ground clear controls. | 230 | 29.44 | 301.54
16007 | TIN-INTERP | Interpolated Ground | 102319.5 | -6.02 | 274.11 | 0 | 27.55 | 0 | OK | Ground clear controls. | 230 | 29.44 | 301.66
16008 | TIN-INTERP | Interpolated Ground | 102319.52 | 5.35 | 273.71 | 0 | 16.17 | 0 | OK | Ground clear controls. | 230 | 29.44 | 289.88
16009 | TIN-INTERP | Interpolated Ground | 102319.52 | -6.56 | 274.08 | 0 | 15.91 | 0 | OK | Ground clear controls. | 230 | 29.44 | 289.99
16010 | TIN-INTERP | Interpolated Ground | 102359.46 | -8.42 | 278.65 | 0 | 17.89 | 0 | OK | Ground clear controls. | 230 | 29.44 | 296.54
16011 | TIN-INTERP | Interpolated Ground | 102359.48 | 6.83 | 278.58 | 0 | 17.8 | 0 | OK | Ground clear controls. | 230 | 29.44 | 296.38
16012 | TIN-INTERP | Interpolated Ground | 102359.49 | 4.76 | 278.99 | 0 | 23.55 | 0 | OK | Ground clear controls. | 230 | 29.44 | 302.54
16013 | TIN-INTERP | Interpolated Ground | 102359.5 | -6.35 | 279.09 | 0 | 23.59 | 0 | OK | Ground clear controls. | 230 | 29.44 | 302.68
16014 | TIN-INTERP | Interpolated Ground | 102359.52 | 5.33 | 278.87 | 0 | 11.89 | 0 | OK | Ground clear controls. | 230 | 29.44 | 290.76
16015 | TIN-INTERP | Interpolated Ground | 102359.52 | -6.93 | 278.94 | 0 | 11.94 | 0 | OK | Ground clear controls. | 230 | 29.44 | 290.88
16016 | TIN-INTERP | Interpolated Ground | 102399.46 | -8.79 | 277.14 | 0 | 21.31 | 0 | OK | Ground clear controls. | 230 | 29.44 | 298.45
16017 | TIN-INTERP | Interpolated Ground | 102399.48 | 6.81 | 275.39 | 0 | 22.9 | 0 | OK | Ground clear controls. | 230 | 29.44 | 298.29
16018 | TIN-INTERP | Interpolated Ground | 102399.49 | 4.7 | 276.13 | 0 | 28.38 | 0 | OK | Ground clear controls. | 230 | 29.44 | 304.51
16019 | TIN-INTERP | Interpolated Ground | 102399.5 | -6.67 | 277.66 | 0 | 26.98 | 0 | OK | Ground clear controls. | 230 | 29.44 | 304.64
16020 | TIN-INTERP | Interpolated Ground | 102399.52 | -7.3 | 277.53 | 0 | 15.2 | 0 | OK | Ground clear controls. | 230 | 29.44 | 292.73
16021 | TIN-INTERP | Interpolated Ground | 102399.52 | 5.3 | 276.02 | 0 | 16.6 | 0 | OK | Ground clear controls. | 230 | 29.44 | 292.62
16022 | TIN-INTERP | Interpolated Ground | 102439.46 | -9.15 | 277.9 | 0 | 23.41 | 0 | OK | Ground clear controls. | 230 | 29.44 | 301.31
16023 | TIN-INTERP | Interpolated Ground | 102439.48 | 6.78 | 278.78 | 0 | 22.4 | 0 | OK | Ground clear controls. | 230 | 29.44 | 301.18
16024 | TIN-INTERP | Interpolated Ground | 102439.49 | 4.63 | 278.9 | 0 | 28.55 | 0 | OK | Ground clear controls. | 230 | 29.44 | 307.45
16025 | TIN-INTERP | Interpolated Ground | 102439.5 | -6.99 | 278.12 | 0 | 29.44 | 0 | OK | Ground clear controls. | 230 | 29.44 | 307.56
16026 | TIN-INTERP | Interpolated Ground | 102439.51 | -7.67 | 278.04 | 0 | 17.51 | 0 | OK | Ground clear controls. | 230 | 17.51 | 295.55
16027 | TIN-INTERP | Interpolated Ground | 102439.52 | 5.27 | 278.87 | 0 | 16.58 | 0 | OK | Ground clear controls. | 230 | 16.58 | 295.45
16028 | TIN-INTERP | Interpolated Ground | 102466.1 | -9.4 | 280.19 | 0 | 23.57 | 0 | OK | Ground clear controls. | 231 | 71.28 | 303.76
16029 | TIN-INTERP | Interpolated Ground | 102466.26 | -7.91 | 280.68 | 0 | 17.28 | 0 | OK | Ground clear controls. | 231 | 71.28 | 297.96
16030 | TIN-INTERP | Interpolated Ground | 102467 | 4.6 | 281.39 | 0 | 28.7 | 0 | OK | Ground clear controls. | 231 | 71.28 | 310.09
16031 | TIN-INTERP | Interpolated Ground | 102467 | 5.28 | 281.29 | 0 | 16.71 | 0 | OK | Ground clear controls. | 231 | 71.28 | 298
16032 | TIN-INTERP | Interpolated Ground | 102467 | 6.79 | 280.94 | 0 | 22.86 | 0 | OK | Ground clear controls. | 231 | 71.28 | 303.8
16033 | TIN-INTERP | Interpolated Ground | 102467.69 | -7.21 | 280.92 | 0 | 29.14 | 0 | OK | Ground clear controls. | 231 | 71.28 | 310.06
16034 | TIN-INTERP | Interpolated Ground | 102506.34 | 6.74 | 270.07 | 0 | 25.87 | 0 | OK | Ground clear controls. | 231 | 71.28 | 295.94
16035 | TIN-INTERP | Interpolated Ground | 102506.49 | 5.24 | 271.07 | 0 | 19.15 | 0 | OK | Ground clear controls. | 231 | 71.28 | 290.22
16036 | TIN-INTERP | Interpolated Ground | 102506.53 | 4.58 | 271.17 | 0 | 31.01 | 0 | OK | Ground clear controls. | 231 | 71.28 | 302.18
16037 | TIN-INTERP | Interpolated Ground | 102507.69 | -6.94 | 274.15 | 0 | 28.12 | 0 | OK | Ground clear controls. | 231 | 71.28 | 302.27
16038 | TIN-INTERP | Interpolated Ground | 102507.74 | -7.63 | 274.28 | 0 | 15.98 | 0 | OK | Ground clear controls. | 231 | 71.28 | 290.26
16039 | TIN-INTERP | Interpolated Ground | 102507.86 | -9.11 | 274.61 | 0 | 21.38 | 0 | OK | Ground clear controls. | 231 | 71.28 | 295.99
16040 | TIN-INTERP | Interpolated Ground | 102546.34 | 6.73 | 251.87 | 0 | 37.2 | 0 | OK | Ground clear controls. | 231 | 71.28 | 289.07
16041 | TIN-INTERP | Interpolated Ground | 102546.49 | 5.22 | 250.99 | 0 | 32.44 | 0 | OK | Ground clear controls. | 231 | 71.28 | 283.43
16042 | TIN-INTERP | Interpolated Ground | 102546.53 | 4.58 | 250.58 | 0 | 44.69 | 0 | OK | Ground clear controls. | 231 | 71.28 | 295.27
16043 | TIN-INTERP | Interpolated Ground | 102547.69 | -6.68 | 248.39 | 0 | 47.05 | 0 | OK | Ground clear controls. | 231 | 71.28 | 295.44
16044 | TIN-INTERP | Interpolated Ground | 102547.74 | -7.34 | 248.32 | 0 | 35.21 | 0 | OK | Ground clear controls. | 231 | 71.28 | 283.53
16045 | TIN-INTERP | Interpolated Ground | 102547.86 | -8.83 | 247.92 | 0 | 41.29 | 0 | OK | Ground clear controls. | 231 | 71.28 | 289.21
16046 | TIN-INTERP | Interpolated Ground | 102586.34 | 6.71 | 227.08 | 0 | 56.14 | 0 | OK | Ground clear controls. | 231 | 71.28 | 283.22
16047 | TIN-INTERP | Interpolated Ground | 102586.49 | 5.21 | 227.35 | 0 | 50.26 | 0 | OK | Ground clear controls. | 231 | 71.28 | 277.61
16048 | TIN-INTERP | Interpolated Ground | 102586.53 | 4.59 | 227.5 | 0 | 61.84 | 0 | OK | Ground clear controls. | 231 | 71.28 | 289.34
16049 | TIN-INTERP | Interpolated Ground | 102587.69 | -6.41 | 227.97 | 0 | 61.6 | 0 | OK | Ground clear controls. | 231 | 71.28 | 289.57
16050 | TIN-INTERP | Interpolated Ground | 102587.74 | -7.05 | 227.86 | 0 | 49.91 | 0 | OK | Ground clear controls. | 231 | 71.28 | 277.77
16051 | TIN-INTERP | Interpolated Ground | 102587.86 | -8.54 | 227.87 | 0 | 55.53 | 0 | OK | Ground clear controls. | 231 | 71.28 | 283.4
16052 | TIN-INTERP | Interpolated Ground | 102626.34 | 6.69 | 214.05 | 0 | 64.3 | 0 | OK | Ground clear controls. | 231 | 71.28 | 278.35
16053 | TIN-INTERP | Interpolated Ground | 102626.49 | 5.19 | 213.62 | 0 | 59.18 | 0 | OK | Ground clear controls. | 231 | 71.28 | 272.8
16054 | TIN-INTERP | Interpolated Ground | 102626.53 | 4.59 | 213.48 | 0 | 70.93 | 0 | OK | Ground clear controls. | 231 | 71.28 | 284.41
16055 | TIN-INTERP | Interpolated Ground | 102627.69 | -6.15 | 213.4 | 0 | 71.28 | 0 | OK | Ground clear controls. | 231 | 71.28 | 284.68
16056 | TIN-INTERP | Interpolated Ground | 102627.74 | -6.77 | 213.47 | 0 | 59.5 | 0 | OK | Ground clear controls. | 231 | 65.09 | 272.97
16057 | TIN-INTERP | Interpolated Ground | 102627.86 | -8.26 | 213.48 | 0 | 65.09 | 0 | OK | Ground clear controls. | 231 | 65.09 | 278.57
16058 | TIN-INTERP | Interpolated Ground | 102666.34 | 6.68 | 223.76 | 0 | 50.72 | 0 | OK | Ground clear controls. | 231 | 62.58 | 274.48
16059 | TIN-INTERP | Interpolated Ground | 102666.49 | 5.18 | 222.95 | 0 | 46.01 | 0 | OK | Ground clear controls. | 231 | 62.58 | 268.96
16060 | TIN-INTERP | Interpolated Ground | 102666.53 | 4.59 | 222.62 | 0 | 57.83 | 0 | OK | Ground clear controls. | 231 | 62.58 | 280.45
16061 | TIN-INTERP | Interpolated Ground | 102667.69 | -5.88 | 218.16 | 0 | 62.58 | 0 | OK | Ground clear controls. | 231 | 62.58 | 280.74
16062 | TIN-INTERP | Interpolated Ground | 102667.74 | -6.48 | 217.79 | 0 | 51.35 | 0 | OK | Ground clear controls. | 231 | 57.66 | 269.14
16063 | TIN-INTERP | Interpolated Ground | 102667.86 | -7.98 | 217.05 | 0 | 57.66 | 0 | OK | Ground clear controls. | 231 | 57.66 | 274.71
16064 | TIN-INTERP | Interpolated Ground | 102706.34 | 6.66 | 228.72 | 0 | 42.88 | 0 | OK | Ground clear controls. | 231 | 55.84 | 271.6
16065 | TIN-INTERP | Interpolated Ground | 102706.49 | 5.16 | 228.06 | 0 | 38.03 | 0 | OK | Ground clear controls. | 231 | 55.84 | 266.09
16066 | TIN-INTERP | Interpolated Ground | 102706.53 | 4.59 | 227.73 | 0 | 49.75 | 0 | OK | Ground clear controls. | 231 | 55.84 | 277.48
16067 | TIN-INTERP | Interpolated Ground | 102707.69 | -5.62 | 221.92 | 0 | 55.84 | 0 | OK | Ground clear controls. | 231 | 55.84 | 277.76
16068 | TIN-INTERP | Interpolated Ground | 102707.73 | -6.2 | 221.73 | 0 | 44.55 | 0 | OK | Ground clear controls. | 231 | 50.52 | 266.28
16069 | TIN-INTERP | Interpolated Ground | 102707.86 | -7.69 | 221.3 | 0 | 50.52 | 0 | OK | Ground clear controls. | 231 | 50.52 | 271.82
16070 | TIN-INTERP | Interpolated Ground | 102746.34 | 6.65 | 234.82 | 0 | 34.88 | 0 | OK | Ground clear controls. | 231 | 44.72 | 269.7
16071 | TIN-INTERP | Interpolated Ground | 102746.49 | 5.15 | 234.09 | 0 | 30.13 | 0 | OK | Ground clear controls. | 231 | 44.72 | 264.22
16072 | TIN-INTERP | Interpolated Ground | 102746.53 | 4.6 | 233.82 | 0 | 41.68 | 0 | OK | Ground clear controls. | 231 | 44.72 | 275.5
16073 | TIN-INTERP | Interpolated Ground | 102747.69 | -5.35 | 231.01 | 0 | 44.72 | 0 | OK | Ground clear controls. | 231 | 44.72 | 275.73
16074 | TIN-INTERP | Interpolated Ground | 102747.73 | -5.91 | 230.81 | 0 | 33.57 | 0 | OK | Ground clear controls. | 231 | 39.6 | 264.38
16075 | TIN-INTERP | Interpolated Ground | 102747.86 | -7.41 | 230.31 | 0 | 39.6 | 0 | OK | Ground clear controls. | 231 | 39.6 | 269.91
16076 | TIN-INTERP | Interpolated Ground | 102786.34 | 6.63 | 240.33 | 0 | 28.46 | 0 | OK | Ground clear controls. | 231 | 37.92 | 268.79
16077 | TIN-INTERP | Interpolated Ground | 102786.49 | 5.13 | 239.65 | 0 | 23.66 | 0 | OK | Ground clear controls. | 231 | 37.92 | 263.31
16078 | TIN-INTERP | Interpolated Ground | 102786.53 | 4.6 | 239.44 | 0 | 35.04 | 0 | OK | Ground clear controls. | 231 | 37.92 | 274.48
16079 | TIN-INTERP | Interpolated Ground | 102787.69 | -5.09 | 236.74 | 0 | 37.92 | 0 | OK | Ground clear controls. | 231 | 37.92 | 274.66
16080 | TIN-INTERP | Interpolated Ground | 102787.73 | -5.62 | 236.55 | 0 | 26.89 | 0 | OK | Ground clear controls. | 231 | 33.23 | 263.44
16081 | TIN-INTERP | Interpolated Ground | 102787.85 | -7.12 | 235.73 | 0 | 33.23 | 0 | OK | Ground clear controls. | 231 | 33.23 | 268.96
16082 | TIN-INTERP | Interpolated Ground | 102826.34 | 6.62 | 251.07 | 0 | 17.8 | 0 | OK | Ground clear controls. | 231 | 28.42 | 268.87
16083 | TIN-INTERP | Interpolated Ground | 102826.49 | 5.12 | 250.97 | 0 | 12.42 | 0 | OK | Ground clear controls. | 231 | 28.42 | 263.39
16084 | TIN-INTERP | Interpolated Ground | 102826.53 | 4.6 | 250.95 | 0 | 23.51 | 0 | OK | Ground clear controls. | 231 | 28.42 | 274.46
16085 | TIN-INTERP | Interpolated Ground | 102827.68 | -4.82 | 246.13 | 0 | 28.42 | 0 | OK | Ground clear controls. | 231 | 28.42 | 274.55
16086 | TIN-INTERP | Interpolated Ground | 102827.73 | -5.34 | 245.92 | 0 | 17.54 | 0 | OK | Ground clear controls. | 231 | 23.55 | 263.46
16087 | TIN-INTERP | Interpolated Ground | 102827.85 | -6.84 | 245.42 | 0 | 23.55 | 0 | OK | Ground clear controls. | 231 | 23.55 | 268.97
16088 | TIN-INTERP | Interpolated Ground | 102851.8 | -6.67 | 249.29 | 0 | 20.15 | 0 | OK | Ground clear controls. | 232 | 45.09 | 269.44
16089 | TIN-INTERP | Interpolated Ground | 102851.84 | -4.66 | 249.46 | 0 | 25.48 | 0 | OK | Ground clear controls. | 232 | 45.09 | 274.94
16090 | TIN-INTERP | Interpolated Ground | 102851.92 | -5.17 | 249.41 | 0 | 14.53 | 0 | OK | Ground clear controls. | 232 | 45.09 | 263.94
16091 | TIN-INTERP | Interpolated Ground | 102851.93 | 5.11 | 248.7 | 0 | 15.24 | 0 | OK | Ground clear controls. | 232 | 45.09 | 263.94
16092 | TIN-INTERP | Interpolated Ground | 102851.98 | 6.61 | 248.54 | 0 | 20.9 | 0 | OK | Ground clear controls. | 232 | 45.09 | 269.44
16093 | TIN-INTERP | Interpolated Ground | 102851.99 | 4.6 | 248.72 | 0 | 26.22 | 0 | OK | Ground clear controls. | 232 | 45.09 | 274.94
16094 | TIN-INTERP | Interpolated Ground | 102891.8 | -6.66 | 240.51 | 0 | 20.33 | 0 | OK | Ground clear controls. | 232 | 45.09 | 260.84
16095 | TIN-INTERP | Interpolated Ground | 102891.84 | -4.65 | 239.74 | 0 | 26.63 | 0 | OK | Ground clear controls. | 232 | 45.09 | 266.37
16096 | TIN-INTERP | Interpolated Ground | 102891.92 | -5.16 | 239.91 | 0 | 15.46 | 0 | OK | Ground clear controls. | 232 | 45.09 | 255.37
16097 | TIN-INTERP | Interpolated Ground | 102891.93 | 5.11 | 238.56 | 0 | 16.77 | 0 | OK | Ground clear controls. | 232 | 45.09 | 255.33
16098 | TIN-INTERP | Interpolated Ground | 102891.98 | 6.61 | 238.27 | 0 | 22.54 | 0 | OK | Ground clear controls. | 232 | 45.09 | 260.81
16099 | TIN-INTERP | Interpolated Ground | 102891.99 | 4.6 | 238.53 | 0 | 27.81 | 0 | OK | Ground clear controls. | 232 | 45.09 | 266.34
16100 | TIN-INTERP | Interpolated Ground | 102931.8 | -6.65 | 222.63 | 0 | 30.6 | 0 | OK | Ground clear controls. | 232 | 45.09 | 253.23
16101 | TIN-INTERP | Interpolated Ground | 102931.84 | -4.64 | 222.25 | 0 | 36.54 | 0 | OK | Ground clear controls. | 232 | 45.09 | 258.79
16102 | TIN-INTERP | Interpolated Ground | 102931.92 | -5.15 | 222.33 | 0 | 25.46 | 0 | OK | Ground clear controls. | 232 | 45.09 | 247.79
16103 | TIN-INTERP | Interpolated Ground | 102931.93 | 5.11 | 219.68 | 0 | 28.03 | 0 | OK | Ground clear controls. | 232 | 45.09 | 247.71
16104 | TIN-INTERP | Interpolated Ground | 102931.98 | 6.61 | 218.99 | 0 | 34.2 | 0 | OK | Ground clear controls. | 232 | 45.09 | 253.19
16105 | TIN-INTERP | Interpolated Ground | 102931.99 | 4.6 | 219.82 | 0 | 38.91 | 0 | OK | Ground clear controls. | 232 | 45.09 | 258.73
16106 | TIN-INTERP | Interpolated Ground | 102971.8 | -6.64 | 211.17 | 0 | 35.44 | 0 | OK | Ground clear controls. | 232 | 45.09 | 246.61
16107 | TIN-INTERP | Interpolated Ground | 102971.84 | -4.64 | 211.22 | 0 | 40.94 | 0 | OK | Ground clear controls. | 232 | 45.09 | 252.16
16108 | TIN-INTERP | Interpolated Ground | 102971.92 | -5.14 | 211.19 | 0 | 29.97 | 0 | OK | Ground clear controls. | 232 | 45.09 | 241.16
16109 | TIN-INTERP | Interpolated Ground | 102971.93 | 5.1 | 209.49 | 0 | 31.6 | 0 | OK | Ground clear controls. | 232 | 45.09 | 241.09
16110 | TIN-INTERP | Interpolated Ground | 102971.98 | 6.6 | 209.13 | 0 | 37.44 | 0 | OK | Ground clear controls. | 232 | 45.09 | 246.57
16111 | TIN-INTERP | Interpolated Ground | 102971.99 | 4.6 | 209.57 | 0 | 42.54 | 0 | OK | Ground clear controls. | 232 | 45.09 | 252.11
16112 | TIN-INTERP | Interpolated Ground | 103011.8 | -6.63 | 205.22 | 0 | 35.75 | 0 | OK | Ground clear controls. | 232 | 45.09 | 240.97
16113 | TIN-INTERP | Interpolated Ground | 103011.84 | -4.63 | 204.87 | 0 | 41.64 | 0 | OK | Ground clear controls. | 232 | 45.09 | 246.51
16114 | TIN-INTERP | Interpolated Ground | 103011.92 | -5.13 | 204.96 | 0 | 30.55 | 0 | OK | Ground clear controls. | 232 | 45.09 | 235.51
16115 | TIN-INTERP | Interpolated Ground | 103011.93 | 5.1 | 201.12 | 0 | 34.33 | 0 | OK | Ground clear controls. | 232 | 45.09 | 235.45
16116 | TIN-INTERP | Interpolated Ground | 103011.98 | 6.6 | 200.46 | 0 | 40.47 | 0 | OK | Ground clear controls. | 232 | 45.09 | 240.93
16117 | TIN-INTERP | Interpolated Ground | 103011.99 | 4.6 | 201.37 | 0 | 45.09 | 0 | OK | Ground clear controls. | 232 | 45.09 | 246.46
16118 | TIN-INTERP | Interpolated Ground | 103051.8 | -6.62 | 211.15 | 0 | 25.15 | 0 | OK | Ground clear controls. | 232 | 34.23 | 236.3
16119 | TIN-INTERP | Interpolated Ground | 103051.84 | -4.62 | 210.31 | 0 | 31.52 | 0 | OK | Ground clear controls. | 232 | 34.23 | 241.83
16120 | TIN-INTERP | Interpolated Ground | 103051.92 | -5.12 | 210.46 | 0 | 20.36 | 0 | OK | Ground clear controls. | 232 | 34.23 | 230.82
16121 | TIN-INTERP | Interpolated Ground | 103051.93 | 5.1 | 207.27 | 0 | 23.53 | 0 | OK | Ground clear controls. | 232 | 34.23 | 230.8
16122 | TIN-INTERP | Interpolated Ground | 103051.98 | 6.6 | 206.53 | 0 | 29.75 | 0 | OK | Ground clear controls. | 232 | 34.23 | 236.28
16123 | TIN-INTERP | Interpolated Ground | 103051.99 | 4.61 | 207.57 | 0 | 34.23 | 0 | OK | Ground clear controls. | 232 | 34.23 | 241.8
16124 | TIN-INTERP | Interpolated Ground | 103072.1 | -5.11 | 209.68 | 0 | 19.13 | 0 | OK | Ground clear controls. | 233 | 61.14 | 228.81
16125 | TIN-INTERP | Interpolated Ground | 103072.11 | -4.61 | 209.7 | 0 | 30.11 | 0 | OK | Ground clear controls. | 233 | 61.14 | 239.81
16126 | TIN-INTERP | Interpolated Ground | 103072.13 | -6.61 | 209.64 | 0 | 24.68 | 0 | OK | Ground clear controls. | 233 | 61.14 | 234.32
16127 | TIN-INTERP | Interpolated Ground | 103072.19 | 6.6 | 210.95 | 0 | 23.36 | 0 | OK | Ground clear controls. | 233 | 61.14 | 234.31
16128 | TIN-INTERP | Interpolated Ground | 103072.22 | 4.61 | 210.73 | 0 | 29.08 | 0 | OK | Ground clear controls. | 233 | 61.14 | 239.81
16129 | TIN-INTERP | Interpolated Ground | 103072.23 | 5.1 | 210.8 | 0 | 18.01 | 0 | OK | Ground clear controls. | 233 | 61.14 | 228.81
16130 | TIN-INTERP | Interpolated Ground | 103112.1 | -5.13 | 202.06 | 0 | 15.81 | 0 | OK | Ground clear controls. | 233 | 61.14 | 217.87
16131 | TIN-INTERP | Interpolated Ground | 103112.11 | -4.64 | 202.32 | 0 | 26.56 | 0 | OK | Ground clear controls. | 233 | 61.14 | 228.88
16132 | TIN-INTERP | Interpolated Ground | 103112.13 | -6.63 | 201.44 | 0 | 21.81 | 0 | OK | Ground clear controls. | 233 | 61.14 | 223.25
16133 | TIN-INTERP | Interpolated Ground | 103112.18 | 6.62 | 205.35 | 0 | 17.86 | 0 | OK | Ground clear controls. | 233 | 61.14 | 223.21
16134 | TIN-INTERP | Interpolated Ground | 103112.22 | 4.63 | 204.57 | 0 | 24.26 | 0 | OK | Ground clear controls. | 233 | 61.14 | 228.83
16135 | TIN-INTERP | Interpolated Ground | 103112.23 | 5.12 | 204.78 | 0 | 13 | 0 | OK | Ground clear controls. | 233 | 61.14 | 217.78
16136 | TIN-INTERP | Interpolated Ground | 103152.1 | -5.16 | 190.33 | 0 | 17.59 | 0 | OK | Ground clear controls. | 233 | 61.14 | 207.92
16137 | TIN-INTERP | Interpolated Ground | 103152.11 | -4.67 | 190.39 | 0 | 28.55 | 0 | OK | Ground clear controls. | 233 | 61.14 | 218.94
16138 | TIN-INTERP | Interpolated Ground | 103152.13 | -6.66 | 190.18 | 0 | 23.03 | 0 | OK | Ground clear controls. | 233 | 61.14 | 213.21
16139 | TIN-INTERP | Interpolated Ground | 103152.18 | 6.63 | 193.36 | 0 | 19.78 | 0 | OK | Ground clear controls. | 233 | 61.14 | 213.14
16140 | TIN-INTERP | Interpolated Ground | 103152.22 | 4.65 | 192.49 | 0 | 26.35 | 0 | OK | Ground clear controls. | 233 | 61.14 | 218.84
16141 | TIN-INTERP | Interpolated Ground | 103152.23 | 5.13 | 192.65 | 0 | 15.11 | 0 | OK | Ground clear controls. | 233 | 61.14 | 207.76
16142 | TIN-INTERP | Interpolated Ground | 103192.1 | -5.18 | 179.24 | 0 | 19.73 | 0 | OK | Ground clear controls. | 233 | 61.14 | 198.97
16143 | TIN-INTERP | Interpolated Ground | 103192.11 | -4.7 | 179.33 | 0 | 30.67 | 0 | OK | Ground clear controls. | 233 | 61.14 | 210
16144 | TIN-INTERP | Interpolated Ground | 103192.13 | -6.68 | 178.92 | 0 | 25.25 | 0 | OK | Ground clear controls. | 233 | 61.14 | 204.17
16145 | TIN-INTERP | Interpolated Ground | 103192.18 | 6.65 | 180.28 | 0 | 23.79 | 0 | OK | Ground clear controls. | 233 | 61.14 | 204.07
16146 | TIN-INTERP | Interpolated Ground | 103192.22 | 4.67 | 180.49 | 0 | 29.38 | 0 | OK | Ground clear controls. | 233 | 61.14 | 209.87
16147 | TIN-INTERP | Interpolated Ground | 103192.23 | 5.15 | 180.35 | 0 | 18.4 | 0 | OK | Ground clear controls. | 233 | 61.14 | 198.75
16148 | TIN-INTERP | Interpolated Ground | 103232.1 | -5.2 | 166.31 | 0 | 24.69 | 0 | OK | Ground clear controls. | 233 | 61.14 | 191
16149 | TIN-INTERP | Interpolated Ground | 103232.11 | -4.73 | 166.43 | 0 | 35.62 | 0 | OK | Ground clear controls. | 233 | 61.14 | 202.05
16150 | TIN-INTERP | Interpolated Ground | 103232.13 | -6.7 | 165.91 | 0 | 30.23 | 0 | OK | Ground clear controls. | 233 | 61.14 | 196.14
16151 | TIN-INTERP | Interpolated Ground | 103232.18 | 6.66 | 170.51 | 0 | 25.51 | 0 | OK | Ground clear controls. | 233 | 61.14 | 196.02
16152 | TIN-INTERP | Interpolated Ground | 103232.22 | 4.69 | 169.96 | 0 | 31.93 | 0 | OK | Ground clear controls. | 233 | 61.14 | 201.89
16153 | TIN-INTERP | Interpolated Ground | 103232.23 | 5.16 | 170.08 | 0 | 20.66 | 0 | OK | Ground clear controls. | 233 | 61.14 | 190.74
16154 | TIN-INTERP | Interpolated Ground | 103272.1 | -5.22 | 155.52 | 0 | 28.49 | 0 | OK | Ground clear controls. | 233 | 61.14 | 184.01
16155 | TIN-INTERP | Interpolated Ground | 103272.11 | -4.75 | 155.67 | 0 | 39.41 | 0 | OK | Ground clear controls. | 233 | 61.14 | 195.08
16156 | TIN-INTERP | Interpolated Ground | 103272.13 | -6.72 | 155.19 | 0 | 33.92 | 0 | OK | Ground clear controls. | 233 | 61.14 | 189.11
16157 | TIN-INTERP | Interpolated Ground | 103272.18 | 6.68 | 161.08 | 0 | 27.89 | 0 | OK | Ground clear controls. | 233 | 61.14 | 188.97
16158 | TIN-INTERP | Interpolated Ground | 103272.22 | 4.71 | 160.71 | 0 | 34.19 | 0 | OK | Ground clear controls. | 233 | 61.14 | 194.9
16159 | TIN-INTERP | Interpolated Ground | 103272.23 | 5.18 | 160.83 | 0 | 22.89 | 0 | OK | Ground clear controls. | 233 | 61.14 | 183.72
16160 | TIN-INTERP | Interpolated Ground | 103312.1 | -5.24 | 153.02 | 0 | 24.99 | 0 | OK | Ground clear controls. | 233 | 61.14 | 178.01
16161 | TIN-INTERP | Interpolated Ground | 103312.11 | -4.78 | 153.17 | 0 | 35.92 | 0 | OK | Ground clear controls. | 233 | 61.14 | 189.09
16162 | TIN-INTERP | Interpolated Ground | 103312.13 | -6.74 | 152.54 | 0 | 30.53 | 0 | OK | Ground clear controls. | 233 | 61.14 | 183.07
16163 | TIN-INTERP | Interpolated Ground | 103312.18 | 6.69 | 154.86 | 0 | 28.06 | 0 | OK | Ground clear controls. | 233 | 61.14 | 182.92
16164 | TIN-INTERP | Interpolated Ground | 103312.22 | 4.73 | 154.5 | 0 | 34.4 | 0 | OK | Ground clear controls. | 233 | 61.14 | 188.9
16165 | TIN-INTERP | Interpolated Ground | 103312.23 | 5.19 | 154.55 | 0 | 23.12 | 0 | OK | Ground clear controls. | 233 | 61.14 | 177.67
16166 | TIN-INTERP | Interpolated Ground | 103352.1 | -5.26 | 147.55 | 0 | 25.43 | 0 | OK | Ground clear controls. | 233 | 61.14 | 172.98
16167 | TIN-INTERP | Interpolated Ground | 103352.11 | -4.81 | 147.48 | 0 | 36.6 | 0 | OK | Ground clear controls. | 233 | 61.14 | 184.08
16168 | TIN-INTERP | Interpolated Ground | 103352.13 | -6.76 | 147.8 | 0 | 30.23 | 0 | OK | Ground clear controls. | 233 | 61.14 | 178.03
16169 | TIN-INTERP | Interpolated Ground | 103352.18 | 6.71 | 146.65 | 0 | 31.22 | 0 | OK | Ground clear controls. | 233 | 61.14 | 177.87
16170 | TIN-INTERP | Interpolated Ground | 103352.22 | 4.75 | 146.73 | 0 | 37.16 | 0 | OK | Ground clear controls. | 233 | 61.14 | 183.89
16171 | TIN-INTERP | Interpolated Ground | 103352.23 | 5.21 | 146.7 | 0 | 25.94 | 0 | OK | Ground clear controls. | 233 | 61.14 | 172.64
16172 | TIN-INTERP | Interpolated Ground | 103392.1 | -5.29 | 143.71 | 0 | 25.23 | 0 | OK | Ground clear controls. | 233 | 61.14 | 168.94
16173 | TIN-INTERP | Interpolated Ground | 103392.11 | -4.84 | 143.53 | 0 | 36.52 | 0 | OK | Ground clear controls. | 233 | 61.14 | 180.05
16174 | TIN-INTERP | Interpolated Ground | 103392.13 | -6.79 | 144.02 | 0 | 29.95 | 0 | OK | Ground clear controls. | 233 | 61.14 | 173.97
16175 | TIN-INTERP | Interpolated Ground | 103392.18 | 6.72 | 141.25 | 0 | 32.58 | 0 | OK | Ground clear controls. | 233 | 61.14 | 173.83
16176 | TIN-INTERP | Interpolated Ground | 103392.22 | 4.78 | 141.32 | 0 | 38.53 | 0 | OK | Ground clear controls. | 233 | 61.14 | 179.85
16177 | TIN-INTERP | Interpolated Ground | 103392.23 | 5.22 | 141.35 | 0 | 27.24 | 0 | OK | Ground clear controls. | 233 | 61.14 | 168.59
16178 | TIN-INTERP | Interpolated Ground | 103432.1 | -5.31 | 136.96 | 0 | 28.89 | 0 | OK | Ground clear controls. | 233 | 61.14 | 165.85
16179 | TIN-INTERP | Interpolated Ground | 103432.11 | -4.86 | 137 | 0 | 39.99 | 0 | OK | Ground clear controls. | 233 | 61.14 | 176.99
16180 | TIN-INTERP | Interpolated Ground | 103432.13 | -6.81 | 136.9 | 0 | 34.01 | 0 | OK | Ground clear controls. | 233 | 61.14 | 170.91
16181 | TIN-INTERP | Interpolated Ground | 103432.18 | 6.74 | 134.3 | 0 | 36.46 | 0 | OK | Ground clear controls. | 233 | 61.14 | 170.76
16182 | TIN-INTERP | Interpolated Ground | 103432.22 | 4.8 | 136.29 | 0 | 40.51 | 0 | OK | Ground clear controls. | 233 | 61.14 | 176.8
16183 | TIN-INTERP | Interpolated Ground | 103432.23 | 5.24 | 135.73 | 0 | 29.79 | 0 | OK | Ground clear controls. | 233 | 61.14 | 165.52
16184 | TIN-INTERP | Interpolated Ground | 103472.1 | -5.33 | 113.55 | 0 | 50.18 | 0 | OK | Ground clear controls. | 233 | 61.14 | 163.73
16185 | TIN-INTERP | Interpolated Ground | 103472.11 | -4.89 | 113.76 | 0 | 61.14 | 0 | OK | Ground clear controls. | 233 | 61.14 | 174.9
16186 | TIN-INTERP | Interpolated Ground | 103472.13 | -6.83 | 113.09 | 0 | 55.73 | 0 | OK | Ground clear controls. | 233 | 59.53 | 168.82
16187 | TIN-INTERP | Interpolated Ground | 103472.18 | 6.75 | 115.51 | 0 | 53.17 | 0 | OK | Ground clear controls. | 233 | 59.53 | 168.68
16188 | TIN-INTERP | Interpolated Ground | 103472.22 | 4.82 | 115.19 | 0 | 59.53 | 0 | OK | Ground clear controls. | 233 | 59.53 | 174.72
16189 | TIN-INTERP | Interpolated Ground | 103472.23 | 5.25 | 115.15 | 0 | 48.28 | 0 | OK | Ground clear controls. | 233 | 48.28 | 163.43
16190 | TIN-INTERP | Interpolated Ground | 103512.1 | -5.35 | 134.33 | 0 | 28.26 | 0 | OK | Ground clear controls. | 233 | 39.44 | 162.59
16191 | TIN-INTERP | Interpolated Ground | 103512.11 | -4.92 | 134.34 | 0 | 39.44 | 0 | OK | Ground clear controls. | 233 | 39.44 | 173.78
16192 | TIN-INTERP | Interpolated Ground | 103512.13 | -6.85 | 134.23 | 0 | 33.49 | 0 | OK | Ground clear controls. | 233 | 39.07 | 167.72
16193 | TIN-INTERP | Interpolated Ground | 103512.18 | 6.77 | 134.65 | 0 | 32.94 | 0 | OK | Ground clear controls. | 233 | 39.07 | 167.59
16194 | TIN-INTERP | Interpolated Ground | 103512.22 | 4.84 | 134.55 | 0 | 39.07 | 0 | OK | Ground clear controls. | 233 | 39.07 | 173.62
16195 | TIN-INTERP | Interpolated Ground | 103512.23 | 5.27 | 134.56 | 0 | 27.75 | 0 | OK | Ground clear controls. | 233 | 37.08 | 162.31
16196 | TIN-INTERP | Interpolated Ground | 103552.1 | -5.37 | 136.41 | 0 | 26.01 | 0 | OK | Ground clear controls. | 233 | 37.08 | 162.42
16197 | TIN-INTERP | Interpolated Ground | 103552.11 | -4.95 | 136.55 | 0 | 37.08 | 0 | OK | Ground clear controls. | 233 | 37.08 | 173.63
16198 | TIN-INTERP | Interpolated Ground | 103552.13 | -6.87 | 135.9 | 0 | 31.7 | 0 | OK | Ground clear controls. | 233 | 33.3 | 167.6
16199 | TIN-INTERP | Interpolated Ground | 103552.18 | 6.78 | 141.24 | 0 | 26.25 | 0 | OK | Ground clear controls. | 233 | 33.3 | 167.49
16200 | TIN-INTERP | Interpolated Ground | 103552.22 | 4.86 | 140.43 | 0 | 33.07 | 0 | OK | Ground clear controls. | 233 | 33.3 | 173.5
16201 | TIN-INTERP | Interpolated Ground | 103552.23 | 5.28 | 140.58 | 0 | 21.6 | 0 | OK | Ground clear controls. | 233 | 33.3 | 162.18
16202 | TIN-INTERP | Interpolated Ground | 103592.1 | -5.39 | 140.9 | 0 | 22.32 | 0 | OK | Ground clear controls. | 233 | 33.3 | 163.22
16203 | TIN-INTERP | Interpolated Ground | 103592.11 | -4.98 | 141.14 | 0 | 33.3 | 0 | OK | Ground clear controls. | 233 | 33.3 | 174.44
16204 | TIN-INTERP | Interpolated Ground | 103592.13 | -6.89 | 140.11 | 0 | 28.36 | 0 | OK | Ground clear controls. | 233 | 29.05 | 168.47
16205 | TIN-INTERP | Interpolated Ground | 103592.18 | 6.8 | 146.05 | 0 | 22.33 | 0 | OK | Ground clear controls. | 233 | 29.05 | 168.38
16206 | TIN-INTERP | Interpolated Ground | 103592.22 | 4.88 | 145.3 | 0 | 29.05 | 0 | OK | Ground clear controls. | 233 | 29.05 | 174.35
16207 | TIN-INTERP | Interpolated Ground | 103592.23 | 5.3 | 145.46 | 0 | 17.57 | 0 | OK | Ground clear controls. | 233 | 28.34 | 163.03
16208 | TIN-INTERP | Interpolated Ground | 103632.1 | -5.42 | 147.89 | 0 | 17.08 | 0 | OK | Ground clear controls. | 233 | 28.34 | 164.97
16209 | TIN-INTERP | Interpolated Ground | 103632.11 | -5 | 147.89 | 0 | 28.34 | 0 | OK | Ground clear controls. | 233 | 28.34 | 176.23
16210 | TIN-INTERP | Interpolated Ground | 103632.13 | -6.92 | 147.87 | 0 | 22.44 | 0 | OK | Ground clear controls. | 233 | 27.67 | 170.31
16211 | TIN-INTERP | Interpolated Ground | 103632.18 | 6.81 | 149.33 | 0 | 20.93 | 0 | OK | Ground clear controls. | 233 | 27.67 | 170.26
16212 | TIN-INTERP | Interpolated Ground | 103632.22 | 4.9 | 149.03 | 0 | 27.14 | 0 | OK | Ground clear controls. | 233 | 27.67 | 176.17
16213 | TIN-INTERP | Interpolated Ground | 103632.23 | 5.31 | 149.06 | 0 | 15.8 | 0 | OK | Ground clear controls. | 233 | 27.67 | 164.86
16214 | TIN-INTERP | Interpolated Ground | 103672.1 | -5.44 | 151.33 | 0 | 16.36 | 0 | OK | Ground clear controls. | 233 | 27.67 | 167.69
16215 | TIN-INTERP | Interpolated Ground | 103672.11 | -5.03 | 151.32 | 0 | 27.67 | 0 | OK | Ground clear controls. | 233 | 27.67 | 178.99
16216 | TIN-INTERP | Interpolated Ground | 103672.13 | -6.94 | 151.29 | 0 | 21.85 | 0 | OK | Ground clear controls. | 233 | 27.67 | 173.14
16217 | TIN-INTERP | Interpolated Ground | 103672.18 | 6.83 | 151.22 | 0 | 21.91 | 0 | OK | Ground clear controls. | 233 | 27.67 | 173.13
16218 | TIN-INTERP | Interpolated Ground | 103672.22 | 4.92 | 151.31 | 0 | 27.67 | 0 | OK | Ground clear controls. | 233 | 27.67 | 178.98
16219 | TIN-INTERP | Interpolated Ground | 103672.23 | 5.33 | 151.29 | 0 | 16.37 | 0 | OK | Ground clear controls. | 233 | 16.37 | 167.66
16220 | TIN-INTERP | Interpolated Ground | 103693.35 | 4.93 | 149.94 | 0 | 30.91 | 0 | OK | Ground clear controls. | 234 | 70.1 | 180.85
16221 | TIN-INTERP | Interpolated Ground | 103693.41 | -5.05 | 150.27 | 0 | 30.58 | 0 | OK | Ground clear controls. | 234 | 70.1 | 180.85
16222 | TIN-INTERP | Interpolated Ground | 103693.44 | -6.95 | 150.18 | 0 | 24.87 | 0 | OK | Ground clear controls. | 234 | 70.1 | 175.05
16223 | TIN-INTERP | Interpolated Ground | 103693.44 | -5.45 | 150.24 | 0 | 19.31 | 0 | OK | Ground clear controls. | 234 | 70.1 | 169.55
16224 | TIN-INTERP | Interpolated Ground | 103693.45 | 6.84 | 149.39 | 0 | 25.66 | 0 | OK | Ground clear controls. | 234 | 70.1 | 175.05
16225 | TIN-INTERP | Interpolated Ground | 103693.51 | 5.34 | 149.84 | 0 | 19.71 | 0 | OK | Ground clear controls. | 234 | 70.1 | 169.55
16226 | TIN-INTERP | Interpolated Ground | 103733.35 | 4.92 | 142.16 | 0 | 29.31 | 0 | OK | Ground clear controls. | 234 | 70.1 | 171.47
16227 | TIN-INTERP | Interpolated Ground | 103733.41 | -5.01 | 146.28 | 0 | 25.3 | 0 | OK | Ground clear controls. | 234 | 70.1 | 171.58
16228 | TIN-INTERP | Interpolated Ground | 103733.44 | -6.92 | 146.96 | 0 | 18.77 | 0 | OK | Ground clear controls. | 234 | 70.1 | 165.73
16229 | TIN-INTERP | Interpolated Ground | 103733.44 | -5.41 | 146.43 | 0 | 13.91 | 0 | OK | Ground clear controls. | 234 | 70.1 | 160.34
16230 | TIN-INTERP | Interpolated Ground | 103733.45 | 6.83 | 141.35 | 0 | 24.35 | 0 | OK | Ground clear controls. | 234 | 70.1 | 165.7
16231 | TIN-INTERP | Interpolated Ground | 103733.51 | 5.33 | 141.93 | 0 | 18.39 | 0 | OK | Ground clear controls. | 234 | 70.1 | 160.32
16232 | TIN-INTERP | Interpolated Ground | 103773.35 | 4.91 | 129.94 | 0 | 33.17 | 0 | OK | Ground clear controls. | 234 | 70.1 | 163.11
16233 | TIN-INTERP | Interpolated Ground | 103773.41 | -4.97 | 131.63 | 0 | 31.68 | 0 | OK | Ground clear controls. | 234 | 70.1 | 163.31
16234 | TIN-INTERP | Interpolated Ground | 103773.44 | -6.88 | 131.47 | 0 | 25.95 | 0 | OK | Ground clear controls. | 234 | 70.1 | 157.42
16235 | TIN-INTERP | Interpolated Ground | 103773.44 | -5.38 | 131.63 | 0 | 20.49 | 0 | OK | Ground clear controls. | 234 | 70.1 | 152.12
16236 | TIN-INTERP | Interpolated Ground | 103773.45 | 6.83 | 129.01 | 0 | 28.37 | 0 | OK | Ground clear controls. | 234 | 70.1 | 157.38
16237 | TIN-INTERP | Interpolated Ground | 103773.51 | 5.33 | 129.57 | 0 | 22.51 | 0 | OK | Ground clear controls. | 234 | 70.1 | 152.08
16238 | TIN-INTERP | Interpolated Ground | 103813.35 | 4.9 | 107.81 | 0 | 47.95 | 0 | OK | Ground clear controls. | 234 | 70.1 | 155.76
16239 | TIN-INTERP | Interpolated Ground | 103813.41 | -4.93 | 109.72 | 0 | 46.31 | 0 | OK | Ground clear controls. | 234 | 70.1 | 156.03
16240 | TIN-INTERP | Interpolated Ground | 103813.44 | -6.85 | 109.74 | 0 | 40.37 | 0 | OK | Ground clear controls. | 234 | 70.1 | 150.11
16241 | TIN-INTERP | Interpolated Ground | 103813.44 | -5.35 | 109.66 | 0 | 35.22 | 0 | OK | Ground clear controls. | 234 | 70.1 | 144.88
16242 | TIN-INTERP | Interpolated Ground | 103813.45 | 6.82 | 107.73 | 0 | 42.32 | 0 | OK | Ground clear controls. | 234 | 70.1 | 150.05
16243 | TIN-INTERP | Interpolated Ground | 103813.51 | 5.32 | 107.77 | 0 | 37.06 | 0 | OK | Ground clear controls. | 234 | 70.1 | 144.83
16244 | TIN-INTERP | Interpolated Ground | 103853.35 | 4.89 | 89.1 | 0 | 60.3 | 0 | OK | Ground clear controls. | 234 | 70.1 | 149.4
16245 | TIN-INTERP | Interpolated Ground | 103853.41 | -4.89 | 79.64 | 0 | 70.1 | 0 | OK | Ground clear controls. | 234 | 70.1 | 149.74
16246 | TIN-INTERP | Interpolated Ground | 103853.44 | -6.81 | 78.68 | 0 | 65.11 | 0 | OK | Ground clear controls. | 234 | 65.11 | 143.79
16247 | TIN-INTERP | Interpolated Ground | 103853.44 | -5.31 | 79 | 0 | 59.63 | 0 | OK | Ground clear controls. | 234 | 59.63 | 138.63
16248 | TIN-INTERP | Interpolated Ground | 103853.45 | 6.82 | 92.96 | 0 | 50.76 | 0 | OK | Ground clear controls. | 234 | 50.76 | 143.72
16249 | TIN-INTERP | Interpolated Ground | 103853.51 | 5.32 | 90.14 | 0 | 48.43 | 0 | OK | Ground clear controls. | 234 | 48.43 | 138.57
16250 | TIN-INTERP | Interpolated Ground | 103893.35 | 4.88 | 105.82 | 0 | 38.22 | 0 | OK | Ground clear controls. | 234 | 46.45 | 144.04
16251 | TIN-INTERP | Interpolated Ground | 103893.41 | -4.85 | 97.97 | 0 | 46.45 | 0 | OK | Ground clear controls. | 234 | 46.45 | 144.42
16252 | TIN-INTERP | Interpolated Ground | 103893.44 | -6.78 | 96.23 | 0 | 42.24 | 0 | OK | Ground clear controls. | 234 | 45.85 | 138.47
16253 | TIN-INTERP | Interpolated Ground | 103893.44 | -5.28 | 97.65 | 0 | 35.7 | 0 | OK | Ground clear controls. | 234 | 45.85 | 133.35
16254 | TIN-INTERP | Interpolated Ground | 103893.45 | 6.81 | 106.49 | 0 | 31.9 | 0 | OK | Ground clear controls. | 234 | 45.85 | 138.39
16255 | TIN-INTERP | Interpolated Ground | 103893.51 | 5.31 | 105.86 | 0 | 27.41 | 0 | OK | Ground clear controls. | 234 | 45.85 | 133.27
16256 | TIN-INTERP | Interpolated Ground | 103933.35 | 4.87 | 105.57 | 0 | 34.1 | 0 | OK | Ground clear controls. | 234 | 45.85 | 139.67
16257 | TIN-INTERP | Interpolated Ground | 103933.41 | -4.81 | 94.23 | 0 | 45.85 | 0 | OK | Ground clear controls. | 234 | 45.85 | 140.08
16258 | TIN-INTERP | Interpolated Ground | 103933.44 | -6.75 | 91.49 | 0 | 42.64 | 0 | OK | Ground clear controls. | 234 | 44.97 | 134.13
16259 | TIN-INTERP | Interpolated Ground | 103933.44 | -5.25 | 93.63 | 0 | 35.42 | 0 | OK | Ground clear controls. | 234 | 44.97 | 129.05
16260 | TIN-INTERP | Interpolated Ground | 103933.45 | 6.81 | 107.02 | 0 | 27.03 | 0 | OK | Ground clear controls. | 234 | 44.97 | 134.05
16261 | TIN-INTERP | Interpolated Ground | 103933.51 | 5.31 | 105.85 | 0 | 23.12 | 0 | OK | Ground clear controls. | 234 | 44.97 | 128.97
16262 | TIN-INTERP | Interpolated Ground | 103973.35 | 4.86 | 98.9 | 0 | 37.4 | 0 | OK | Ground clear controls. | 234 | 44.97 | 136.3
16263 | TIN-INTERP | Interpolated Ground | 103973.41 | -4.77 | 91.75 | 0 | 44.97 | 0 | OK | Ground clear controls. | 234 | 44.97 | 136.72
16264 | TIN-INTERP | Interpolated Ground | 103973.44 | -6.71 | 90.52 | 0 | 40.26 | 0 | OK | Ground clear controls. | 234 | 40.26 | 130.78
16265 | TIN-INTERP | Interpolated Ground | 103973.44 | -5.21 | 91.44 | 0 | 34.26 | 0 | OK | Ground clear controls. | 234 | 35.44 | 125.7
16266 | TIN-INTERP | Interpolated Ground | 103973.45 | 6.8 | 100.6 | 0 | 30.1 | 0 | OK | Ground clear controls. | 234 | 35.44 | 130.7
16267 | TIN-INTERP | Interpolated Ground | 103973.51 | 5.31 | 99.35 | 0 | 26.28 | 0 | OK | Ground clear controls. | 234 | 35.44 | 125.63
16268 | TIN-INTERP | Interpolated Ground | 104013.35 | 4.85 | 102.53 | 0 | 31.39 | 0 | OK | Ground clear controls. | 234 | 35.44 | 133.92
16269 | TIN-INTERP | Interpolated Ground | 104013.41 | -4.73 | 98.9 | 0 | 35.44 | 0 | OK | Ground clear controls. | 234 | 35.44 | 134.34
16270 | TIN-INTERP | Interpolated Ground | 104013.44 | -6.68 | 97.95 | 0 | 30.47 | 0 | OK | Ground clear controls. | 234 | 30.47 | 128.42
16271 | TIN-INTERP | Interpolated Ground | 104013.44 | -5.18 | 98.68 | 0 | 24.66 | 0 | OK | Ground clear controls. | 234 | 30.36 | 123.34
16272 | TIN-INTERP | Interpolated Ground | 104013.45 | 6.8 | 103.78 | 0 | 24.55 | 0 | OK | Ground clear controls. | 234 | 30.36 | 128.33
16273 | TIN-INTERP | Interpolated Ground | 104013.51 | 5.3 | 102.78 | 0 | 20.49 | 0 | OK | Ground clear controls. | 234 | 30.36 | 123.27
16274 | TIN-INTERP | Interpolated Ground | 104053.35 | 4.83 | 108.05 | 0 | 24.48 | 0 | OK | Ground clear controls. | 234 | 30.36 | 132.53
16275 | TIN-INTERP | Interpolated Ground | 104053.41 | -4.69 | 108.23 | 0 | 24.7 | 0 | OK | Ground clear controls. | 234 | 30.36 | 132.93
16276 | TIN-INTERP | Interpolated Ground | 104053.44 | -6.65 | 107.91 | 0 | 19.13 | 0 | OK | Ground clear controls. | 234 | 30.36 | 127.04
16277 | TIN-INTERP | Interpolated Ground | 104053.44 | -5.15 | 108.19 | 0 | 13.75 | 0 | OK | Ground clear controls. | 234 | 30.36 | 121.94
16278 | TIN-INTERP | Interpolated Ground | 104053.45 | 6.8 | 108.44 | 0 | 18.52 | 0 | OK | Ground clear controls. | 234 | 30.36 | 126.96
16279 | TIN-INTERP | Interpolated Ground | 104053.51 | 5.3 | 108.09 | 0 | 13.78 | 0 | OK | Ground clear controls. | 234 | 30.36 | 121.87
16280 | TIN-INTERP | Interpolated Ground | 104093.35 | 4.82 | 106.69 | 0 | 25.43 | 0 | OK | Ground clear controls. | 234 | 30.36 | 132.12
16281 | TIN-INTERP | Interpolated Ground | 104093.41 | -4.65 | 105.72 | 0 | 26.77 | 0 | OK | Ground clear controls. | 234 | 30.36 | 132.49
16282 | TIN-INTERP | Interpolated Ground | 104093.44 | -6.61 | 105.58 | 0 | 21.07 | 0 | OK | Ground clear controls. | 234 | 30.36 | 126.65
16283 | TIN-INTERP | Interpolated Ground | 104093.44 | -5.11 | 105.67 | 0 | 15.84 | 0 | OK | Ground clear controls. | 234 | 30.36 | 121.51
16284 | TIN-INTERP | Interpolated Ground | 104093.45 | 6.79 | 106.9 | 0 | 19.67 | 0 | OK | Ground clear controls. | 234 | 30.36 | 126.57
16285 | TIN-INTERP | Interpolated Ground | 104093.51 | 5.29 | 106.79 | 0 | 14.66 | 0 | OK | Ground clear controls. | 234 | 30.36 | 121.45
16286 | TIN-INTERP | Interpolated Ground | 104133.35 | 4.81 | 108.56 | 0 | 24.14 | 0 | OK | Ground clear controls. | 234 | 30.36 | 132.7
16287 | TIN-INTERP | Interpolated Ground | 104133.41 | -4.6 | 107.6 | 0 | 25.42 | 0 | OK | Ground clear controls. | 234 | 30.36 | 133.02
16288 | TIN-INTERP | Interpolated Ground | 104133.44 | -6.58 | 107.54 | 0 | 19.7 | 0 | OK | Ground clear controls. | 234 | 30.36 | 127.24
16289 | TIN-INTERP | Interpolated Ground | 104133.44 | -5.08 | 107.56 | 0 | 14.49 | 0 | OK | Ground clear controls. | 234 | 30.36 | 122.05
16290 | TIN-INTERP | Interpolated Ground | 104133.45 | 6.79 | 109.32 | 0 | 17.85 | 0 | OK | Ground clear controls. | 234 | 30.36 | 127.17
16291 | TIN-INTERP | Interpolated Ground | 104133.51 | 5.29 | 108.78 | 0 | 13.21 | 0 | OK | Ground clear controls. | 234 | 30.36 | 121.99
16292 | TIN-INTERP | Interpolated Ground | 104173.35 | 4.8 | 108.68 | 0 | 25.59 | 0 | OK | Ground clear controls. | 234 | 30.36 | 134.27
16293 | TIN-INTERP | Interpolated Ground | 104173.41 | -4.56 | 106.95 | 0 | 27.57 | 0 | OK | Ground clear controls. | 234 | 30.36 | 134.52
16294 | TIN-INTERP | Interpolated Ground | 104173.44 | -6.55 | 106.81 | 0 | 21.99 | 0 | OK | Ground clear controls. | 234 | 30.36 | 128.8
16295 | TIN-INTERP | Interpolated Ground | 104173.44 | -5.04 | 106.89 | 0 | 16.67 | 0 | OK | Ground clear controls. | 234 | 30.36 | 123.56
16296 | TIN-INTERP | Interpolated Ground | 104173.45 | 6.78 | 109.24 | 0 | 19.51 | 0 | OK | Ground clear controls. | 234 | 30.36 | 128.75
16297 | TIN-INTERP | Interpolated Ground | 104173.51 | 5.28 | 108.73 | 0 | 14.78 | 0 | OK | Ground clear controls. | 234 | 30.36 | 123.51
16298 | TIN-INTERP | Interpolated Ground | 104213.35 | 4.79 | 109.16 | 0 | 27.67 | 0 | OK | Ground clear controls. | 234 | 30.36 | 136.83
16299 | TIN-INTERP | Interpolated Ground | 104213.41 | -4.52 | 106.64 | 0 | 30.36 | 0 | OK | Ground clear controls. | 234 | 30.36 | 137
16300 | TIN-INTERP | Interpolated Ground | 104213.44 | -6.51 | 106.32 | 0 | 25.04 | 0 | OK | Ground clear controls. | 234 | 29.83 | 131.36
16301 | TIN-INTERP | Interpolated Ground | 104213.44 | -5.01 | 106.54 | 0 | 19.48 | 0 | OK | Ground clear controls. | 234 | 29.83 | 126.02
16302 | TIN-INTERP | Interpolated Ground | 104213.45 | 6.78 | 109.83 | 0 | 21.49 | 0 | OK | Ground clear controls. | 234 | 29.83 | 131.32
16303 | TIN-INTERP | Interpolated Ground | 104213.51 | 5.28 | 109.29 | 0 | 16.71 | 0 | OK | Ground clear controls. | 234 | 29.83 | 126
16304 | TIN-INTERP | Interpolated Ground | 104253.35 | 4.78 | 113.56 | 0 | 26.82 | 0 | OK | Ground clear controls. | 234 | 29.83 | 140.38
16305 | TIN-INTERP | Interpolated Ground | 104253.41 | -4.48 | 110.62 | 0 | 29.83 | 0 | OK | Ground clear controls. | 234 | 29.83 | 140.45
16306 | TIN-INTERP | Interpolated Ground | 104253.44 | -6.48 | 109.74 | 0 | 25.16 | 0 | OK | Ground clear controls. | 234 | 25.16 | 134.9
16307 | TIN-INTERP | Interpolated Ground | 104253.44 | -4.98 | 110.36 | 0 | 19.11 | 0 | OK | Ground clear controls. | 234 | 21.21 | 129.47
16308 | TIN-INTERP | Interpolated Ground | 104253.45 | 6.77 | 113.67 | 0 | 21.21 | 0 | OK | Ground clear controls. | 234 | 21.21 | 134.88
16309 | TIN-INTERP | Interpolated Ground | 104253.51 | 5.27 | 113.69 | 0 | 15.77 | 0 | OK | Ground clear controls. | 234 | 15.77 | 129.46
16310 | TIN-INTERP | Interpolated Ground | 104277.87 | -4.96 | 117.27 | 0 | 14.77 | 0 | OK | Ground clear controls. | 235 | 60.97 | 132.04
16311 | TIN-INTERP | Interpolated Ground | 104277.91 | -6.46 | 117.11 | 0 | 20.43 | 0 | OK | Ground clear controls. | 235 | 60.97 | 137.54
16312 | TIN-INTERP | Interpolated Ground | 104277.91 | -4.46 | 117.32 | 0 | 25.72 | 0 | OK | Ground clear controls. | 235 | 60.97 | 143.04
16313 | TIN-INTERP | Interpolated Ground | 104277.94 | 4.77 | 117.15 | 0 | 25.89 | 0 | OK | Ground clear controls. | 235 | 60.97 | 143.04
16314 | TIN-INTERP | Interpolated Ground | 104277.98 | 5.27 | 117.09 | 0 | 14.96 | 0 | OK | Ground clear controls. | 235 | 60.97 | 132.05
16315 | TIN-INTERP | Interpolated Ground | 104278 | 6.77 | 116.89 | 0 | 20.65 | 0 | OK | Ground clear controls. | 235 | 60.97 | 137.54
16316 | TIN-INTERP | Interpolated Ground | 104317.83 | -4.93 | 112.32 | 0 | 14.83 | 0 | OK | Ground clear controls. | 235 | 60.97 | 127.15
16317 | TIN-INTERP | Interpolated Ground | 104317.86 | -6.43 | 112.46 | 0 | 20.14 | 0 | OK | Ground clear controls. | 235 | 60.97 | 132.6
16318 | TIN-INTERP | Interpolated Ground | 104317.88 | -4.44 | 112.29 | 0 | 25.89 | 0 | OK | Ground clear controls. | 235 | 60.97 | 138.18
16319 | TIN-INTERP | Interpolated Ground | 104317.93 | 4.88 | 111.02 | 0 | 27.08 | 0 | OK | Ground clear controls. | 235 | 60.97 | 138.1
16320 | TIN-INTERP | Interpolated Ground | 104317.98 | 5.36 | 111.06 | 0 | 16.1 | 0 | OK | Ground clear controls. | 235 | 60.97 | 127.16
16321 | TIN-INTERP | Interpolated Ground | 104318 | 6.86 | 111.19 | 0 | 21.41 | 0 | OK | Ground clear controls. | 235 | 60.97 | 132.6
16322 | TIN-INTERP | Interpolated Ground | 104357.83 | -4.9 | 94.32 | 0 | 28.91 | 0 | OK | Ground clear controls. | 235 | 60.97 | 123.23
16323 | TIN-INTERP | Interpolated Ground | 104357.86 | -6.4 | 94.19 | 0 | 34.47 | 0 | OK | Ground clear controls. | 235 | 60.97 | 128.66
16324 | TIN-INTERP | Interpolated Ground | 104357.88 | -4.42 | 94.55 | 0 | 39.75 | 0 | OK | Ground clear controls. | 235 | 60.97 | 134.3
16325 | TIN-INTERP | Interpolated Ground | 104357.93 | 4.98 | 104.33 | 0 | 29.83 | 0 | OK | Ground clear controls. | 235 | 60.97 | 134.16
16326 | TIN-INTERP | Interpolated Ground | 104357.98 | 5.46 | 104.94 | 0 | 18.31 | 0 | OK | Ground clear controls. | 235 | 60.97 | 123.25
16327 | TIN-INTERP | Interpolated Ground | 104358 | 6.96 | 106.37 | 0 | 22.26 | 0 | OK | Ground clear controls. | 235 | 60.97 | 128.63
16328 | TIN-INTERP | Interpolated Ground | 104397.83 | -4.87 | 86.77 | 0 | 33.53 | 0 | OK | Ground clear controls. | 235 | 60.97 | 120.3
16329 | TIN-INTERP | Interpolated Ground | 104397.86 | -6.38 | 84.98 | 0 | 40.72 | 0 | OK | Ground clear controls. | 235 | 60.97 | 125.7
16330 | TIN-INTERP | Interpolated Ground | 104397.88 | -4.4 | 87.47 | 0 | 43.92 | 0 | OK | Ground clear controls. | 235 | 60.97 | 131.39
16331 | TIN-INTERP | Interpolated Ground | 104397.93 | 5.08 | 95.31 | 0 | 35.9 | 0 | OK | Ground clear controls. | 235 | 60.97 | 131.21
16332 | TIN-INTERP | Interpolated Ground | 104397.98 | 5.55 | 95.59 | 0 | 24.73 | 0 | OK | Ground clear controls. | 235 | 60.97 | 120.32
16333 | TIN-INTERP | Interpolated Ground | 104398 | 7.05 | 96.63 | 0 | 29.05 | 0 | OK | Ground clear controls. | 235 | 60.97 | 125.68
16334 | TIN-INTERP | Interpolated Ground | 104437.83 | -4.84 | 75.06 | 0 | 43.27 | 0 | OK | Ground clear controls. | 235 | 60.97 | 118.33
16335 | TIN-INTERP | Interpolated Ground | 104437.86 | -6.35 | 73.32 | 0 | 50.39 | 0 | OK | Ground clear controls. | 235 | 60.97 | 123.71
16336 | TIN-INTERP | Interpolated Ground | 104437.88 | -4.39 | 75.58 | 0 | 53.87 | 0 | OK | Ground clear controls. | 235 | 60.97 | 129.45
16337 | TIN-INTERP | Interpolated Ground | 104437.93 | 5.18 | 83.66 | 0 | 45.6 | 0 | OK | Ground clear controls. | 235 | 60.97 | 129.26
16338 | TIN-INTERP | Interpolated Ground | 104437.98 | 5.65 | 83.93 | 0 | 34.42 | 0 | OK | Ground clear controls. | 235 | 60.97 | 118.35
16339 | TIN-INTERP | Interpolated Ground | 104438 | 7.14 | 85.02 | 0 | 38.67 | 0 | OK | Ground clear controls. | 235 | 60.97 | 123.69
16340 | TIN-INTERP | Interpolated Ground | 104477.83 | -4.81 | 67.81 | 0 | 49.52 | 0 | OK | Ground clear controls. | 235 | 60.97 | 117.33
16341 | TIN-INTERP | Interpolated Ground | 104477.86 | -6.32 | 68.28 | 0 | 54.43 | 0 | OK | Ground clear controls. | 235 | 60.97 | 122.71
16342 | TIN-INTERP | Interpolated Ground | 104477.88 | -4.37 | 67.64 | 0 | 60.85 | 0 | OK | Ground clear controls. | 235 | 60.97 | 128.49
16343 | TIN-INTERP | Interpolated Ground | 104477.93 | 5.29 | 72.36 | 0 | 55.94 | 0 | OK | Ground clear controls. | 235 | 60.97 | 128.3
16344 | TIN-INTERP | Interpolated Ground | 104477.98 | 5.74 | 72.76 | 0 | 44.6 | 0 | OK | Ground clear controls. | 235 | 60.97 | 117.36
16345 | TIN-INTERP | Interpolated Ground | 104478 | 7.24 | 73.91 | 0 | 48.78 | 0 | OK | Ground clear controls. | 235 | 60.97 | 122.69
16346 | TIN-INTERP | Interpolated Ground | 104517.83 | -4.79 | 69.52 | 0 | 47.78 | 0 | OK | Ground clear controls. | 235 | 60.97 | 117.3
16347 | TIN-INTERP | Interpolated Ground | 104517.86 | -6.29 | 69.78 | 0 | 52.91 | 0 | OK | Ground clear controls. | 235 | 60.97 | 122.69
16348 | TIN-INTERP | Interpolated Ground | 104517.88 | -4.35 | 69.42 | 0 | 59.07 | 0 | OK | Ground clear controls. | 235 | 60.97 | 128.49
16349 | TIN-INTERP | Interpolated Ground | 104517.93 | 5.39 | 67.35 | 0 | 60.97 | 0 | OK | Ground clear controls. | 235 | 60.97 | 128.32
16350 | TIN-INTERP | Interpolated Ground | 104517.98 | 5.83 | 67.35 | 0 | 49.98 | 0 | OK | Ground clear controls. | 235 | 54.88 | 117.33
16351 | TIN-INTERP | Interpolated Ground | 104518 | 7.33 | 67.8 | 0 | 54.88 | 0 | OK | Ground clear controls. | 235 | 54.88 | 122.68
16352 | TIN-INTERP | Interpolated Ground | 104557.83 | -4.76 | 91.48 | 0 | 26.76 | 0 | OK | Ground clear controls. | 235 | 38.39 | 118.24
16353 | TIN-INTERP | Interpolated Ground | 104557.86 | -6.27 | 92.15 | 0 | 31.5 | 0 | OK | Ground clear controls. | 235 | 38.39 | 123.65
16354 | TIN-INTERP | Interpolated Ground | 104557.88 | -4.33 | 91.47 | 0 | 37.99 | 0 | OK | Ground clear controls. | 235 | 38.39 | 129.46
16355 | TIN-INTERP | Interpolated Ground | 104557.93 | 5.49 | 90.94 | 0 | 38.39 | 0 | OK | Ground clear controls. | 235 | 38.39 | 129.33
16356 | TIN-INTERP | Interpolated Ground | 104557.98 | 5.93 | 91.04 | 0 | 27.23 | 0 | OK | Ground clear controls. | 235 | 32.78 | 118.27
16357 | TIN-INTERP | Interpolated Ground | 104558 | 7.43 | 90.87 | 0 | 32.78 | 0 | OK | Ground clear controls. | 235 | 32.78 | 123.65
16358 | TIN-INTERP | Interpolated Ground | 104597.83 | -4.73 | 109.46 | 0 | 10.69 | 0 | OK | Ground clear controls. | 235 | 28.62 | 120.15
16359 | TIN-INTERP | Interpolated Ground | 104597.86 | -6.24 | 109.43 | 0 | 16.17 | 0 | OK | Ground clear controls. | 235 | 28.62 | 125.6
16360 | TIN-INTERP | Interpolated Ground | 104597.88 | -4.31 | 109.44 | 0 | 21.97 | 0 | OK | Ground clear controls. | 235 | 28.62 | 131.41
16361 | TIN-INTERP | Interpolated Ground | 104597.93 | 5.59 | 109.12 | 0 | 22.21 | 0 | OK | Ground clear controls. | 235 | 28.62 | 131.33
16362 | TIN-INTERP | Interpolated Ground | 104597.98 | 6.02 | 108.97 | 0 | 11.21 | 0 | OK | Ground clear controls. | 235 | 28.62 | 120.18
16363 | TIN-INTERP | Interpolated Ground | 104598 | 7.52 | 108.07 | 0 | 17.54 | 0 | OK | Ground clear controls. | 235 | 28.62 | 125.61
16364 | TIN-INTERP | Interpolated Ground | 104637.83 | -4.7 | 107.36 | 0 | 15.66 | 0 | OK | Ground clear controls. | 235 | 28.62 | 123.02
16365 | TIN-INTERP | Interpolated Ground | 104637.86 | -6.21 | 107.77 | 0 | 20.76 | 0 | OK | Ground clear controls. | 235 | 28.62 | 128.53
16366 | TIN-INTERP | Interpolated Ground | 104637.88 | -4.29 | 107.29 | 0 | 27.04 | 0 | OK | Ground clear controls. | 235 | 28.62 | 134.33
16367 | TIN-INTERP | Interpolated Ground | 104637.93 | 5.7 | 105.72 | 0 | 28.62 | 0 | OK | Ground clear controls. | 235 | 28.62 | 134.34
16368 | TIN-INTERP | Interpolated Ground | 104637.98 | 6.12 | 105.66 | 0 | 17.4 | 0 | OK | Ground clear controls. | 235 | 23.14 | 123.06
16369 | TIN-INTERP | Interpolated Ground | 104638 | 7.61 | 105.41 | 0 | 23.14 | 0 | OK | Ground clear controls. | 235 | 23.14 | 128.55
16370 | TIN-INTERP | Interpolated Ground | 104642.93 | -4.29 | 107.15 | 0 | 27.62 | 0 | OK | Ground clear controls. | 236 | 63.05 | 134.77
16371 | TIN-INTERP | Interpolated Ground | 104642.94 | -6.21 | 107.24 | 0 | 21.73 | 0 | OK | Ground clear controls. | 236 | 63.05 | 128.97
16372 | TIN-INTERP | Interpolated Ground | 104642.94 | -4.7 | 107.16 | 0 | 16.3 | 0 | OK | Ground clear controls. | 236 | 63.05 | 123.46
16373 | TIN-INTERP | Interpolated Ground | 104643.18 | 6.12 | 105.69 | 0 | 17.79 | 0 | OK | Ground clear controls. | 236 | 63.05 | 123.48
16374 | TIN-INTERP | Interpolated Ground | 104643.21 | 5.7 | 105.73 | 0 | 29.04 | 0 | OK | Ground clear controls. | 236 | 63.05 | 134.77
16375 | TIN-INTERP | Interpolated Ground | 104643.36 | 7.61 | 105.49 | 0 | 23.48 | 0 | OK | Ground clear controls. | 236 | 63.05 | 128.97
16376 | TIN-INTERP | Interpolated Ground | 104682.55 | -6.22 | 108.97 | 0 | 14.81 | 0 | OK | Ground clear controls. | 236 | 63.05 | 123.78
16377 | TIN-INTERP | Interpolated Ground | 104682.66 | -4.27 | 107.64 | 0 | 22.04 | 0 | OK | Ground clear controls. | 236 | 63.05 | 129.68
16378 | TIN-INTERP | Interpolated Ground | 104682.68 | -4.7 | 107.94 | 0 | 10.4 | 0 | OK | Ground clear controls. | 236 | 63.05 | 118.34
16379 | TIN-INTERP | Interpolated Ground | 104683.18 | 6.29 | 103.3 | 0 | 15.04 | 0 | OK | Ground clear controls. | 236 | 63.05 | 118.34
16380 | TIN-INTERP | Interpolated Ground | 104683.21 | 5.85 | 103.43 | 0 | 26.17 | 0 | OK | Ground clear controls. | 236 | 63.05 | 129.6
16381 | TIN-INTERP | Interpolated Ground | 104683.36 | 7.78 | 102.82 | 0 | 21.02 | 0 | OK | Ground clear controls. | 236 | 63.05 | 123.84
16382 | TIN-INTERP | Interpolated Ground | 104722.55 | -6.24 | 88.13 | 0 | 31.44 | 0 | OK | Ground clear controls. | 236 | 63.05 | 119.57
16383 | TIN-INTERP | Interpolated Ground | 104722.66 | -4.26 | 86.51 | 0 | 39.07 | 0 | OK | Ground clear controls. | 236 | 63.05 | 125.58
16384 | TIN-INTERP | Interpolated Ground | 104722.68 | -4.71 | 86.83 | 0 | 27.36 | 0 | OK | Ground clear controls. | 236 | 63.05 | 114.19
16385 | TIN-INTERP | Interpolated Ground | 104723.18 | 6.46 | 83.31 | 0 | 30.88 | 0 | OK | Ground clear controls. | 236 | 63.05 | 114.19
16386 | TIN-INTERP | Interpolated Ground | 104723.21 | 5.99 | 83.38 | 0 | 42.06 | 0 | OK | Ground clear controls. | 236 | 63.05 | 125.44
16387 | TIN-INTERP | Interpolated Ground | 104723.36 | 7.94 | 82.9 | 0 | 36.78 | 0 | OK | Ground clear controls. | 236 | 63.05 | 119.68
16388 | TIN-INTERP | Interpolated Ground | 104762.55 | -6.26 | 70.85 | 0 | 45.52 | 0 | OK | Ground clear controls. | 236 | 63.05 | 116.37
16389 | TIN-INTERP | Interpolated Ground | 104762.66 | -4.26 | 70.01 | 0 | 52.44 | 0 | OK | Ground clear controls. | 236 | 63.05 | 122.45
16390 | TIN-INTERP | Interpolated Ground | 104762.68 | -4.72 | 70.16 | 0 | 40.86 | 0 | OK | Ground clear controls. | 236 | 63.05 | 111.02
16391 | TIN-INTERP | Interpolated Ground | 104763.18 | 6.63 | 66.84 | 0 | 44.17 | 0 | OK | Ground clear controls. | 236 | 63.05 | 111.01
16392 | TIN-INTERP | Interpolated Ground | 104763.21 | 6.13 | 66.84 | 0 | 55.44 | 0 | OK | Ground clear controls. | 236 | 63.05 | 122.28
16393 | TIN-INTERP | Interpolated Ground | 104763.36 | 8.11 | 66.88 | 0 | 49.64 | 0 | OK | Ground clear controls. | 236 | 63.05 | 116.52
16394 | TIN-INTERP | Interpolated Ground | 104802.55 | -6.28 | 66.85 | 0 | 47.3 | 0 | OK | Ground clear controls. | 236 | 63.05 | 114.15
16395 | TIN-INTERP | Interpolated Ground | 104802.66 | -4.25 | 66.74 | 0 | 53.57 | 0 | OK | Ground clear controls. | 236 | 63.05 | 120.31
16396 | TIN-INTERP | Interpolated Ground | 104802.68 | -4.73 | 66.75 | 0 | 42.06 | 0 | OK | Ground clear controls. | 236 | 63.05 | 108.81
16397 | TIN-INTERP | Interpolated Ground | 104803.18 | 6.8 | 67.2 | 0 | 41.61 | 0 | OK | Ground clear controls. | 236 | 63.05 | 108.81
16398 | TIN-INTERP | Interpolated Ground | 104803.21 | 6.27 | 67.22 | 0 | 52.88 | 0 | OK | Ground clear controls. | 236 | 63.05 | 120.1
16399 | TIN-INTERP | Interpolated Ground | 104803.36 | 8.28 | 67.26 | 0 | 47.07 | 0 | OK | Ground clear controls. | 236 | 63.05 | 114.33
16400 | TIN-INTERP | Interpolated Ground | 104842.55 | -6.3 | 63.36 | 0 | 49.55 | 0 | OK | Ground clear controls. | 236 | 63.05 | 112.91
16401 | TIN-INTERP | Interpolated Ground | 104842.66 | -4.24 | 63.38 | 0 | 55.75 | 0 | OK | Ground clear controls. | 236 | 63.05 | 119.13
16402 | TIN-INTERP | Interpolated Ground | 104842.68 | -4.74 | 63.27 | 0 | 44.3 | 0 | OK | Ground clear controls. | 236 | 63.05 | 107.57
16403 | TIN-INTERP | Interpolated Ground | 104843.18 | 6.96 | 65.73 | 0 | 41.86 | 0 | OK | Ground clear controls. | 236 | 63.05 | 107.59
16404 | TIN-INTERP | Interpolated Ground | 104843.21 | 6.42 | 65.68 | 0 | 53.23 | 0 | OK | Ground clear controls. | 236 | 63.05 | 118.91
16405 | TIN-INTERP | Interpolated Ground | 104843.36 | 8.44 | 65.94 | 0 | 47.19 | 0 | OK | Ground clear controls. | 236 | 63.05 | 113.13
16406 | TIN-INTERP | Interpolated Ground | 104882.55 | -6.32 | 65.26 | 0 | 47.39 | 0 | OK | Ground clear controls. | 236 | 63.05 | 112.65
16407 | TIN-INTERP | Interpolated Ground | 104882.66 | -4.23 | 65.16 | 0 | 53.77 | 0 | OK | Ground clear controls. | 236 | 63.05 | 118.93
16408 | TIN-INTERP | Interpolated Ground | 104882.68 | -4.75 | 65.16 | 0 | 42.15 | 0 | OK | Ground clear controls. | 236 | 63.05 | 107.31
16409 | TIN-INTERP | Interpolated Ground | 104883.18 | 7.13 | 64.75 | 0 | 42.6 | 0 | OK | Ground clear controls. | 236 | 63.05 | 107.35
16410 | TIN-INTERP | Interpolated Ground | 104883.21 | 6.56 | 64.78 | 0 | 53.94 | 0 | OK | Ground clear controls. | 236 | 63.05 | 118.72
16411 | TIN-INTERP | Interpolated Ground | 104883.36 | 8.61 | 64.79 | 0 | 48.11 | 0 | OK | Ground clear controls. | 236 | 63.05 | 112.9
16412 | TIN-INTERP | Interpolated Ground | 104922.55 | -6.34 | 64.69 | 0 | 48.7 | 0 | OK | Ground clear controls. | 236 | 63.05 | 113.39
16413 | TIN-INTERP | Interpolated Ground | 104922.66 | -4.22 | 64.5 | 0 | 55.2 | 0 | OK | Ground clear controls. | 236 | 63.05 | 119.7
16414 | TIN-INTERP | Interpolated Ground | 104922.68 | -4.76 | 64.68 | 0 | 43.34 | 0 | OK | Ground clear controls. | 236 | 63.05 | 108.02
16415 | TIN-INTERP | Interpolated Ground | 104923.18 | 7.3 | 63.81 | 0 | 44.26 | 0 | OK | Ground clear controls. | 236 | 63.05 | 108.07
16416 | TIN-INTERP | Interpolated Ground | 104923.21 | 6.7 | 63.76 | 0 | 55.76 | 0 | OK | Ground clear controls. | 236 | 63.05 | 119.52
16417 | TIN-INTERP | Interpolated Ground | 104923.36 | 8.77 | 63.89 | 0 | 49.77 | 0 | OK | Ground clear controls. | 236 | 63.05 | 113.66
16418 | TIN-INTERP | Interpolated Ground | 104962.55 | -6.36 | 68.86 | 0 | 46.25 | 0 | OK | Ground clear controls. | 236 | 63.05 | 115.11
16419 | TIN-INTERP | Interpolated Ground | 104962.66 | -4.21 | 69.85 | 0 | 51.6 | 0 | OK | Ground clear controls. | 236 | 63.05 | 121.45
16420 | TIN-INTERP | Interpolated Ground | 104962.68 | -4.77 | 69.62 | 0 | 40.07 | 0 | OK | Ground clear controls. | 236 | 63.05 | 109.69
16421 | TIN-INTERP | Interpolated Ground | 104963.18 | 7.47 | 74.13 | 0 | 35.65 | 0 | OK | Ground clear controls. | 236 | 63.05 | 109.78
16422 | TIN-INTERP | Interpolated Ground | 104963.21 | 6.84 | 74.11 | 0 | 47.21 | 0 | OK | Ground clear controls. | 236 | 63.05 | 121.32
16423 | TIN-INTERP | Interpolated Ground | 104963.36 | 8.94 | 74.51 | 0 | 40.89 | 0 | OK | Ground clear controls. | 236 | 63.05 | 115.4
16424 | TIN-INTERP | Interpolated Ground | 105002.55 | -6.38 | 61.5 | 0 | 56.32 | 0 | OK | Ground clear controls. | 236 | 63.05 | 117.82
16425 | TIN-INTERP | Interpolated Ground | 105002.66 | -4.2 | 61.14 | 0 | 63.03 | 0 | OK | Ground clear controls. | 236 | 63.05 | 124.17
16426 | TIN-INTERP | Interpolated Ground | 105002.68 | -4.78 | 61.24 | 0 | 51.1 | 0 | OK | Ground clear controls. | 236 | 63.05 | 112.34
16427 | TIN-INTERP | Interpolated Ground | 105003.18 | 7.63 | 61.03 | 0 | 51.42 | 0 | OK | Ground clear controls. | 236 | 63.05 | 112.45
16428 | TIN-INTERP | Interpolated Ground | 105003.21 | 6.99 | 61.05 | 0 | 63.05 | 0 | OK | Ground clear controls. | 236 | 63.05 | 124.1
16429 | TIN-INTERP | Interpolated Ground | 105003.36 | 9.11 | 60.96 | 0 | 57.16 | 0 | OK | Ground clear controls. | 236 | 62.78 | 118.12
16430 | TIN-INTERP | Interpolated Ground | 105042.55 | -6.4 | 69.43 | 0 | 52.08 | 0 | OK | Ground clear controls. | 236 | 62.78 | 121.51
16431 | TIN-INTERP | Interpolated Ground | 105042.66 | -4.19 | 68.56 | 0 | 59.32 | 0 | OK | Ground clear controls. | 236 | 62.78 | 127.88
16432 | TIN-INTERP | Interpolated Ground | 105042.68 | -4.79 | 68.78 | 0 | 47.18 | 0 | OK | Ground clear controls. | 236 | 62.78 | 115.96
16433 | TIN-INTERP | Interpolated Ground | 105043.18 | 7.8 | 64.84 | 0 | 51.27 | 0 | OK | Ground clear controls. | 236 | 62.78 | 116.11
16434 | TIN-INTERP | Interpolated Ground | 105043.21 | 7.13 | 65.1 | 0 | 62.78 | 0 | OK | Ground clear controls. | 236 | 62.78 | 127.88
16435 | TIN-INTERP | Interpolated Ground | 105043.36 | 9.27 | 64.42 | 0 | 57.41 | 0 | OK | Ground clear controls. | 236 | 57.41 | 121.83
16436 | TIN-INTERP | Interpolated Ground | 105082.55 | -6.42 | 96.52 | 0 | 29.67 | 0 | OK | Ground clear controls. | 236 | 43.34 | 126.19
16437 | TIN-INTERP | Interpolated Ground | 105082.66 | -4.18 | 95.67 | 0 | 36.88 | 0 | OK | Ground clear controls. | 236 | 43.34 | 132.55
16438 | TIN-INTERP | Interpolated Ground | 105082.68 | -4.8 | 96.01 | 0 | 24.54 | 0 | OK | Ground clear controls. | 236 | 43.34 | 120.55
16439 | TIN-INTERP | Interpolated Ground | 105083.18 | 7.97 | 88.67 | 0 | 32.07 | 0 | OK | Ground clear controls. | 236 | 43.34 | 120.74
16440 | TIN-INTERP | Interpolated Ground | 105083.21 | 7.27 | 89.32 | 0 | 43.34 | 0 | OK | Ground clear controls. | 236 | 43.34 | 132.66
16441 | TIN-INTERP | Interpolated Ground | 105083.36 | 9.44 | 87.62 | 0 | 38.91 | 0 | OK | Ground clear controls. | 236 | 38.91 | 126.53
16442 | TIN-INTERP | Interpolated Ground | 105118.14 | 9.58 | 103.91 | 0 | 27.5 | 0 | OK | Ground clear controls. | 237 | 45.72 | 131.41
16443 | TIN-INTERP | Interpolated Ground | 105118.37 | 8.12 | 104.41 | 0 | 21.21 | 0 | OK | Ground clear controls. | 237 | 45.72 | 125.62
16444 | TIN-INTERP | Interpolated Ground | 105118.48 | 7.4 | 104.58 | 0 | 33.12 | 0 | OK | Ground clear controls. | 237 | 45.72 | 137.7
16445 | TIN-INTERP | Interpolated Ground | 105119.17 | -6.45 | 107.8 | 0 | 23.62 | 0 | OK | Ground clear controls. | 237 | 45.72 | 131.42
16446 | TIN-INTERP | Interpolated Ground | 105119.17 | -4.82 | 107.68 | 0 | 17.96 | 0 | OK | Ground clear controls. | 237 | 45.72 | 125.64
16447 | TIN-INTERP | Interpolated Ground | 105119.17 | -4.19 | 107.58 | 0 | 30.14 | 0 | OK | Ground clear controls. | 237 | 45.72 | 137.72
16448 | TIN-INTERP | Interpolated Ground | 105158.51 | -6.7 | 107.04 | 0 | 23.43 | 0 | OK | Ground clear controls. | 237 | 45.72 | 130.47
16449 | TIN-INTERP | Interpolated Ground | 105158.68 | -5.09 | 106.39 | 0 | 18.39 | 0 | OK | Ground clear controls. | 237 | 45.72 | 124.78
16450 | TIN-INTERP | Interpolated Ground | 105158.76 | -4.46 | 106.08 | 0 | 30.78 | 0 | OK | Ground clear controls. | 237 | 45.72 | 136.86
16451 | TIN-INTERP | Interpolated Ground | 105159.8 | 7.14 | 101.17 | 0 | 35.61 | 0 | OK | Ground clear controls. | 237 | 45.72 | 136.78
16452 | TIN-INTERP | Interpolated Ground | 105159.82 | 7.86 | 100.91 | 0 | 23.86 | 0 | OK | Ground clear controls. | 237 | 45.72 | 124.77
16453 | TIN-INTERP | Interpolated Ground | 105159.85 | 9.35 | 99.59 | 0 | 30.89 | 0 | OK | Ground clear controls. | 237 | 45.72 | 130.48
16454 | TIN-INTERP | Interpolated Ground | 105198.51 | -6.98 | 100.36 | 0 | 30.16 | 0 | OK | Ground clear controls. | 237 | 45.72 | 130.52
16455 | TIN-INTERP | Interpolated Ground | 105198.68 | -5.39 | 99.61 | 0 | 25.28 | 0 | OK | Ground clear controls. | 237 | 45.72 | 124.89
16456 | TIN-INTERP | Interpolated Ground | 105198.76 | -4.74 | 99.24 | 0 | 37.73 | 0 | OK | Ground clear controls. | 237 | 45.72 | 136.97
16457 | TIN-INTERP | Interpolated Ground | 105199.8 | 6.88 | 91.99 | 0 | 44.86 | 0 | OK | Ground clear controls. | 237 | 45.72 | 136.85
16458 | TIN-INTERP | Interpolated Ground | 105199.82 | 7.6 | 91.9 | 0 | 32.98 | 0 | OK | Ground clear controls. | 237 | 45.72 | 124.88
16459 | TIN-INTERP | Interpolated Ground | 105199.85 | 9.08 | 90.6 | 0 | 39.95 | 0 | OK | Ground clear controls. | 237 | 45.72 | 130.55
16460 | TIN-INTERP | Interpolated Ground | 105238.5 | -7.26 | 106.05 | 0 | 25.52 | 0 | OK | Ground clear controls. | 237 | 45.72 | 131.57
16461 | TIN-INTERP | Interpolated Ground | 105238.68 | -5.69 | 105.41 | 0 | 20.58 | 0 | OK | Ground clear controls. | 237 | 45.72 | 125.99
16462 | TIN-INTERP | Interpolated Ground | 105238.76 | -5.03 | 105.09 | 0 | 32.97 | 0 | OK | Ground clear controls. | 237 | 45.72 | 138.06
16463 | TIN-INTERP | Interpolated Ground | 105239.8 | 6.62 | 98.06 | 0 | 39.86 | 0 | OK | Ground clear controls. | 237 | 45.72 | 137.92
16464 | TIN-INTERP | Interpolated Ground | 105239.81 | 7.33 | 97.37 | 0 | 28.61 | 0 | OK | Ground clear controls. | 237 | 45.72 | 125.98
16465 | TIN-INTERP | Interpolated Ground | 105239.85 | 8.82 | 95.51 | 0 | 36.1 | 0 | OK | Ground clear controls. | 237 | 45.72 | 131.61
16466 | TIN-INTERP | Interpolated Ground | 105278.5 | -7.54 | 108.88 | 0 | 24.73 | 0 | OK | Ground clear controls. | 237 | 45.72 | 133.61
16467 | TIN-INTERP | Interpolated Ground | 105278.68 | -5.98 | 108.17 | 0 | 19.89 | 0 | OK | Ground clear controls. | 237 | 45.72 | 128.06
16468 | TIN-INTERP | Interpolated Ground | 105278.76 | -5.32 | 107.86 | 0 | 32.27 | 0 | OK | Ground clear controls. | 237 | 45.72 | 140.13
16469 | TIN-INTERP | Interpolated Ground | 105279.8 | 6.35 | 101.97 | 0 | 38.01 | 0 | OK | Ground clear controls. | 237 | 45.72 | 139.98
16470 | TIN-INTERP | Interpolated Ground | 105279.81 | 7.07 | 101.48 | 0 | 26.57 | 0 | OK | Ground clear controls. | 237 | 45.72 | 128.05
16471 | TIN-INTERP | Interpolated Ground | 105279.85 | 8.55 | 100.79 | 0 | 32.87 | 0 | OK | Ground clear controls. | 237 | 45.72 | 133.66
16472 | TIN-INTERP | Interpolated Ground | 105318.5 | -7.82 | 106.83 | 0 | 29.83 | 0 | OK | Ground clear controls. | 237 | 45.72 | 136.66
16473 | TIN-INTERP | Interpolated Ground | 105318.68 | -6.28 | 106.38 | 0 | 24.73 | 0 | OK | Ground clear controls. | 237 | 45.72 | 131.11
16474 | TIN-INTERP | Interpolated Ground | 105318.75 | -5.61 | 106.16 | 0 | 37.03 | 0 | OK | Ground clear controls. | 237 | 45.72 | 143.19
16475 | TIN-INTERP | Interpolated Ground | 105319.8 | 6.09 | 101.48 | 0 | 41.53 | 0 | OK | Ground clear controls. | 237 | 45.72 | 143.01
16476 | TIN-INTERP | Interpolated Ground | 105319.81 | 6.8 | 101.32 | 0 | 29.78 | 0 | OK | Ground clear controls. | 237 | 45.72 | 131.1
16477 | TIN-INTERP | Interpolated Ground | 105319.85 | 8.29 | 100.8 | 0 | 35.89 | 0 | OK | Ground clear controls. | 237 | 45.72 | 136.69
16478 | TIN-INTERP | Interpolated Ground | 105358.5 | -8.1 | 105.86 | 0 | 34.84 | 0 | OK | Ground clear controls. | 237 | 45.72 | 140.7
16479 | TIN-INTERP | Interpolated Ground | 105358.67 | -6.57 | 105.24 | 0 | 29.91 | 0 | OK | Ground clear controls. | 237 | 45.72 | 135.15
16480 | TIN-INTERP | Interpolated Ground | 105358.75 | -5.89 | 104.98 | 0 | 42.24 | 0 | OK | Ground clear controls. | 237 | 45.72 | 147.22
16481 | TIN-INTERP | Interpolated Ground | 105359.8 | 5.83 | 101.34 | 0 | 45.72 | 0 | OK | Ground clear controls. | 237 | 45.72 | 147.06
16482 | TIN-INTERP | Interpolated Ground | 105359.81 | 6.54 | 101.21 | 0 | 33.92 | 0 | OK | Ground clear controls. | 237 | 44.7 | 135.13
16483 | TIN-INTERP | Interpolated Ground | 105359.85 | 8.03 | 100.94 | 0 | 39.8 | 0 | OK | Ground clear controls. | 237 | 44.7 | 140.74
16484 | TIN-INTERP | Interpolated Ground | 105398.5 | -8.38 | 106.76 | 0 | 38.99 | 0 | OK | Ground clear controls. | 237 | 44.7 | 145.75
16485 | TIN-INTERP | Interpolated Ground | 105398.67 | -6.87 | 107.32 | 0 | 32.85 | 0 | OK | Ground clear controls. | 237 | 44.7 | 140.17
16486 | TIN-INTERP | Interpolated Ground | 105398.75 | -6.18 | 107.55 | 0 | 44.7 | 0 | OK | Ground clear controls. | 237 | 44.7 | 152.25
16487 | TIN-INTERP | Interpolated Ground | 105399.8 | 5.57 | 110.29 | 0 | 41.81 | 0 | OK | Ground clear controls. | 237 | 41.81 | 152.1
16488 | TIN-INTERP | Interpolated Ground | 105399.81 | 6.27 | 110.35 | 0 | 29.8 | 0 | OK | Ground clear controls. | 237 | 35.28 | 140.15
16489 | TIN-INTERP | Interpolated Ground | 105399.85 | 7.76 | 110.49 | 0 | 35.28 | 0 | OK | Ground clear controls. | 237 | 35.28 | 145.77
16490 | TIN-INTERP | Interpolated Ground | 105438.5 | -8.67 | 125.48 | 0 | 26.33 | 0 | OK | Ground clear controls. | 237 | 31.77 | 151.81
16491 | TIN-INTERP | Interpolated Ground | 105438.67 | -7.16 | 126.2 | 0 | 19.98 | 0 | OK | Ground clear controls. | 237 | 31.77 | 146.18
16492 | TIN-INTERP | Interpolated Ground | 105438.75 | -6.47 | 126.5 | 0 | 31.77 | 0 | OK | Ground clear controls. | 237 | 31.77 | 158.27
16493 | TIN-INTERP | Interpolated Ground | 105439.8 | 5.31 | 129.1 | 0 | 29.03 | 0 | OK | Ground clear controls. | 237 | 29.84 | 158.13
16494 | TIN-INTERP | Interpolated Ground | 105439.81 | 6.01 | 128.94 | 0 | 17.22 | 0 | OK | Ground clear controls. | 237 | 29.84 | 146.16
16495 | TIN-INTERP | Interpolated Ground | 105439.85 | 7.5 | 128.64 | 0 | 23.16 | 0 | OK | Ground clear controls. | 237 | 29.84 | 151.8
16496 | TIN-INTERP | Interpolated Ground | 105478.5 | -8.95 | 142 | 0 | 16.88 | 0 | OK | Ground clear controls. | 237 | 29.84 | 158.88
16497 | TIN-INTERP | Interpolated Ground | 105478.67 | -7.46 | 141.52 | 0 | 11.66 | 0 | OK | Ground clear controls. | 237 | 29.84 | 153.18
16498 | TIN-INTERP | Interpolated Ground | 105478.75 | -6.76 | 141.29 | 0 | 23.99 | 0 | OK | Ground clear controls. | 237 | 29.84 | 165.28
16499 | TIN-INTERP | Interpolated Ground | 105479.8 | 5.04 | 135.34 | 0 | 29.84 | 0 | OK | Ground clear controls. | 237 | 29.84 | 165.18
16500 | TIN-INTERP | Interpolated Ground | 105479.81 | 5.74 | 135.04 | 0 | 18.1 | 0 | OK | Ground clear controls. | 237 | 28.97 | 153.14
16501 | TIN-INTERP | Interpolated Ground | 105479.85 | 7.23 | 134.32 | 0 | 24.52 | 0 | OK | Ground clear controls. | 237 | 28.97 | 158.84
16502 | TIN-INTERP | Interpolated Ground | 105518.5 | -9.23 | 143.53 | 0 | 23.44 | 0 | OK | Ground clear controls. | 237 | 28.97 | 166.97
16503 | TIN-INTERP | Interpolated Ground | 105518.67 | -7.75 | 144.06 | 0 | 17.12 | 0 | OK | Ground clear controls. | 237 | 28.97 | 161.18
16504 | TIN-INTERP | Interpolated Ground | 105518.75 | -7.04 | 144.32 | 0 | 28.97 | 0 | OK | Ground clear controls. | 237 | 28.97 | 173.29
16505 | TIN-INTERP | Interpolated Ground | 105519.79 | 4.78 | 146.18 | 0 | 27.05 | 0 | OK | Ground clear controls. | 237 | 27.05 | 173.23
16506 | TIN-INTERP | Interpolated Ground | 105519.81 | 5.47 | 146.18 | 0 | 14.94 | 0 | OK | Ground clear controls. | 237 | 20.87 | 161.12
16507 | TIN-INTERP | Interpolated Ground | 105519.85 | 6.97 | 146.02 | 0 | 20.87 | 0 | OK | Ground clear controls. | 237 | 20.87 | 166.89
16508 | TIN-INTERP | Interpolated Ground | 105520.81 | -9.24 | 143.05 | 0 | 24.42 | 0 | OK | Ground clear controls. | 238 | 58.41 | 167.47
16509 | TIN-INTERP | Interpolated Ground | 105521 | -7.77 | 143.66 | 0 | 18.02 | 0 | OK | Ground clear controls. | 238 | 58.41 | 161.68
16510 | TIN-INTERP | Interpolated Ground | 105521.02 | -7.06 | 143.89 | 0 | 29.88 | 0 | OK | Ground clear controls. | 238 | 58.41 | 173.77
16511 | TIN-INTERP | Interpolated Ground | 105522.02 | 4.78 | 146.03 | 0 | 27.74 | 0 | OK | Ground clear controls. | 238 | 58.41 | 173.77
16512 | TIN-INTERP | Interpolated Ground | 105522.02 | 5.47 | 146.07 | 0 | 15.6 | 0 | OK | Ground clear controls. | 238 | 58.41 | 161.67
16513 | TIN-INTERP | Interpolated Ground | 105522.02 | 6.97 | 145.99 | 0 | 21.48 | 0 | OK | Ground clear controls. | 238 | 58.41 | 167.47
16514 | TIN-INTERP | Interpolated Ground | 105561.1 | 6.93 | 129.86 | 0 | 30.85 | 0 | OK | Ground clear controls. | 238 | 58.41 | 160.71
16515 | TIN-INTERP | Interpolated Ground | 105561.23 | 5.43 | 129.75 | 0 | 25.22 | 0 | OK | Ground clear controls. | 238 | 58.41 | 154.97
16516 | TIN-INTERP | Interpolated Ground | 105561.32 | 4.75 | 129.66 | 0 | 37.34 | 0 | OK | Ground clear controls. | 238 | 58.41 | 167
16517 | TIN-INTERP | Interpolated Ground | 105562.54 | -7.09 | 128.72 | 0 | 38.32 | 0 | OK | Ground clear controls. | 238 | 58.41 | 167.04
16518 | TIN-INTERP | Interpolated Ground | 105562.67 | -7.79 | 128.59 | 0 | 26.43 | 0 | OK | Ground clear controls. | 238 | 58.41 | 155.02
16519 | TIN-INTERP | Interpolated Ground | 105562.79 | -9.27 | 128.32 | 0 | 32.33 | 0 | OK | Ground clear controls. | 238 | 58.41 | 160.65
16520 | TIN-INTERP | Interpolated Ground | 105601.1 | 6.96 | 111.11 | 0 | 43.87 | 0 | OK | Ground clear controls. | 238 | 58.41 | 154.98
16521 | TIN-INTERP | Interpolated Ground | 105601.23 | 5.45 | 111.12 | 0 | 38.16 | 0 | OK | Ground clear controls. | 238 | 58.41 | 149.28
16522 | TIN-INTERP | Interpolated Ground | 105601.32 | 4.77 | 111.35 | 0 | 49.9 | 0 | OK | Ground clear controls. | 238 | 58.41 | 161.25
16523 | TIN-INTERP | Interpolated Ground | 105602.54 | -7.07 | 116.12 | 0 | 45.21 | 0 | OK | Ground clear controls. | 238 | 58.41 | 161.33
16524 | TIN-INTERP | Interpolated Ground | 105602.67 | -7.77 | 115.72 | 0 | 33.66 | 0 | OK | Ground clear controls. | 238 | 58.41 | 149.38
16525 | TIN-INTERP | Interpolated Ground | 105602.79 | -9.25 | 114.72 | 0 | 40.15 | 0 | OK | Ground clear controls. | 238 | 58.41 | 154.87
16526 | TIN-INTERP | Interpolated Ground | 105641.1 | 6.98 | 96.37 | 0 | 53.92 | 0 | OK | Ground clear controls. | 238 | 58.41 | 150.29
16527 | TIN-INTERP | Interpolated Ground | 105641.23 | 5.47 | 97.52 | 0 | 47.1 | 0 | OK | Ground clear controls. | 238 | 58.41 | 144.62
16528 | TIN-INTERP | Interpolated Ground | 105641.32 | 4.79 | 98.15 | 0 | 58.41 | 0 | OK | Ground clear controls. | 238 | 58.41 | 156.56
16529 | TIN-INTERP | Interpolated Ground | 105642.54 | -7.05 | 107.14 | 0 | 49.52 | 0 | OK | Ground clear controls. | 238 | 50 | 156.66
16530 | TIN-INTERP | Interpolated Ground | 105642.67 | -7.75 | 107.58 | 0 | 37.18 | 0 | OK | Ground clear controls. | 238 | 50 | 144.76
16531 | TIN-INTERP | Interpolated Ground | 105642.79 | -9.23 | 108.31 | 0 | 41.84 | 0 | OK | Ground clear controls. | 238 | 50 | 150.15
16532 | TIN-INTERP | Interpolated Ground | 105681.1 | 7 | 101.32 | 0 | 45.29 | 0 | OK | Ground clear controls. | 238 | 50 | 146.61
16533 | TIN-INTERP | Interpolated Ground | 105681.23 | 5.49 | 102.31 | 0 | 38.66 | 0 | OK | Ground clear controls. | 238 | 50 | 140.97
16534 | TIN-INTERP | Interpolated Ground | 105681.32 | 4.81 | 102.88 | 0 | 50 | 0 | OK | Ground clear controls. | 238 | 50 | 152.88
16535 | TIN-INTERP | Interpolated Ground | 105682.54 | -7.03 | 111.47 | 0 | 41.54 | 0 | OK | Ground clear controls. | 238 | 49.53 | 153.01
16536 | TIN-INTERP | Interpolated Ground | 105682.67 | -7.73 | 112.08 | 0 | 29.06 | 0 | OK | Ground clear controls. | 238 | 49.53 | 141.14
16537 | TIN-INTERP | Interpolated Ground | 105682.79 | -9.21 | 113.27 | 0 | 33.19 | 0 | OK | Ground clear controls. | 238 | 49.53 | 146.46
16538 | TIN-INTERP | Interpolated Ground | 105721.1 | 7.02 | 105.98 | 0 | 37.99 | 0 | OK | Ground clear controls. | 238 | 49.53 | 143.97
16539 | TIN-INTERP | Interpolated Ground | 105721.23 | 5.51 | 107.11 | 0 | 31.24 | 0 | OK | Ground clear controls. | 238 | 49.53 | 138.35
16540 | TIN-INTERP | Interpolated Ground | 105721.32 | 4.83 | 107.37 | 0 | 42.86 | 0 | OK | Ground clear controls. | 238 | 49.53 | 150.23
16541 | TIN-INTERP | Interpolated Ground | 105722.54 | -7.01 | 112.48 | 0 | 37.91 | 0 | OK | Ground clear controls. | 238 | 49.53 | 150.39
16542 | TIN-INTERP | Interpolated Ground | 105722.67 | -7.71 | 112.56 | 0 | 26 | 0 | OK | Ground clear controls. | 238 | 49.53 | 138.56
16543 | TIN-INTERP | Interpolated Ground | 105722.79 | -9.19 | 113.18 | 0 | 30.64 | 0 | OK | Ground clear controls. | 238 | 49.53 | 143.82
16544 | TIN-INTERP | Interpolated Ground | 105761.1 | 7.04 | 109.45 | 0 | 32.9 | 0 | OK | Ground clear controls. | 238 | 49.53 | 142.35
16545 | TIN-INTERP | Interpolated Ground | 105761.23 | 5.53 | 109.32 | 0 | 27.42 | 0 | OK | Ground clear controls. | 238 | 49.53 | 136.74
16546 | TIN-INTERP | Interpolated Ground | 105761.32 | 4.85 | 109.16 | 0 | 39.44 | 0 | OK | Ground clear controls. | 238 | 49.53 | 148.6
16547 | TIN-INTERP | Interpolated Ground | 105762.54 | -6.99 | 110.78 | 0 | 38.02 | 0 | OK | Ground clear controls. | 238 | 49.53 | 148.8
16548 | TIN-INTERP | Interpolated Ground | 105762.67 | -7.69 | 111.06 | 0 | 25.92 | 0 | OK | Ground clear controls. | 238 | 49.53 | 136.98
16549 | TIN-INTERP | Interpolated Ground | 105762.79 | -9.17 | 111.62 | 0 | 30.6 | 0 | OK | Ground clear controls. | 238 | 49.53 | 142.22
16550 | TIN-INTERP | Interpolated Ground | 105801.1 | 7.07 | 108.17 | 0 | 33.58 | 0 | OK | Ground clear controls. | 238 | 49.53 | 141.75
16551 | TIN-INTERP | Interpolated Ground | 105801.23 | 5.55 | 108.12 | 0 | 28.01 | 0 | OK | Ground clear controls. | 238 | 49.53 | 136.13
16552 | TIN-INTERP | Interpolated Ground | 105801.32 | 4.87 | 108.11 | 0 | 39.9 | 0 | OK | Ground clear controls. | 238 | 49.53 | 148.01
16553 | TIN-INTERP | Interpolated Ground | 105802.54 | -6.97 | 108.4 | 0 | 39.83 | 0 | OK | Ground clear controls. | 238 | 49.53 | 148.23
16554 | TIN-INTERP | Interpolated Ground | 105802.67 | -7.67 | 108.5 | 0 | 27.91 | 0 | OK | Ground clear controls. | 238 | 49.53 | 136.41
16555 | TIN-INTERP | Interpolated Ground | 105802.79 | -9.15 | 108.19 | 0 | 33.46 | 0 | OK | Ground clear controls. | 238 | 49.53 | 141.65
16556 | TIN-INTERP | Interpolated Ground | 105841.1 | 7.09 | 116.24 | 0 | 25.93 | 0 | OK | Ground clear controls. | 238 | 49.53 | 142.17
16557 | TIN-INTERP | Interpolated Ground | 105841.23 | 5.57 | 116.49 | 0 | 20.06 | 0 | OK | Ground clear controls. | 238 | 49.53 | 136.55
16558 | TIN-INTERP | Interpolated Ground | 105841.32 | 4.89 | 116.6 | 0 | 31.83 | 0 | OK | Ground clear controls. | 238 | 49.53 | 148.43
16559 | TIN-INTERP | Interpolated Ground | 105842.54 | -6.94 | 119.45 | 0 | 29.23 | 0 | OK | Ground clear controls. | 238 | 49.53 | 148.68
16560 | TIN-INTERP | Interpolated Ground | 105842.67 | -7.64 | 119.65 | 0 | 17.2 | 0 | OK | Ground clear controls. | 238 | 49.53 | 136.85
16561 | TIN-INTERP | Interpolated Ground | 105842.79 | -9.13 | 120.05 | 0 | 22.06 | 0 | OK | Ground clear controls. | 238 | 49.53 | 142.11
16562 | TIN-INTERP | Interpolated Ground | 105881.1 | 7.11 | 120.83 | 0 | 22.77 | 0 | OK | Ground clear controls. | 238 | 49.53 | 143.6
16563 | TIN-INTERP | Interpolated Ground | 105881.23 | 5.59 | 121.66 | 0 | 16.31 | 0 | OK | Ground clear controls. | 238 | 49.53 | 137.97
16564 | TIN-INTERP | Interpolated Ground | 105881.32 | 4.91 | 121.93 | 0 | 27.94 | 0 | OK | Ground clear controls. | 238 | 49.53 | 149.87
16565 | TIN-INTERP | Interpolated Ground | 105882.54 | -6.92 | 125.56 | 0 | 24.59 | 0 | OK | Ground clear controls. | 238 | 49.53 | 150.15
16566 | TIN-INTERP | Interpolated Ground | 105882.67 | -7.62 | 125.72 | 0 | 12.59 | 0 | OK | Ground clear controls. | 238 | 49.53 | 138.31
16567 | TIN-INTERP | Interpolated Ground | 105882.79 | -9.11 | 126.08 | 0 | 17.54 | 0 | OK | Ground clear controls. | 238 | 49.53 | 143.62
16568 | TIN-INTERP | Interpolated Ground | 105921.1 | 7.13 | 119.36 | 0 | 26.71 | 0 | OK | Ground clear controls. | 238 | 49.53 | 146.07
16569 | TIN-INTERP | Interpolated Ground | 105921.23 | 5.61 | 120.05 | 0 | 20.37 | 0 | OK | Ground clear controls. | 238 | 49.53 | 140.42
16570 | TIN-INTERP | Interpolated Ground | 105921.32 | 4.93 | 120.4 | 0 | 31.95 | 0 | OK | Ground clear controls. | 238 | 49.53 | 152.35
16571 | TIN-INTERP | Interpolated Ground | 105922.54 | -6.9 | 123.47 | 0 | 29.18 | 0 | OK | Ground clear controls. | 238 | 49.53 | 152.65
16572 | TIN-INTERP | Interpolated Ground | 105922.67 | -7.6 | 123.5 | 0 | 17.27 | 0 | OK | Ground clear controls. | 238 | 49.53 | 140.77
16573 | TIN-INTERP | Interpolated Ground | 105922.79 | -9.09 | 123.62 | 0 | 22.54 | 0 | OK | Ground clear controls. | 238 | 49.53 | 146.16
16574 | TIN-INTERP | Interpolated Ground | 105961.1 | 7.15 | 112.03 | 0 | 37.53 | 0 | OK | Ground clear controls. | 238 | 49.53 | 149.56
16575 | TIN-INTERP | Interpolated Ground | 105961.23 | 5.64 | 112.23 | 0 | 31.65 | 0 | OK | Ground clear controls. | 238 | 49.53 | 143.88
16576 | TIN-INTERP | Interpolated Ground | 105961.32 | 4.95 | 112.37 | 0 | 43.48 | 0 | OK | Ground clear controls. | 238 | 49.53 | 155.85
16577 | TIN-INTERP | Interpolated Ground | 105962.54 | -6.88 | 115.49 | 0 | 40.68 | 0 | OK | Ground clear controls. | 238 | 49.53 | 156.17
16578 | TIN-INTERP | Interpolated Ground | 105962.67 | -7.58 | 115.68 | 0 | 28.57 | 0 | OK | Ground clear controls. | 238 | 49.53 | 144.25
16579 | TIN-INTERP | Interpolated Ground | 105962.79 | -9.07 | 116.06 | 0 | 33.68 | 0 | OK | Ground clear controls. | 238 | 49.53 | 149.74
16580 | TIN-INTERP | Interpolated Ground | 106001.1 | 7.18 | 110.45 | 0 | 43.63 | 0 | OK | Ground clear controls. | 238 | 49.53 | 154.08
16581 | TIN-INTERP | Interpolated Ground | 106001.23 | 5.66 | 110.76 | 0 | 37.59 | 0 | OK | Ground clear controls. | 238 | 49.53 | 148.35
16582 | TIN-INTERP | Interpolated Ground | 106001.32 | 4.98 | 110.87 | 0 | 49.53 | 0 | OK | Ground clear controls. | 238 | 49.53 | 160.4
16583 | TIN-INTERP | Interpolated Ground | 106002.54 | -6.86 | 113.89 | 0 | 46.83 | 0 | OK | Ground clear controls. | 238 | 46.83 | 160.72
16584 | TIN-INTERP | Interpolated Ground | 106002.67 | -7.56 | 114.08 | 0 | 34.66 | 0 | OK | Ground clear controls. | 238 | 43.92 | 148.74
16585 | TIN-INTERP | Interpolated Ground | 106002.79 | -9.05 | 114.38 | 0 | 39.99 | 0 | OK | Ground clear controls. | 238 | 43.92 | 154.37
16586 | TIN-INTERP | Interpolated Ground | 106041.1 | 7.2 | 121.34 | 0 | 38.29 | 0 | OK | Ground clear controls. | 238 | 43.92 | 159.63
16587 | TIN-INTERP | Interpolated Ground | 106041.23 | 5.68 | 121.87 | 0 | 31.97 | 0 | OK | Ground clear controls. | 238 | 43.92 | 153.84
16588 | TIN-INTERP | Interpolated Ground | 106041.32 | 5 | 122.04 | 0 | 43.92 | 0 | OK | Ground clear controls. | 238 | 43.92 | 165.96
16589 | TIN-INTERP | Interpolated Ground | 106042.54 | -6.84 | 125.36 | 0 | 40.95 | 0 | OK | Ground clear controls. | 238 | 40.95 | 166.31
16590 | TIN-INTERP | Interpolated Ground | 106042.67 | -7.54 | 125.55 | 0 | 28.71 | 0 | OK | Ground clear controls. | 238 | 34.41 | 154.26
16591 | TIN-INTERP | Interpolated Ground | 106042.79 | -9.03 | 125.63 | 0 | 34.41 | 0 | OK | Ground clear controls. | 238 | 34.41 | 160.04
16592 | TIN-INTERP | Interpolated Ground | 106050.26 | -9.03 | 126.11 | 0 | 35.11 | 0 | OK | Ground clear controls. | 239 | 61.65 | 161.22
16593 | TIN-INTERP | Interpolated Ground | 106050.29 | -7.54 | 126.08 | 0 | 29.34 | 0 | OK | Ground clear controls. | 239 | 61.65 | 155.42
16594 | TIN-INTERP | Interpolated Ground | 106050.36 | -6.83 | 126.06 | 0 | 41.46 | 0 | OK | Ground clear controls. | 239 | 61.65 | 167.52
16595 | TIN-INTERP | Interpolated Ground | 106051.03 | 5.02 | 123.46 | 0 | 44.06 | 0 | OK | Ground clear controls. | 239 | 61.65 | 167.52
16596 | TIN-INTERP | Interpolated Ground | 106051.03 | 5.7 | 123.38 | 0 | 32.04 | 0 | OK | Ground clear controls. | 239 | 61.65 | 155.42
16597 | TIN-INTERP | Interpolated Ground | 106051.03 | 7.22 | 123.13 | 0 | 38.1 | 0 | OK | Ground clear controls. | 239 | 61.65 | 161.23
16598 | TIN-INTERP | Interpolated Ground | 106090.42 | 7.17 | 109.76 | 0 | 40.71 | 0 | OK | Ground clear controls. | 239 | 61.65 | 150.47
16599 | TIN-INTERP | Interpolated Ground | 106090.69 | 5.01 | 109.74 | 0 | 47.14 | 0 | OK | Ground clear controls. | 239 | 61.65 | 156.88
16600 | TIN-INTERP | Interpolated Ground | 106090.7 | 5.68 | 109.74 | 0 | 35.24 | 0 | OK | Ground clear controls. | 239 | 61.65 | 144.98
16601 | TIN-INTERP | Interpolated Ground | 106091.36 | -6.72 | 107.65 | 0 | 49.12 | 0 | OK | Ground clear controls. | 239 | 61.65 | 156.77
16602 | TIN-INTERP | Interpolated Ground | 106091.39 | -7.41 | 107.72 | 0 | 37.09 | 0 | OK | Ground clear controls. | 239 | 61.65 | 144.81
16603 | TIN-INTERP | Interpolated Ground | 106091.58 | -8.89 | 107.64 | 0 | 42.88 | 0 | OK | Ground clear controls. | 239 | 61.65 | 150.52
16604 | TIN-INTERP | Interpolated Ground | 106130.42 | 7.16 | 100.14 | 0 | 40.67 | 0 | OK | Ground clear controls. | 239 | 61.65 | 140.81
16605 | TIN-INTERP | Interpolated Ground | 106130.69 | 5.01 | 99.11 | 0 | 48.18 | 0 | OK | Ground clear controls. | 239 | 61.65 | 147.29
16606 | TIN-INTERP | Interpolated Ground | 106130.7 | 5.66 | 99.29 | 0 | 36.3 | 0 | OK | Ground clear controls. | 239 | 61.65 | 135.59
16607 | TIN-INTERP | Interpolated Ground | 106131.36 | -6.59 | 98.52 | 0 | 48.59 | 0 | OK | Ground clear controls. | 239 | 61.65 | 147.11
16608 | TIN-INTERP | Interpolated Ground | 106131.39 | -7.25 | 98.69 | 0 | 36.56 | 0 | OK | Ground clear controls. | 239 | 61.65 | 135.25
16609 | TIN-INTERP | Interpolated Ground | 106131.58 | -8.74 | 99.06 | 0 | 41.84 | 0 | OK | Ground clear controls. | 239 | 61.65 | 140.9
16610 | TIN-INTERP | Interpolated Ground | 106170.42 | 7.14 | 90.62 | 0 | 41.59 | 0 | OK | Ground clear controls. | 239 | 61.65 | 132.21
16611 | TIN-INTERP | Interpolated Ground | 106170.69 | 5.01 | 92.08 | 0 | 46.68 | 0 | OK | Ground clear controls. | 239 | 61.65 | 138.76
16612 | TIN-INTERP | Interpolated Ground | 106170.7 | 5.64 | 91.42 | 0 | 35.79 | 0 | OK | Ground clear controls. | 239 | 61.65 | 127.21
16613 | TIN-INTERP | Interpolated Ground | 106171.36 | -6.45 | 96.63 | 0 | 41.88 | 0 | OK | Ground clear controls. | 239 | 61.65 | 138.51
16614 | TIN-INTERP | Interpolated Ground | 106171.39 | -7.1 | 96.89 | 0 | 29.87 | 0 | OK | Ground clear controls. | 239 | 61.65 | 126.76
16615 | TIN-INTERP | Interpolated Ground | 106171.58 | -8.58 | 97.76 | 0 | 34.58 | 0 | OK | Ground clear controls. | 239 | 61.65 | 132.34
16616 | TIN-INTERP | Interpolated Ground | 106210.42 | 7.12 | 92.32 | 0 | 32.37 | 0 | OK | Ground clear controls. | 239 | 61.65 | 124.69
16617 | TIN-INTERP | Interpolated Ground | 106210.69 | 5.01 | 92.43 | 0 | 38.85 | 0 | OK | Ground clear controls. | 239 | 61.65 | 131.28
16618 | TIN-INTERP | Interpolated Ground | 106210.7 | 5.62 | 92.4 | 0 | 27.47 | 0 | OK | Ground clear controls. | 239 | 61.65 | 119.87
16619 | TIN-INTERP | Interpolated Ground | 106211.36 | -6.32 | 94.03 | 0 | 36.94 | 0 | OK | Ground clear controls. | 239 | 61.65 | 130.97
16620 | TIN-INTERP | Interpolated Ground | 106211.39 | -6.94 | 94.1 | 0 | 25.23 | 0 | OK | Ground clear controls. | 239 | 61.65 | 119.33
16621 | TIN-INTERP | Interpolated Ground | 106211.58 | -8.43 | 94.35 | 0 | 30.5 | 0 | OK | Ground clear controls. | 239 | 61.65 | 124.85
16622 | TIN-INTERP | Interpolated Ground | 106250.42 | 7.11 | 89 | 0 | 29.23 | 0 | OK | Ground clear controls. | 239 | 61.65 | 118.23
16623 | TIN-INTERP | Interpolated Ground | 106250.69 | 5.01 | 89.12 | 0 | 35.73 | 0 | OK | Ground clear controls. | 239 | 61.65 | 124.85
16624 | TIN-INTERP | Interpolated Ground | 106250.7 | 5.61 | 89.07 | 0 | 24.47 | 0 | OK | Ground clear controls. | 239 | 61.65 | 113.54
16625 | TIN-INTERP | Interpolated Ground | 106251.36 | -6.18 | 89.81 | 0 | 34.68 | 0 | OK | Ground clear controls. | 239 | 61.65 | 124.49
16626 | TIN-INTERP | Interpolated Ground | 106251.39 | -6.79 | 89.87 | 0 | 23.06 | 0 | OK | Ground clear controls. | 239 | 61.65 | 112.93
16627 | TIN-INTERP | Interpolated Ground | 106251.58 | -8.27 | 89.91 | 0 | 28.5 | 0 | OK | Ground clear controls. | 239 | 61.65 | 118.41
16628 | TIN-INTERP | Interpolated Ground | 106290.42 | 7.09 | 84.06 | 0 | 28.77 | 0 | OK | Ground clear controls. | 239 | 61.65 | 112.83
16629 | TIN-INTERP | Interpolated Ground | 106290.69 | 5.02 | 84.06 | 0 | 35.4 | 0 | OK | Ground clear controls. | 239 | 61.65 | 119.46
16630 | TIN-INTERP | Interpolated Ground | 106290.7 | 5.59 | 84.01 | 0 | 24.23 | 0 | OK | Ground clear controls. | 239 | 61.65 | 108.24
16631 | TIN-INTERP | Interpolated Ground | 106291.36 | -6.05 | 84.16 | 0 | 34.93 | 0 | OK | Ground clear controls. | 239 | 61.65 | 119.09
16632 | TIN-INTERP | Interpolated Ground | 106291.39 | -6.63 | 84.14 | 0 | 23.45 | 0 | OK | Ground clear controls. | 239 | 61.65 | 107.59
16633 | TIN-INTERP | Interpolated Ground | 106291.58 | -8.12 | 84.18 | 0 | 28.86 | 0 | OK | Ground clear controls. | 239 | 61.65 | 113.04
16634 | TIN-INTERP | Interpolated Ground | 106330.42 | 7.07 | 80.31 | 0 | 28.19 | 0 | OK | Ground clear controls. | 239 | 61.65 | 108.5
16635 | TIN-INTERP | Interpolated Ground | 106330.69 | 5.02 | 80.79 | 0 | 34.32 | 0 | OK | Ground clear controls. | 239 | 61.65 | 115.11
16636 | TIN-INTERP | Interpolated Ground | 106330.7 | 5.57 | 80.6 | 0 | 23.37 | 0 | OK | Ground clear controls. | 239 | 61.65 | 103.97
16637 | TIN-INTERP | Interpolated Ground | 106331.36 | -5.92 | 81.27 | 0 | 33.46 | 0 | OK | Ground clear controls. | 239 | 61.65 | 114.73
16638 | TIN-INTERP | Interpolated Ground | 106331.39 | -6.48 | 81.23 | 0 | 22.06 | 0 | OK | Ground clear controls. | 239 | 61.65 | 103.29
16639 | TIN-INTERP | Interpolated Ground | 106331.58 | -7.97 | 81.01 | 0 | 27.71 | 0 | OK | Ground clear controls. | 239 | 61.65 | 108.72
16640 | TIN-INTERP | Interpolated Ground | 106370.42 | 7.05 | 49.99 | 0 | 55.22 | 0 | OK | Ground clear controls. | 239 | 61.65 | 105.21
16641 | TIN-INTERP | Interpolated Ground | 106370.69 | 5.02 | 50.14 | 0 | 61.65 | 0 | OK | Ground clear controls. | 239 | 61.65 | 111.79
16642 | TIN-INTERP | Interpolated Ground | 106370.7 | 5.55 | 50.12 | 0 | 50.57 | 0 | OK | Ground clear controls. | 239 | 60.67 | 100.69
16643 | TIN-INTERP | Interpolated Ground | 106371.36 | -5.78 | 50.75 | 0 | 60.67 | 0 | OK | Ground clear controls. | 239 | 60.67 | 111.42
16644 | TIN-INTERP | Interpolated Ground | 106371.39 | -6.32 | 50.95 | 0 | 49.08 | 0 | OK | Ground clear controls. | 239 | 58.02 | 100.03
16645 | TIN-INTERP | Interpolated Ground | 106371.58 | -7.81 | 51.19 | 0 | 54.26 | 0 | OK | Ground clear controls. | 239 | 58.02 | 105.45
16646 | TIN-INTERP | Interpolated Ground | 106410.42 | 7.04 | 51.48 | 0 | 51.51 | 0 | OK | Ground clear controls. | 239 | 58.02 | 102.99
16647 | TIN-INTERP | Interpolated Ground | 106410.69 | 5.02 | 51.49 | 0 | 58.02 | 0 | OK | Ground clear controls. | 239 | 58.02 | 109.51
16648 | TIN-INTERP | Interpolated Ground | 106410.7 | 5.54 | 51.53 | 0 | 46.9 | 0 | OK | Ground clear controls. | 239 | 57.85 | 98.43
16649 | TIN-INTERP | Interpolated Ground | 106411.36 | -5.65 | 51.31 | 0 | 57.85 | 0 | OK | Ground clear controls. | 239 | 57.85 | 109.16
16650 | TIN-INTERP | Interpolated Ground | 106411.39 | -6.17 | 51.32 | 0 | 46.5 | 0 | OK | Ground clear controls. | 239 | 55.41 | 97.82
16651 | TIN-INTERP | Interpolated Ground | 106411.58 | -7.66 | 51.2 | 0 | 52.02 | 0 | OK | Ground clear controls. | 239 | 55.41 | 103.22
16652 | TIN-INTERP | Interpolated Ground | 106450.42 | 7.02 | 52.9 | 0 | 48.92 | 0 | OK | Ground clear controls. | 239 | 55.41 | 101.82
16653 | TIN-INTERP | Interpolated Ground | 106450.69 | 5.03 | 52.84 | 0 | 55.41 | 0 | OK | Ground clear controls. | 239 | 55.41 | 108.25
16654 | TIN-INTERP | Interpolated Ground | 106450.7 | 5.52 | 52.86 | 0 | 44.32 | 0 | OK | Ground clear controls. | 239 | 55.08 | 97.18
16655 | TIN-INTERP | Interpolated Ground | 106451.36 | -5.51 | 52.86 | 0 | 55.08 | 0 | OK | Ground clear controls. | 239 | 55.08 | 107.94
16656 | TIN-INTERP | Interpolated Ground | 106451.39 | -6.01 | 52.89 | 0 | 43.74 | 0 | OK | Ground clear controls. | 239 | 49.08 | 96.63
16657 | TIN-INTERP | Interpolated Ground | 106451.58 | -7.5 | 52.96 | 0 | 49.08 | 0 | OK | Ground clear controls. | 239 | 49.08 | 102.04
16658 | TIN-INTERP | Interpolated Ground | 106490.42 | 7 | 65.42 | 0 | 36.27 | 0 | OK | Ground clear controls. | 239 | 42.23 | 101.69
16659 | TIN-INTERP | Interpolated Ground | 106490.69 | 5.03 | 65.8 | 0 | 42.23 | 0 | OK | Ground clear controls. | 239 | 42.23 | 108.03
16660 | TIN-INTERP | Interpolated Ground | 106490.7 | 5.5 | 65.74 | 0 | 31.2 | 0 | OK | Ground clear controls. | 239 | 39.67 | 96.94
16661 | TIN-INTERP | Interpolated Ground | 106491.36 | -5.38 | 68.1 | 0 | 39.67 | 0 | OK | Ground clear controls. | 239 | 39.67 | 107.77
16662 | TIN-INTERP | Interpolated Ground | 106491.39 | -5.86 | 68.14 | 0 | 28.34 | 0 | OK | Ground clear controls. | 239 | 34.09 | 96.48
16663 | TIN-INTERP | Interpolated Ground | 106491.58 | -7.35 | 68.35 | 0 | 33.55 | 0 | OK | Ground clear controls. | 239 | 34.09 | 101.9
16664 | TIN-INTERP | Interpolated Ground | 106530.42 | 6.99 | 75.01 | 0 | 27.61 | 0 | OK | Ground clear controls. | 239 | 34.09 | 102.62
16665 | TIN-INTERP | Interpolated Ground | 106530.69 | 5.03 | 75.17 | 0 | 33.67 | 0 | OK | Ground clear controls. | 239 | 34.09 | 108.84
16666 | TIN-INTERP | Interpolated Ground | 106530.7 | 5.49 | 75.12 | 0 | 22.58 | 0 | OK | Ground clear controls. | 239 | 34.09 | 97.7
16667 | TIN-INTERP | Interpolated Ground | 106531.35 | -5.24 | 76.39 | 0 | 32.26 | 0 | OK | Ground clear controls. | 239 | 34.09 | 108.65
16668 | TIN-INTERP | Interpolated Ground | 106531.39 | -5.7 | 76.44 | 0 | 20.92 | 0 | OK | Ground clear controls. | 239 | 34.09 | 97.36
16669 | TIN-INTERP | Interpolated Ground | 106531.58 | -7.2 | 76.6 | 0 | 26.2 | 0 | OK | Ground clear controls. | 239 | 34.09 | 102.8
16670 | TIN-INTERP | Interpolated Ground | 106570.42 | 6.97 | 78.34 | 0 | 26.25 | 0 | OK | Ground clear controls. | 239 | 34.09 | 104.59
16671 | TIN-INTERP | Interpolated Ground | 106570.69 | 5.03 | 78.41 | 0 | 32.25 | 0 | OK | Ground clear controls. | 239 | 34.09 | 110.66
16672 | TIN-INTERP | Interpolated Ground | 106570.7 | 5.47 | 78.38 | 0 | 21.09 | 0 | OK | Ground clear controls. | 239 | 34.09 | 99.47
16673 | TIN-INTERP | Interpolated Ground | 106571.35 | -5.11 | 78.68 | 0 | 31.89 | 0 | OK | Ground clear controls. | 239 | 34.09 | 110.57
16674 | TIN-INTERP | Interpolated Ground | 106571.39 | -5.54 | 78.67 | 0 | 20.62 | 0 | OK | Ground clear controls. | 239 | 34.09 | 99.29
16675 | TIN-INTERP | Interpolated Ground | 106571.58 | -7.04 | 78.7 | 0 | 26.06 | 0 | OK | Ground clear controls. | 239 | 34.09 | 104.76
16676 | TIN-INTERP | Interpolated Ground | 106610.42 | 6.95 | 79.28 | 0 | 28.33 | 0 | OK | Ground clear controls. | 239 | 34.09 | 107.61
16677 | TIN-INTERP | Interpolated Ground | 106610.69 | 5.03 | 79.44 | 0 | 34.09 | 0 | OK | Ground clear controls. | 239 | 34.09 | 113.53
16678 | TIN-INTERP | Interpolated Ground | 106610.7 | 5.45 | 79.43 | 0 | 22.83 | 0 | OK | Ground clear controls. | 239 | 33.66 | 102.26
16679 | TIN-INTERP | Interpolated Ground | 106611.35 | -4.97 | 79.87 | 0 | 33.66 | 0 | OK | Ground clear controls. | 239 | 33.66 | 113.53
16680 | TIN-INTERP | Interpolated Ground | 106611.39 | -5.39 | 79.89 | 0 | 22.36 | 0 | OK | Ground clear controls. | 239 | 27.82 | 102.25
16681 | TIN-INTERP | Interpolated Ground | 106611.58 | -6.89 | 79.93 | 0 | 27.82 | 0 | OK | Ground clear controls. | 239 | 27.82 | 107.75
16682 | TIN-INTERP | Interpolated Ground | 106622.05 | 5.03 | 79.61 | 0 | 34.92 | 0 | OK | Ground clear controls. | 240 | 55.76 | 114.53
16683 | TIN-INTERP | Interpolated Ground | 106622.08 | 5.45 | 79.62 | 0 | 23.61 | 0 | OK | Ground clear controls. | 240 | 55.76 | 103.23
16684 | TIN-INTERP | Interpolated Ground | 106622.17 | -5.35 | 79.83 | 0 | 23.38 | 0 | OK | Ground clear controls. | 240 | 55.76 | 103.21
16685 | TIN-INTERP | Interpolated Ground | 106622.18 | -4.93 | 79.82 | 0 | 34.69 | 0 | OK | Ground clear controls. | 240 | 55.76 | 114.51
16686 | TIN-INTERP | Interpolated Ground | 106622.2 | -6.85 | 79.78 | 0 | 28.93 | 0 | OK | Ground clear controls. | 240 | 55.76 | 108.71
16687 | TIN-INTERP | Interpolated Ground | 106622.28 | 6.95 | 79.49 | 0 | 29.22 | 0 | OK | Ground clear controls. | 240 | 55.76 | 108.71
16688 | TIN-INTERP | Interpolated Ground | 106662.06 | 4.91 | 63.84 | 0 | 47.81 | 0 | OK | Ground clear controls. | 240 | 55.76 | 111.65
16689 | TIN-INTERP | Interpolated Ground | 106662.08 | 5.35 | 64.17 | 0 | 36.3 | 0 | OK | Ground clear controls. | 240 | 55.76 | 100.47
16690 | TIN-INTERP | Interpolated Ground | 106662.17 | -5.25 | 59.69 | 0 | 40.73 | 0 | OK | Ground clear controls. | 240 | 55.76 | 100.42
16691 | TIN-INTERP | Interpolated Ground | 106662.18 | -4.82 | 59.64 | 0 | 52 | 0 | OK | Ground clear controls. | 240 | 55.76 | 111.64
16692 | TIN-INTERP | Interpolated Ground | 106662.2 | -6.75 | 59.69 | 0 | 46.21 | 0 | OK | Ground clear controls. | 240 | 55.76 | 105.9
16693 | TIN-INTERP | Interpolated Ground | 106662.28 | 6.85 | 65.07 | 0 | 40.8 | 0 | OK | Ground clear controls. | 240 | 55.76 | 105.87
16694 | TIN-INTERP | Interpolated Ground | 106702.06 | 4.8 | 54.07 | 0 | 55.76 | 0 | OK | Ground clear controls. | 240 | 55.76 | 109.83
16695 | TIN-INTERP | Interpolated Ground | 106702.08 | 5.25 | 53.94 | 0 | 44.81 | 0 | OK | Ground clear controls. | 240 | 54.86 | 98.75
16696 | TIN-INTERP | Interpolated Ground | 106702.17 | -5.16 | 54.96 | 0 | 43.71 | 0 | OK | Ground clear controls. | 240 | 54.86 | 98.67
16697 | TIN-INTERP | Interpolated Ground | 106702.17 | -4.71 | 54.96 | 0 | 54.86 | 0 | OK | Ground clear controls. | 240 | 54.86 | 109.82
16698 | TIN-INTERP | Interpolated Ground | 106702.2 | -6.66 | 55.05 | 0 | 49.09 | 0 | OK | Ground clear controls. | 240 | 49.9 | 104.14
16699 | TIN-INTERP | Interpolated Ground | 106702.28 | 6.75 | 54.18 | 0 | 49.9 | 0 | OK | Ground clear controls. | 240 | 49.9 | 104.08
16700 | TIN-INTERP | Interpolated Ground | 106742.06 | 4.68 | 63.01 | 0 | 46.05 | 0 | OK | Ground clear controls. | 240 | 46.05 | 109.06
16701 | TIN-INTERP | Interpolated Ground | 106742.08 | 5.15 | 62.89 | 0 | 35.16 | 0 | OK | Ground clear controls. | 240 | 44 | 98.05
16702 | TIN-INTERP | Interpolated Ground | 106742.17 | -5.06 | 65.08 | 0 | 32.89 | 0 | OK | Ground clear controls. | 240 | 44 | 97.97
16703 | TIN-INTERP | Interpolated Ground | 106742.17 | -4.6 | 65.06 | 0 | 44 | 0 | OK | Ground clear controls. | 240 | 44 | 109.06
16704 | TIN-INTERP | Interpolated Ground | 106742.2 | -6.56 | 65.23 | 0 | 38.2 | 0 | OK | Ground clear controls. | 240 | 43.81 | 103.43
16705 | TIN-INTERP | Interpolated Ground | 106742.28 | 6.65 | 62.57 | 0 | 40.79 | 0 | OK | Ground clear controls. | 240 | 43.81 | 103.36
16706 | TIN-INTERP | Interpolated Ground | 106782.06 | 4.56 | 65.53 | 0 | 43.81 | 0 | OK | Ground clear controls. | 240 | 43.81 | 109.34
16707 | TIN-INTERP | Interpolated Ground | 106782.08 | 5.05 | 65.25 | 0 | 33.14 | 0 | OK | Ground clear controls. | 240 | 39.64 | 98.39
16708 | TIN-INTERP | Interpolated Ground | 106782.17 | -4.97 | 69.9 | 0 | 28.41 | 0 | OK | Ground clear controls. | 240 | 39.64 | 98.31
16709 | TIN-INTERP | Interpolated Ground | 106782.17 | -4.48 | 69.72 | 0 | 39.64 | 0 | OK | Ground clear controls. | 240 | 39.64 | 109.36
16710 | TIN-INTERP | Interpolated Ground | 106782.2 | -6.47 | 70.54 | 0 | 33.23 | 0 | OK | Ground clear controls. | 240 | 39.42 | 103.77
16711 | TIN-INTERP | Interpolated Ground | 106782.28 | 6.55 | 64.28 | 0 | 39.42 | 0 | OK | Ground clear controls. | 240 | 39.42 | 103.7
16712 | TIN-INTERP | Interpolated Ground | 106822.06 | 4.44 | 72.33 | 0 | 38.36 | 0 | OK | Ground clear controls. | 240 | 39.04 | 110.69
16713 | TIN-INTERP | Interpolated Ground | 106822.08 | 4.95 | 72.31 | 0 | 27.45 | 0 | OK | Ground clear controls. | 240 | 39.04 | 99.76
16714 | TIN-INTERP | Interpolated Ground | 106822.17 | -4.87 | 71.47 | 0 | 28.23 | 0 | OK | Ground clear controls. | 240 | 39.04 | 99.7
16715 | TIN-INTERP | Interpolated Ground | 106822.17 | -4.37 | 71.67 | 0 | 39.04 | 0 | OK | Ground clear controls. | 240 | 39.04 | 110.71
16716 | TIN-INTERP | Interpolated Ground | 106822.2 | -6.38 | 70.82 | 0 | 34.34 | 0 | OK | Ground clear controls. | 240 | 38.67 | 105.16
16717 | TIN-INTERP | Interpolated Ground | 106822.28 | 6.45 | 72.3 | 0 | 32.8 | 0 | OK | Ground clear controls. | 240 | 38.67 | 105.1
16718 | TIN-INTERP | Interpolated Ground | 106862.05 | 4.32 | 74.63 | 0 | 38.46 | 0 | OK | Ground clear controls. | 240 | 38.67 | 113.09
16719 | TIN-INTERP | Interpolated Ground | 106862.08 | 4.85 | 74.47 | 0 | 27.7 | 0 | OK | Ground clear controls. | 240 | 38.67 | 102.17
16720 | TIN-INTERP | Interpolated Ground | 106862.17 | -4.78 | 78.48 | 0 | 23.66 | 0 | OK | Ground clear controls. | 240 | 38.67 | 102.14
16721 | TIN-INTERP | Interpolated Ground | 106862.17 | -4.26 | 78.37 | 0 | 34.75 | 0 | OK | Ground clear controls. | 240 | 38.67 | 113.12
16722 | TIN-INTERP | Interpolated Ground | 106862.2 | -6.28 | 78.84 | 0 | 28.77 | 0 | OK | Ground clear controls. | 240 | 38.67 | 107.61
16723 | TIN-INTERP | Interpolated Ground | 106862.28 | 6.35 | 74.38 | 0 | 33.18 | 0 | OK | Ground clear controls. | 240 | 38.67 | 107.56
16724 | TIN-INTERP | Interpolated Ground | 106902.05 | 4.2 | 77.89 | 0 | 38.67 | 0 | OK | Ground clear controls. | 240 | 38.67 | 116.56
16725 | TIN-INTERP | Interpolated Ground | 106902.08 | 4.75 | 77.87 | 0 | 27.73 | 0 | OK | Ground clear controls. | 240 | 38.1 | 105.6
16726 | TIN-INTERP | Interpolated Ground | 106902.17 | -4.68 | 78.49 | 0 | 27.13 | 0 | OK | Ground clear controls. | 240 | 38.1 | 105.62
16727 | TIN-INTERP | Interpolated Ground | 106902.17 | -4.15 | 78.49 | 0 | 38.1 | 0 | OK | Ground clear controls. | 240 | 38.1 | 116.59
16728 | TIN-INTERP | Interpolated Ground | 106902.2 | -6.19 | 78.45 | 0 | 32.66 | 0 | OK | Ground clear controls. | 240 | 33.41 | 111.11
16729 | TIN-INTERP | Interpolated Ground | 106902.28 | 6.25 | 77.67 | 0 | 33.41 | 0 | OK | Ground clear controls. | 240 | 33.41 | 111.08
16730 | TIN-INTERP | Interpolated Ground | 106914.74 | -4.18 | 79.18 | 0 | 38.21 | 0 | OK | Ground clear controls. | 241 | 38.4 | 117.39
16731 | TIN-INTERP | Interpolated Ground | 106914.77 | 4.14 | 78.99 | 0 | 38.4 | 0 | OK | Ground clear controls. | 241 | 38.4 | 117.39
16732 | TIN-INTERP | Interpolated Ground | 106914.92 | -6.23 | 79.14 | 0 | 32.74 | 0 | OK | Ground clear controls. | 241 | 37.88 | 111.88
16733 | TIN-INTERP | Interpolated Ground | 106914.94 | 6.19 | 79.15 | 0 | 32.73 | 0 | OK | Ground clear controls. | 241 | 37.88 | 111.88
16734 | TIN-INTERP | Interpolated Ground | 106914.97 | 4.69 | 78.92 | 0 | 27.45 | 0 | OK | Ground clear controls. | 241 | 37.88 | 106.37
16735 | TIN-INTERP | Interpolated Ground | 106915.03 | -4.73 | 79.12 | 0 | 27.26 | 0 | OK | Ground clear controls. | 241 | 37.88 | 106.38
16736 | TIN-INTERP | Interpolated Ground | 106954.74 | -4.46 | 80.9 | 0 | 36.95 | 0 | OK | Ground clear controls. | 241 | 37.88 | 117.85
16737 | TIN-INTERP | Interpolated Ground | 106954.77 | 4.13 | 80.87 | 0 | 36.96 | 0 | OK | Ground clear controls. | 241 | 37.88 | 117.83
16738 | TIN-INTERP | Interpolated Ground | 106954.92 | -6.49 | 80.84 | 0 | 31.44 | 0 | OK | Ground clear controls. | 241 | 37.88 | 112.28
16739 | TIN-INTERP | Interpolated Ground | 106954.94 | 6.15 | 80.83 | 0 | 31.42 | 0 | OK | Ground clear controls. | 241 | 37.88 | 112.25
16740 | TIN-INTERP | Interpolated Ground | 106954.97 | 4.65 | 80.89 | 0 | 25.85 | 0 | OK | Ground clear controls. | 241 | 37.88 | 106.74
16741 | TIN-INTERP | Interpolated Ground | 106955.03 | -5 | 80.92 | 0 | 25.89 | 0 | OK | Ground clear controls. | 241 | 37.88 | 106.81
16742 | TIN-INTERP | Interpolated Ground | 106994.73 | -4.75 | 83.03 | 0 | 36.23 | 0 | OK | Ground clear controls. | 241 | 37.88 | 119.26
16743 | TIN-INTERP | Interpolated Ground | 106994.77 | 4.12 | 82.65 | 0 | 36.58 | 0 | OK | Ground clear controls. | 241 | 37.88 | 119.23
16744 | TIN-INTERP | Interpolated Ground | 106994.91 | -6.75 | 83.13 | 0 | 30.52 | 0 | OK | Ground clear controls. | 241 | 37.88 | 113.65
16745 | TIN-INTERP | Interpolated Ground | 106994.94 | 6.12 | 82.73 | 0 | 30.86 | 0 | OK | Ground clear controls. | 241 | 37.88 | 113.59
16746 | TIN-INTERP | Interpolated Ground | 106994.97 | 4.61 | 82.63 | 0 | 25.43 | 0 | OK | Ground clear controls. | 241 | 37.88 | 108.06
16747 | TIN-INTERP | Interpolated Ground | 106995.03 | -5.26 | 83.07 | 0 | 25.1 | 0 | OK | Ground clear controls. | 241 | 37.88 | 108.17
16748 | TIN-INTERP | Interpolated Ground | 107034.73 | -5.03 | 89.32 | 0 | 32.29 | 0 | OK | Ground clear controls. | 241 | 37.88 | 121.61
16749 | TIN-INTERP | Interpolated Ground | 107034.77 | 4.11 | 87.52 | 0 | 34.07 | 0 | OK | Ground clear controls. | 241 | 37.88 | 121.59
16750 | TIN-INTERP | Interpolated Ground | 107034.91 | -7.01 | 89.79 | 0 | 26.17 | 0 | OK | Ground clear controls. | 241 | 37.88 | 115.96
16751 | TIN-INTERP | Interpolated Ground | 107034.94 | 6.08 | 87.18 | 0 | 28.71 | 0 | OK | Ground clear controls. | 241 | 37.88 | 115.89
16752 | TIN-INTERP | Interpolated Ground | 107034.97 | 4.58 | 87.51 | 0 | 22.85 | 0 | OK | Ground clear controls. | 241 | 37.88 | 110.36
16753 | TIN-INTERP | Interpolated Ground | 107035.03 | -5.52 | 89.57 | 0 | 20.92 | 0 | OK | Ground clear controls. | 241 | 37.88 | 110.49
16754 | TIN-INTERP | Interpolated Ground | 107074.73 | -5.32 | 90.02 | 0 | 34.91 | 0 | OK | Ground clear controls. | 241 | 37.88 | 124.93
16755 | TIN-INTERP | Interpolated Ground | 107074.77 | 4.1 | 87.02 | 0 | 37.88 | 0 | OK | Ground clear controls. | 241 | 37.88 | 124.9
16756 | TIN-INTERP | Interpolated Ground | 107074.91 | -7.27 | 90.73 | 0 | 28.5 | 0 | OK | Ground clear controls. | 241 | 37.53 | 119.23
16757 | TIN-INTERP | Interpolated Ground | 107074.94 | 6.05 | 86.78 | 0 | 32.38 | 0 | OK | Ground clear controls. | 241 | 37.53 | 119.16
16758 | TIN-INTERP | Interpolated Ground | 107074.97 | 4.54 | 86.91 | 0 | 26.73 | 0 | OK | Ground clear controls. | 241 | 37.53 | 113.64
16759 | TIN-INTERP | Interpolated Ground | 107075.03 | -5.79 | 90.03 | 0 | 23.72 | 0 | OK | Ground clear controls. | 241 | 37.53 | 113.75
16760 | TIN-INTERP | Interpolated Ground | 107114.73 | -5.61 | 91.66 | 0 | 37.53 | 0 | OK | Ground clear controls. | 241 | 37.53 | 129.19
16761 | TIN-INTERP | Interpolated Ground | 107114.77 | 4.08 | 93.48 | 0 | 35.69 | 0 | OK | Ground clear controls. | 241 | 35.69 | 129.17
16762 | TIN-INTERP | Interpolated Ground | 107114.91 | -7.53 | 91.43 | 0 | 32.03 | 0 | OK | Ground clear controls. | 241 | 32.03 | 123.46
16763 | TIN-INTERP | Interpolated Ground | 107114.94 | 6.01 | 94.23 | 0 | 29.18 | 0 | OK | Ground clear controls. | 241 | 29.18 | 123.41
16764 | TIN-INTERP | Interpolated Ground | 107114.97 | 4.51 | 93.67 | 0 | 24.22 | 0 | OK | Ground clear controls. | 241 | 26.31 | 117.89
16765 | TIN-INTERP | Interpolated Ground | 107115.03 | -6.05 | 91.66 | 0 | 26.31 | 0 | OK | Ground clear controls. | 241 | 26.31 | 117.97
16766 | TIN-INTERP | Interpolated Ground | 107143.34 | -7.72 | 101.32 | 0 | 25.73 | 0 | OK | Ground clear controls. | 242 | 54.85 | 127.05
16767 | TIN-INTERP | Interpolated Ground | 107143.65 | 4.08 | 100.69 | 0 | 32.19 | 0 | OK | Ground clear controls. | 242 | 54.85 | 132.88
16768 | TIN-INTERP | Interpolated Ground | 107143.65 | 5.99 | 100.57 | 0 | 26.51 | 0 | OK | Ground clear controls. | 242 | 54.85 | 127.08
16769 | TIN-INTERP | Interpolated Ground | 107143.76 | 4.5 | 100.65 | 0 | 20.94 | 0 | OK | Ground clear controls. | 242 | 54.85 | 121.59
16770 | TIN-INTERP | Interpolated Ground | 107143.87 | -5.81 | 101.22 | 0 | 31.63 | 0 | OK | Ground clear controls. | 242 | 54.85 | 132.85
16771 | TIN-INTERP | Interpolated Ground | 107144.02 | -6.23 | 101.23 | 0 | 20.33 | 0 | OK | Ground clear controls. | 242 | 54.85 | 121.56
16772 | TIN-INTERP | Interpolated Ground | 107183.51 | 6.06 | 95.29 | 0 | 32.56 | 0 | OK | Ground clear controls. | 242 | 54.85 | 127.85
16773 | TIN-INTERP | Interpolated Ground | 107183.6 | 4.14 | 95.53 | 0 | 38.14 | 0 | OK | Ground clear controls. | 242 | 54.85 | 133.67
16774 | TIN-INTERP | Interpolated Ground | 107183.76 | 4.56 | 95.52 | 0 | 26.88 | 0 | OK | Ground clear controls. | 242 | 54.85 | 122.4
16775 | TIN-INTERP | Interpolated Ground | 107183.84 | -7.6 | 97.34 | 0 | 30.52 | 0 | OK | Ground clear controls. | 242 | 54.85 | 127.86
16776 | TIN-INTERP | Interpolated Ground | 107183.87 | -5.67 | 97.02 | 0 | 36.64 | 0 | OK | Ground clear controls. | 242 | 54.85 | 133.66
16777 | TIN-INTERP | Interpolated Ground | 107184.02 | -6.11 | 97.12 | 0 | 25.34 | 0 | OK | Ground clear controls. | 242 | 54.85 | 122.46
16778 | TIN-INTERP | Interpolated Ground | 107223.51 | 6.13 | 100.93 | 0 | 28.66 | 0 | OK | Ground clear controls. | 242 | 54.85 | 129.59
16779 | TIN-INTERP | Interpolated Ground | 107223.6 | 4.2 | 100.98 | 0 | 34.44 | 0 | OK | Ground clear controls. | 242 | 54.85 | 135.42
16780 | TIN-INTERP | Interpolated Ground | 107223.76 | 4.63 | 100.98 | 0 | 23.18 | 0 | OK | Ground clear controls. | 242 | 54.85 | 124.16
16781 | TIN-INTERP | Interpolated Ground | 107223.84 | -7.47 | 100.72 | 0 | 28.9 | 0 | OK | Ground clear controls. | 242 | 54.85 | 129.62
16782 | TIN-INTERP | Interpolated Ground | 107223.87 | -5.54 | 100.8 | 0 | 34.63 | 0 | OK | Ground clear controls. | 242 | 54.85 | 135.43
16783 | TIN-INTERP | Interpolated Ground | 107224.02 | -5.98 | 100.76 | 0 | 23.52 | 0 | OK | Ground clear controls. | 242 | 54.85 | 124.28
16784 | TIN-INTERP | Interpolated Ground | 107263.51 | 6.19 | 85.34 | 0 | 46.95 | 0 | OK | Ground clear controls. | 242 | 54.85 | 132.29
16785 | TIN-INTERP | Interpolated Ground | 107263.6 | 4.25 | 85.03 | 0 | 53.07 | 0 | OK | Ground clear controls. | 242 | 54.85 | 138.1
16786 | TIN-INTERP | Interpolated Ground | 107263.76 | 4.7 | 85.06 | 0 | 41.81 | 0 | OK | Ground clear controls. | 242 | 54.85 | 126.87
16787 | TIN-INTERP | Interpolated Ground | 107263.84 | -7.35 | 83.05 | 0 | 49.3 | 0 | OK | Ground clear controls. | 242 | 54.85 | 132.35
16788 | TIN-INTERP | Interpolated Ground | 107263.87 | -5.41 | 83.29 | 0 | 54.85 | 0 | OK | Ground clear controls. | 242 | 54.85 | 138.14
16789 | TIN-INTERP | Interpolated Ground | 107264.02 | -5.86 | 83.25 | 0 | 43.81 | 0 | OK | Ground clear controls. | 242 | 51.8 | 127.06
16790 | TIN-INTERP | Interpolated Ground | 107303.51 | 6.26 | 89.91 | 0 | 46.05 | 0 | OK | Ground clear controls. | 242 | 51.8 | 135.96
16791 | TIN-INTERP | Interpolated Ground | 107303.6 | 4.31 | 89.96 | 0 | 51.8 | 0 | OK | Ground clear controls. | 242 | 51.8 | 141.76
16792 | TIN-INTERP | Interpolated Ground | 107303.76 | 4.76 | 89.98 | 0 | 40.57 | 0 | OK | Ground clear controls. | 242 | 51.49 | 130.55
16793 | TIN-INTERP | Interpolated Ground | 107303.84 | -7.22 | 90.43 | 0 | 45.6 | 0 | OK | Ground clear controls. | 242 | 51.49 | 136.03
16794 | TIN-INTERP | Interpolated Ground | 107303.87 | -5.27 | 90.31 | 0 | 51.49 | 0 | OK | Ground clear controls. | 242 | 51.49 | 141.8
16795 | TIN-INTERP | Interpolated Ground | 107304.02 | -5.73 | 90.34 | 0 | 40.42 | 0 | OK | Ground clear controls. | 242 | 51.03 | 130.76
16796 | TIN-INTERP | Interpolated Ground | 107343.51 | 6.33 | 97.95 | 0 | 42.64 | 0 | OK | Ground clear controls. | 242 | 51.03 | 140.59
16797 | TIN-INTERP | Interpolated Ground | 107343.6 | 4.37 | 97.25 | 0 | 49.11 | 0 | OK | Ground clear controls. | 242 | 51.03 | 146.36
16798 | TIN-INTERP | Interpolated Ground | 107343.76 | 4.83 | 97.46 | 0 | 37.72 | 0 | OK | Ground clear controls. | 242 | 51.03 | 135.18
16799 | TIN-INTERP | Interpolated Ground | 107343.84 | -7.1 | 95.35 | 0 | 45.33 | 0 | OK | Ground clear controls. | 242 | 51.03 | 140.68
16800 | TIN-INTERP | Interpolated Ground | 107343.87 | -5.14 | 95.39 | 0 | 51.03 | 0 | OK | Ground clear controls. | 242 | 51.03 | 146.42
16801 | TIN-INTERP | Interpolated Ground | 107344.02 | -5.61 | 95.39 | 0 | 40.02 | 0 | OK | Ground clear controls. | 242 | 46.18 | 135.41
16802 | TIN-INTERP | Interpolated Ground | 107383.51 | 6.39 | 112.19 | 0 | 34 | 0 | OK | Ground clear controls. | 242 | 46.18 | 146.19
16803 | TIN-INTERP | Interpolated Ground | 107383.6 | 4.42 | 111.11 | 0 | 40.81 | 0 | OK | Ground clear controls. | 242 | 46.18 | 151.92
16804 | TIN-INTERP | Interpolated Ground | 107383.76 | 4.9 | 111.33 | 0 | 29.45 | 0 | OK | Ground clear controls. | 242 | 46.18 | 140.78
16805 | TIN-INTERP | Interpolated Ground | 107383.84 | -6.98 | 105.24 | 0 | 41.06 | 0 | OK | Ground clear controls. | 242 | 46.18 | 146.3
16806 | TIN-INTERP | Interpolated Ground | 107383.87 | -5.01 | 105.8 | 0 | 46.18 | 0 | OK | Ground clear controls. | 242 | 46.18 | 151.98
16807 | TIN-INTERP | Interpolated Ground | 107384.02 | -5.48 | 105.62 | 0 | 35.38 | 0 | OK | Ground clear controls. | 242 | 39.42 | 141
16808 | TIN-INTERP | Interpolated Ground | 107423.51 | 6.46 | 123.34 | 0 | 29.43 | 0 | OK | Ground clear controls. | 242 | 39.42 | 152.77
16809 | TIN-INTERP | Interpolated Ground | 107423.6 | 4.48 | 121.94 | 0 | 36.5 | 0 | OK | Ground clear controls. | 242 | 39.42 | 158.44
16810 | TIN-INTERP | Interpolated Ground | 107423.76 | 4.96 | 122.34 | 0 | 25 | 0 | OK | Ground clear controls. | 242 | 39.42 | 147.34
16811 | TIN-INTERP | Interpolated Ground | 107423.84 | -6.85 | 119.03 | 0 | 33.85 | 0 | OK | Ground clear controls. | 242 | 39.42 | 152.88
16812 | TIN-INTERP | Interpolated Ground | 107423.87 | -4.87 | 119.09 | 0 | 39.42 | 0 | OK | Ground clear controls. | 242 | 39.42 | 158.51
16813 | TIN-INTERP | Interpolated Ground | 107424.02 | -5.35 | 119.2 | 0 | 28.34 | 0 | OK | Ground clear controls. | 242 | 29.06 | 147.54
16814 | TIN-INTERP | Interpolated Ground | 107463.51 | 6.53 | 139.37 | 0 | 20.96 | 0 | OK | Ground clear controls. | 242 | 29.06 | 160.33
16815 | TIN-INTERP | Interpolated Ground | 107463.6 | 4.54 | 138.32 | 0 | 27.6 | 0 | OK | Ground clear controls. | 242 | 29.06 | 165.92
16816 | TIN-INTERP | Interpolated Ground | 107463.76 | 5.03 | 138.66 | 0 | 16.22 | 0 | OK | Ground clear controls. | 242 | 29.06 | 154.88
16817 | TIN-INTERP | Interpolated Ground | 107463.84 | -6.73 | 136.84 | 0 | 23.59 | 0 | OK | Ground clear controls. | 242 | 29.06 | 160.43
16818 | TIN-INTERP | Interpolated Ground | 107463.87 | -4.74 | 136.93 | 0 | 29.06 | 0 | OK | Ground clear controls. | 242 | 29.06 | 165.99
16819 | TIN-INTERP | Interpolated Ground | 107464.02 | -5.23 | 137.02 | 0 | 18.01 | 0 | OK | Ground clear controls. | 242 | 18.01 | 155.03
16820 | TIN-INTERP | Interpolated Ground | 107493.81 | -6.63 | 147.13 | 0 | 19.61 | 0 | OK | Ground clear controls. | 243 | 58.25 | 166.74
16821 | TIN-INTERP | Interpolated Ground | 107493.87 | -4.64 | 147.14 | 0 | 25.1 | 0 | OK | Ground clear controls. | 243 | 58.25 | 172.24
16822 | TIN-INTERP | Interpolated Ground | 107493.88 | -5.14 | 147.12 | 0 | 14.12 | 0 | OK | Ground clear controls. | 243 | 58.25 | 161.24
16823 | TIN-INTERP | Interpolated Ground | 107493.93 | 6.58 | 145.8 | 0 | 20.94 | 0 | OK | Ground clear controls. | 243 | 58.25 | 166.74
16824 | TIN-INTERP | Interpolated Ground | 107493.93 | 4.58 | 146.22 | 0 | 26.02 | 0 | OK | Ground clear controls. | 243 | 58.25 | 172.24
16825 | TIN-INTERP | Interpolated Ground | 107494.1 | 5.08 | 146.12 | 0 | 15.13 | 0 | OK | Ground clear controls. | 243 | 58.25 | 161.25
16826 | TIN-INTERP | Interpolated Ground | 107533.82 | -6.63 | 143.32 | 0 | 22.66 | 0 | OK | Ground clear controls. | 243 | 58.25 | 165.98
16827 | TIN-INTERP | Interpolated Ground | 107533.87 | -4.63 | 142.34 | 0 | 29.21 | 0 | OK | Ground clear controls. | 243 | 58.25 | 171.55
16828 | TIN-INTERP | Interpolated Ground | 107533.88 | -5.13 | 142.54 | 0 | 18.07 | 0 | OK | Ground clear controls. | 243 | 58.25 | 160.61
16829 | TIN-INTERP | Interpolated Ground | 107533.93 | 6.58 | 138.42 | 0 | 27.52 | 0 | OK | Ground clear controls. | 243 | 58.25 | 165.94
16830 | TIN-INTERP | Interpolated Ground | 107533.93 | 4.58 | 139.35 | 0 | 32.17 | 0 | OK | Ground clear controls. | 243 | 58.25 | 171.52
16831 | TIN-INTERP | Interpolated Ground | 107534.1 | 5.08 | 139.36 | 0 | 21.22 | 0 | OK | Ground clear controls. | 243 | 58.25 | 160.58
16832 | TIN-INTERP | Interpolated Ground | 107573.82 | -6.63 | 140.01 | 0 | 26.16 | 0 | OK | Ground clear controls. | 243 | 58.25 | 166.17
16833 | TIN-INTERP | Interpolated Ground | 107573.87 | -4.63 | 138.36 | 0 | 33.45 | 0 | OK | Ground clear controls. | 243 | 58.25 | 171.81
16834 | TIN-INTERP | Interpolated Ground | 107573.88 | -5.13 | 138.66 | 0 | 22.25 | 0 | OK | Ground clear controls. | 243 | 58.25 | 160.91
16835 | TIN-INTERP | Interpolated Ground | 107573.93 | 6.58 | 132.57 | 0 | 33.53 | 0 | OK | Ground clear controls. | 243 | 58.25 | 166.1
16836 | TIN-INTERP | Interpolated Ground | 107573.93 | 4.58 | 133.62 | 0 | 38.13 | 0 | OK | Ground clear controls. | 243 | 58.25 | 171.75
16837 | TIN-INTERP | Interpolated Ground | 107574.1 | 5.08 | 133.46 | 0 | 27.39 | 0 | OK | Ground clear controls. | 243 | 58.25 | 160.85
16838 | TIN-INTERP | Interpolated Ground | 107613.82 | -6.63 | 119.86 | 0 | 47.45 | 0 | OK | Ground clear controls. | 243 | 58.25 | 167.31
16839 | TIN-INTERP | Interpolated Ground | 107613.87 | -4.63 | 119.78 | 0 | 53.21 | 0 | OK | Ground clear controls. | 243 | 58.25 | 172.99
16840 | TIN-INTERP | Interpolated Ground | 107613.88 | -5.13 | 119.81 | 0 | 42.34 | 0 | OK | Ground clear controls. | 243 | 58.25 | 162.15
16841 | TIN-INTERP | Interpolated Ground | 107613.93 | 6.58 | 118.38 | 0 | 48.84 | 0 | OK | Ground clear controls. | 243 | 58.25 | 167.22
16842 | TIN-INTERP | Interpolated Ground | 107613.93 | 4.59 | 118.66 | 0 | 54.25 | 0 | OK | Ground clear controls. | 243 | 58.25 | 172.91
16843 | TIN-INTERP | Interpolated Ground | 107614.1 | 5.08 | 118.61 | 0 | 43.45 | 0 | OK | Ground clear controls. | 243 | 58.25 | 162.06
16844 | TIN-INTERP | Interpolated Ground | 107653.82 | -6.62 | 136.23 | 0 | 33.19 | 0 | OK | Ground clear controls. | 243 | 58.25 | 169.42
16845 | TIN-INTERP | Interpolated Ground | 107653.87 | -4.62 | 134.61 | 0 | 40.51 | 0 | OK | Ground clear controls. | 243 | 58.25 | 175.12
16846 | TIN-INTERP | Interpolated Ground | 107653.88 | -5.12 | 135.11 | 0 | 29.2 | 0 | OK | Ground clear controls. | 243 | 58.25 | 164.31
16847 | TIN-INTERP | Interpolated Ground | 107653.93 | 6.59 | 129.52 | 0 | 39.78 | 0 | OK | Ground clear controls. | 243 | 58.25 | 169.3
16848 | TIN-INTERP | Interpolated Ground | 107653.93 | 4.59 | 129.82 | 0 | 45.21 | 0 | OK | Ground clear controls. | 243 | 58.25 | 175.03
16849 | TIN-INTERP | Interpolated Ground | 107654.1 | 5.09 | 129.85 | 0 | 34.35 | 0 | OK | Ground clear controls. | 243 | 58.25 | 164.2
16850 | TIN-INTERP | Interpolated Ground | 107693.82 | -6.62 | 151.98 | 0 | 20.49 | 0 | OK | Ground clear controls. | 243 | 58.25 | 172.47
16851 | TIN-INTERP | Interpolated Ground | 107693.87 | -4.62 | 151.69 | 0 | 26.51 | 0 | OK | Ground clear controls. | 243 | 58.25 | 178.2
16852 | TIN-INTERP | Interpolated Ground | 107693.88 | -5.12 | 151.77 | 0 | 15.63 | 0 | OK | Ground clear controls. | 243 | 58.25 | 167.4
16853 | TIN-INTERP | Interpolated Ground | 107693.93 | 6.59 | 150.99 | 0 | 21.37 | 0 | OK | Ground clear controls. | 243 | 58.25 | 172.36
16854 | TIN-INTERP | Interpolated Ground | 107693.93 | 4.59 | 151.21 | 0 | 26.89 | 0 | OK | Ground clear controls. | 243 | 58.25 | 178.1
16855 | TIN-INTERP | Interpolated Ground | 107694.1 | 5.09 | 151.21 | 0 | 16.09 | 0 | OK | Ground clear controls. | 243 | 58.25 | 167.3
16856 | TIN-INTERP | Interpolated Ground | 107733.82 | -6.62 | 139.99 | 0 | 36.51 | 0 | OK | Ground clear controls. | 243 | 58.25 | 176.5
16857 | TIN-INTERP | Interpolated Ground | 107733.87 | -4.62 | 139.15 | 0 | 43.08 | 0 | OK | Ground clear controls. | 243 | 58.25 | 182.23
16858 | TIN-INTERP | Interpolated Ground | 107733.88 | -5.12 | 139.14 | 0 | 32.28 | 0 | OK | Ground clear controls. | 243 | 58.25 | 171.42
16859 | TIN-INTERP | Interpolated Ground | 107733.93 | 6.59 | 139.42 | 0 | 36.96 | 0 | OK | Ground clear controls. | 243 | 58.25 | 176.38
16860 | TIN-INTERP | Interpolated Ground | 107733.93 | 4.59 | 139.63 | 0 | 42.49 | 0 | OK | Ground clear controls. | 243 | 58.25 | 182.12
16861 | TIN-INTERP | Interpolated Ground | 107734.1 | 5.09 | 139.52 | 0 | 31.8 | 0 | OK | Ground clear controls. | 243 | 58.25 | 171.32
16862 | TIN-INTERP | Interpolated Ground | 107773.82 | -6.61 | 128.84 | 0 | 52.63 | 0 | OK | Ground clear controls. | 243 | 58.25 | 181.47
16863 | TIN-INTERP | Interpolated Ground | 107773.87 | -4.62 | 129.34 | 0 | 57.86 | 0 | OK | Ground clear controls. | 243 | 58.25 | 187.2
16864 | TIN-INTERP | Interpolated Ground | 107773.88 | -5.12 | 129.14 | 0 | 47.25 | 0 | OK | Ground clear controls. | 243 | 58.25 | 176.39
16865 | TIN-INTERP | Interpolated Ground | 107773.93 | 6.59 | 128.52 | 0 | 52.84 | 0 | OK | Ground clear controls. | 243 | 58.25 | 181.36
16866 | TIN-INTERP | Interpolated Ground | 107773.93 | 4.59 | 128.84 | 0 | 58.25 | 0 | OK | Ground clear controls. | 243 | 58.25 | 187.09
16867 | TIN-INTERP | Interpolated Ground | 107774.1 | 5.09 | 128.78 | 0 | 47.51 | 0 | OK | Ground clear controls. | 243 | 55 | 176.29
16868 | TIN-INTERP | Interpolated Ground | 107813.82 | -6.61 | 140.9 | 0 | 46.53 | 0 | OK | Ground clear controls. | 243 | 55 | 187.43
16869 | TIN-INTERP | Interpolated Ground | 107813.87 | -4.61 | 139.79 | 0 | 53.33 | 0 | OK | Ground clear controls. | 243 | 55 | 193.12
16870 | TIN-INTERP | Interpolated Ground | 107813.88 | -5.11 | 140 | 0 | 42.29 | 0 | OK | Ground clear controls. | 243 | 55 | 182.29
16871 | TIN-INTERP | Interpolated Ground | 107813.93 | 6.59 | 137.59 | 0 | 49.75 | 0 | OK | Ground clear controls. | 243 | 55 | 187.34
16872 | TIN-INTERP | Interpolated Ground | 107813.93 | 4.59 | 138.03 | 0 | 55 | 0 | OK | Ground clear controls. | 243 | 55 | 193.03
16873 | TIN-INTERP | Interpolated Ground | 107814.1 | 5.09 | 137.95 | 0 | 44.26 | 0 | OK | Ground clear controls. | 243 | 50.22 | 182.21
16874 | TIN-INTERP | Interpolated Ground | 107853.82 | -6.61 | 149.24 | 0 | 45.1 | 0 | OK | Ground clear controls. | 243 | 50.22 | 194.34
16875 | TIN-INTERP | Interpolated Ground | 107853.87 | -4.61 | 149.78 | 0 | 50.22 | 0 | OK | Ground clear controls. | 243 | 50.22 | 200
16876 | TIN-INTERP | Interpolated Ground | 107853.88 | -5.11 | 149.52 | 0 | 39.61 | 0 | OK | Ground clear controls. | 243 | 50.2 | 189.13
16877 | TIN-INTERP | Interpolated Ground | 107853.93 | 6.59 | 149.99 | 0 | 44.27 | 0 | OK | Ground clear controls. | 243 | 50.2 | 194.26
16878 | TIN-INTERP | Interpolated Ground | 107853.93 | 4.59 | 149.73 | 0 | 50.2 | 0 | OK | Ground clear controls. | 243 | 50.2 | 199.93
16879 | TIN-INTERP | Interpolated Ground | 107854.1 | 5.09 | 149.8 | 0 | 39.28 | 0 | OK | Ground clear controls. | 243 | 39.28 | 189.08
16880 | TIN-INTERP | Interpolated Ground | 107893.82 | -6.61 | 170.52 | 0 | 31.7 | 0 | OK | Ground clear controls. | 243 | 37.01 | 202.22
16881 | TIN-INTERP | Interpolated Ground | 107893.87 | -4.61 | 170.82 | 0 | 37.01 | 0 | OK | Ground clear controls. | 243 | 37.01 | 207.83
16882 | TIN-INTERP | Interpolated Ground | 107893.88 | -5.11 | 170.81 | 0 | 26.11 | 0 | OK | Ground clear controls. | 243 | 36.2 | 196.92
16883 | TIN-INTERP | Interpolated Ground | 107893.93 | 6.6 | 171.88 | 0 | 30.31 | 0 | OK | Ground clear controls. | 243 | 36.2 | 202.19
16884 | TIN-INTERP | Interpolated Ground | 107893.93 | 4.6 | 171.59 | 0 | 36.2 | 0 | OK | Ground clear controls. | 243 | 36.2 | 207.79
16885 | TIN-INTERP | Interpolated Ground | 107894.1 | 5.1 | 171.71 | 0 | 25.19 | 0 | OK | Ground clear controls. | 243 | 34.77 | 196.9
16886 | TIN-INTERP | Interpolated Ground | 107933.82 | -6.6 | 182.95 | 0 | 28.14 | 0 | OK | Ground clear controls. | 243 | 34.77 | 211.09
16887 | TIN-INTERP | Interpolated Ground | 107933.87 | -4.6 | 183.01 | 0 | 33.61 | 0 | OK | Ground clear controls. | 243 | 34.77 | 216.62
16888 | TIN-INTERP | Interpolated Ground | 107933.88 | -5.1 | 183.08 | 0 | 22.57 | 0 | OK | Ground clear controls. | 243 | 34.77 | 205.65
16889 | TIN-INTERP | Interpolated Ground | 107933.93 | 6.6 | 181.46 | 0 | 29.63 | 0 | OK | Ground clear controls. | 243 | 34.77 | 211.09
16890 | TIN-INTERP | Interpolated Ground | 107933.93 | 4.6 | 181.84 | 0 | 34.77 | 0 | OK | Ground clear controls. | 243 | 34.77 | 216.61
16891 | TIN-INTERP | Interpolated Ground | 107934.1 | 5.1 | 181.81 | 0 | 23.88 | 0 | OK | Ground clear controls. | 243 | 23.88 | 205.69
16892 | TIN-INTERP | Interpolated Ground | 107936.74 | -5.1 | 183.73 | 0 | 22.57 | 0 | OK | Ground clear controls. | 244 | 51.55 | 206.3
16893 | TIN-INTERP | Interpolated Ground | 107936.76 | 5.1 | 182.36 | 0 | 23.94 | 0 | OK | Ground clear controls. | 244 | 51.55 | 206.3
16894 | TIN-INTERP | Interpolated Ground | 107936.8 | -4.6 | 183.72 | 0 | 33.58 | 0 | OK | Ground clear controls. | 244 | 51.55 | 217.3
16895 | TIN-INTERP | Interpolated Ground | 107936.86 | -6.6 | 183.7 | 0 | 28.1 | 0 | OK | Ground clear controls. | 244 | 51.55 | 211.8
16896 | TIN-INTERP | Interpolated Ground | 107936.89 | 4.6 | 182.54 | 0 | 34.76 | 0 | OK | Ground clear controls. | 244 | 51.55 | 217.3
16897 | TIN-INTERP | Interpolated Ground | 107936.95 | 6.6 | 181.89 | 0 | 29.91 | 0 | OK | Ground clear controls. | 244 | 51.55 | 211.8
16898 | TIN-INTERP | Interpolated Ground | 107976.74 | -5.11 | 179.37 | 0 | 28.43 | 0 | OK | Ground clear controls. | 244 | 51.55 | 207.8
16899 | TIN-INTERP | Interpolated Ground | 107976.76 | 5.09 | 178.44 | 0 | 29.31 | 0 | OK | Ground clear controls. | 244 | 51.55 | 207.75
16900 | TIN-INTERP | Interpolated Ground | 107976.8 | -4.61 | 179.3 | 0 | 39.46 | 0 | OK | Ground clear controls. | 244 | 51.55 | 218.76
16901 | TIN-INTERP | Interpolated Ground | 107976.86 | -6.61 | 179.54 | 0 | 33.65 | 0 | OK | Ground clear controls. | 244 | 51.55 | 213.19
16902 | TIN-INTERP | Interpolated Ground | 107976.89 | 4.59 | 178.46 | 0 | 40.3 | 0 | OK | Ground clear controls. | 244 | 51.55 | 218.76
16903 | TIN-INTERP | Interpolated Ground | 107976.95 | 6.59 | 178.32 | 0 | 34.87 | 0 | OK | Ground clear controls. | 244 | 51.55 | 213.19
16904 | TIN-INTERP | Interpolated Ground | 108016.74 | -5.11 | 179.63 | 0 | 30.59 | 0 | OK | Ground clear controls. | 244 | 51.55 | 210.22
16905 | TIN-INTERP | Interpolated Ground | 108016.76 | 5.09 | 174.51 | 0 | 35.62 | 0 | OK | Ground clear controls. | 244 | 51.55 | 210.13
16906 | TIN-INTERP | Interpolated Ground | 108016.8 | -4.61 | 179.42 | 0 | 41.72 | 0 | OK | Ground clear controls. | 244 | 51.55 | 221.14
16907 | TIN-INTERP | Interpolated Ground | 108016.86 | -6.61 | 180.15 | 0 | 35.38 | 0 | OK | Ground clear controls. | 244 | 51.55 | 215.53
16908 | TIN-INTERP | Interpolated Ground | 108016.89 | 4.59 | 174.72 | 0 | 46.42 | 0 | OK | Ground clear controls. | 244 | 51.55 | 221.14
16909 | TIN-INTERP | Interpolated Ground | 108016.95 | 6.59 | 173.94 | 0 | 41.59 | 0 | OK | Ground clear controls. | 244 | 51.55 | 215.53
16910 | TIN-INTERP | Interpolated Ground | 108056.74 | -5.12 | 184.18 | 0 | 29.41 | 0 | OK | Ground clear controls. | 244 | 51.55 | 213.59
16911 | TIN-INTERP | Interpolated Ground | 108056.76 | 5.09 | 181.33 | 0 | 32.15 | 0 | OK | Ground clear controls. | 244 | 51.55 | 213.48
16912 | TIN-INTERP | Interpolated Ground | 108056.8 | -4.62 | 184.04 | 0 | 40.45 | 0 | OK | Ground clear controls. | 244 | 51.55 | 224.49
16913 | TIN-INTERP | Interpolated Ground | 108056.86 | -6.62 | 184.57 | 0 | 34.27 | 0 | OK | Ground clear controls. | 244 | 51.55 | 218.84
16914 | TIN-INTERP | Interpolated Ground | 108056.89 | 4.59 | 181.45 | 0 | 43.04 | 0 | OK | Ground clear controls. | 244 | 51.55 | 224.49
16915 | TIN-INTERP | Interpolated Ground | 108056.95 | 6.59 | 180.91 | 0 | 37.93 | 0 | OK | Ground clear controls. | 244 | 51.55 | 218.84
16916 | TIN-INTERP | Interpolated Ground | 108096.74 | -5.13 | 194.49 | 0 | 23.42 | 0 | OK | Ground clear controls. | 244 | 51.55 | 217.91
16917 | TIN-INTERP | Interpolated Ground | 108096.76 | 5.09 | 189.43 | 0 | 28.34 | 0 | OK | Ground clear controls. | 244 | 51.55 | 217.77
16918 | TIN-INTERP | Interpolated Ground | 108096.8 | -4.62 | 194.29 | 0 | 34.5 | 0 | OK | Ground clear controls. | 244 | 51.55 | 228.79
16919 | TIN-INTERP | Interpolated Ground | 108096.86 | -6.63 | 195.28 | 0 | 27.82 | 0 | OK | Ground clear controls. | 244 | 51.55 | 223.1
16920 | TIN-INTERP | Interpolated Ground | 108096.89 | 4.59 | 189.76 | 0 | 39.03 | 0 | OK | Ground clear controls. | 244 | 51.55 | 228.79
16921 | TIN-INTERP | Interpolated Ground | 108096.95 | 6.59 | 188.97 | 0 | 34.14 | 0 | OK | Ground clear controls. | 244 | 51.55 | 223.11
16922 | TIN-INTERP | Interpolated Ground | 108136.74 | -5.13 | 203.79 | 0 | 19.39 | 0 | OK | Ground clear controls. | 244 | 51.55 | 223.18
16923 | TIN-INTERP | Interpolated Ground | 108136.76 | 5.08 | 200.67 | 0 | 22.35 | 0 | OK | Ground clear controls. | 244 | 51.55 | 223.02
16924 | TIN-INTERP | Interpolated Ground | 108136.8 | -4.63 | 203.67 | 0 | 30.37 | 0 | OK | Ground clear controls. | 244 | 51.55 | 234.04
16925 | TIN-INTERP | Interpolated Ground | 108136.86 | -6.63 | 204.15 | 0 | 24.18 | 0 | OK | Ground clear controls. | 244 | 51.55 | 228.33
16926 | TIN-INTERP | Interpolated Ground | 108136.89 | 4.58 | 200.84 | 0 | 33.2 | 0 | OK | Ground clear controls. | 244 | 51.55 | 234.04
16927 | TIN-INTERP | Interpolated Ground | 108136.95 | 6.58 | 200.2 | 0 | 28.14 | 0 | OK | Ground clear controls. | 244 | 51.55 | 228.34
16928 | TIN-INTERP | Interpolated Ground | 108176.74 | -5.14 | 204.55 | 0 | 24.84 | 0 | OK | Ground clear controls. | 244 | 51.55 | 229.39
16929 | TIN-INTERP | Interpolated Ground | 108176.76 | 5.08 | 203.06 | 0 | 26.17 | 0 | OK | Ground clear controls. | 244 | 51.55 | 229.23
16930 | TIN-INTERP | Interpolated Ground | 108176.8 | -4.64 | 204.51 | 0 | 35.74 | 0 | OK | Ground clear controls. | 244 | 51.55 | 240.25
16931 | TIN-INTERP | Interpolated Ground | 108176.86 | -6.64 | 204.65 | 0 | 29.88 | 0 | OK | Ground clear controls. | 244 | 51.55 | 234.53
16932 | TIN-INTERP | Interpolated Ground | 108176.89 | 4.58 | 203.13 | 0 | 37.12 | 0 | OK | Ground clear controls. | 244 | 51.55 | 240.25
16933 | TIN-INTERP | Interpolated Ground | 108176.95 | 6.58 | 202.86 | 0 | 31.68 | 0 | OK | Ground clear controls. | 244 | 51.55 | 234.54
16934 | TIN-INTERP | Interpolated Ground | 108216.74 | -5.14 | 207.47 | 0 | 29.09 | 0 | OK | Ground clear controls. | 244 | 51.55 | 236.56
16935 | TIN-INTERP | Interpolated Ground | 108216.76 | 5.08 | 207.15 | 0 | 29.24 | 0 | OK | Ground clear controls. | 244 | 51.55 | 236.39
16936 | TIN-INTERP | Interpolated Ground | 108216.8 | -4.64 | 207.44 | 0 | 39.97 | 0 | OK | Ground clear controls. | 244 | 51.55 | 247.41
16937 | TIN-INTERP | Interpolated Ground | 108216.86 | -6.64 | 207.51 | 0 | 34.19 | 0 | OK | Ground clear controls. | 244 | 51.55 | 241.7
16938 | TIN-INTERP | Interpolated Ground | 108216.89 | 4.58 | 207.2 | 0 | 40.22 | 0 | OK | Ground clear controls. | 244 | 51.55 | 247.42
16939 | TIN-INTERP | Interpolated Ground | 108216.95 | 6.58 | 207.16 | 0 | 34.54 | 0 | OK | Ground clear controls. | 244 | 51.55 | 241.7
16940 | TIN-INTERP | Interpolated Ground | 108256.74 | -5.15 | 208.28 | 0 | 36.4 | 0 | OK | Ground clear controls. | 244 | 51.55 | 244.68
16941 | TIN-INTERP | Interpolated Ground | 108256.76 | 5.07 | 207.4 | 0 | 37.13 | 0 | OK | Ground clear controls. | 244 | 51.55 | 244.53
16942 | TIN-INTERP | Interpolated Ground | 108256.8 | -4.65 | 208.22 | 0 | 47.33 | 0 | OK | Ground clear controls. | 244 | 51.55 | 255.55
16943 | TIN-INTERP | Interpolated Ground | 108256.86 | -6.65 | 208.74 | 0 | 41.1 | 0 | OK | Ground clear controls. | 244 | 51.55 | 249.84
16944 | TIN-INTERP | Interpolated Ground | 108256.89 | 4.57 | 207.46 | 0 | 48.09 | 0 | OK | Ground clear controls. | 244 | 51.55 | 255.55
16945 | TIN-INTERP | Interpolated Ground | 108256.95 | 6.57 | 207.33 | 0 | 42.53 | 0 | OK | Ground clear controls. | 244 | 51.55 | 249.86
16946 | TIN-INTERP | Interpolated Ground | 108296.74 | -5.15 | 213.52 | 0 | 40.25 | 0 | OK | Ground clear controls. | 244 | 51.55 | 253.77
16947 | TIN-INTERP | Interpolated Ground | 108296.76 | 5.07 | 213.09 | 0 | 40.53 | 0 | OK | Ground clear controls. | 244 | 51.55 | 253.62
16948 | TIN-INTERP | Interpolated Ground | 108296.8 | -4.65 | 213.55 | 0 | 51.11 | 0 | OK | Ground clear controls. | 244 | 51.55 | 264.66
16949 | TIN-INTERP | Interpolated Ground | 108296.86 | -6.65 | 213.67 | 0 | 45.29 | 0 | OK | Ground clear controls. | 244 | 51.55 | 258.96
16950 | TIN-INTERP | Interpolated Ground | 108296.89 | 4.57 | 213.11 | 0 | 51.55 | 0 | OK | Ground clear controls. | 244 | 51.55 | 264.66
16951 | TIN-INTERP | Interpolated Ground | 108296.95 | 6.57 | 213.11 | 0 | 45.87 | 0 | OK | Ground clear controls. | 244 | 50.96 | 258.98
16952 | TIN-INTERP | Interpolated Ground | 108336.74 | -5.16 | 226.18 | 0 | 37.64 | 0 | OK | Ground clear controls. | 244 | 50.96 | 263.82
16953 | TIN-INTERP | Interpolated Ground | 108336.76 | 5.07 | 223.63 | 0 | 40.08 | 0 | OK | Ground clear controls. | 244 | 50.96 | 263.71
16954 | TIN-INTERP | Interpolated Ground | 108336.8 | -4.66 | 225.85 | 0 | 48.89 | 0 | OK | Ground clear controls. | 244 | 50.96 | 274.74
16955 | TIN-INTERP | Interpolated Ground | 108336.86 | -6.66 | 227.3 | 0 | 41.77 | 0 | OK | Ground clear controls. | 244 | 50.96 | 269.07
16956 | TIN-INTERP | Interpolated Ground | 108336.89 | 4.57 | 223.78 | 0 | 50.96 | 0 | OK | Ground clear controls. | 244 | 50.96 | 274.74
16957 | TIN-INTERP | Interpolated Ground | 108336.95 | 6.57 | 223.43 | 0 | 45.66 | 0 | OK | Ground clear controls. | 244 | 46.2 | 269.09
16958 | TIN-INTERP | Interpolated Ground | 108376.74 | -5.16 | 244.91 | 0 | 29.94 | 0 | OK | Ground clear controls. | 244 | 46.2 | 274.85
16959 | TIN-INTERP | Interpolated Ground | 108376.76 | 5.06 | 239.31 | 0 | 35.44 | 0 | OK | Ground clear controls. | 244 | 46.2 | 274.75
16960 | TIN-INTERP | Interpolated Ground | 108376.8 | -4.66 | 244.73 | 0 | 41.06 | 0 | OK | Ground clear controls. | 244 | 46.2 | 285.79
16961 | TIN-INTERP | Interpolated Ground | 108376.86 | -6.67 | 245.48 | 0 | 34.7 | 0 | OK | Ground clear controls. | 244 | 46.2 | 280.18
16962 | TIN-INTERP | Interpolated Ground | 108376.89 | 4.56 | 239.6 | 0 | 46.2 | 0 | OK | Ground clear controls. | 244 | 46.2 | 285.8
16963 | TIN-INTERP | Interpolated Ground | 108376.95 | 6.57 | 238.86 | 0 | 41.33 | 0 | OK | Ground clear controls. | 244 | 41.33 | 280.19
16964 | TIN-INTERP | Interpolated Ground | 108416.74 | -5.17 | 271.04 | 0 | 15.82 | 0 | OK | Ground clear controls. | 244 | 33.51 | 286.86
16965 | TIN-INTERP | Interpolated Ground | 108416.76 | 5.06 | 263.34 | 0 | 23.45 | 0 | OK | Ground clear controls. | 244 | 33.51 | 286.79
16966 | TIN-INTERP | Interpolated Ground | 108416.8 | -4.67 | 270.92 | 0 | 26.91 | 0 | OK | Ground clear controls. | 244 | 33.51 | 297.83
16967 | TIN-INTERP | Interpolated Ground | 108416.86 | -6.67 | 271.79 | 0 | 20.48 | 0 | OK | Ground clear controls. | 244 | 33.51 | 292.27
16968 | TIN-INTERP | Interpolated Ground | 108416.89 | 4.56 | 264.34 | 0 | 33.51 | 0 | OK | Ground clear controls. | 244 | 33.51 | 297.85
16969 | TIN-INTERP | Interpolated Ground | 108416.95 | 6.56 | 261.44 | 0 | 30.84 | 0 | OK | Ground clear controls. | 244 | 30.84 | 292.28
16970 | TIN-INTERP | Interpolated Ground | 108456.74 | -5.18 | 281.32 | 0 | 18.53 | 0 | OK | Ground clear controls. | 244 | 29.41 | 299.85
16971 | TIN-INTERP | Interpolated Ground | 108456.76 | 5.06 | 282.93 | 0 | 16.91 | 0 | OK | Ground clear controls. | 244 | 29.41 | 299.84
16972 | TIN-INTERP | Interpolated Ground | 108456.8 | -4.67 | 281.46 | 0 | 29.41 | 0 | OK | Ground clear controls. | 244 | 29.41 | 310.87
16973 | TIN-INTERP | Interpolated Ground | 108456.86 | -6.68 | 281.03 | 0 | 24.34 | 0 | OK | Ground clear controls. | 244 | 28.17 | 305.37
16974 | TIN-INTERP | Interpolated Ground | 108456.89 | 4.56 | 282.72 | 0 | 28.17 | 0 | OK | Ground clear controls. | 244 | 28.17 | 310.89
16975 | TIN-INTERP | Interpolated Ground | 108456.95 | 6.56 | 282.95 | 0 | 22.44 | 0 | OK | Ground clear controls. | 244 | 22.44 | 305.39
16976 | TIN-INTERP | Interpolated Ground | 108459.86 | -4.67 | 280.9 | 0 | 31 | 0 | OK | Ground clear controls. | 245 | 54.51 | 311.9
16977 | TIN-INTERP | Interpolated Ground | 108459.87 | -5.18 | 280.79 | 0 | 20.11 | 0 | OK | Ground clear controls. | 245 | 54.51 | 300.9
16978 | TIN-INTERP | Interpolated Ground | 108459.87 | -6.68 | 280.4 | 0 | 26 | 0 | OK | Ground clear controls. | 245 | 54.51 | 306.4
16979 | TIN-INTERP | Interpolated Ground | 108459.9 | 4.56 | 282.54 | 0 | 29.36 | 0 | OK | Ground clear controls. | 245 | 54.51 | 311.9
16980 | TIN-INTERP | Interpolated Ground | 108459.9 | 5.06 | 282.64 | 0 | 18.26 | 0 | OK | Ground clear controls. | 245 | 54.51 | 300.9
16981 | TIN-INTERP | Interpolated Ground | 108459.94 | 6.56 | 282.82 | 0 | 23.58 | 0 | OK | Ground clear controls. | 245 | 54.51 | 306.4
16982 | TIN-INTERP | Interpolated Ground | 108499.86 | -4.92 | 267.85 | 0 | 40.24 | 0 | OK | Ground clear controls. | 245 | 54.51 | 308.09
16983 | TIN-INTERP | Interpolated Ground | 108499.86 | -5.43 | 267.57 | 0 | 29.46 | 0 | OK | Ground clear controls. | 245 | 54.51 | 297.03
16984 | TIN-INTERP | Interpolated Ground | 108499.87 | -6.94 | 266.71 | 0 | 35.78 | 0 | OK | Ground clear controls. | 245 | 54.51 | 302.49
16985 | TIN-INTERP | Interpolated Ground | 108499.9 | 4.53 | 273.86 | 0 | 34.21 | 0 | OK | Ground clear controls. | 245 | 54.51 | 308.07
16986 | TIN-INTERP | Interpolated Ground | 108499.9 | 5.04 | 273.93 | 0 | 23.04 | 0 | OK | Ground clear controls. | 245 | 54.51 | 296.97
16987 | TIN-INTERP | Interpolated Ground | 108499.94 | 6.54 | 274.22 | 0 | 28.26 | 0 | OK | Ground clear controls. | 245 | 54.51 | 302.48
16988 | TIN-INTERP | Interpolated Ground | 108539.86 | -5.16 | 257.09 | 0 | 48.12 | 0 | OK | Ground clear controls. | 245 | 54.51 | 305.21
16989 | TIN-INTERP | Interpolated Ground | 108539.86 | -5.69 | 256.77 | 0 | 37.33 | 0 | OK | Ground clear controls. | 245 | 54.51 | 294.1
16990 | TIN-INTERP | Interpolated Ground | 108539.87 | -7.21 | 255.92 | 0 | 43.6 | 0 | OK | Ground clear controls. | 245 | 54.51 | 299.52
16991 | TIN-INTERP | Interpolated Ground | 108539.9 | 4.5 | 259.94 | 0 | 45.24 | 0 | OK | Ground clear controls. | 245 | 54.51 | 305.18
16992 | TIN-INTERP | Interpolated Ground | 108539.9 | 5.03 | 260.1 | 0 | 33.88 | 0 | OK | Ground clear controls. | 245 | 54.51 | 293.98
16993 | TIN-INTERP | Interpolated Ground | 108539.94 | 6.53 | 260.4 | 0 | 39.09 | 0 | OK | Ground clear controls. | 245 | 54.51 | 299.49
16994 | TIN-INTERP | Interpolated Ground | 108579.85 | -5.4 | 248.77 | 0 | 54.51 | 0 | OK | Ground clear controls. | 245 | 54.51 | 303.28
16995 | TIN-INTERP | Interpolated Ground | 108579.86 | -5.95 | 248.44 | 0 | 43.64 | 0 | OK | Ground clear controls. | 245 | 53.7 | 292.08
16996 | TIN-INTERP | Interpolated Ground | 108579.87 | -7.47 | 247.74 | 0 | 49.76 | 0 | OK | Ground clear controls. | 245 | 53.7 | 297.5
16997 | TIN-INTERP | Interpolated Ground | 108579.9 | 4.47 | 251.88 | 0 | 51.35 | 0 | OK | Ground clear controls. | 245 | 53.7 | 303.23
16998 | TIN-INTERP | Interpolated Ground | 108579.9 | 5.02 | 251.96 | 0 | 39.97 | 0 | OK | Ground clear controls. | 245 | 53.7 | 291.93
16999 | TIN-INTERP | Interpolated Ground | 108579.94 | 6.52 | 252 | 0 | 45.45 | 0 | OK | Ground clear controls. | 245 | 53.7 | 297.45
17000 | TIN-INTERP | Interpolated Ground | 108619.85 | -5.64 | 252.46 | 0 | 49.81 | 0 | OK | Ground clear controls. | 245 | 53.7 | 302.27
17001 | TIN-INTERP | Interpolated Ground | 108619.86 | -6.2 | 252.34 | 0 | 38.66 | 0 | OK | Ground clear controls. | 245 | 53.7 | 291
17002 | TIN-INTERP | Interpolated Ground | 108619.87 | -7.73 | 252.05 | 0 | 44.36 | 0 | OK | Ground clear controls. | 245 | 53.7 | 296.41
17003 | TIN-INTERP | Interpolated Ground | 108619.9 | 4.44 | 255.64 | 0 | 46.57 | 0 | OK | Ground clear controls. | 245 | 53.7 | 302.21
17004 | TIN-INTERP | Interpolated Ground | 108619.9 | 5 | 255.82 | 0 | 34.99 | 0 | OK | Ground clear controls. | 245 | 53.7 | 290.81
17005 | TIN-INTERP | Interpolated Ground | 108619.94 | 6.5 | 256.04 | 0 | 40.31 | 0 | OK | Ground clear controls. | 245 | 53.7 | 296.35
17006 | TIN-INTERP | Interpolated Ground | 108659.85 | -5.88 | 254.79 | 0 | 47.42 | 0 | OK | Ground clear controls. | 245 | 53.7 | 302.21
17007 | TIN-INTERP | Interpolated Ground | 108659.86 | -6.46 | 254.52 | 0 | 36.33 | 0 | OK | Ground clear controls. | 245 | 53.7 | 290.85
17008 | TIN-INTERP | Interpolated Ground | 108659.87 | -8 | 253.65 | 0 | 42.61 | 0 | OK | Ground clear controls. | 245 | 53.7 | 296.26
17009 | TIN-INTERP | Interpolated Ground | 108659.9 | 4.41 | 258.19 | 0 | 43.95 | 0 | OK | Ground clear controls. | 245 | 53.7 | 302.14
17010 | TIN-INTERP | Interpolated Ground | 108659.9 | 4.99 | 258.29 | 0 | 32.34 | 0 | OK | Ground clear controls. | 245 | 53.7 | 290.63
17011 | TIN-INTERP | Interpolated Ground | 108659.94 | 6.49 | 258.55 | 0 | 37.64 | 0 | OK | Ground clear controls. | 245 | 53.7 | 296.19
17012 | TIN-INTERP | Interpolated Ground | 108699.85 | -6.12 | 249.38 | 0 | 53.7 | 0 | OK | Ground clear controls. | 245 | 53.7 | 303.08
17013 | TIN-INTERP | Interpolated Ground | 108699.86 | -6.72 | 249.19 | 0 | 42.42 | 0 | OK | Ground clear controls. | 245 | 51.15 | 291.61
17014 | TIN-INTERP | Interpolated Ground | 108699.87 | -8.26 | 248.85 | 0 | 48.21 | 0 | OK | Ground clear controls. | 245 | 51.15 | 297.06
17015 | TIN-INTERP | Interpolated Ground | 108699.9 | 4.38 | 251.84 | 0 | 51.15 | 0 | OK | Ground clear controls. | 245 | 51.15 | 302.99
17016 | TIN-INTERP | Interpolated Ground | 108699.9 | 4.97 | 251.94 | 0 | 39.45 | 0 | OK | Ground clear controls. | 245 | 44.81 | 291.39
17017 | TIN-INTERP | Interpolated Ground | 108699.94 | 6.47 | 252.17 | 0 | 44.81 | 0 | OK | Ground clear controls. | 245 | 44.81 | 296.98
17018 | TIN-INTERP | Interpolated Ground | 108739.85 | -6.37 | 261.12 | 0 | 43.76 | 0 | OK | Ground clear controls. | 245 | 43.76 | 304.88
17019 | TIN-INTERP | Interpolated Ground | 108739.86 | -6.98 | 260.87 | 0 | 32.44 | 0 | OK | Ground clear controls. | 245 | 39.65 | 293.31
17020 | TIN-INTERP | Interpolated Ground | 108739.86 | -8.53 | 260.28 | 0 | 38.52 | 0 | OK | Ground clear controls. | 245 | 39.65 | 298.8
17021 | TIN-INTERP | Interpolated Ground | 108739.9 | 4.35 | 265.13 | 0 | 39.65 | 0 | OK | Ground clear controls. | 245 | 39.65 | 304.78
17022 | TIN-INTERP | Interpolated Ground | 108739.9 | 4.96 | 265.41 | 0 | 27.68 | 0 | OK | Ground clear controls. | 245 | 39.65 | 293.09
17023 | TIN-INTERP | Interpolated Ground | 108739.94 | 6.46 | 265.94 | 0 | 32.76 | 0 | OK | Ground clear controls. | 245 | 39.65 | 298.7
17024 | TIN-INTERP | Interpolated Ground | 108779.85 | -6.61 | 267.98 | 0 | 39.65 | 0 | OK | Ground clear controls. | 245 | 39.65 | 307.63
17025 | TIN-INTERP | Interpolated Ground | 108779.86 | -7.23 | 267.94 | 0 | 28 | 0 | OK | Ground clear controls. | 245 | 39.58 | 295.94
17026 | TIN-INTERP | Interpolated Ground | 108779.86 | -8.79 | 267.87 | 0 | 33.62 | 0 | OK | Ground clear controls. | 245 | 39.58 | 301.49
17027 | TIN-INTERP | Interpolated Ground | 108779.9 | 4.32 | 267.94 | 0 | 39.58 | 0 | OK | Ground clear controls. | 245 | 39.58 | 307.52
17028 | TIN-INTERP | Interpolated Ground | 108779.9 | 4.94 | 267.99 | 0 | 27.74 | 0 | OK | Ground clear controls. | 245 | 33.43 | 295.73
17029 | TIN-INTERP | Interpolated Ground | 108779.94 | 6.45 | 267.94 | 0 | 33.43 | 0 | OK | Ground clear controls. | 245 | 33.43 | 301.37
17030 | TIN-INTERP | Interpolated Ground | 108819.85 | -6.85 | 281.9 | 0 | 29.41 | 0 | OK | Ground clear controls. | 245 | 32.38 | 311.31
17031 | TIN-INTERP | Interpolated Ground | 108819.86 | -7.49 | 281.67 | 0 | 17.82 | 0 | OK | Ground clear controls. | 245 | 32.38 | 299.49
17032 | TIN-INTERP | Interpolated Ground | 108819.86 | -9.06 | 281.01 | 0 | 24.1 | 0 | OK | Ground clear controls. | 245 | 32.38 | 305.11
17033 | TIN-INTERP | Interpolated Ground | 108819.9 | 4.29 | 284.84 | 0 | 26.36 | 0 | OK | Ground clear controls. | 245 | 32.38 | 311.2
17034 | TIN-INTERP | Interpolated Ground | 108819.9 | 4.93 | 284.93 | 0 | 14.36 | 0 | OK | Ground clear controls. | 245 | 32.38 | 299.29
17035 | TIN-INTERP | Interpolated Ground | 108819.94 | 6.43 | 285.21 | 0 | 19.77 | 0 | OK | Ground clear controls. | 245 | 32.38 | 304.98
17036 | TIN-INTERP | Interpolated Ground | 108859.85 | -7.09 | 283.55 | 0 | 32.38 | 0 | OK | Ground clear controls. | 245 | 32.38 | 315.93
17037 | TIN-INTERP | Interpolated Ground | 108859.86 | -7.75 | 283.46 | 0 | 20.52 | 0 | OK | Ground clear controls. | 245 | 30.45 | 303.98
17038 | TIN-INTERP | Interpolated Ground | 108859.86 | -9.32 | 283.1 | 0 | 26.6 | 0 | OK | Ground clear controls. | 245 | 30.45 | 309.7
17039 | TIN-INTERP | Interpolated Ground | 108859.9 | 4.26 | 285.36 | 0 | 30.45 | 0 | OK | Ground clear controls. | 245 | 30.45 | 315.81
17040 | TIN-INTERP | Interpolated Ground | 108859.9 | 4.92 | 285.56 | 0 | 18.25 | 0 | OK | Ground clear controls. | 245 | 23.27 | 303.81
17041 | TIN-INTERP | Interpolated Ground | 108859.94 | 6.42 | 286.27 | 0 | 23.27 | 0 | OK | Ground clear controls. | 245 | 23.27 | 309.54
17042 | TIN-INTERP | Interpolated Ground | 108892.52 | 4.27 | 293.75 | 0 | 26.6 | 0 | OK | Ground clear controls. | 246 | 63.69 | 320.35
17043 | TIN-INTERP | Interpolated Ground | 108892.52 | 4.94 | 293.74 | 0 | 14.53 | 0 | OK | Ground clear controls. | 246 | 63.69 | 308.27
17044 | TIN-INTERP | Interpolated Ground | 108892.52 | 6.45 | 293.83 | 0 | 20.23 | 0 | OK | Ground clear controls. | 246 | 63.69 | 314.06
17045 | TIN-INTERP | Interpolated Ground | 108893.38 | -7.26 | 293.17 | 0 | 27.13 | 0 | OK | Ground clear controls. | 246 | 63.69 | 320.3
17046 | TIN-INTERP | Interpolated Ground | 108893.39 | -7.94 | 293.14 | 0 | 15.07 | 0 | OK | Ground clear controls. | 246 | 63.69 | 308.21
17047 | TIN-INTERP | Interpolated Ground | 108893.63 | -9.5 | 292.88 | 0 | 21.12 | 0 | OK | Ground clear controls. | 246 | 63.69 | 314
17048 | TIN-INTERP | Interpolated Ground | 108931.94 | 6.44 | 282.23 | 0 | 26.72 | 0 | OK | Ground clear controls. | 246 | 63.69 | 308.95
17049 | TIN-INTERP | Interpolated Ground | 108932.09 | 4.94 | 282.45 | 0 | 20.76 | 0 | OK | Ground clear controls. | 246 | 63.69 | 303.21
17050 | TIN-INTERP | Interpolated Ground | 108932.19 | 4.3 | 282.6 | 0 | 32.55 | 0 | OK | Ground clear controls. | 246 | 63.69 | 315.15
17051 | TIN-INTERP | Interpolated Ground | 108933.38 | -6.91 | 283.65 | 0 | 31.47 | 0 | OK | Ground clear controls. | 246 | 63.69 | 315.12
17052 | TIN-INTERP | Interpolated Ground | 108933.39 | -7.57 | 283.74 | 0 | 19.46 | 0 | OK | Ground clear controls. | 246 | 63.69 | 303.2
17053 | TIN-INTERP | Interpolated Ground | 108933.63 | -9.12 | 283.88 | 0 | 25.05 | 0 | OK | Ground clear controls. | 246 | 63.69 | 308.93
17054 | TIN-INTERP | Interpolated Ground | 108971.94 | 6.47 | 269.25 | 0 | 35.53 | 0 | OK | Ground clear controls. | 246 | 63.69 | 304.78
17055 | TIN-INTERP | Interpolated Ground | 108972.09 | 4.96 | 268.93 | 0 | 30.16 | 0 | OK | Ground clear controls. | 246 | 63.69 | 299.09
17056 | TIN-INTERP | Interpolated Ground | 108972.19 | 4.34 | 268.74 | 0 | 42.15 | 0 | OK | Ground clear controls. | 246 | 63.69 | 310.89
17057 | TIN-INTERP | Interpolated Ground | 108973.38 | -6.57 | 265.93 | 0 | 44.94 | 0 | OK | Ground clear controls. | 246 | 63.69 | 310.87
17058 | TIN-INTERP | Interpolated Ground | 108973.39 | -7.2 | 265.86 | 0 | 33.24 | 0 | OK | Ground clear controls. | 246 | 63.69 | 299.1
17059 | TIN-INTERP | Interpolated Ground | 108973.63 | -8.74 | 265.76 | 0 | 39.02 | 0 | OK | Ground clear controls. | 246 | 63.69 | 304.78
17060 | TIN-INTERP | Interpolated Ground | 109011.94 | 6.49 | 257.07 | 0 | 44.47 | 0 | OK | Ground clear controls. | 246 | 63.69 | 301.54
17061 | TIN-INTERP | Interpolated Ground | 109012.09 | 4.98 | 256.78 | 0 | 39.12 | 0 | OK | Ground clear controls. | 246 | 63.69 | 295.9
17062 | TIN-INTERP | Interpolated Ground | 109012.19 | 4.38 | 256.6 | 0 | 50.95 | 0 | OK | Ground clear controls. | 246 | 63.69 | 307.55
17063 | TIN-INTERP | Interpolated Ground | 109013.37 | -6.22 | 251.51 | 0 | 56.03 | 0 | OK | Ground clear controls. | 246 | 63.69 | 307.54
17064 | TIN-INTERP | Interpolated Ground | 109013.39 | -6.83 | 251.23 | 0 | 44.7 | 0 | OK | Ground clear controls. | 246 | 63.69 | 295.93
17065 | TIN-INTERP | Interpolated Ground | 109013.63 | -8.36 | 250.61 | 0 | 50.96 | 0 | OK | Ground clear controls. | 246 | 63.69 | 301.57
17066 | TIN-INTERP | Interpolated Ground | 109051.94 | 6.51 | 242.08 | 0 | 57.16 | 0 | OK | Ground clear controls. | 246 | 63.69 | 299.24
17067 | TIN-INTERP | Interpolated Ground | 109052.09 | 5.01 | 241.9 | 0 | 51.74 | 0 | OK | Ground clear controls. | 246 | 63.69 | 293.64
17068 | TIN-INTERP | Interpolated Ground | 109052.19 | 4.43 | 241.84 | 0 | 63.3 | 0 | OK | Ground clear controls. | 246 | 63.69 | 305.14
17069 | TIN-INTERP | Interpolated Ground | 109053.37 | -5.87 | 241.45 | 0 | 63.69 | 0 | OK | Ground clear controls. | 246 | 63.69 | 305.14
17070 | TIN-INTERP | Interpolated Ground | 109053.38 | -6.46 | 241.45 | 0 | 52.23 | 0 | OK | Ground clear controls. | 246 | 57.9 | 293.68
17071 | TIN-INTERP | Interpolated Ground | 109053.62 | -7.98 | 241.38 | 0 | 57.9 | 0 | OK | Ground clear controls. | 246 | 57.9 | 299.28
17072 | TIN-INTERP | Interpolated Ground | 109091.94 | 6.53 | 254.4 | 0 | 43.47 | 0 | OK | Ground clear controls. | 246 | 52.6 | 297.87
17073 | TIN-INTERP | Interpolated Ground | 109092.09 | 5.03 | 253.65 | 0 | 38.66 | 0 | OK | Ground clear controls. | 246 | 52.6 | 292.31
17074 | TIN-INTERP | Interpolated Ground | 109092.19 | 4.47 | 253.34 | 0 | 50.31 | 0 | OK | Ground clear controls. | 246 | 52.6 | 303.65
17075 | TIN-INTERP | Interpolated Ground | 109093.37 | -5.53 | 251.07 | 0 | 52.6 | 0 | OK | Ground clear controls. | 246 | 52.6 | 303.67
17076 | TIN-INTERP | Interpolated Ground | 109093.38 | -6.08 | 250.8 | 0 | 41.56 | 0 | OK | Ground clear controls. | 246 | 47.73 | 292.36
17077 | TIN-INTERP | Interpolated Ground | 109093.62 | -7.6 | 250.19 | 0 | 47.73 | 0 | OK | Ground clear controls. | 246 | 47.73 | 297.92
17078 | TIN-INTERP | Interpolated Ground | 109131.94 | 6.55 | 266.35 | 0 | 31.08 | 0 | OK | Ground clear controls. | 246 | 43.06 | 297.43
17079 | TIN-INTERP | Interpolated Ground | 109132.09 | 5.05 | 265.44 | 0 | 26.47 | 0 | OK | Ground clear controls. | 246 | 43.06 | 291.91
17080 | TIN-INTERP | Interpolated Ground | 109132.19 | 4.51 | 265.03 | 0 | 38.07 | 0 | OK | Ground clear controls. | 246 | 43.06 | 303.1
17081 | TIN-INTERP | Interpolated Ground | 109133.37 | -5.18 | 260.06 | 0 | 43.06 | 0 | OK | Ground clear controls. | 246 | 43.06 | 303.12
17082 | TIN-INTERP | Interpolated Ground | 109133.38 | -5.71 | 259.95 | 0 | 32.01 | 0 | OK | Ground clear controls. | 246 | 37.61 | 291.96
17083 | TIN-INTERP | Interpolated Ground | 109133.62 | -7.22 | 259.88 | 0 | 37.61 | 0 | OK | Ground clear controls. | 246 | 37.61 | 297.49
17084 | TIN-INTERP | Interpolated Ground | 109171.94 | 6.57 | 279.4 | 0 | 18.52 | 0 | OK | Ground clear controls. | 246 | 26.21 | 297.92
17085 | TIN-INTERP | Interpolated Ground | 109172.09 | 5.07 | 278.87 | 0 | 13.55 | 0 | OK | Ground clear controls. | 246 | 26.21 | 292.42
17086 | TIN-INTERP | Interpolated Ground | 109172.19 | 4.56 | 278.71 | 0 | 24.75 | 0 | OK | Ground clear controls. | 246 | 26.21 | 303.46
17087 | TIN-INTERP | Interpolated Ground | 109173.37 | -4.83 | 277.27 | 0 | 26.21 | 0 | OK | Ground clear controls. | 246 | 26.21 | 303.48
17088 | TIN-INTERP | Interpolated Ground | 109173.38 | -5.34 | 277.23 | 0 | 15.24 | 0 | OK | Ground clear controls. | 246 | 20.94 | 292.47
17089 | TIN-INTERP | Interpolated Ground | 109173.62 | -6.84 | 277.03 | 0 | 20.94 | 0 | OK | Ground clear controls. | 246 | 20.94 | 297.97
17090 | TIN-INTERP | Interpolated Ground | 109177.92 | 6.57 | 279.45 | 0 | 18.63 | 0 | OK | Ground clear controls. | 247 | 63.16 | 298.08
17091 | TIN-INTERP | Interpolated Ground | 109177.94 | 4.56 | 279.33 | 0 | 24.25 | 0 | OK | Ground clear controls. | 247 | 63.16 | 303.58
17092 | TIN-INTERP | Interpolated Ground | 109177.95 | -4.79 | 277.55 | 0 | 26.03 | 0 | OK | Ground clear controls. | 247 | 63.16 | 303.58
17093 | TIN-INTERP | Interpolated Ground | 109177.97 | 5.07 | 279.35 | 0 | 13.23 | 0 | OK | Ground clear controls. | 247 | 63.16 | 292.58
17094 | TIN-INTERP | Interpolated Ground | 109177.97 | -6.8 | 277.37 | 0 | 20.72 | 0 | OK | Ground clear controls. | 247 | 63.16 | 298.09
17095 | TIN-INTERP | Interpolated Ground | 109178.11 | -5.3 | 277.49 | 0 | 15.1 | 0 | OK | Ground clear controls. | 247 | 63.16 | 292.59
17096 | TIN-INTERP | Interpolated Ground | 109217.92 | 6.58 | 260.37 | 0 | 34.54 | 0 | OK | Ground clear controls. | 247 | 63.16 | 294.91
17097 | TIN-INTERP | Interpolated Ground | 109217.94 | 4.57 | 260.51 | 0 | 39.91 | 0 | OK | Ground clear controls. | 247 | 63.16 | 300.42
17098 | TIN-INTERP | Interpolated Ground | 109217.95 | -4.76 | 262.64 | 0 | 37.8 | 0 | OK | Ground clear controls. | 247 | 63.16 | 300.44
17099 | TIN-INTERP | Interpolated Ground | 109217.97 | 5.08 | 260.44 | 0 | 28.98 | 0 | OK | Ground clear controls. | 247 | 63.16 | 289.42
17100 | TIN-INTERP | Interpolated Ground | 109217.97 | -6.77 | 263.19 | 0 | 31.74 | 0 | OK | Ground clear controls. | 247 | 63.16 | 294.93
17101 | TIN-INTERP | Interpolated Ground | 109218.11 | -5.26 | 262.66 | 0 | 26.81 | 0 | OK | Ground clear controls. | 247 | 63.16 | 289.47
17102 | TIN-INTERP | Interpolated Ground | 109257.92 | 6.58 | 245.06 | 0 | 47.61 | 0 | OK | Ground clear controls. | 247 | 63.16 | 292.67
17103 | TIN-INTERP | Interpolated Ground | 109257.94 | 4.57 | 245.99 | 0 | 52.21 | 0 | OK | Ground clear controls. | 247 | 63.16 | 298.2
17104 | TIN-INTERP | Interpolated Ground | 109257.95 | -4.73 | 252.32 | 0 | 45.89 | 0 | OK | Ground clear controls. | 247 | 63.16 | 298.21
17105 | TIN-INTERP | Interpolated Ground | 109257.97 | 5.08 | 245.68 | 0 | 41.51 | 0 | OK | Ground clear controls. | 247 | 63.16 | 287.19
17106 | TIN-INTERP | Interpolated Ground | 109257.97 | -6.73 | 253.91 | 0 | 38.79 | 0 | OK | Ground clear controls. | 247 | 63.16 | 292.7
17107 | TIN-INTERP | Interpolated Ground | 109258.11 | -5.23 | 252.81 | 0 | 34.45 | 0 | OK | Ground clear controls. | 247 | 63.16 | 287.26
17108 | TIN-INTERP | Interpolated Ground | 109297.92 | 6.58 | 232.67 | 0 | 58.69 | 0 | OK | Ground clear controls. | 247 | 63.16 | 291.36
17109 | TIN-INTERP | Interpolated Ground | 109297.94 | 4.58 | 233.74 | 0 | 63.16 | 0 | OK | Ground clear controls. | 247 | 63.16 | 296.9
17110 | TIN-INTERP | Interpolated Ground | 109297.95 | -4.69 | 237.4 | 0 | 59.51 | 0 | OK | Ground clear controls. | 247 | 59.51 | 296.91
17111 | TIN-INTERP | Interpolated Ground | 109297.97 | 5.08 | 233.49 | 0 | 52.4 | 0 | OK | Ground clear controls. | 247 | 59.44 | 285.89
17112 | TIN-INTERP | Interpolated Ground | 109297.97 | -6.7 | 237.88 | 0 | 53.51 | 0 | OK | Ground clear controls. | 247 | 59.44 | 291.39
17113 | TIN-INTERP | Interpolated Ground | 109298.11 | -5.2 | 237.44 | 0 | 48.52 | 0 | OK | Ground clear controls. | 247 | 59.44 | 285.96
17114 | TIN-INTERP | Interpolated Ground | 109337.92 | 6.59 | 239.21 | 0 | 51.78 | 0 | OK | Ground clear controls. | 247 | 59.44 | 290.99
17115 | TIN-INTERP | Interpolated Ground | 109337.94 | 4.58 | 239.04 | 0 | 57.48 | 0 | OK | Ground clear controls. | 247 | 59.44 | 296.52
17116 | TIN-INTERP | Interpolated Ground | 109337.95 | -4.66 | 237.09 | 0 | 59.44 | 0 | OK | Ground clear controls. | 247 | 59.44 | 296.53
17117 | TIN-INTERP | Interpolated Ground | 109337.97 | 5.09 | 239.08 | 0 | 46.44 | 0 | OK | Ground clear controls. | 247 | 54.4 | 285.52
17118 | TIN-INTERP | Interpolated Ground | 109337.97 | -6.66 | 236.61 | 0 | 54.4 | 0 | OK | Ground clear controls. | 247 | 54.4 | 291.01
17119 | TIN-INTERP | Interpolated Ground | 109338.11 | -5.16 | 237.03 | 0 | 48.54 | 0 | OK | Ground clear controls. | 247 | 48.54 | 285.57
17120 | TIN-INTERP | Interpolated Ground | 109377.92 | 6.59 | 262.13 | 0 | 29.42 | 0 | OK | Ground clear controls. | 247 | 40.74 | 291.55
17121 | TIN-INTERP | Interpolated Ground | 109377.94 | 4.59 | 261.19 | 0 | 35.87 | 0 | OK | Ground clear controls. | 247 | 40.74 | 297.06
17122 | TIN-INTERP | Interpolated Ground | 109377.95 | -4.63 | 256.34 | 0 | 40.74 | 0 | OK | Ground clear controls. | 247 | 40.74 | 297.08
17123 | TIN-INTERP | Interpolated Ground | 109377.97 | 5.09 | 261.33 | 0 | 24.74 | 0 | OK | Ground clear controls. | 247 | 35.33 | 286.07
17124 | TIN-INTERP | Interpolated Ground | 109377.97 | -6.63 | 256.24 | 0 | 35.33 | 0 | OK | Ground clear controls. | 247 | 35.33 | 291.57
17125 | TIN-INTERP | Interpolated Ground | 109378.11 | -5.13 | 256.38 | 0 | 29.73 | 0 | OK | Ground clear controls. | 247 | 29.73 | 286.11
17126 | TIN-INTERP | Interpolated Ground | 109417.28 | -5.1 | 272.3 | 0 | 15.22 | 0 | OK | Ground clear controls. | 248 | 80.02 | 287.52
17127 | TIN-INTERP | Interpolated Ground | 109417.29 | -4.6 | 272.33 | 0 | 26.19 | 0 | OK | Ground clear controls. | 248 | 80.02 | 298.52
17128 | TIN-INTERP | Interpolated Ground | 109417.3 | 6.59 | 273.45 | 0 | 19.57 | 0 | OK | Ground clear controls. | 248 | 80.02 | 293.02
17129 | TIN-INTERP | Interpolated Ground | 109417.31 | 5.09 | 273.29 | 0 | 14.22 | 0 | OK | Ground clear controls. | 248 | 80.02 | 287.51
17130 | TIN-INTERP | Interpolated Ground | 109417.34 | -6.6 | 272.03 | 0 | 20.98 | 0 | OK | Ground clear controls. | 248 | 80.02 | 293.01
17131 | TIN-INTERP | Interpolated Ground | 109417.36 | 4.59 | 273.31 | 0 | 25.2 | 0 | OK | Ground clear controls. | 248 | 80.02 | 298.51
17132 | TIN-INTERP | Interpolated Ground | 109457.28 | -5.05 | 249.44 | 0 | 26.06 | 0 | OK | Ground clear controls. | 248 | 80.02 | 275.5
17133 | TIN-INTERP | Interpolated Ground | 109457.29 | -4.55 | 249.81 | 0 | 36.73 | 0 | OK | Ground clear controls. | 248 | 80.02 | 286.54
17134 | TIN-INTERP | Interpolated Ground | 109457.3 | 6.55 | 258.28 | 0 | 22.65 | 0 | OK | Ground clear controls. | 248 | 80.02 | 280.93
17135 | TIN-INTERP | Interpolated Ground | 109457.31 | 5.05 | 257.34 | 0 | 18.12 | 0 | OK | Ground clear controls. | 248 | 80.02 | 275.46
17136 | TIN-INTERP | Interpolated Ground | 109457.34 | -6.55 | 248.05 | 0 | 32.95 | 0 | OK | Ground clear controls. | 248 | 80.02 | 281
17137 | TIN-INTERP | Interpolated Ground | 109457.36 | 4.55 | 256.97 | 0 | 29.63 | 0 | OK | Ground clear controls. | 248 | 80.02 | 286.6
17138 | TIN-INTERP | Interpolated Ground | 109497.28 | -5 | 207.96 | 0 | 56.51 | 0 | OK | Ground clear controls. | 248 | 80.02 | 264.47
17139 | TIN-INTERP | Interpolated Ground | 109497.29 | -4.5 | 208.08 | 0 | 67.47 | 0 | OK | Ground clear controls. | 248 | 80.02 | 275.55
17140 | TIN-INTERP | Interpolated Ground | 109497.3 | 6.5 | 212.6 | 0 | 57.23 | 0 | OK | Ground clear controls. | 248 | 80.02 | 269.83
17141 | TIN-INTERP | Interpolated Ground | 109497.31 | 5 | 212.06 | 0 | 52.32 | 0 | OK | Ground clear controls. | 248 | 80.02 | 264.38
17142 | TIN-INTERP | Interpolated Ground | 109497.34 | -6.5 | 207.39 | 0 | 62.57 | 0 | OK | Ground clear controls. | 248 | 80.02 | 269.96
17143 | TIN-INTERP | Interpolated Ground | 109497.36 | 4.5 | 211.77 | 0 | 63.88 | 0 | OK | Ground clear controls. | 248 | 80.02 | 275.65
17144 | TIN-INTERP | Interpolated Ground | 109537.28 | -4.96 | 193.43 | 0 | 60.97 | 0 | OK | Ground clear controls. | 248 | 80.02 | 254.4
17145 | TIN-INTERP | Interpolated Ground | 109537.29 | -4.46 | 193.6 | 0 | 71.94 | 0 | OK | Ground clear controls. | 248 | 80.02 | 265.54
17146 | TIN-INTERP | Interpolated Ground | 109537.3 | 6.46 | 196.45 | 0 | 63.27 | 0 | OK | Ground clear controls. | 248 | 80.02 | 259.72
17147 | TIN-INTERP | Interpolated Ground | 109537.31 | 4.96 | 196.36 | 0 | 57.91 | 0 | OK | Ground clear controls. | 248 | 80.02 | 254.27
17148 | TIN-INTERP | Interpolated Ground | 109537.34 | -6.46 | 192.84 | 0 | 67.05 | 0 | OK | Ground clear controls. | 248 | 80.02 | 259.89
17149 | TIN-INTERP | Interpolated Ground | 109537.36 | 4.46 | 196.29 | 0 | 69.38 | 0 | OK | Ground clear controls. | 248 | 80.02 | 265.67
17150 | TIN-INTERP | Interpolated Ground | 109577.28 | -4.91 | 186.15 | 0 | 59.15 | 0 | OK | Ground clear controls. | 248 | 80.02 | 245.3
17151 | TIN-INTERP | Interpolated Ground | 109577.29 | -4.41 | 186.26 | 0 | 70.24 | 0 | OK | Ground clear controls. | 248 | 80.02 | 256.5
17152 | TIN-INTERP | Interpolated Ground | 109577.3 | 6.41 | 188.31 | 0 | 62.29 | 0 | OK | Ground clear controls. | 248 | 80.02 | 250.6
17153 | TIN-INTERP | Interpolated Ground | 109577.31 | 4.91 | 188.01 | 0 | 57.14 | 0 | OK | Ground clear controls. | 248 | 80.02 | 245.15
17154 | TIN-INTERP | Interpolated Ground | 109577.34 | -6.41 | 185.8 | 0 | 65 | 0 | OK | Ground clear controls. | 248 | 80.02 | 250.8
17155 | TIN-INTERP | Interpolated Ground | 109577.36 | 4.41 | 187.9 | 0 | 68.76 | 0 | OK | Ground clear controls. | 248 | 80.02 | 256.66
17156 | TIN-INTERP | Interpolated Ground | 109617.28 | -4.87 | 169.52 | 0 | 67.63 | 0 | OK | Ground clear controls. | 248 | 80.02 | 237.15
17157 | TIN-INTERP | Interpolated Ground | 109617.29 | -4.37 | 169.19 | 0 | 79.24 | 0 | OK | Ground clear controls. | 248 | 80.02 | 248.43
17158 | TIN-INTERP | Interpolated Ground | 109617.3 | 6.36 | 166.71 | 0 | 75.73 | 0 | OK | Ground clear controls. | 248 | 80.02 | 242.44
17159 | TIN-INTERP | Interpolated Ground | 109617.31 | 4.86 | 168.1 | 0 | 68.89 | 0 | OK | Ground clear controls. | 248 | 80.02 | 236.99
17160 | TIN-INTERP | Interpolated Ground | 109617.34 | -6.37 | 169.89 | 0 | 72.79 | 0 | OK | Ground clear controls. | 248 | 80.02 | 242.68
17161 | TIN-INTERP | Interpolated Ground | 109617.36 | 4.36 | 168.58 | 0 | 80.02 | 0 | OK | Ground clear controls. | 248 | 80.02 | 248.6
17162 | TIN-INTERP | Interpolated Ground | 109657.28 | -4.82 | 168.2 | 0 | 61.77 | 0 | OK | Ground clear controls. | 248 | 72.98 | 229.97
17163 | TIN-INTERP | Interpolated Ground | 109657.29 | -4.32 | 168.34 | 0 | 72.98 | 0 | OK | Ground clear controls. | 248 | 72.98 | 241.32
17164 | TIN-INTERP | Interpolated Ground | 109657.3 | 6.32 | 175.54 | 0 | 59.73 | 0 | OK | Ground clear controls. | 248 | 67.8 | 235.27
17165 | TIN-INTERP | Interpolated Ground | 109657.31 | 4.82 | 174.61 | 0 | 55.19 | 0 | OK | Ground clear controls. | 248 | 67.8 | 229.8
17166 | TIN-INTERP | Interpolated Ground | 109657.34 | -6.32 | 167.72 | 0 | 67.8 | 0 | OK | Ground clear controls. | 248 | 67.8 | 235.52
17167 | TIN-INTERP | Interpolated Ground | 109657.36 | 4.32 | 174.31 | 0 | 67.21 | 0 | OK | Ground clear controls. | 248 | 67.21 | 241.52
17168 | TIN-INTERP | Interpolated Ground | 109697.28 | -4.77 | 188.3 | 0 | 35.44 | 0 | OK | Ground clear controls. | 248 | 46.82 | 223.74
17169 | TIN-INTERP | Interpolated Ground | 109697.29 | -4.27 | 188.35 | 0 | 46.82 | 0 | OK | Ground clear controls. | 248 | 46.82 | 235.17
17170 | TIN-INTERP | Interpolated Ground | 109697.3 | 6.27 | 189.85 | 0 | 39.21 | 0 | OK | Ground clear controls. | 248 | 45.95 | 229.06
17171 | TIN-INTERP | Interpolated Ground | 109697.31 | 4.77 | 189.53 | 0 | 34.04 | 0 | OK | Ground clear controls. | 248 | 45.95 | 223.57
17172 | TIN-INTERP | Interpolated Ground | 109697.34 | -6.27 | 188 | 0 | 41.3 | 0 | OK | Ground clear controls. | 248 | 45.95 | 229.3
17173 | TIN-INTERP | Interpolated Ground | 109697.36 | 4.27 | 189.42 | 0 | 45.95 | 0 | OK | Ground clear controls. | 248 | 45.95 | 235.37
17174 | TIN-INTERP | Interpolated Ground | 109737.28 | -4.73 | 187.74 | 0 | 30.71 | 0 | OK | Ground clear controls. | 248 | 42.09 | 218.45
17175 | TIN-INTERP | Interpolated Ground | 109737.29 | -4.23 | 187.89 | 0 | 42.09 | 0 | OK | Ground clear controls. | 248 | 42.09 | 229.98
17176 | TIN-INTERP | Interpolated Ground | 109737.3 | 6.23 | 190.48 | 0 | 33.34 | 0 | OK | Ground clear controls. | 248 | 40.15 | 223.82
17177 | TIN-INTERP | Interpolated Ground | 109737.31 | 4.73 | 190.18 | 0 | 28.12 | 0 | OK | Ground clear controls. | 248 | 40.15 | 218.3
17178 | TIN-INTERP | Interpolated Ground | 109737.34 | -6.23 | 187.32 | 0 | 36.73 | 0 | OK | Ground clear controls. | 248 | 40.15 | 224.05
17179 | TIN-INTERP | Interpolated Ground | 109737.36 | 4.23 | 190.01 | 0 | 40.15 | 0 | OK | Ground clear controls. | 248 | 40.15 | 230.16
17180 | TIN-INTERP | Interpolated Ground | 109777.28 | -4.68 | 186.98 | 0 | 27.15 | 0 | OK | Ground clear controls. | 248 | 38.72 | 214.13
17181 | TIN-INTERP | Interpolated Ground | 109777.29 | -4.18 | 187.03 | 0 | 38.72 | 0 | OK | Ground clear controls. | 248 | 38.72 | 225.75
17182 | TIN-INTERP | Interpolated Ground | 109777.3 | 6.18 | 187.7 | 0 | 31.84 | 0 | OK | Ground clear controls. | 248 | 38.33 | 219.54
17183 | TIN-INTERP | Interpolated Ground | 109777.31 | 4.68 | 187.61 | 0 | 26.37 | 0 | OK | Ground clear controls. | 248 | 38.33 | 213.98
17184 | TIN-INTERP | Interpolated Ground | 109777.34 | -6.18 | 186.81 | 0 | 32.94 | 0 | OK | Ground clear controls. | 248 | 38.33 | 219.75
17185 | TIN-INTERP | Interpolated Ground | 109777.36 | 4.18 | 187.58 | 0 | 38.33 | 0 | OK | Ground clear controls. | 248 | 38.33 | 225.91
17186 | TIN-INTERP | Interpolated Ground | 109817.28 | -4.64 | 185.73 | 0 | 25 | 0 | OK | Ground clear controls. | 248 | 36.59 | 210.73
17187 | TIN-INTERP | Interpolated Ground | 109817.29 | -4.14 | 185.87 | 0 | 36.59 | 0 | OK | Ground clear controls. | 248 | 36.59 | 222.46
17188 | TIN-INTERP | Interpolated Ground | 109817.3 | 6.14 | 188.6 | 0 | 27.61 | 0 | OK | Ground clear controls. | 248 | 36.54 | 216.21
17189 | TIN-INTERP | Interpolated Ground | 109817.31 | 4.64 | 188.2 | 0 | 22.41 | 0 | OK | Ground clear controls. | 248 | 36.54 | 210.61
17190 | TIN-INTERP | Interpolated Ground | 109817.34 | -6.14 | 185.28 | 0 | 31.11 | 0 | OK | Ground clear controls. | 248 | 36.54 | 216.39
17191 | TIN-INTERP | Interpolated Ground | 109817.36 | 4.14 | 188.07 | 0 | 34.53 | 0 | OK | Ground clear controls. | 248 | 36.54 | 222.6
17192 | TIN-INTERP | Interpolated Ground | 109857.28 | -4.59 | 183.5 | 0 | 24.78 | 0 | OK | Ground clear controls. | 248 | 36.54 | 208.28
17193 | TIN-INTERP | Interpolated Ground | 109857.29 | -4.09 | 183.59 | 0 | 36.54 | 0 | OK | Ground clear controls. | 248 | 36.54 | 220.13
17194 | TIN-INTERP | Interpolated Ground | 109857.3 | 6.09 | 185.27 | 0 | 28.58 | 0 | OK | Ground clear controls. | 248 | 36 | 213.85
17195 | TIN-INTERP | Interpolated Ground | 109857.31 | 4.59 | 184.99 | 0 | 23.21 | 0 | OK | Ground clear controls. | 248 | 36 | 208.2
17196 | TIN-INTERP | Interpolated Ground | 109857.34 | -6.09 | 183.17 | 0 | 30.82 | 0 | OK | Ground clear controls. | 248 | 36 | 213.99
17197 | TIN-INTERP | Interpolated Ground | 109857.36 | 4.09 | 184.84 | 0 | 35.38 | 0 | OK | Ground clear controls. | 248 | 36 | 220.22
17198 | TIN-INTERP | Interpolated Ground | 109897.28 | -4.55 | 182.42 | 0 | 24.35 | 0 | OK | Ground clear controls. | 248 | 36 | 206.77
17199 | TIN-INTERP | Interpolated Ground | 109897.29 | -4.05 | 182.75 | 0 | 36 | 0 | OK | Ground clear controls. | 248 | 36 | 218.75
17200 | TIN-INTERP | Interpolated Ground | 109897.3 | 6.04 | 186.04 | 0 | 26.41 | 0 | OK | Ground clear controls. | 248 | 33.14 | 212.45
17201 | TIN-INTERP | Interpolated Ground | 109897.31 | 4.54 | 185.76 | 0 | 20.96 | 0 | OK | Ground clear controls. | 248 | 33.14 | 206.72
17202 | TIN-INTERP | Interpolated Ground | 109897.34 | -6.05 | 181.26 | 0 | 31.26 | 0 | OK | Ground clear controls. | 248 | 33.14 | 212.52
17203 | TIN-INTERP | Interpolated Ground | 109897.36 | 4.04 | 185.66 | 0 | 33.14 | 0 | OK | Ground clear controls. | 248 | 33.14 | 218.8
17204 | TIN-INTERP | Interpolated Ground | 109939.05 | 4.5 | 182.63 | 0 | 23.3 | 0 | OK | Ground clear controls. | 249 | 102.94 | 205.93
17205 | TIN-INTERP | Interpolated Ground | 109939.05 | 6 | 182.88 | 0 | 28.87 | 0 | OK | Ground clear controls. | 249 | 102.94 | 211.75
17206 | TIN-INTERP | Interpolated Ground | 109939.05 | 4 | 182.6 | 0 | 35.45 | 0 | OK | Ground clear controls. | 249 | 102.94 | 218.05
17207 | TIN-INTERP | Interpolated Ground | 109939.05 | -4.51 | 179.9 | 0 | 26.02 | 0 | OK | Ground clear controls. | 249 | 102.94 | 205.92
17208 | TIN-INTERP | Interpolated Ground | 109939.06 | -4.01 | 180.14 | 0 | 37.91 | 0 | OK | Ground clear controls. | 249 | 102.94 | 218.05
17209 | TIN-INTERP | Interpolated Ground | 109939.06 | -6.01 | 178.97 | 0 | 32.78 | 0 | OK | Ground clear controls. | 249 | 102.94 | 211.75
17210 | TIN-INTERP | Interpolated Ground | 109979.05 | 4.53 | 163.82 | 0 | 38.43 | 0 | OK | Ground clear controls. | 249 | 102.94 | 202.25
17211 | TIN-INTERP | Interpolated Ground | 109979.05 | 6.03 | 164.29 | 0 | 44.08 | 0 | OK | Ground clear controls. | 249 | 102.94 | 208.37
17212 | TIN-INTERP | Interpolated Ground | 109979.05 | 4.04 | 163.66 | 0 | 50.93 | 0 | OK | Ground clear controls. | 249 | 102.94 | 214.59
17213 | TIN-INTERP | Interpolated Ground | 109979.05 | -4.6 | 161.78 | 0 | 40.41 | 0 | OK | Ground clear controls. | 249 | 102.94 | 202.19
17214 | TIN-INTERP | Interpolated Ground | 109979.06 | -4.11 | 161.81 | 0 | 52.78 | 0 | OK | Ground clear controls. | 249 | 102.94 | 214.59
17215 | TIN-INTERP | Interpolated Ground | 109979.06 | -6.1 | 161.65 | 0 | 46.69 | 0 | OK | Ground clear controls. | 249 | 102.94 | 208.34
17216 | TIN-INTERP | Interpolated Ground | 110019.05 | 4.56 | 157.79 | 0 | 41.74 | 0 | OK | Ground clear controls. | 249 | 102.94 | 199.53
17217 | TIN-INTERP | Interpolated Ground | 110019.05 | 6.06 | 157.6 | 0 | 48.3 | 0 | OK | Ground clear controls. | 249 | 102.94 | 205.9
17218 | TIN-INTERP | Interpolated Ground | 110019.05 | 4.08 | 157.81 | 0 | 54.23 | 0 | OK | Ground clear controls. | 249 | 102.94 | 212.04
17219 | TIN-INTERP | Interpolated Ground | 110019.05 | -4.7 | 157.19 | 0 | 42.24 | 0 | OK | Ground clear controls. | 249 | 102.94 | 199.43
17220 | TIN-INTERP | Interpolated Ground | 110019.06 | -4.21 | 157.27 | 0 | 54.78 | 0 | OK | Ground clear controls. | 249 | 102.94 | 212.05
17221 | TIN-INTERP | Interpolated Ground | 110019.06 | -6.2 | 156.98 | 0 | 48.86 | 0 | OK | Ground clear controls. | 249 | 102.94 | 205.84
17222 | TIN-INTERP | Interpolated Ground | 110059.05 | 4.6 | 133.43 | 0 | 64.33 | 0 | OK | Ground clear controls. | 249 | 102.94 | 197.76
17223 | TIN-INTERP | Interpolated Ground | 110059.05 | 6.09 | 132.61 | 0 | 71.73 | 0 | OK | Ground clear controls. | 249 | 102.94 | 204.34
17224 | TIN-INTERP | Interpolated Ground | 110059.05 | 4.11 | 133.66 | 0 | 76.75 | 0 | OK | Ground clear controls. | 249 | 102.94 | 210.41
17225 | TIN-INTERP | Interpolated Ground | 110059.05 | -4.79 | 135.83 | 0 | 61.81 | 0 | OK | Ground clear controls. | 249 | 102.94 | 197.64
17226 | TIN-INTERP | Interpolated Ground | 110059.06 | -4.31 | 135.78 | 0 | 74.65 | 0 | OK | Ground clear controls. | 249 | 102.94 | 210.43
17227 | TIN-INTERP | Interpolated Ground | 110059.06 | -6.29 | 136.1 | 0 | 68.17 | 0 | OK | Ground clear controls. | 249 | 102.94 | 204.27
17228 | TIN-INTERP | Interpolated Ground | 110099.05 | 4.63 | 106.65 | 0 | 90.3 | 0 | OK | Ground clear controls. | 249 | 102.94 | 196.95
17229 | TIN-INTERP | Interpolated Ground | 110099.05 | 6.12 | 105.94 | 0 | 97.74 | 0 | OK | Ground clear controls. | 249 | 102.94 | 203.68
17230 | TIN-INTERP | Interpolated Ground | 110099.05 | 4.15 | 106.76 | 0 | 102.94 | 0 | OK | Ground clear controls. | 249 | 102.94 | 209.7
17231 | TIN-INTERP | Interpolated Ground | 110099.05 | -4.88 | 109.8 | 0 | 87 | 0 | OK | Ground clear controls. | 249 | 100.01 | 196.8
17232 | TIN-INTERP | Interpolated Ground | 110099.06 | -4.42 | 109.71 | 0 | 100.01 | 0 | OK | Ground clear controls. | 249 | 100.01 | 209.72
17233 | TIN-INTERP | Interpolated Ground | 110099.06 | -6.39 | 110.3 | 0 | 93.3 | 0 | OK | Ground clear controls. | 249 | 93.3 | 203.6
17234 | TIN-INTERP | Interpolated Ground | 110139.05 | 4.66 | 129.52 | 0 | 67.58 | 0 | OK | Ground clear controls. | 249 | 86 | 197.1
17235 | TIN-INTERP | Interpolated Ground | 110139.05 | 6.15 | 130.69 | 0 | 73.25 | 0 | OK | Ground clear controls. | 249 | 86 | 203.94
17236 | TIN-INTERP | Interpolated Ground | 110139.05 | 4.19 | 129.27 | 0 | 80.63 | 0 | OK | Ground clear controls. | 249 | 86 | 209.9
17237 | TIN-INTERP | Interpolated Ground | 110139.05 | -4.98 | 124.16 | 0 | 72.78 | 0 | OK | Ground clear controls. | 249 | 86 | 196.94
17238 | TIN-INTERP | Interpolated Ground | 110139.06 | -4.52 | 123.93 | 0 | 86 | 0 | OK | Ground clear controls. | 249 | 86 | 209.93
17239 | TIN-INTERP | Interpolated Ground | 110139.06 | -6.48 | 125.47 | 0 | 78.38 | 0 | OK | Ground clear controls. | 249 | 78.38 | 203.85
17240 | TIN-INTERP | Interpolated Ground | 110179.05 | 4.69 | 152.7 | 0 | 45.52 | 0 | OK | Ground clear controls. | 249 | 61.4 | 198.22
17241 | TIN-INTERP | Interpolated Ground | 110179.05 | 6.18 | 153.18 | 0 | 51.93 | 0 | OK | Ground clear controls. | 249 | 61.4 | 205.11
17242 | TIN-INTERP | Interpolated Ground | 110179.05 | 4.23 | 152.58 | 0 | 58.44 | 0 | OK | Ground clear controls. | 249 | 61.4 | 211.02
17243 | TIN-INTERP | Interpolated Ground | 110179.05 | -5.07 | 149.52 | 0 | 48.54 | 0 | OK | Ground clear controls. | 249 | 61.4 | 198.06
17244 | TIN-INTERP | Interpolated Ground | 110179.06 | -4.62 | 149.66 | 0 | 61.4 | 0 | OK | Ground clear controls. | 249 | 61.4 | 211.06
17245 | TIN-INTERP | Interpolated Ground | 110179.06 | -6.58 | 148.97 | 0 | 56.05 | 0 | OK | Ground clear controls. | 249 | 56.05 | 205.02
17246 | TIN-INTERP | Interpolated Ground | 110219.05 | 4.72 | 165.39 | 0 | 34.9 | 0 | OK | Ground clear controls. | 249 | 49.19 | 200.29
17247 | TIN-INTERP | Interpolated Ground | 110219.05 | 6.21 | 165.57 | 0 | 41.61 | 0 | OK | Ground clear controls. | 249 | 49.19 | 207.18
17248 | TIN-INTERP | Interpolated Ground | 110219.05 | 4.26 | 165.35 | 0 | 47.71 | 0 | OK | Ground clear controls. | 249 | 49.19 | 213.06
17249 | TIN-INTERP | Interpolated Ground | 110219.05 | -5.17 | 164.02 | 0 | 36.11 | 0 | OK | Ground clear controls. | 249 | 49.19 | 200.13
17250 | TIN-INTERP | Interpolated Ground | 110219.06 | -4.72 | 163.92 | 0 | 49.19 | 0 | OK | Ground clear controls. | 249 | 49.19 | 213.11
17251 | TIN-INTERP | Interpolated Ground | 110219.06 | -6.67 | 164.08 | 0 | 43.02 | 0 | OK | Ground clear controls. | 249 | 48.15 | 207.1
17252 | TIN-INTERP | Interpolated Ground | 110259.05 | 4.75 | 173.67 | 0 | 29.66 | 0 | OK | Ground clear controls. | 249 | 48.15 | 203.33
17253 | TIN-INTERP | Interpolated Ground | 110259.05 | 6.24 | 173.87 | 0 | 36.3 | 0 | OK | Ground clear controls. | 249 | 48.15 | 210.17
17254 | TIN-INTERP | Interpolated Ground | 110259.05 | 4.3 | 173.6 | 0 | 42.41 | 0 | OK | Ground clear controls. | 249 | 48.15 | 216.01
17255 | TIN-INTERP | Interpolated Ground | 110259.05 | -5.26 | 170.68 | 0 | 32.5 | 0 | OK | Ground clear controls. | 249 | 48.15 | 203.18
17256 | TIN-INTERP | Interpolated Ground | 110259.05 | -4.83 | 170.84 | 0 | 45.23 | 0 | OK | Ground clear controls. | 249 | 48.15 | 216.07
17257 | TIN-INTERP | Interpolated Ground | 110259.06 | -6.77 | 170.17 | 0 | 39.94 | 0 | OK | Ground clear controls. | 249 | 48.15 | 210.11
17258 | TIN-INTERP | Interpolated Ground | 110299.05 | 4.78 | 176.94 | 0 | 30.38 | 0 | OK | Ground clear controls. | 249 | 48.15 | 207.32
17259 | TIN-INTERP | Interpolated Ground | 110299.05 | 6.27 | 178.02 | 0 | 36.04 | 0 | OK | Ground clear controls. | 249 | 48.15 | 214.06
17260 | TIN-INTERP | Interpolated Ground | 110299.05 | 4.34 | 176.66 | 0 | 43.22 | 0 | OK | Ground clear controls. | 249 | 48.15 | 219.88
17261 | TIN-INTERP | Interpolated Ground | 110299.05 | -5.36 | 171.55 | 0 | 35.64 | 0 | OK | Ground clear controls. | 249 | 48.15 | 207.19
17262 | TIN-INTERP | Interpolated Ground | 110299.05 | -4.93 | 171.8 | 0 | 48.15 | 0 | OK | Ground clear controls. | 249 | 48.15 | 219.95
17263 | TIN-INTERP | Interpolated Ground | 110299.06 | -6.86 | 170.82 | 0 | 43.2 | 0 | OK | Ground clear controls. | 249 | 43.34 | 214.02
17264 | TIN-INTERP | Interpolated Ground | 110339.05 | 4.81 | 188.16 | 0 | 24.12 | 0 | OK | Ground clear controls. | 249 | 43.34 | 212.28
17265 | TIN-INTERP | Interpolated Ground | 110339.05 | 6.3 | 188.69 | 0 | 30.18 | 0 | OK | Ground clear controls. | 249 | 43.34 | 218.87
17266 | TIN-INTERP | Interpolated Ground | 110339.05 | 4.38 | 188.01 | 0 | 36.67 | 0 | OK | Ground clear controls. | 249 | 43.34 | 224.68
17267 | TIN-INTERP | Interpolated Ground | 110339.05 | -5.45 | 183.03 | 0 | 29.17 | 0 | OK | Ground clear controls. | 249 | 43.34 | 212.2
17268 | TIN-INTERP | Interpolated Ground | 110339.05 | -5.03 | 183.26 | 0 | 41.49 | 0 | OK | Ground clear controls. | 249 | 43.34 | 224.75
17269 | TIN-INTERP | Interpolated Ground | 110339.06 | -6.96 | 182.14 | 0 | 36.71 | 0 | OK | Ground clear controls. | 249 | 43.34 | 218.85
17270 | TIN-INTERP | Interpolated Ground | 110379.05 | 4.84 | 193.15 | 0 | 25.07 | 0 | OK | Ground clear controls. | 249 | 43.34 | 218.22
17271 | TIN-INTERP | Interpolated Ground | 110379.05 | 6.33 | 194.38 | 0 | 30.22 | 0 | OK | Ground clear controls. | 249 | 43.34 | 224.6
17272 | TIN-INTERP | Interpolated Ground | 110379.05 | 4.41 | 192.79 | 0 | 37.61 | 0 | OK | Ground clear controls. | 249 | 43.34 | 230.4
17273 | TIN-INTERP | Interpolated Ground | 110379.05 | -5.55 | 187 | 0 | 31.17 | 0 | OK | Ground clear controls. | 249 | 43.34 | 218.17
17274 | TIN-INTERP | Interpolated Ground | 110379.05 | -5.13 | 187.15 | 0 | 43.34 | 0 | OK | Ground clear controls. | 249 | 43.34 | 230.49
17275 | TIN-INTERP | Interpolated Ground | 110379.06 | -7.05 | 186.56 | 0 | 38.07 | 0 | OK | Ground clear controls. | 249 | 38.07 | 224.63
17276 | TIN-INTERP | Interpolated Ground | 110419.05 | 4.87 | 211.04 | 0 | 14.07 | 0 | OK | Ground clear controls. | 249 | 32.65 | 225.11
17277 | TIN-INTERP | Interpolated Ground | 110419.05 | 6.36 | 211.83 | 0 | 19.41 | 0 | OK | Ground clear controls. | 249 | 32.65 | 231.24
17278 | TIN-INTERP | Interpolated Ground | 110419.05 | 4.45 | 210.82 | 0 | 26.22 | 0 | OK | Ground clear controls. | 249 | 32.65 | 237.04
17279 | TIN-INTERP | Interpolated Ground | 110419.05 | -5.64 | 204.06 | 0 | 21.05 | 0 | OK | Ground clear controls. | 249 | 32.65 | 225.11
17280 | TIN-INTERP | Interpolated Ground | 110419.05 | -5.24 | 204.49 | 0 | 32.65 | 0 | OK | Ground clear controls. | 249 | 32.65 | 237.14
17281 | TIN-INTERP | Interpolated Ground | 110419.06 | -7.15 | 202.47 | 0 | 28.84 | 0 | OK | Ground clear controls. | 249 | 28.96 | 231.31
17282 | TIN-INTERP | Interpolated Ground | 110459.05 | 4.9 | 218.68 | 0 | 14.3 | 0 | OK | Ground clear controls. | 249 | 28.96 | 232.98
17283 | TIN-INTERP | Interpolated Ground | 110459.05 | 6.39 | 218.74 | 0 | 20.07 | 0 | OK | Ground clear controls. | 249 | 28.96 | 238.81
17284 | TIN-INTERP | Interpolated Ground | 110459.05 | 4.49 | 218.58 | 0 | 26.03 | 0 | OK | Ground clear controls. | 249 | 28.96 | 244.61
17285 | TIN-INTERP | Interpolated Ground | 110459.05 | -5.74 | 215.57 | 0 | 17.47 | 0 | OK | Ground clear controls. | 249 | 28.96 | 233.04
17286 | TIN-INTERP | Interpolated Ground | 110459.05 | -5.34 | 215.76 | 0 | 28.96 | 0 | OK | Ground clear controls. | 249 | 28.96 | 244.72
17287 | TIN-INTERP | Interpolated Ground | 110459.06 | -7.24 | 214.57 | 0 | 24.35 | 0 | OK | Ground clear controls. | 249 | 24.35 | 238.92
17288 | TIN-INTERP | Interpolated Ground | 110496.68 | -7.33 | 218.79 | 0 | 28.15 | 0 | OK | Ground clear controls. | 250 | 51.94 | 246.94
17289 | TIN-INTERP | Interpolated Ground | 110496.79 | -5.83 | 219.12 | 0 | 22.32 | 0 | OK | Ground clear controls. | 250 | 51.94 | 241.44
17290 | TIN-INTERP | Interpolated Ground | 110496.8 | -5.44 | 219.15 | 0 | 33.59 | 0 | OK | Ground clear controls. | 250 | 51.94 | 252.74
17291 | TIN-INTERP | Interpolated Ground | 110497.13 | 4.53 | 218.52 | 0 | 34.22 | 0 | OK | Ground clear controls. | 250 | 51.94 | 252.74
17292 | TIN-INTERP | Interpolated Ground | 110497.13 | 4.94 | 218.46 | 0 | 22.98 | 0 | OK | Ground clear controls. | 250 | 51.94 | 241.44
17293 | TIN-INTERP | Interpolated Ground | 110497.13 | 6.43 | 218.11 | 0 | 28.84 | 0 | OK | Ground clear controls. | 250 | 51.94 | 246.95
17294 | TIN-INTERP | Interpolated Ground | 110536.91 | 6.44 | 210.58 | 0 | 25.25 | 0 | OK | Ground clear controls. | 250 | 51.94 | 235.83
17295 | TIN-INTERP | Interpolated Ground | 110536.97 | 4.95 | 210.42 | 0 | 19.7 | 0 | OK | Ground clear controls. | 250 | 51.94 | 230.12
17296 | TIN-INTERP | Interpolated Ground | 110536.98 | 4.53 | 210.37 | 0 | 31.22 | 0 | OK | Ground clear controls. | 250 | 51.94 | 241.59
17297 | TIN-INTERP | Interpolated Ground | 110537.24 | -5.36 | 214.8 | 0 | 26.8 | 0 | OK | Ground clear controls. | 250 | 51.94 | 241.6
17298 | TIN-INTERP | Interpolated Ground | 110537.27 | -5.76 | 214.8 | 0 | 15.31 | 0 | OK | Ground clear controls. | 250 | 51.94 | 230.11
17299 | TIN-INTERP | Interpolated Ground | 110537.28 | -7.27 | 215.16 | 0 | 20.67 | 0 | OK | Ground clear controls. | 250 | 51.94 | 235.83
17300 | TIN-INTERP | Interpolated Ground | 110576.91 | 6.46 | 191.91 | 0 | 33.76 | 0 | OK | Ground clear controls. | 250 | 51.94 | 225.67
17301 | TIN-INTERP | Interpolated Ground | 110576.97 | 4.97 | 192.22 | 0 | 27.57 | 0 | OK | Ground clear controls. | 250 | 51.94 | 219.79
17302 | TIN-INTERP | Interpolated Ground | 110576.98 | 4.54 | 192.26 | 0 | 39.11 | 0 | OK | Ground clear controls. | 250 | 51.94 | 231.37
17303 | TIN-INTERP | Interpolated Ground | 110577.24 | -5.28 | 193.99 | 0 | 37.43 | 0 | OK | Ground clear controls. | 250 | 51.94 | 231.42
17304 | TIN-INTERP | Interpolated Ground | 110577.27 | -5.69 | 194.28 | 0 | 25.5 | 0 | OK | Ground clear controls. | 250 | 51.94 | 219.78
17305 | TIN-INTERP | Interpolated Ground | 110577.28 | -7.2 | 194.98 | 0 | 30.7 | 0 | OK | Ground clear controls. | 250 | 51.94 | 225.68
17306 | TIN-INTERP | Interpolated Ground | 110616.91 | 6.48 | 177.68 | 0 | 38.78 | 0 | OK | Ground clear controls. | 250 | 51.94 | 216.46
17307 | TIN-INTERP | Interpolated Ground | 110616.97 | 4.99 | 178.1 | 0 | 32.37 | 0 | OK | Ground clear controls. | 250 | 51.94 | 210.47
17308 | TIN-INTERP | Interpolated Ground | 110616.98 | 4.55 | 178.19 | 0 | 43.94 | 0 | OK | Ground clear controls. | 250 | 51.94 | 222.13
17309 | TIN-INTERP | Interpolated Ground | 110617.24 | -5.2 | 180.97 | 0 | 41.21 | 0 | OK | Ground clear controls. | 250 | 51.94 | 222.18
17310 | TIN-INTERP | Interpolated Ground | 110617.27 | -5.62 | 180.85 | 0 | 29.6 | 0 | OK | Ground clear controls. | 250 | 51.94 | 210.45
17311 | TIN-INTERP | Interpolated Ground | 110617.28 | -7.13 | 180.87 | 0 | 35.6 | 0 | OK | Ground clear controls. | 250 | 51.94 | 216.47
17312 | TIN-INTERP | Interpolated Ground | 110656.91 | 6.5 | 161.66 | 0 | 46.54 | 0 | OK | Ground clear controls. | 250 | 51.94 | 208.2
17313 | TIN-INTERP | Interpolated Ground | 110656.97 | 5.01 | 161.79 | 0 | 40.35 | 0 | OK | Ground clear controls. | 250 | 51.94 | 202.14
17314 | TIN-INTERP | Interpolated Ground | 110656.98 | 4.56 | 161.89 | 0 | 51.94 | 0 | OK | Ground clear controls. | 250 | 51.94 | 213.83
17315 | TIN-INTERP | Interpolated Ground | 110657.24 | -5.12 | 163.34 | 0 | 50.54 | 0 | OK | Ground clear controls. | 250 | 50.54 | 213.88
17316 | TIN-INTERP | Interpolated Ground | 110657.27 | -5.55 | 163.5 | 0 | 38.62 | 0 | OK | Ground clear controls. | 250 | 48.12 | 202.12
17317 | TIN-INTERP | Interpolated Ground | 110657.28 | -7.05 | 164.13 | 0 | 44.07 | 0 | OK | Ground clear controls. | 250 | 48.12 | 208.2
17318 | TIN-INTERP | Interpolated Ground | 110696.91 | 6.52 | 165.4 | 0 | 35.48 | 0 | OK | Ground clear controls. | 250 | 48.12 | 200.88
17319 | TIN-INTERP | Interpolated Ground | 110696.97 | 5.02 | 166.56 | 0 | 28.23 | 0 | OK | Ground clear controls. | 250 | 48.12 | 194.79
17320 | TIN-INTERP | Interpolated Ground | 110696.98 | 4.57 | 166.95 | 0 | 39.52 | 0 | OK | Ground clear controls. | 250 | 48.12 | 206.47
17321 | TIN-INTERP | Interpolated Ground | 110697.24 | -5.03 | 172.6 | 0 | 33.93 | 0 | OK | Ground clear controls. | 250 | 48.12 | 206.53
17322 | TIN-INTERP | Interpolated Ground | 110697.27 | -5.47 | 172.64 | 0 | 22.13 | 0 | OK | Ground clear controls. | 250 | 48.12 | 194.77
17323 | TIN-INTERP | Interpolated Ground | 110697.28 | -6.98 | 172.63 | 0 | 28.25 | 0 | OK | Ground clear controls. | 250 | 48.12 | 200.88
17324 | TIN-INTERP | Interpolated Ground | 110736.91 | 6.53 | 159.77 | 0 | 34.71 | 0 | OK | Ground clear controls. | 250 | 48.12 | 194.48
17325 | TIN-INTERP | Interpolated Ground | 110736.97 | 5.04 | 160.45 | 0 | 27.98 | 0 | OK | Ground clear controls. | 250 | 48.12 | 188.43
17326 | TIN-INTERP | Interpolated Ground | 110736.98 | 4.58 | 160.57 | 0 | 39.49 | 0 | OK | Ground clear controls. | 250 | 48.12 | 200.06
17327 | TIN-INTERP | Interpolated Ground | 110737.24 | -4.95 | 164.27 | 0 | 35.83 | 0 | OK | Ground clear controls. | 250 | 48.12 | 200.1
17328 | TIN-INTERP | Interpolated Ground | 110737.27 | -5.4 | 164.56 | 0 | 23.85 | 0 | OK | Ground clear controls. | 250 | 48.12 | 188.41
17329 | TIN-INTERP | Interpolated Ground | 110737.28 | -6.91 | 165.12 | 0 | 29.37 | 0 | OK | Ground clear controls. | 250 | 48.12 | 194.49
17330 | TIN-INTERP | Interpolated Ground | 110776.91 | 6.55 | 145.91 | 0 | 43.12 | 0 | OK | Ground clear controls. | 250 | 48.12 | 189.03
17331 | TIN-INTERP | Interpolated Ground | 110776.97 | 5.06 | 146.29 | 0 | 36.76 | 0 | OK | Ground clear controls. | 250 | 48.12 | 183.05
17332 | TIN-INTERP | Interpolated Ground | 110776.98 | 4.58 | 146.45 | 0 | 48.12 | 0 | OK | Ground clear controls. | 250 | 48.12 | 194.57
17333 | TIN-INTERP | Interpolated Ground | 110777.24 | -4.87 | 150.01 | 0 | 44.6 | 0 | OK | Ground clear controls. | 250 | 44.6 | 194.61
17334 | TIN-INTERP | Interpolated Ground | 110777.27 | -5.33 | 150.12 | 0 | 32.9 | 0 | OK | Ground clear controls. | 250 | 44.28 | 183.02
17335 | TIN-INTERP | Interpolated Ground | 110777.28 | -6.84 | 150.74 | 0 | 38.29 | 0 | OK | Ground clear controls. | 250 | 44.28 | 189.03
17336 | TIN-INTERP | Interpolated Ground | 110816.91 | 6.57 | 151.53 | 0 | 32.98 | 0 | OK | Ground clear controls. | 250 | 44.28 | 184.51
17337 | TIN-INTERP | Interpolated Ground | 110816.97 | 5.07 | 152.16 | 0 | 26.48 | 0 | OK | Ground clear controls. | 250 | 44.28 | 178.64
17338 | TIN-INTERP | Interpolated Ground | 110816.98 | 4.59 | 152.37 | 0 | 37.65 | 0 | OK | Ground clear controls. | 250 | 44.28 | 190.02
17339 | TIN-INTERP | Interpolated Ground | 110817.24 | -4.79 | 157.11 | 0 | 32.94 | 0 | OK | Ground clear controls. | 250 | 44.28 | 190.05
17340 | TIN-INTERP | Interpolated Ground | 110817.27 | -5.26 | 157.29 | 0 | 21.33 | 0 | OK | Ground clear controls. | 250 | 44.28 | 178.62
17341 | TIN-INTERP | Interpolated Ground | 110817.28 | -6.76 | 157.84 | 0 | 26.66 | 0 | OK | Ground clear controls. | 250 | 44.28 | 184.5
17342 | TIN-INTERP | Interpolated Ground | 110856.91 | 6.59 | 141.33 | 0 | 39.57 | 0 | OK | Ground clear controls. | 250 | 44.28 | 180.9
17343 | TIN-INTERP | Interpolated Ground | 110856.97 | 5.09 | 141.94 | 0 | 33.27 | 0 | OK | Ground clear controls. | 250 | 44.28 | 175.21
17344 | TIN-INTERP | Interpolated Ground | 110856.98 | 4.6 | 142.13 | 0 | 44.28 | 0 | OK | Ground clear controls. | 250 | 44.28 | 186.41
17345 | TIN-INTERP | Interpolated Ground | 110857.24 | -4.7 | 146.63 | 0 | 39.78 | 0 | OK | Ground clear controls. | 250 | 39.78 | 186.41
17346 | TIN-INTERP | Interpolated Ground | 110857.27 | -5.19 | 146.79 | 0 | 28.4 | 0 | OK | Ground clear controls. | 250 | 33.91 | 175.19
17347 | TIN-INTERP | Interpolated Ground | 110857.28 | -6.69 | 146.97 | 0 | 33.91 | 0 | OK | Ground clear controls. | 250 | 33.91 | 180.88
17348 | TIN-INTERP | Interpolated Ground | 110892.32 | -6.63 | 153.11 | 0 | 25.37 | 0 | OK | Ground clear controls. | 251 | 59.04 | 178.48
17349 | TIN-INTERP | Interpolated Ground | 110892.34 | -4.63 | 152.84 | 0 | 31.14 | 0 | OK | Ground clear controls. | 251 | 59.04 | 183.98
17350 | TIN-INTERP | Interpolated Ground | 110892.34 | -5.12 | 152.93 | 0 | 20.05 | 0 | OK | Ground clear controls. | 251 | 59.04 | 172.98
17351 | TIN-INTERP | Interpolated Ground | 110892.36 | 4.61 | 151.49 | 0 | 32.49 | 0 | OK | Ground clear controls. | 251 | 59.04 | 183.98
17352 | TIN-INTERP | Interpolated Ground | 110892.39 | 5.1 | 151.34 | 0 | 21.64 | 0 | OK | Ground clear controls. | 251 | 59.04 | 172.98
17353 | TIN-INTERP | Interpolated Ground | 110892.41 | 6.6 | 151.12 | 0 | 27.36 | 0 | OK | Ground clear controls. | 251 | 59.04 | 178.48
17354 | TIN-INTERP | Interpolated Ground | 110932.32 | -6.65 | 133.2 | 0 | 35.52 | 0 | OK | Ground clear controls. | 251 | 59.04 | 168.72
17355 | TIN-INTERP | Interpolated Ground | 110932.33 | -4.66 | 133.43 | 0 | 40.81 | 0 | OK | Ground clear controls. | 251 | 59.04 | 174.24
17356 | TIN-INTERP | Interpolated Ground | 110932.34 | -5.15 | 133.21 | 0 | 29.69 | 0 | OK | Ground clear controls. | 251 | 59.04 | 162.9
17357 | TIN-INTERP | Interpolated Ground | 110932.36 | 4.63 | 133.83 | 0 | 40.37 | 0 | OK | Ground clear controls. | 251 | 59.04 | 174.2
17358 | TIN-INTERP | Interpolated Ground | 110932.39 | 5.12 | 133.79 | 0 | 29.12 | 0 | OK | Ground clear controls. | 251 | 59.04 | 162.91
17359 | TIN-INTERP | Interpolated Ground | 110932.41 | 6.62 | 133.9 | 0 | 34.82 | 0 | OK | Ground clear controls. | 251 | 59.04 | 168.72
17360 | TIN-INTERP | Interpolated Ground | 110972.32 | -6.67 | 116.61 | 0 | 43.3 | 0 | OK | Ground clear controls. | 251 | 59.04 | 159.91
17361 | TIN-INTERP | Interpolated Ground | 110972.33 | -4.69 | 116.65 | 0 | 48.8 | 0 | OK | Ground clear controls. | 251 | 59.04 | 165.45
17362 | TIN-INTERP | Interpolated Ground | 110972.34 | -5.17 | 116.63 | 0 | 37.18 | 0 | OK | Ground clear controls. | 251 | 59.04 | 153.81
17363 | TIN-INTERP | Interpolated Ground | 110972.36 | 4.65 | 117.78 | 0 | 47.59 | 0 | OK | Ground clear controls. | 251 | 59.04 | 165.37
17364 | TIN-INTERP | Interpolated Ground | 110972.39 | 5.14 | 117.91 | 0 | 35.92 | 0 | OK | Ground clear controls. | 251 | 59.04 | 153.83
17365 | TIN-INTERP | Interpolated Ground | 110972.41 | 6.63 | 118.21 | 0 | 41.7 | 0 | OK | Ground clear controls. | 251 | 59.04 | 159.91
17366 | TIN-INTERP | Interpolated Ground | 111012.32 | -6.69 | 108.42 | 0 | 43.62 | 0 | OK | Ground clear controls. | 251 | 59.04 | 152.04
17367 | TIN-INTERP | Interpolated Ground | 111012.33 | -4.72 | 108.55 | 0 | 49.06 | 0 | OK | Ground clear controls. | 251 | 59.04 | 157.61
17368 | TIN-INTERP | Interpolated Ground | 111012.34 | -5.19 | 108.58 | 0 | 37.14 | 0 | OK | Ground clear controls. | 251 | 59.04 | 145.72
17369 | TIN-INTERP | Interpolated Ground | 111012.36 | 4.67 | 107.81 | 0 | 49.69 | 0 | OK | Ground clear controls. | 251 | 59.04 | 157.5
17370 | TIN-INTERP | Interpolated Ground | 111012.39 | 5.15 | 107.74 | 0 | 38 | 0 | OK | Ground clear controls. | 251 | 59.04 | 145.74
17371 | TIN-INTERP | Interpolated Ground | 111012.41 | 6.65 | 107.28 | 0 | 44.75 | 0 | OK | Ground clear controls. | 251 | 59.04 | 152.03
17372 | TIN-INTERP | Interpolated Ground | 111052.32 | -6.72 | 105.9 | 0 | 39.22 | 0 | OK | Ground clear controls. | 251 | 59.04 | 145.12
17373 | TIN-INTERP | Interpolated Ground | 111052.33 | -4.75 | 105.17 | 0 | 45.53 | 0 | OK | Ground clear controls. | 251 | 59.04 | 150.7
17374 | TIN-INTERP | Interpolated Ground | 111052.34 | -5.22 | 105.36 | 0 | 33.26 | 0 | OK | Ground clear controls. | 251 | 59.04 | 138.62
17375 | TIN-INTERP | Interpolated Ground | 111052.36 | 4.7 | 103.24 | 0 | 47.32 | 0 | OK | Ground clear controls. | 251 | 59.04 | 150.56
17376 | TIN-INTERP | Interpolated Ground | 111052.39 | 5.17 | 103.24 | 0 | 35.4 | 0 | OK | Ground clear controls. | 251 | 59.04 | 138.64
17377 | TIN-INTERP | Interpolated Ground | 111052.41 | 6.67 | 103.15 | 0 | 41.96 | 0 | OK | Ground clear controls. | 251 | 59.04 | 145.11
17378 | TIN-INTERP | Interpolated Ground | 111092.32 | -6.74 | 103.01 | 0 | 36.12 | 0 | OK | Ground clear controls. | 251 | 59.04 | 139.13
17379 | TIN-INTERP | Interpolated Ground | 111092.33 | -4.78 | 100.8 | 0 | 43.94 | 0 | OK | Ground clear controls. | 251 | 59.04 | 144.74
17380 | TIN-INTERP | Interpolated Ground | 111092.34 | -5.24 | 101.52 | 0 | 31 | 0 | OK | Ground clear controls. | 251 | 59.04 | 132.52
17381 | TIN-INTERP | Interpolated Ground | 111092.36 | 4.72 | 96.21 | 0 | 48.38 | 0 | OK | Ground clear controls. | 251 | 59.04 | 144.59
17382 | TIN-INTERP | Interpolated Ground | 111092.39 | 5.18 | 95.85 | 0 | 36.69 | 0 | OK | Ground clear controls. | 251 | 59.04 | 132.54
17383 | TIN-INTERP | Interpolated Ground | 111092.41 | 6.68 | 94.6 | 0 | 44.53 | 0 | OK | Ground clear controls. | 251 | 59.04 | 139.13
17384 | TIN-INTERP | Interpolated Ground | 111132.32 | -6.76 | 88.87 | 0 | 45.21 | 0 | OK | Ground clear controls. | 251 | 59.04 | 134.08
17385 | TIN-INTERP | Interpolated Ground | 111132.33 | -4.81 | 88.03 | 0 | 51.69 | 0 | OK | Ground clear controls. | 251 | 59.04 | 139.72
17386 | TIN-INTERP | Interpolated Ground | 111132.34 | -5.26 | 88.23 | 0 | 39.16 | 0 | OK | Ground clear controls. | 251 | 59.04 | 127.39
17387 | TIN-INTERP | Interpolated Ground | 111132.36 | 4.74 | 80.51 | 0 | 59.04 | 0 | OK | Ground clear controls. | 251 | 59.04 | 139.55
17388 | TIN-INTERP | Interpolated Ground | 111132.39 | 5.2 | 80.18 | 0 | 47.24 | 0 | OK | Ground clear controls. | 251 | 57.26 | 127.42
17389 | TIN-INTERP | Interpolated Ground | 111132.41 | 6.7 | 79.59 | 0 | 54.49 | 0 | OK | Ground clear controls. | 251 | 57.26 | 134.08
17390 | TIN-INTERP | Interpolated Ground | 111172.32 | -6.79 | 82.77 | 0 | 47.19 | 0 | OK | Ground clear controls. | 251 | 57.26 | 129.96
17391 | TIN-INTERP | Interpolated Ground | 111172.33 | -4.84 | 82.31 | 0 | 53.31 | 0 | OK | Ground clear controls. | 251 | 57.26 | 135.62
17392 | TIN-INTERP | Interpolated Ground | 111172.34 | -5.29 | 82.45 | 0 | 40.81 | 0 | OK | Ground clear controls. | 251 | 57.26 | 123.26
17393 | TIN-INTERP | Interpolated Ground | 111172.36 | 4.76 | 81.35 | 0 | 54.09 | 0 | OK | Ground clear controls. | 251 | 57.26 | 135.44
17394 | TIN-INTERP | Interpolated Ground | 111172.39 | 5.21 | 81.1 | 0 | 42.18 | 0 | OK | Ground clear controls. | 251 | 57.26 | 123.28
17395 | TIN-INTERP | Interpolated Ground | 111172.41 | 6.71 | 80.39 | 0 | 49.57 | 0 | OK | Ground clear controls. | 251 | 57.26 | 129.96
17396 | TIN-INTERP | Interpolated Ground | 111212.32 | -6.81 | 76.49 | 0 | 50.28 | 0 | OK | Ground clear controls. | 251 | 57.26 | 126.77
17397 | TIN-INTERP | Interpolated Ground | 111212.33 | -4.86 | 75.61 | 0 | 56.83 | 0 | OK | Ground clear controls. | 251 | 57.26 | 132.44
17398 | TIN-INTERP | Interpolated Ground | 111212.34 | -5.31 | 75.76 | 0 | 44.33 | 0 | OK | Ground clear controls. | 251 | 57.26 | 120.09
17399 | TIN-INTERP | Interpolated Ground | 111212.36 | 4.78 | 75.02 | 0 | 57.26 | 0 | OK | Ground clear controls. | 251 | 57.26 | 132.28
17400 | TIN-INTERP | Interpolated Ground | 111212.39 | 5.23 | 75.23 | 0 | 44.88 | 0 | OK | Ground clear controls. | 251 | 50.88 | 120.11
17401 | TIN-INTERP | Interpolated Ground | 111212.41 | 6.73 | 75.99 | 0 | 50.78 | 0 | OK | Ground clear controls. | 251 | 50.88 | 126.77
17402 | TIN-INTERP | Interpolated Ground | 111252.32 | -6.83 | 78.81 | 0 | 45.71 | 0 | OK | Ground clear controls. | 251 | 50.88 | 124.52
17403 | TIN-INTERP | Interpolated Ground | 111252.33 | -4.89 | 80 | 0 | 50.21 | 0 | OK | Ground clear controls. | 251 | 50.88 | 130.21
17404 | TIN-INTERP | Interpolated Ground | 111252.34 | -5.33 | 79.78 | 0 | 38.13 | 0 | OK | Ground clear controls. | 251 | 50.88 | 117.91
17405 | TIN-INTERP | Interpolated Ground | 111252.36 | 4.8 | 84.16 | 0 | 45.9 | 0 | OK | Ground clear controls. | 251 | 50.88 | 130.06
17406 | TIN-INTERP | Interpolated Ground | 111252.39 | 5.24 | 84.34 | 0 | 33.6 | 0 | OK | Ground clear controls. | 251 | 50.88 | 117.94
17407 | TIN-INTERP | Interpolated Ground | 111252.41 | 6.74 | 84.94 | 0 | 39.57 | 0 | OK | Ground clear controls. | 251 | 50.88 | 124.51
17408 | TIN-INTERP | Interpolated Ground | 111292.32 | -6.85 | 83.34 | 0 | 39.84 | 0 | OK | Ground clear controls. | 251 | 50.88 | 123.18
17409 | TIN-INTERP | Interpolated Ground | 111292.33 | -4.92 | 84.49 | 0 | 44.41 | 0 | OK | Ground clear controls. | 251 | 50.88 | 128.9
17410 | TIN-INTERP | Interpolated Ground | 111292.34 | -5.35 | 84.22 | 0 | 32.48 | 0 | OK | Ground clear controls. | 251 | 50.88 | 116.7
17411 | TIN-INTERP | Interpolated Ground | 111292.36 | 4.83 | 92.45 | 0 | 36.32 | 0 | OK | Ground clear controls. | 251 | 50.88 | 128.77
17412 | TIN-INTERP | Interpolated Ground | 111292.39 | 5.26 | 92.75 | 0 | 23.98 | 0 | OK | Ground clear controls. | 251 | 50.88 | 116.73
17413 | TIN-INTERP | Interpolated Ground | 111292.41 | 6.76 | 93.45 | 0 | 29.73 | 0 | OK | Ground clear controls. | 251 | 50.88 | 123.18
17414 | TIN-INTERP | Interpolated Ground | 111332.32 | -6.88 | 89.23 | 0 | 33.55 | 0 | OK | Ground clear controls. | 251 | 50.88 | 122.78
17415 | TIN-INTERP | Interpolated Ground | 111332.33 | -4.95 | 90.38 | 0 | 38.13 | 0 | OK | Ground clear controls. | 251 | 50.88 | 128.51
17416 | TIN-INTERP | Interpolated Ground | 111332.34 | -5.38 | 90.14 | 0 | 26.34 | 0 | OK | Ground clear controls. | 251 | 50.88 | 116.48
17417 | TIN-INTERP | Interpolated Ground | 111332.36 | 4.85 | 94.87 | 0 | 33.53 | 0 | OK | Ground clear controls. | 251 | 50.88 | 128.4
17418 | TIN-INTERP | Interpolated Ground | 111332.39 | 5.27 | 95.16 | 0 | 21.33 | 0 | OK | Ground clear controls. | 251 | 50.88 | 116.49
17419 | TIN-INTERP | Interpolated Ground | 111332.41 | 6.77 | 95.85 | 0 | 26.92 | 0 | OK | Ground clear controls. | 251 | 50.88 | 122.77
17420 | TIN-INTERP | Interpolated Ground | 111372.32 | -6.9 | 78.32 | 0 | 44.98 | 0 | OK | Ground clear controls. | 251 | 50.88 | 123.3
17421 | TIN-INTERP | Interpolated Ground | 111372.33 | -4.98 | 78.18 | 0 | 50.88 | 0 | OK | Ground clear controls. | 251 | 50.88 | 129.06
17422 | TIN-INTERP | Interpolated Ground | 111372.34 | -5.4 | 78.29 | 0 | 38.92 | 0 | OK | Ground clear controls. | 251 | 50.85 | 117.21
17423 | TIN-INTERP | Interpolated Ground | 111372.36 | 4.87 | 78.13 | 0 | 50.85 | 0 | OK | Ground clear controls. | 251 | 50.85 | 128.98
17424 | TIN-INTERP | Interpolated Ground | 111372.39 | 5.29 | 78.11 | 0 | 39.12 | 0 | OK | Ground clear controls. | 251 | 47.28 | 117.23
17425 | TIN-INTERP | Interpolated Ground | 111372.41 | 6.79 | 78.12 | 0 | 45.18 | 0 | OK | Ground clear controls. | 251 | 47.28 | 123.3
17426 | TIN-INTERP | Interpolated Ground | 111412.32 | -6.92 | 82.49 | 0 | 42.25 | 0 | OK | Ground clear controls. | 251 | 47.28 | 124.74
17427 | TIN-INTERP | Interpolated Ground | 111412.33 | -5.01 | 83.24 | 0 | 47.28 | 0 | OK | Ground clear controls. | 251 | 47.28 | 130.52
17428 | TIN-INTERP | Interpolated Ground | 111412.34 | -5.42 | 83.13 | 0 | 35.81 | 0 | OK | Ground clear controls. | 251 | 41.49 | 118.94
17429 | TIN-INTERP | Interpolated Ground | 111412.36 | 4.89 | 88.99 | 0 | 41.49 | 0 | OK | Ground clear controls. | 251 | 41.49 | 130.48
17430 | TIN-INTERP | Interpolated Ground | 111412.39 | 5.31 | 89.14 | 0 | 29.8 | 0 | OK | Ground clear controls. | 251 | 35.12 | 118.94
17431 | TIN-INTERP | Interpolated Ground | 111412.41 | 6.8 | 89.62 | 0 | 35.12 | 0 | OK | Ground clear controls. | 251 | 35.12 | 124.74
17432 | TIN-INTERP | Interpolated Ground | 111451.09 | -6.94 | 93.04 | 0 | 33.99 | 0 | OK | Ground clear controls. | 252 | 56.96 | 127.03
17433 | TIN-INTERP | Interpolated Ground | 111451.11 | -5.45 | 93.46 | 0 | 28.07 | 0 | OK | Ground clear controls. | 252 | 56.96 | 121.53
17434 | TIN-INTERP | Interpolated Ground | 111451.12 | -5.04 | 93.61 | 0 | 39.22 | 0 | OK | Ground clear controls. | 252 | 56.96 | 132.83
17435 | TIN-INTERP | Interpolated Ground | 111451.12 | 5.32 | 96.98 | 0 | 24.55 | 0 | OK | Ground clear controls. | 252 | 56.96 | 121.53
17436 | TIN-INTERP | Interpolated Ground | 111451.14 | 4.91 | 96.78 | 0 | 36.05 | 0 | OK | Ground clear controls. | 252 | 56.96 | 132.83
17437 | TIN-INTERP | Interpolated Ground | 111451.15 | 6.82 | 97.31 | 0 | 29.72 | 0 | OK | Ground clear controls. | 252 | 56.96 | 127.03
17438 | TIN-INTERP | Interpolated Ground | 111491.1 | -6.91 | 87.5 | 0 | 36.53 | 0 | OK | Ground clear controls. | 252 | 56.96 | 124.03
17439 | TIN-INTERP | Interpolated Ground | 111491.11 | -5.41 | 87.86 | 0 | 30.45 | 0 | OK | Ground clear controls. | 252 | 56.96 | 118.31
17440 | TIN-INTERP | Interpolated Ground | 111491.12 | -4.99 | 87.94 | 0 | 41.86 | 0 | OK | Ground clear controls. | 252 | 56.96 | 129.8
17441 | TIN-INTERP | Interpolated Ground | 111491.12 | 5.3 | 89.74 | 0 | 28.58 | 0 | OK | Ground clear controls. | 252 | 56.96 | 118.32
17442 | TIN-INTERP | Interpolated Ground | 111491.14 | 4.88 | 89.74 | 0 | 40.04 | 0 | OK | Ground clear controls. | 252 | 56.96 | 129.78
17443 | TIN-INTERP | Interpolated Ground | 111491.15 | 6.8 | 90.01 | 0 | 34.03 | 0 | OK | Ground clear controls. | 252 | 56.96 | 124.04
17444 | TIN-INTERP | Interpolated Ground | 111531.1 | -6.87 | 72.3 | 0 | 49.66 | 0 | OK | Ground clear controls. | 252 | 56.96 | 121.96
17445 | TIN-INTERP | Interpolated Ground | 111531.11 | -5.38 | 72.14 | 0 | 43.94 | 0 | OK | Ground clear controls. | 252 | 56.96 | 116.08
17446 | TIN-INTERP | Interpolated Ground | 111531.12 | -4.95 | 72.13 | 0 | 55.58 | 0 | OK | Ground clear controls. | 252 | 56.96 | 127.71
17447 | TIN-INTERP | Interpolated Ground | 111531.12 | 5.28 | 72.35 | 0 | 43.75 | 0 | OK | Ground clear controls. | 252 | 56.96 | 116.1
17448 | TIN-INTERP | Interpolated Ground | 111531.14 | 4.85 | 72.19 | 0 | 55.47 | 0 | OK | Ground clear controls. | 252 | 56.96 | 127.66
17449 | TIN-INTERP | Interpolated Ground | 111531.15 | 6.78 | 72.67 | 0 | 49.3 | 0 | OK | Ground clear controls. | 252 | 56.96 | 121.97
17450 | TIN-INTERP | Interpolated Ground | 111571.1 | -6.84 | 69.3 | 0 | 51.52 | 0 | OK | Ground clear controls. | 252 | 56.96 | 120.82
17451 | TIN-INTERP | Interpolated Ground | 111571.11 | -5.34 | 69.53 | 0 | 45.29 | 0 | OK | Ground clear controls. | 252 | 56.96 | 114.82
17452 | TIN-INTERP | Interpolated Ground | 111571.12 | -4.91 | 69.58 | 0 | 56.96 | 0 | OK | Ground clear controls. | 252 | 56.96 | 126.54
17453 | TIN-INTERP | Interpolated Ground | 111571.12 | 5.26 | 72.23 | 0 | 42.61 | 0 | OK | Ground clear controls. | 252 | 54.5 | 114.84
17454 | TIN-INTERP | Interpolated Ground | 111571.14 | 4.82 | 71.98 | 0 | 54.5 | 0 | OK | Ground clear controls. | 252 | 54.5 | 126.48
17455 | TIN-INTERP | Interpolated Ground | 111571.15 | 6.75 | 73.35 | 0 | 47.49 | 0 | OK | Ground clear controls. | 252 | 47.49 | 120.84
17456 | TIN-INTERP | Interpolated Ground | 111611.1 | -6.8 | 81.26 | 0 | 39.34 | 0 | OK | Ground clear controls. | 252 | 45.56 | 120.6
17457 | TIN-INTERP | Interpolated Ground | 111611.11 | -5.31 | 81.93 | 0 | 32.61 | 0 | OK | Ground clear controls. | 252 | 45.56 | 114.54
17458 | TIN-INTERP | Interpolated Ground | 111611.12 | -4.86 | 82.06 | 0 | 44.23 | 0 | OK | Ground clear controls. | 252 | 45.56 | 126.29
17459 | TIN-INTERP | Interpolated Ground | 111611.12 | 5.23 | 86.27 | 0 | 28.29 | 0 | OK | Ground clear controls. | 252 | 45.56 | 114.56
17460 | TIN-INTERP | Interpolated Ground | 111611.14 | 4.79 | 86.07 | 0 | 40.16 | 0 | OK | Ground clear controls. | 252 | 45.56 | 126.23
17461 | TIN-INTERP | Interpolated Ground | 111611.15 | 6.73 | 86.77 | 0 | 33.86 | 0 | OK | Ground clear controls. | 252 | 45.56 | 120.63
17462 | TIN-INTERP | Interpolated Ground | 111651.1 | -6.77 | 92.14 | 0 | 29.17 | 0 | OK | Ground clear controls. | 252 | 45.56 | 121.31
17463 | TIN-INTERP | Interpolated Ground | 111651.11 | -5.27 | 92.81 | 0 | 22.42 | 0 | OK | Ground clear controls. | 252 | 45.56 | 115.23
17464 | TIN-INTERP | Interpolated Ground | 111651.12 | -4.82 | 92.94 | 0 | 34.03 | 0 | OK | Ground clear controls. | 252 | 45.56 | 126.97
17465 | TIN-INTERP | Interpolated Ground | 111651.12 | 5.21 | 96 | 0 | 19.25 | 0 | OK | Ground clear controls. | 252 | 45.56 | 115.25
17466 | TIN-INTERP | Interpolated Ground | 111651.14 | 4.76 | 95.82 | 0 | 31.08 | 0 | OK | Ground clear controls. | 252 | 45.56 | 126.9
17467 | TIN-INTERP | Interpolated Ground | 111651.15 | 6.71 | 96.52 | 0 | 24.82 | 0 | OK | Ground clear controls. | 252 | 45.56 | 121.34
17468 | TIN-INTERP | Interpolated Ground | 111691.1 | -6.73 | 98.96 | 0 | 24 | 0 | OK | Ground clear controls. | 252 | 45.56 | 122.96
17469 | TIN-INTERP | Interpolated Ground | 111691.11 | -5.24 | 99.53 | 0 | 17.37 | 0 | OK | Ground clear controls. | 252 | 45.56 | 116.9
17470 | TIN-INTERP | Interpolated Ground | 111691.12 | -4.77 | 99.69 | 0 | 28.9 | 0 | OK | Ground clear controls. | 252 | 45.56 | 128.59
17471 | TIN-INTERP | Interpolated Ground | 111691.12 | 5.19 | 104.38 | 0 | 12.53 | 0 | OK | Ground clear controls. | 252 | 45.56 | 116.91
17472 | TIN-INTERP | Interpolated Ground | 111691.14 | 4.73 | 104.13 | 0 | 24.39 | 0 | OK | Ground clear controls. | 252 | 45.56 | 128.52
17473 | TIN-INTERP | Interpolated Ground | 111691.15 | 6.69 | 105.14 | 0 | 17.84 | 0 | OK | Ground clear controls. | 252 | 45.56 | 122.98
17474 | TIN-INTERP | Interpolated Ground | 111731.1 | -6.7 | 103.49 | 0 | 22.04 | 0 | OK | Ground clear controls. | 252 | 45.56 | 125.53
17475 | TIN-INTERP | Interpolated Ground | 111731.11 | -5.2 | 103.9 | 0 | 15.66 | 0 | OK | Ground clear controls. | 252 | 45.56 | 119.56
17476 | TIN-INTERP | Interpolated Ground | 111731.12 | -4.73 | 104.1 | 0 | 27.03 | 0 | OK | Ground clear controls. | 252 | 45.56 | 131.13
17477 | TIN-INTERP | Interpolated Ground | 111731.12 | 5.17 | 107.94 | 0 | 11.62 | 0 | OK | Ground clear controls. | 252 | 45.56 | 119.56
17478 | TIN-INTERP | Interpolated Ground | 111731.14 | 4.7 | 107.78 | 0 | 23.28 | 0 | OK | Ground clear controls. | 252 | 45.56 | 131.06
17479 | TIN-INTERP | Interpolated Ground | 111731.15 | 6.67 | 108.27 | 0 | 17.28 | 0 | OK | Ground clear controls. | 252 | 45.56 | 125.55
17480 | TIN-INTERP | Interpolated Ground | 111771.1 | -6.66 | 92.73 | 0 | 36.3 | 0 | OK | Ground clear controls. | 252 | 45.56 | 129.03
17481 | TIN-INTERP | Interpolated Ground | 111771.11 | -5.16 | 92.76 | 0 | 30.42 | 0 | OK | Ground clear controls. | 252 | 45.56 | 123.18
17482 | TIN-INTERP | Interpolated Ground | 111771.12 | -4.68 | 92.77 | 0 | 41.82 | 0 | OK | Ground clear controls. | 252 | 45.56 | 134.59
17483 | TIN-INTERP | Interpolated Ground | 111771.12 | 5.15 | 94.83 | 0 | 28.35 | 0 | OK | Ground clear controls. | 252 | 45.56 | 123.18
17484 | TIN-INTERP | Interpolated Ground | 111771.14 | 4.67 | 94.83 | 0 | 39.72 | 0 | OK | Ground clear controls. | 252 | 45.56 | 134.55
17485 | TIN-INTERP | Interpolated Ground | 111771.15 | 6.65 | 94.95 | 0 | 34.09 | 0 | OK | Ground clear controls. | 252 | 45.56 | 129.04
17486 | TIN-INTERP | Interpolated Ground | 111811.1 | -6.63 | 93.09 | 0 | 40.37 | 0 | OK | Ground clear controls. | 252 | 45.56 | 133.46
17487 | TIN-INTERP | Interpolated Ground | 111811.11 | -5.13 | 93.3 | 0 | 34.49 | 0 | OK | Ground clear controls. | 252 | 45.56 | 127.79
17488 | TIN-INTERP | Interpolated Ground | 111811.12 | -4.64 | 93.43 | 0 | 45.56 | 0 | OK | Ground clear controls. | 252 | 45.56 | 138.99
17489 | TIN-INTERP | Interpolated Ground | 111811.12 | 5.13 | 95.16 | 0 | 32.62 | 0 | OK | Ground clear controls. | 252 | 43.87 | 127.78
17490 | TIN-INTERP | Interpolated Ground | 111811.14 | 4.63 | 95.09 | 0 | 43.87 | 0 | OK | Ground clear controls. | 252 | 43.87 | 138.96
17491 | TIN-INTERP | Interpolated Ground | 111811.15 | 6.63 | 95.18 | 0 | 38.28 | 0 | OK | Ground clear controls. | 252 | 38.28 | 133.46
17492 | TIN-INTERP | Interpolated Ground | 111842.79 | -6.6 | 105.06 | 0 | 32.58 | 0 | OK | Ground clear controls. | 253 | 47.79 | 137.64
17493 | TIN-INTERP | Interpolated Ground | 111842.8 | -5.1 | 105.62 | 0 | 26.52 | 0 | OK | Ground clear controls. | 253 | 47.79 | 132.14
17494 | TIN-INTERP | Interpolated Ground | 111842.85 | -4.6 | 105.61 | 0 | 37.53 | 0 | OK | Ground clear controls. | 253 | 47.79 | 143.14
17495 | TIN-INTERP | Interpolated Ground | 111842.93 | 4.61 | 107.63 | 0 | 35.51 | 0 | OK | Ground clear controls. | 253 | 47.79 | 143.14
17496 | TIN-INTERP | Interpolated Ground | 111842.96 | 6.61 | 108.06 | 0 | 29.58 | 0 | OK | Ground clear controls. | 253 | 47.79 | 137.64
17497 | TIN-INTERP | Interpolated Ground | 111842.97 | 5.11 | 107.72 | 0 | 24.42 | 0 | OK | Ground clear controls. | 253 | 47.79 | 132.14
17498 | TIN-INTERP | Interpolated Ground | 111882.79 | -6.6 | 92.32 | 0 | 39.23 | 0 | OK | Ground clear controls. | 253 | 47.79 | 131.55
17499 | TIN-INTERP | Interpolated Ground | 111882.8 | -5.1 | 92.93 | 0 | 32.93 | 0 | OK | Ground clear controls. | 253 | 47.79 | 125.86
17500 | TIN-INTERP | Interpolated Ground | 111882.84 | -4.6 | 93.06 | 0 | 44.01 | 0 | OK | Ground clear controls. | 253 | 47.79 | 137.07
17501 | TIN-INTERP | Interpolated Ground | 111882.93 | 4.61 | 95.44 | 0 | 41.59 | 0 | OK | Ground clear controls. | 253 | 47.79 | 137.03
17502 | TIN-INTERP | Interpolated Ground | 111882.96 | 6.61 | 96.38 | 0 | 35.18 | 0 | OK | Ground clear controls. | 253 | 47.79 | 131.56
17503 | TIN-INTERP | Interpolated Ground | 111882.97 | 5.11 | 95.62 | 0 | 30.27 | 0 | OK | Ground clear controls. | 253 | 47.79 | 125.89
17504 | TIN-INTERP | Interpolated Ground | 111922.79 | -6.6 | 89.45 | 0 | 36.95 | 0 | OK | Ground clear controls. | 253 | 47.79 | 126.4
17505 | TIN-INTERP | Interpolated Ground | 111922.8 | -5.1 | 89.9 | 0 | 30.66 | 0 | OK | Ground clear controls. | 253 | 47.79 | 120.56
17506 | TIN-INTERP | Interpolated Ground | 111922.84 | -4.6 | 90.03 | 0 | 41.91 | 0 | OK | Ground clear controls. | 253 | 47.79 | 131.94
17507 | TIN-INTERP | Interpolated Ground | 111922.93 | 4.61 | 92.88 | 0 | 38.98 | 0 | OK | Ground clear controls. | 253 | 47.79 | 131.86
17508 | TIN-INTERP | Interpolated Ground | 111922.96 | 6.6 | 93.34 | 0 | 33.06 | 0 | OK | Ground clear controls. | 253 | 47.79 | 126.4
17509 | TIN-INTERP | Interpolated Ground | 111922.97 | 5.1 | 92.98 | 0 | 27.62 | 0 | OK | Ground clear controls. | 253 | 47.79 | 120.6
17510 | TIN-INTERP | Interpolated Ground | 111962.79 | -6.6 | 96.1 | 0 | 26.08 | 0 | OK | Ground clear controls. | 253 | 47.79 | 122.18
17511 | TIN-INTERP | Interpolated Ground | 111962.8 | -5.1 | 96.69 | 0 | 19.56 | 0 | OK | Ground clear controls. | 253 | 47.79 | 116.25
17512 | TIN-INTERP | Interpolated Ground | 111962.84 | -4.61 | 96.88 | 0 | 30.83 | 0 | OK | Ground clear controls. | 253 | 47.79 | 127.71
17513 | TIN-INTERP | Interpolated Ground | 111962.93 | 4.6 | 99.9 | 0 | 27.72 | 0 | OK | Ground clear controls. | 253 | 47.79 | 127.62
17514 | TIN-INTERP | Interpolated Ground | 111962.96 | 6.6 | 100.56 | 0 | 21.62 | 0 | OK | Ground clear controls. | 253 | 47.79 | 122.18
17515 | TIN-INTERP | Interpolated Ground | 111962.97 | 5.1 | 100.06 | 0 | 16.24 | 0 | OK | Ground clear controls. | 253 | 47.79 | 116.3
17516 | TIN-INTERP | Interpolated Ground | 112002.79 | -6.6 | 87.79 | 0 | 31.08 | 0 | OK | Ground clear controls. | 253 | 47.79 | 118.87
17517 | TIN-INTERP | Interpolated Ground | 112002.8 | -5.1 | 87.84 | 0 | 25.06 | 0 | OK | Ground clear controls. | 253 | 47.79 | 112.9
17518 | TIN-INTERP | Interpolated Ground | 112002.84 | -4.61 | 87.72 | 0 | 36.7 | 0 | OK | Ground clear controls. | 253 | 47.79 | 124.42
17519 | TIN-INTERP | Interpolated Ground | 112002.93 | 4.6 | 87.81 | 0 | 36.51 | 0 | OK | Ground clear controls. | 253 | 47.79 | 124.32
17520 | TIN-INTERP | Interpolated Ground | 112002.96 | 6.6 | 88.11 | 0 | 30.78 | 0 | OK | Ground clear controls. | 253 | 47.79 | 118.89
17521 | TIN-INTERP | Interpolated Ground | 112002.97 | 5.1 | 87.87 | 0 | 25.1 | 0 | OK | Ground clear controls. | 253 | 47.79 | 112.97
17522 | TIN-INTERP | Interpolated Ground | 112042.79 | -6.61 | 74 | 0 | 42.51 | 0 | OK | Ground clear controls. | 253 | 47.79 | 116.51
17523 | TIN-INTERP | Interpolated Ground | 112042.8 | -5.1 | 74.23 | 0 | 36.31 | 0 | OK | Ground clear controls. | 253 | 47.79 | 110.54
17524 | TIN-INTERP | Interpolated Ground | 112042.84 | -4.61 | 74.27 | 0 | 47.79 | 0 | OK | Ground clear controls. | 253 | 47.79 | 122.06
17525 | TIN-INTERP | Interpolated Ground | 112042.93 | 4.6 | 75.24 | 0 | 46.71 | 0 | OK | Ground clear controls. | 253 | 46.71 | 121.95
17526 | TIN-INTERP | Interpolated Ground | 112042.96 | 6.6 | 75.55 | 0 | 40.97 | 0 | OK | Ground clear controls. | 253 | 42.34 | 116.52
17527 | TIN-INTERP | Interpolated Ground | 112042.97 | 5.1 | 75.25 | 0 | 35.35 | 0 | OK | Ground clear controls. | 253 | 42.34 | 110.6
17528 | TIN-INTERP | Interpolated Ground | 112082.79 | -6.61 | 81.88 | 0 | 33.19 | 0 | OK | Ground clear controls. | 253 | 42.34 | 115.07
17529 | TIN-INTERP | Interpolated Ground | 112082.8 | -5.11 | 82.63 | 0 | 26.53 | 0 | OK | Ground clear controls. | 253 | 42.34 | 109.16
17530 | TIN-INTERP | Interpolated Ground | 112082.84 | -4.61 | 82.84 | 0 | 37.76 | 0 | OK | Ground clear controls. | 253 | 42.34 | 120.6
17531 | TIN-INTERP | Interpolated Ground | 112082.93 | 4.6 | 86.16 | 0 | 34.36 | 0 | OK | Ground clear controls. | 253 | 42.34 | 120.52
17532 | TIN-INTERP | Interpolated Ground | 112082.96 | 6.6 | 86.77 | 0 | 28.3 | 0 | OK | Ground clear controls. | 253 | 42.34 | 115.07
17533 | TIN-INTERP | Interpolated Ground | 112082.97 | 5.1 | 86.33 | 0 | 22.88 | 0 | OK | Ground clear controls. | 253 | 42.34 | 109.21
17534 | TIN-INTERP | Interpolated Ground | 112122.79 | -6.61 | 77.36 | 0 | 37.19 | 0 | OK | Ground clear controls. | 253 | 42.34 | 114.55
17535 | TIN-INTERP | Interpolated Ground | 112122.8 | -5.11 | 77.65 | 0 | 31.09 | 0 | OK | Ground clear controls. | 253 | 42.34 | 108.74
17536 | TIN-INTERP | Interpolated Ground | 112122.84 | -4.61 | 77.73 | 0 | 42.34 | 0 | OK | Ground clear controls. | 253 | 42.34 | 120.07
17537 | TIN-INTERP | Interpolated Ground | 112122.93 | 4.6 | 79.7 | 0 | 40.31 | 0 | OK | Ground clear controls. | 253 | 40.31 | 120.01
17538 | TIN-INTERP | Interpolated Ground | 112122.96 | 6.6 | 80.34 | 0 | 34.22 | 0 | OK | Ground clear controls. | 253 | 39.17 | 114.56
17539 | TIN-INTERP | Interpolated Ground | 112122.97 | 5.1 | 79.92 | 0 | 28.86 | 0 | OK | Ground clear controls. | 253 | 39.17 | 108.78
17540 | TIN-INTERP | Interpolated Ground | 112162.79 | -6.61 | 80.82 | 0 | 34.13 | 0 | OK | Ground clear controls. | 253 | 39.17 | 114.95
17541 | TIN-INTERP | Interpolated Ground | 112162.8 | -5.11 | 81.18 | 0 | 28.12 | 0 | OK | Ground clear controls. | 253 | 39.17 | 109.3
17542 | TIN-INTERP | Interpolated Ground | 112162.84 | -4.61 | 81.29 | 0 | 39.17 | 0 | OK | Ground clear controls. | 253 | 39.17 | 120.46
17543 | TIN-INTERP | Interpolated Ground | 112162.93 | 4.59 | 82.25 | 0 | 38.19 | 0 | OK | Ground clear controls. | 253 | 38.19 | 120.44
17544 | TIN-INTERP | Interpolated Ground | 112162.96 | 6.59 | 82.52 | 0 | 32.43 | 0 | OK | Ground clear controls. | 253 | 32.43 | 114.95
17545 | TIN-INTERP | Interpolated Ground | 112162.97 | 5.09 | 82.32 | 0 | 27.01 | 0 | OK | Ground clear controls. | 253 | 27.01 | 109.33
17546 | TIN-INTERP | Interpolated Ground | 112193.34 | 5.09 | 94.29 | 0 | 16.09 | 0 | OK | Ground clear controls. | 254 | 50.79 | 110.38
17547 | TIN-INTERP | Interpolated Ground | 112193.41 | 6.59 | 94.32 | 0 | 21.56 | 0 | OK | Ground clear controls. | 254 | 50.79 | 115.88
17548 | TIN-INTERP | Interpolated Ground | 112193.41 | -6.61 | 90.89 | 0 | 24.99 | 0 | OK | Ground clear controls. | 254 | 50.79 | 115.88
17549 | TIN-INTERP | Interpolated Ground | 112193.43 | 4.59 | 94.26 | 0 | 27.12 | 0 | OK | Ground clear controls. | 254 | 50.79 | 121.38
17550 | TIN-INTERP | Interpolated Ground | 112193.46 | -4.61 | 91.4 | 0 | 29.98 | 0 | OK | Ground clear controls. | 254 | 50.79 | 121.38
17551 | TIN-INTERP | Interpolated Ground | 112193.46 | -5.11 | 91.27 | 0 | 19.11 | 0 | OK | Ground clear controls. | 254 | 50.79 | 110.38
17552 | TIN-INTERP | Interpolated Ground | 112233.34 | 5.1 | 93.17 | 0 | 13.42 | 0 | OK | Ground clear controls. | 254 | 50.79 | 106.59
17553 | TIN-INTERP | Interpolated Ground | 112233.41 | 6.59 | 93.59 | 0 | 18.67 | 0 | OK | Ground clear controls. | 254 | 50.79 | 112.26
17554 | TIN-INTERP | Interpolated Ground | 112233.41 | -6.61 | 87.28 | 0 | 24.97 | 0 | OK | Ground clear controls. | 254 | 50.79 | 112.25
17555 | TIN-INTERP | Interpolated Ground | 112233.43 | 4.59 | 92.97 | 0 | 24.77 | 0 | OK | Ground clear controls. | 254 | 50.79 | 117.74
17556 | TIN-INTERP | Interpolated Ground | 112233.46 | -4.61 | 88.55 | 0 | 29.23 | 0 | OK | Ground clear controls. | 254 | 50.79 | 117.78
17557 | TIN-INTERP | Interpolated Ground | 112233.46 | -5.11 | 88.16 | 0 | 18.43 | 0 | OK | Ground clear controls. | 254 | 50.79 | 106.59
17558 | TIN-INTERP | Interpolated Ground | 112273.34 | 5.1 | 81.3 | 0 | 22.47 | 0 | OK | Ground clear controls. | 254 | 50.79 | 103.77
17559 | TIN-INTERP | Interpolated Ground | 112273.41 | 6.6 | 81.35 | 0 | 28.21 | 0 | OK | Ground clear controls. | 254 | 50.79 | 109.56
17560 | TIN-INTERP | Interpolated Ground | 112273.41 | -6.6 | 80.71 | 0 | 28.85 | 0 | OK | Ground clear controls. | 254 | 50.79 | 109.56
17561 | TIN-INTERP | Interpolated Ground | 112273.43 | 4.6 | 81.19 | 0 | 33.84 | 0 | OK | Ground clear controls. | 254 | 50.79 | 115.03
17562 | TIN-INTERP | Interpolated Ground | 112273.46 | -4.6 | 80.74 | 0 | 34.36 | 0 | OK | Ground clear controls. | 254 | 50.79 | 115.1
17563 | TIN-INTERP | Interpolated Ground | 112273.46 | -5.1 | 80.77 | 0 | 23 | 0 | OK | Ground clear controls. | 254 | 50.79 | 103.77
17564 | TIN-INTERP | Interpolated Ground | 112313.34 | 5.1 | 63.54 | 0 | 38.38 | 0 | OK | Ground clear controls. | 254 | 50.79 | 101.92
17565 | TIN-INTERP | Interpolated Ground | 112313.41 | 6.6 | 64.18 | 0 | 43.61 | 0 | OK | Ground clear controls. | 254 | 50.79 | 107.79
17566 | TIN-INTERP | Interpolated Ground | 112313.41 | -6.6 | 64.21 | 0 | 43.58 | 0 | OK | Ground clear controls. | 254 | 50.79 | 107.79
17567 | TIN-INTERP | Interpolated Ground | 112313.43 | 4.6 | 63.5 | 0 | 49.74 | 0 | OK | Ground clear controls. | 254 | 50.79 | 113.24
17568 | TIN-INTERP | Interpolated Ground | 112313.46 | -4.6 | 64.06 | 0 | 49.28 | 0 | OK | Ground clear controls. | 254 | 50.79 | 113.34
17569 | TIN-INTERP | Interpolated Ground | 112313.46 | -5.1 | 64.09 | 0 | 37.84 | 0 | OK | Ground clear controls. | 254 | 50.79 | 101.93
17570 | TIN-INTERP | Interpolated Ground | 112353.34 | 5.1 | 61.62 | 0 | 39.41 | 0 | OK | Ground clear controls. | 254 | 50.79 | 101.03
17571 | TIN-INTERP | Interpolated Ground | 112353.41 | 6.6 | 61.81 | 0 | 45.13 | 0 | OK | Ground clear controls. | 254 | 50.79 | 106.94
17572 | TIN-INTERP | Interpolated Ground | 112353.41 | -6.6 | 61.73 | 0 | 45.21 | 0 | OK | Ground clear controls. | 254 | 50.79 | 106.94
17573 | TIN-INTERP | Interpolated Ground | 112353.43 | 4.6 | 61.6 | 0 | 50.79 | 0 | OK | Ground clear controls. | 254 | 50.79 | 112.39
17574 | TIN-INTERP | Interpolated Ground | 112353.46 | -4.6 | 61.8 | 0 | 50.69 | 0 | OK | Ground clear controls. | 254 | 50.69 | 112.49
17575 | TIN-INTERP | Interpolated Ground | 112353.46 | -5.1 | 61.82 | 0 | 39.23 | 0 | OK | Ground clear controls. | 254 | 40.16 | 101.05
17576 | TIN-INTERP | Interpolated Ground | 112393.34 | 5.1 | 72.65 | 0 | 28.48 | 0 | OK | Ground clear controls. | 254 | 40.16 | 101.13
17577 | TIN-INTERP | Interpolated Ground | 112393.41 | 6.6 | 72.68 | 0 | 34.33 | 0 | OK | Ground clear controls. | 254 | 40.16 | 107.01
17578 | TIN-INTERP | Interpolated Ground | 112393.41 | -6.6 | 72.53 | 0 | 34.47 | 0 | OK | Ground clear controls. | 254 | 40.16 | 107
17579 | TIN-INTERP | Interpolated Ground | 112393.43 | 4.6 | 72.71 | 0 | 39.76 | 0 | OK | Ground clear controls. | 254 | 40.16 | 112.47
17580 | TIN-INTERP | Interpolated Ground | 112393.46 | -4.6 | 72.4 | 0 | 40.16 | 0 | OK | Ground clear controls. | 254 | 40.16 | 112.56
17581 | TIN-INTERP | Interpolated Ground | 112393.46 | -5.1 | 72.38 | 0 | 28.76 | 0 | OK | Ground clear controls. | 254 | 33.94 | 101.14
17582 | TIN-INTERP | Interpolated Ground | 112433.34 | 5.1 | 81.03 | 0 | 21.16 | 0 | OK | Ground clear controls. | 254 | 33.94 | 102.19
17583 | TIN-INTERP | Interpolated Ground | 112433.41 | 6.6 | 81.39 | 0 | 26.61 | 0 | OK | Ground clear controls. | 254 | 33.94 | 108
17584 | TIN-INTERP | Interpolated Ground | 112433.41 | -6.6 | 79.5 | 0 | 28.5 | 0 | OK | Ground clear controls. | 254 | 33.94 | 108
17585 | TIN-INTERP | Interpolated Ground | 112433.43 | 4.6 | 80.89 | 0 | 32.58 | 0 | OK | Ground clear controls. | 254 | 33.94 | 113.47
17586 | TIN-INTERP | Interpolated Ground | 112433.46 | -4.6 | 79.61 | 0 | 33.94 | 0 | OK | Ground clear controls. | 254 | 33.94 | 113.55
17587 | TIN-INTERP | Interpolated Ground | 112433.46 | -5.1 | 79.63 | 0 | 22.57 | 0 | OK | Ground clear controls. | 254 | 32.75 | 102.2
17588 | TIN-INTERP | Interpolated Ground | 112473.34 | 5.11 | 84.81 | 0 | 19.41 | 0 | OK | Ground clear controls. | 254 | 32.75 | 104.22
17589 | TIN-INTERP | Interpolated Ground | 112473.41 | 6.61 | 85.18 | 0 | 24.75 | 0 | OK | Ground clear controls. | 254 | 32.75 | 109.93
17590 | TIN-INTERP | Interpolated Ground | 112473.41 | -6.6 | 82.3 | 0 | 27.62 | 0 | OK | Ground clear controls. | 254 | 32.75 | 109.92
17591 | TIN-INTERP | Interpolated Ground | 112473.43 | 4.61 | 84.77 | 0 | 30.63 | 0 | OK | Ground clear controls. | 254 | 32.75 | 115.4
17592 | TIN-INTERP | Interpolated Ground | 112473.46 | -4.6 | 82.7 | 0 | 32.75 | 0 | OK | Ground clear controls. | 254 | 32.75 | 115.45
17593 | TIN-INTERP | Interpolated Ground | 112473.46 | -5.1 | 82.59 | 0 | 21.65 | 0 | OK | Ground clear controls. | 254 | 26.55 | 104.24
17594 | TIN-INTERP | Interpolated Ground | 112513.34 | 5.11 | 94.28 | 0 | 12.95 | 0 | OK | Ground clear controls. | 254 | 26.55 | 107.23
17595 | TIN-INTERP | Interpolated Ground | 112513.41 | 6.61 | 94.38 | 0 | 18.39 | 0 | OK | Ground clear controls. | 254 | 26.55 | 112.77
17596 | TIN-INTERP | Interpolated Ground | 112513.41 | -6.6 | 91.2 | 0 | 21.57 | 0 | OK | Ground clear controls. | 254 | 26.55 | 112.77
17597 | TIN-INTERP | Interpolated Ground | 112513.43 | 4.61 | 94.21 | 0 | 24.05 | 0 | OK | Ground clear controls. | 254 | 26.55 | 118.26
17598 | TIN-INTERP | Interpolated Ground | 112513.46 | -4.6 | 91.73 | 0 | 26.55 | 0 | OK | Ground clear controls. | 254 | 26.55 | 118.28
17599 | TIN-INTERP | Interpolated Ground | 112513.46 | -5.1 | 91.59 | 0 | 15.65 | 0 | OK | Ground clear controls. | 254 | 15.65 | 107.24
17600 | TIN-INTERP | Interpolated Ground | 112519.36 | 0 | 93.14 | 0 | 34.15 | 0 | OK | Ground clear controls. | 255 | 50.89 | 127.29
17601 | TIN-INTERP | Interpolated Ground | 112519.37 | 6.61 | 94.28 | 0 | 18.99 | 0 | OK | Ground clear controls. | 255 | 50.89 | 113.27
17602 | TIN-INTERP | Interpolated Ground | 112519.41 | 4.61 | 94.11 | 0 | 24.66 | 0 | OK | Ground clear controls. | 255 | 50.89 | 118.77
17603 | TIN-INTERP | Interpolated Ground | 112519.41 | 5.11 | 94.14 | 0 | 13.63 | 0 | OK | Ground clear controls. | 255 | 50.89 | 107.77
17604 | TIN-INTERP | Interpolated Ground | 112519.41 | -4.6 | 92 | 0 | 26.77 | 0 | OK | Ground clear controls. | 255 | 50.89 | 118.77
17605 | TIN-INTERP | Interpolated Ground | 112519.43 | -6.6 | 91.37 | 0 | 21.9 | 0 | OK | Ground clear controls. | 255 | 50.89 | 113.27
17606 | TIN-INTERP | Interpolated Ground | 112519.49 | -5.1 | 91.85 | 0 | 15.92 | 0 | OK | Ground clear controls. | 255 | 50.89 | 107.77
17607 | TIN-INTERP | Interpolated Ground | 112559.36 | 0 | 88.15 | 0 | 38.08 | 0 | OK | Ground clear controls. | 255 | 50.89 | 126.23
17608 | TIN-INTERP | Interpolated Ground | 112559.37 | 6.63 | 88.98 | 0 | 22.75 | 0 | OK | Ground clear controls. | 255 | 50.89 | 111.73
17609 | TIN-INTERP | Interpolated Ground | 112559.41 | 4.63 | 88.8 | 0 | 28.41 | 0 | OK | Ground clear controls. | 255 | 50.89 | 117.21
17610 | TIN-INTERP | Interpolated Ground | 112559.41 | 5.13 | 88.85 | 0 | 17.26 | 0 | OK | Ground clear controls. | 255 | 50.89 | 106.11
17611 | TIN-INTERP | Interpolated Ground | 112559.41 | -4.58 | 86.81 | 0 | 30.44 | 0 | OK | Ground clear controls. | 255 | 50.89 | 117.25
17612 | TIN-INTERP | Interpolated Ground | 112559.43 | -6.58 | 86.12 | 0 | 25.62 | 0 | OK | Ground clear controls. | 255 | 50.89 | 111.74
17613 | TIN-INTERP | Interpolated Ground | 112559.49 | -5.09 | 86.72 | 0 | 19.41 | 0 | OK | Ground clear controls. | 255 | 50.89 | 106.13
17614 | TIN-INTERP | Interpolated Ground | 112599.36 | 0 | 74.99 | 0 | 50.89 | 0 | OK | Ground clear controls. | 255 | 50.89 | 125.88
17615 | TIN-INTERP | Interpolated Ground | 112599.37 | 6.65 | 76.3 | 0 | 34.81 | 0 | OK | Ground clear controls. | 255 | 43.49 | 111.11
17616 | TIN-INTERP | Interpolated Ground | 112599.41 | 4.65 | 75.9 | 0 | 40.69 | 0 | OK | Ground clear controls. | 255 | 43.49 | 116.59
17617 | TIN-INTERP | Interpolated Ground | 112599.41 | 5.15 | 75.98 | 0 | 29.43 | 0 | OK | Ground clear controls. | 255 | 43.49 | 105.41
17618 | TIN-INTERP | Interpolated Ground | 112599.41 | -4.57 | 74.62 | 0 | 42.02 | 0 | OK | Ground clear controls. | 255 | 43.49 | 116.64
17619 | TIN-INTERP | Interpolated Ground | 112599.43 | -6.57 | 74.68 | 0 | 36.44 | 0 | OK | Ground clear controls. | 255 | 43.49 | 111.12
17620 | TIN-INTERP | Interpolated Ground | 112599.49 | -5.07 | 74.55 | 0 | 30.89 | 0 | OK | Ground clear controls. | 255 | 43.49 | 105.44
17621 | TIN-INTERP | Interpolated Ground | 112639.36 | 0.01 | 82.77 | 0 | 43.49 | 0 | OK | Ground clear controls. | 255 | 43.49 | 126.26
17622 | TIN-INTERP | Interpolated Ground | 112639.37 | 6.68 | 84.12 | 0 | 27.29 | 0 | OK | Ground clear controls. | 255 | 39.48 | 111.41
17623 | TIN-INTERP | Interpolated Ground | 112639.41 | 4.67 | 83.72 | 0 | 33.16 | 0 | OK | Ground clear controls. | 255 | 39.48 | 116.88
17624 | TIN-INTERP | Interpolated Ground | 112639.41 | 5.18 | 83.81 | 0 | 21.88 | 0 | OK | Ground clear controls. | 255 | 39.48 | 105.69
17625 | TIN-INTERP | Interpolated Ground | 112639.41 | -4.56 | 82.02 | 0 | 34.92 | 0 | OK | Ground clear controls. | 255 | 39.48 | 116.94
17626 | TIN-INTERP | Interpolated Ground | 112639.43 | -6.56 | 81.82 | 0 | 29.59 | 0 | OK | Ground clear controls. | 255 | 39.48 | 111.41
17627 | TIN-INTERP | Interpolated Ground | 112639.49 | -5.06 | 82.01 | 0 | 23.71 | 0 | OK | Ground clear controls. | 255 | 39.48 | 105.72
17628 | TIN-INTERP | Interpolated Ground | 112679.36 | 0.01 | 94.44 | 0 | 32.9 | 0 | OK | Ground clear controls. | 255 | 39.48 | 127.34
17629 | TIN-INTERP | Interpolated Ground | 112679.37 | 6.7 | 95.62 | 0 | 17 | 0 | OK | Ground clear controls. | 255 | 39.48 | 112.62
17630 | TIN-INTERP | Interpolated Ground | 112679.41 | 4.7 | 95.46 | 0 | 22.65 | 0 | OK | Ground clear controls. | 255 | 39.48 | 118.11
17631 | TIN-INTERP | Interpolated Ground | 112679.41 | 5.2 | 95.5 | 0 | 11.43 | 0 | OK | Ground clear controls. | 255 | 39.48 | 106.93
17632 | TIN-INTERP | Interpolated Ground | 112679.41 | -4.55 | 93.09 | 0 | 25.07 | 0 | OK | Ground clear controls. | 255 | 39.48 | 118.16
17633 | TIN-INTERP | Interpolated Ground | 112679.43 | -6.55 | 92.38 | 0 | 20.26 | 0 | OK | Ground clear controls. | 255 | 39.48 | 112.64
17634 | TIN-INTERP | Interpolated Ground | 112679.49 | -5.05 | 92.88 | 0 | 14.09 | 0 | OK | Ground clear controls. | 255 | 39.48 | 106.97
17635 | TIN-INTERP | Interpolated Ground | 112719.36 | 0.01 | 89.66 | 0 | 39.48 | 0 | OK | Ground clear controls. | 255 | 39.48 | 129.14
17636 | TIN-INTERP | Interpolated Ground | 112719.37 | 6.72 | 90.76 | 0 | 24.01 | 0 | OK | Ground clear controls. | 255 | 34.8 | 114.77
17637 | TIN-INTERP | Interpolated Ground | 112719.41 | 4.72 | 90.34 | 0 | 29.92 | 0 | OK | Ground clear controls. | 255 | 34.8 | 120.26
17638 | TIN-INTERP | Interpolated Ground | 112719.41 | 5.22 | 90.44 | 0 | 18.7 | 0 | OK | Ground clear controls. | 255 | 34.8 | 109.14
17639 | TIN-INTERP | Interpolated Ground | 112719.41 | -4.53 | 89.12 | 0 | 31.17 | 0 | OK | Ground clear controls. | 255 | 34.8 | 120.29
17640 | TIN-INTERP | Interpolated Ground | 112719.43 | -6.54 | 88.91 | 0 | 25.87 | 0 | OK | Ground clear controls. | 255 | 34.8 | 114.78
17641 | TIN-INTERP | Interpolated Ground | 112719.49 | -5.04 | 89.11 | 0 | 20.05 | 0 | OK | Ground clear controls. | 255 | 34.8 | 109.16
17642 | TIN-INTERP | Interpolated Ground | 112759.36 | 0.01 | 96.85 | 0 | 34.8 | 0 | OK | Ground clear controls. | 255 | 34.8 | 131.65
17643 | TIN-INTERP | Interpolated Ground | 112759.37 | 6.75 | 98 | 0 | 19.83 | 0 | OK | Ground clear controls. | 255 | 26.59 | 117.83
17644 | TIN-INTERP | Interpolated Ground | 112759.41 | 4.74 | 97.67 | 0 | 25.67 | 0 | OK | Ground clear controls. | 255 | 26.59 | 123.34
17645 | TIN-INTERP | Interpolated Ground | 112759.41 | 5.24 | 97.77 | 0 | 14.55 | 0 | OK | Ground clear controls. | 255 | 26.59 | 112.32
17646 | TIN-INTERP | Interpolated Ground | 112759.41 | -4.52 | 96.75 | 0 | 26.59 | 0 | OK | Ground clear controls. | 255 | 26.59 | 123.34
17647 | TIN-INTERP | Interpolated Ground | 112759.43 | -6.53 | 96.63 | 0 | 21.21 | 0 | OK | Ground clear controls. | 255 | 21.21 | 117.84
17648 | TIN-INTERP | Interpolated Ground | 112759.49 | -5.03 | 96.76 | 0 | 15.57 | 0 | OK | Ground clear controls. | 255 | 15.57 | 112.33
17649 | TIN-INTERP | Interpolated Ground | 112763.11 | -4.52 | 96.68 | 0 | 26.99 | 0 | OK | Ground clear controls. | 256 | 58.07 | 123.67
17650 | TIN-INTERP | Interpolated Ground | 112763.13 | 6.75 | 98.13 | 0 | 20.04 | 0 | OK | Ground clear controls. | 256 | 58.07 | 118.17
17651 | TIN-INTERP | Interpolated Ground | 112763.15 | 4.74 | 97.93 | 0 | 25.75 | 0 | OK | Ground clear controls. | 256 | 58.07 | 123.68
17652 | TIN-INTERP | Interpolated Ground | 112763.16 | -6.52 | 96.6 | 0 | 21.57 | 0 | OK | Ground clear controls. | 256 | 58.07 | 118.17
17653 | TIN-INTERP | Interpolated Ground | 112763.16 | 0.01 | 97.26 | 0 | 34.67 | 0 | OK | Ground clear controls. | 256 | 58.07 | 131.93
17654 | TIN-INTERP | Interpolated Ground | 112763.18 | -5.03 | 96.64 | 0 | 16.03 | 0 | OK | Ground clear controls. | 256 | 58.07 | 112.67
17655 | TIN-INTERP | Interpolated Ground | 112763.18 | 5.25 | 98 | 0 | 14.67 | 0 | OK | Ground clear controls. | 256 | 58.07 | 112.67
17656 | TIN-INTERP | Interpolated Ground | 112803.11 | -4.47 | 94.29 | 0 | 24.61 | 0 | OK | Ground clear controls. | 256 | 58.07 | 118.9
17657 | TIN-INTERP | Interpolated Ground | 112803.14 | 7.06 | 94.01 | 0 | 19.27 | 0 | OK | Ground clear controls. | 256 | 58.07 | 113.28
17658 | TIN-INTERP | Interpolated Ground | 112803.15 | 5.04 | 93.83 | 0 | 25.02 | 0 | OK | Ground clear controls. | 256 | 58.07 | 118.85
17659 | TIN-INTERP | Interpolated Ground | 112803.15 | -6.49 | 94.32 | 0 | 18.99 | 0 | OK | Ground clear controls. | 256 | 58.07 | 113.31
17660 | TIN-INTERP | Interpolated Ground | 112803.16 | 0.03 | 93.84 | 0 | 34.13 | 0 | OK | Ground clear controls. | 256 | 58.07 | 127.97
17661 | TIN-INTERP | Interpolated Ground | 112803.18 | -4.99 | 94.27 | 0 | 13.32 | 0 | OK | Ground clear controls. | 256 | 58.07 | 107.59
17662 | TIN-INTERP | Interpolated Ground | 112803.18 | 5.56 | 93.91 | 0 | 13.65 | 0 | OK | Ground clear controls. | 256 | 58.07 | 107.56
17663 | TIN-INTERP | Interpolated Ground | 112843.11 | -4.41 | 84.9 | 0 | 30.14 | 0 | OK | Ground clear controls. | 256 | 58.07 | 115.04
17664 | TIN-INTERP | Interpolated Ground | 112843.14 | 7.37 | 85.02 | 0 | 24.31 | 0 | OK | Ground clear controls. | 256 | 58.07 | 109.33
17665 | TIN-INTERP | Interpolated Ground | 112843.15 | 5.33 | 84.88 | 0 | 30.08 | 0 | OK | Ground clear controls. | 256 | 58.07 | 114.96
17666 | TIN-INTERP | Interpolated Ground | 112843.15 | -6.45 | 85.02 | 0 | 24.35 | 0 | OK | Ground clear controls. | 256 | 58.07 | 109.37
17667 | TIN-INTERP | Interpolated Ground | 112843.16 | 0.05 | 84.83 | 0 | 39.96 | 0 | OK | Ground clear controls. | 256 | 58.07 | 124.79
17668 | TIN-INTERP | Interpolated Ground | 112843.18 | -4.96 | 84.89 | 0 | 18.57 | 0 | OK | Ground clear controls. | 256 | 58.07 | 103.46
17669 | TIN-INTERP | Interpolated Ground | 112843.18 | 5.87 | 85 | 0 | 18.41 | 0 | OK | Ground clear controls. | 256 | 58.07 | 103.41
17670 | TIN-INTERP | Interpolated Ground | 112883.11 | -4.36 | 77.36 | 0 | 34.74 | 0 | OK | Ground clear controls. | 256 | 58.07 | 112.1
17671 | TIN-INTERP | Interpolated Ground | 112883.14 | 7.68 | 77.61 | 0 | 28.7 | 0 | OK | Ground clear controls. | 256 | 58.07 | 106.31
17672 | TIN-INTERP | Interpolated Ground | 112883.15 | 5.62 | 77.8 | 0 | 34.2 | 0 | OK | Ground clear controls. | 256 | 58.07 | 112
17673 | TIN-INTERP | Interpolated Ground | 112883.15 | -6.41 | 77.21 | 0 | 29.14 | 0 | OK | Ground clear controls. | 256 | 58.07 | 106.35
17674 | TIN-INTERP | Interpolated Ground | 112883.16 | 0.07 | 77.7 | 0 | 44.71 | 0 | OK | Ground clear controls. | 256 | 58.07 | 122.41
17675 | TIN-INTERP | Interpolated Ground | 112883.18 | -4.92 | 77.36 | 0 | 22.94 | 0 | OK | Ground clear controls. | 256 | 58.07 | 100.3
17676 | TIN-INTERP | Interpolated Ground | 112883.18 | 6.17 | 77.71 | 0 | 22.52 | 0 | OK | Ground clear controls. | 256 | 58.07 | 100.23
17677 | TIN-INTERP | Interpolated Ground | 112923.11 | -4.3 | 76.25 | 0 | 33.83 | 0 | OK | Ground clear controls. | 256 | 58.07 | 110.08
17678 | TIN-INTERP | Interpolated Ground | 112923.13 | 8 | 77.57 | 0 | 26.65 | 0 | OK | Ground clear controls. | 256 | 58.07 | 104.22
17679 | TIN-INTERP | Interpolated Ground | 112923.15 | 5.91 | 76.99 | 0 | 32.99 | 0 | OK | Ground clear controls. | 256 | 58.07 | 109.98
17680 | TIN-INTERP | Interpolated Ground | 112923.15 | -6.37 | 76.08 | 0 | 28.17 | 0 | OK | Ground clear controls. | 256 | 58.07 | 104.25
17681 | TIN-INTERP | Interpolated Ground | 112923.16 | 0.09 | 76.49 | 0 | 44.34 | 0 | OK | Ground clear controls. | 256 | 58.07 | 120.83
17682 | TIN-INTERP | Interpolated Ground | 112923.18 | 6.48 | 77.16 | 0 | 20.87 | 0 | OK | Ground clear controls. | 256 | 58.07 | 98.03
17683 | TIN-INTERP | Interpolated Ground | 112923.18 | -4.89 | 76.22 | 0 | 21.88 | 0 | OK | Ground clear controls. | 256 | 58.07 | 98.1
17684 | TIN-INTERP | Interpolated Ground | 112963.11 | -4.25 | 78.77 | 0 | 30.21 | 0 | OK | Ground clear controls. | 256 | 58.07 | 108.98
17685 | TIN-INTERP | Interpolated Ground | 112963.13 | 8.31 | 80.69 | 0 | 22.36 | 0 | OK | Ground clear controls. | 256 | 58.07 | 103.05
17686 | TIN-INTERP | Interpolated Ground | 112963.14 | 6.2 | 80.44 | 0 | 28.43 | 0 | OK | Ground clear controls. | 256 | 58.07 | 108.87
17687 | TIN-INTERP | Interpolated Ground | 112963.15 | -6.33 | 78.19 | 0 | 24.89 | 0 | OK | Ground clear controls. | 256 | 58.07 | 103.08
17688 | TIN-INTERP | Interpolated Ground | 112963.16 | 0.11 | 80.28 | 0 | 39.75 | 0 | OK | Ground clear controls. | 256 | 58.07 | 120.03
17689 | TIN-INTERP | Interpolated Ground | 112963.18 | 6.79 | 80.53 | 0 | 16.26 | 0 | OK | Ground clear controls. | 256 | 58.07 | 96.79
17690 | TIN-INTERP | Interpolated Ground | 112963.18 | -4.85 | 78.62 | 0 | 18.25 | 0 | OK | Ground clear controls. | 256 | 58.07 | 96.87
17691 | TIN-INTERP | Interpolated Ground | 113003.11 | -4.2 | 77.79 | 0 | 31.01 | 0 | OK | Ground clear controls. | 256 | 58.07 | 108.8
17692 | TIN-INTERP | Interpolated Ground | 113003.13 | 8.62 | 80.41 | 0 | 22.39 | 0 | OK | Ground clear controls. | 256 | 58.07 | 102.8
17693 | TIN-INTERP | Interpolated Ground | 113003.14 | 6.49 | 80.58 | 0 | 28.12 | 0 | OK | Ground clear controls. | 256 | 58.07 | 108.7
17694 | TIN-INTERP | Interpolated Ground | 113003.15 | -6.29 | 77.28 | 0 | 25.54 | 0 | OK | Ground clear controls. | 256 | 58.07 | 102.82
17695 | TIN-INTERP | Interpolated Ground | 113003.16 | 0.14 | 78.78 | 0 | 41.26 | 0 | OK | Ground clear controls. | 256 | 58.07 | 120.04
17696 | TIN-INTERP | Interpolated Ground | 113003.18 | 7.1 | 80.82 | 0 | 15.71 | 0 | OK | Ground clear controls. | 256 | 58.07 | 96.53
17697 | TIN-INTERP | Interpolated Ground | 113003.18 | -4.82 | 77.61 | 0 | 18.98 | 0 | OK | Ground clear controls. | 256 | 58.07 | 96.59
17698 | TIN-INTERP | Interpolated Ground | 113043.11 | -4.14 | 77.67 | 0 | 31.86 | 0 | OK | Ground clear controls. | 256 | 58.07 | 109.53
17699 | TIN-INTERP | Interpolated Ground | 113043.13 | 8.93 | 79.56 | 0 | 23.92 | 0 | OK | Ground clear controls. | 256 | 58.07 | 103.48
17700 | TIN-INTERP | Interpolated Ground | 113043.14 | 6.79 | 79.17 | 0 | 30.29 | 0 | OK | Ground clear controls. | 256 | 58.07 | 109.46
17701 | TIN-INTERP | Interpolated Ground | 113043.15 | -6.25 | 77.39 | 0 | 26.09 | 0 | OK | Ground clear controls. | 256 | 58.07 | 103.48
17702 | TIN-INTERP | Interpolated Ground | 113043.16 | 0.16 | 78.24 | 0 | 42.58 | 0 | OK | Ground clear controls. | 256 | 58.07 | 120.82
17703 | TIN-INTERP | Interpolated Ground | 113043.17 | 7.41 | 79.34 | 0 | 17.89 | 0 | OK | Ground clear controls. | 256 | 58.07 | 97.23
17704 | TIN-INTERP | Interpolated Ground | 113043.18 | -4.78 | 77.58 | 0 | 19.69 | 0 | OK | Ground clear controls. | 256 | 58.07 | 97.27
17705 | TIN-INTERP | Interpolated Ground | 113083.11 | -4.09 | 77.93 | 0 | 33.25 | 0 | OK | Ground clear controls. | 256 | 58.07 | 111.18
17706 | TIN-INTERP | Interpolated Ground | 113083.13 | 9.24 | 76.55 | 0 | 28.54 | 0 | OK | Ground clear controls. | 256 | 58.07 | 105.09
17707 | TIN-INTERP | Interpolated Ground | 113083.14 | 7.08 | 76.81 | 0 | 34.33 | 0 | OK | Ground clear controls. | 256 | 58.07 | 111.14
17708 | TIN-INTERP | Interpolated Ground | 113083.15 | -6.22 | 77.82 | 0 | 27.23 | 0 | OK | Ground clear controls. | 256 | 58.07 | 105.05
17709 | TIN-INTERP | Interpolated Ground | 113083.16 | 0.18 | 77.73 | 0 | 44.67 | 0 | OK | Ground clear controls. | 256 | 58.07 | 122.4
17710 | TIN-INTERP | Interpolated Ground | 113083.17 | 7.72 | 76.72 | 0 | 22.18 | 0 | OK | Ground clear controls. | 256 | 58.07 | 98.9
17711 | TIN-INTERP | Interpolated Ground | 113083.18 | -4.75 | 77.99 | 0 | 20.92 | 0 | OK | Ground clear controls. | 256 | 58.07 | 98.91
17712 | TIN-INTERP | Interpolated Ground | 113123.11 | -4.03 | 65.99 | 0 | 47.77 | 0 | OK | Ground clear controls. | 256 | 58.07 | 113.76
17713 | TIN-INTERP | Interpolated Ground | 113123.13 | 9.55 | 68.42 | 0 | 39.21 | 0 | OK | Ground clear controls. | 256 | 58.07 | 107.63
17714 | TIN-INTERP | Interpolated Ground | 113123.14 | 7.37 | 67.95 | 0 | 45.82 | 0 | OK | Ground clear controls. | 256 | 58.07 | 113.77
17715 | TIN-INTERP | Interpolated Ground | 113123.15 | -6.18 | 65.56 | 0 | 41.99 | 0 | OK | Ground clear controls. | 256 | 58.07 | 107.55
17716 | TIN-INTERP | Interpolated Ground | 113123.16 | 0.2 | 66.71 | 0 | 58.07 | 0 | OK | Ground clear controls. | 256 | 58.07 | 124.78
17717 | TIN-INTERP | Interpolated Ground | 113123.17 | 8.03 | 68.12 | 0 | 33.42 | 0 | OK | Ground clear controls. | 256 | 47.04 | 101.54
17718 | TIN-INTERP | Interpolated Ground | 113123.18 | -4.72 | 65.86 | 0 | 35.65 | 0 | OK | Ground clear controls. | 256 | 47.04 | 101.51
17719 | TIN-INTERP | Interpolated Ground | 113163.11 | -3.98 | 80.34 | 0 | 36.91 | 0 | OK | Ground clear controls. | 256 | 47.04 | 117.25
17720 | TIN-INTERP | Interpolated Ground | 113163.13 | 9.87 | 81.99 | 0 | 29.11 | 0 | OK | Ground clear controls. | 256 | 47.04 | 111.1
17721 | TIN-INTERP | Interpolated Ground | 113163.14 | 7.66 | 81.61 | 0 | 35.7 | 0 | OK | Ground clear controls. | 256 | 47.04 | 117.31
17722 | TIN-INTERP | Interpolated Ground | 113163.15 | -6.14 | 80 | 0 | 30.97 | 0 | OK | Ground clear controls. | 256 | 47.04 | 110.97
17723 | TIN-INTERP | Interpolated Ground | 113163.16 | 0.22 | 80.9 | 0 | 47.04 | 0 | OK | Ground clear controls. | 256 | 47.04 | 127.94
17724 | TIN-INTERP | Interpolated Ground | 113163.17 | 8.34 | 81.71 | 0 | 23.44 | 0 | OK | Ground clear controls. | 256 | 24.84 | 105.15
17725 | TIN-INTERP | Interpolated Ground | 113163.18 | -4.68 | 80.22 | 0 | 24.84 | 0 | OK | Ground clear controls. | 256 | 24.84 | 105.06
17726 | TIN-INTERP | Interpolated Ground | 113182.29 | 7.8 | 84.14 | 0 | 35.2 | 0 | OK | Ground clear controls. | 257 | 65.3 | 119.34
17727 | TIN-INTERP | Interpolated Ground | 113183.28 | -6.17 | 82.33 | 0 | 30.79 | 0 | OK | Ground clear controls. | 257 | 65.3 | 113.12
17728 | TIN-INTERP | Interpolated Ground | 113183.28 | -4.7 | 82.58 | 0 | 24.7 | 0 | OK | Ground clear controls. | 257 | 65.3 | 107.28
17729 | TIN-INTERP | Interpolated Ground | 113183.28 | -3.99 | 82.69 | 0 | 36.72 | 0 | OK | Ground clear controls. | 257 | 65.3 | 119.41
17730 | TIN-INTERP | Interpolated Ground | 113183.31 | 0.23 | 83.24 | 0 | 46.59 | 0 | OK | Ground clear controls. | 257 | 65.3 | 129.83
17731 | TIN-INTERP | Interpolated Ground | 113184.33 | 8.48 | 84.23 | 0 | 22.99 | 0 | OK | Ground clear controls. | 257 | 65.3 | 107.22
17732 | TIN-INTERP | Interpolated Ground | 113184.5 | 10.01 | 84.49 | 0 | 28.58 | 0 | OK | Ground clear controls. | 257 | 65.3 | 113.07
17733 | TIN-INTERP | Interpolated Ground | 113222.61 | -6.23 | 71.2 | 0 | 39.75 | 0 | OK | Ground clear controls. | 257 | 65.3 | 110.95
17734 | TIN-INTERP | Interpolated Ground | 113222.75 | -4.77 | 71.6 | 0 | 33.41 | 0 | OK | Ground clear controls. | 257 | 65.3 | 105.01
17735 | TIN-INTERP | Interpolated Ground | 113222.85 | -4.1 | 71.84 | 0 | 45.33 | 0 | OK | Ground clear controls. | 257 | 65.3 | 117.17
17736 | TIN-INTERP | Interpolated Ground | 113223.31 | 0.19 | 72.54 | 0 | 55.2 | 0 | OK | Ground clear controls. | 257 | 65.3 | 127.74
17737 | TIN-INTERP | Interpolated Ground | 113224.15 | 7.45 | 75 | 0 | 42.06 | 0 | OK | Ground clear controls. | 257 | 65.3 | 117.06
17738 | TIN-INTERP | Interpolated Ground | 113224.33 | 8.08 | 75 | 0 | 29.95 | 0 | OK | Ground clear controls. | 257 | 65.3 | 104.95
17739 | TIN-INTERP | Interpolated Ground | 113224.5 | 9.6 | 75.41 | 0 | 35.47 | 0 | OK | Ground clear controls. | 257 | 65.3 | 110.88
17740 | TIN-INTERP | Interpolated Ground | 113262.61 | -6.33 | 70.41 | 0 | 39.27 | 0 | OK | Ground clear controls. | 257 | 65.3 | 109.68
17741 | TIN-INTERP | Interpolated Ground | 113262.75 | -4.86 | 70.63 | 0 | 33.06 | 0 | OK | Ground clear controls. | 257 | 65.3 | 103.69
17742 | TIN-INTERP | Interpolated Ground | 113262.85 | -4.23 | 70.72 | 0 | 45.12 | 0 | OK | Ground clear controls. | 257 | 65.3 | 115.84
17743 | TIN-INTERP | Interpolated Ground | 113263.31 | 0.16 | 72.15 | 0 | 54.32 | 0 | OK | Ground clear controls. | 257 | 65.3 | 126.47
17744 | TIN-INTERP | Interpolated Ground | 113264.15 | 7.08 | 73.7 | 0 | 42.01 | 0 | OK | Ground clear controls. | 257 | 65.3 | 115.71
17745 | TIN-INTERP | Interpolated Ground | 113264.32 | 7.68 | 73.91 | 0 | 29.73 | 0 | OK | Ground clear controls. | 257 | 65.3 | 103.64
17746 | TIN-INTERP | Interpolated Ground | 113264.5 | 9.19 | 74.34 | 0 | 35.29 | 0 | OK | Ground clear controls. | 257 | 65.3 | 109.63
17747 | TIN-INTERP | Interpolated Ground | 113302.61 | -6.43 | 78.08 | 0 | 31.25 | 0 | OK | Ground clear controls. | 257 | 65.3 | 109.33
17748 | TIN-INTERP | Interpolated Ground | 113302.75 | -4.95 | 78.02 | 0 | 25.3 | 0 | OK | Ground clear controls. | 257 | 65.3 | 103.32
17749 | TIN-INTERP | Interpolated Ground | 113302.85 | -4.36 | 78.01 | 0 | 37.41 | 0 | OK | Ground clear controls. | 257 | 65.3 | 115.42
17750 | TIN-INTERP | Interpolated Ground | 113303.31 | 0.13 | 78.17 | 0 | 47.83 | 0 | OK | Ground clear controls. | 257 | 65.3 | 126
17751 | TIN-INTERP | Interpolated Ground | 113304.14 | 6.71 | 80.19 | 0 | 35.1 | 0 | OK | Ground clear controls. | 257 | 65.3 | 115.29
17752 | TIN-INTERP | Interpolated Ground | 113304.32 | 7.27 | 80.29 | 0 | 23.01 | 0 | OK | Ground clear controls. | 257 | 65.3 | 103.3
17753 | TIN-INTERP | Interpolated Ground | 113304.5 | 8.79 | 80.57 | 0 | 28.73 | 0 | OK | Ground clear controls. | 257 | 65.3 | 109.3
17754 | TIN-INTERP | Interpolated Ground | 113342.61 | -6.53 | 60.61 | 0 | 49.28 | 0 | OK | Ground clear controls. | 257 | 65.3 | 109.89
17755 | TIN-INTERP | Interpolated Ground | 113342.75 | -5.05 | 60.45 | 0 | 43.47 | 0 | OK | Ground clear controls. | 257 | 65.3 | 103.92
17756 | TIN-INTERP | Interpolated Ground | 113342.85 | -4.5 | 60.4 | 0 | 55.53 | 0 | OK | Ground clear controls. | 257 | 65.3 | 115.93
17757 | TIN-INTERP | Interpolated Ground | 113343.31 | 0.1 | 61.1 | 0 | 65.26 | 0 | OK | Ground clear controls. | 257 | 65.3 | 126.36
17758 | TIN-INTERP | Interpolated Ground | 113344.14 | 6.34 | 61.52 | 0 | 54.3 | 0 | OK | Ground clear controls. | 257 | 65.3 | 115.82
17759 | TIN-INTERP | Interpolated Ground | 113344.32 | 6.87 | 61.52 | 0 | 42.4 | 0 | OK | Ground clear controls. | 257 | 65.3 | 103.92
17760 | TIN-INTERP | Interpolated Ground | 113344.49 | 8.38 | 61.35 | 0 | 48.55 | 0 | OK | Ground clear controls. | 257 | 65.3 | 109.9
17761 | TIN-INTERP | Interpolated Ground | 113382.61 | -6.63 | 60.65 | 0 | 50.71 | 0 | OK | Ground clear controls. | 257 | 65.3 | 111.36
17762 | TIN-INTERP | Interpolated Ground | 113382.75 | -5.14 | 61.23 | 0 | 44.24 | 0 | OK | Ground clear controls. | 257 | 65.3 | 105.47
17763 | TIN-INTERP | Interpolated Ground | 113382.85 | -4.63 | 61.3 | 0 | 56.04 | 0 | OK | Ground clear controls. | 257 | 65.3 | 117.34
17764 | TIN-INTERP | Interpolated Ground | 113383.31 | 0.06 | 62.22 | 0 | 65.3 | 0 | OK | Ground clear controls. | 257 | 65.3 | 127.52
17765 | TIN-INTERP | Interpolated Ground | 113384.14 | 5.97 | 63.41 | 0 | 53.87 | 0 | OK | Ground clear controls. | 257 | 56.02 | 117.28
17766 | TIN-INTERP | Interpolated Ground | 113384.32 | 6.47 | 63.48 | 0 | 42.03 | 0 | OK | Ground clear controls. | 257 | 56.02 | 105.51
17767 | TIN-INTERP | Interpolated Ground | 113384.49 | 7.97 | 63.82 | 0 | 47.59 | 0 | OK | Ground clear controls. | 257 | 56.02 | 111.41
17768 | TIN-INTERP | Interpolated Ground | 113422.61 | -6.73 | 72.04 | 0 | 41.71 | 0 | OK | Ground clear controls. | 257 | 56.02 | 113.75
17769 | TIN-INTERP | Interpolated Ground | 113422.75 | -5.24 | 72.4 | 0 | 35.58 | 0 | OK | Ground clear controls. | 257 | 56.02 | 107.98
17770 | TIN-INTERP | Interpolated Ground | 113422.85 | -4.76 | 72.56 | 0 | 47.1 | 0 | OK | Ground clear controls. | 257 | 56.02 | 119.66
17771 | TIN-INTERP | Interpolated Ground | 113423.31 | 0.03 | 73.47 | 0 | 56.02 | 0 | OK | Ground clear controls. | 257 | 56.02 | 129.49
17772 | TIN-INTERP | Interpolated Ground | 113424.14 | 5.6 | 75.13 | 0 | 44.54 | 0 | OK | Ground clear controls. | 257 | 46.27 | 119.67
17773 | TIN-INTERP | Interpolated Ground | 113424.32 | 6.06 | 75.27 | 0 | 32.79 | 0 | OK | Ground clear controls. | 257 | 46.27 | 108.06
17774 | TIN-INTERP | Interpolated Ground | 113424.49 | 7.57 | 75.71 | 0 | 38.15 | 0 | OK | Ground clear controls. | 257 | 46.27 | 113.86
17775 | TIN-INTERP | Interpolated Ground | 113462.61 | -6.83 | 83.51 | 0 | 33.53 | 0 | OK | Ground clear controls. | 257 | 46.27 | 117.04
17776 | TIN-INTERP | Interpolated Ground | 113462.75 | -5.33 | 84.18 | 0 | 27.26 | 0 | OK | Ground clear controls. | 257 | 46.27 | 111.44
17777 | TIN-INTERP | Interpolated Ground | 113462.85 | -4.9 | 84.34 | 0 | 38.56 | 0 | OK | Ground clear controls. | 257 | 46.27 | 122.9
17778 | TIN-INTERP | Interpolated Ground | 113463.31 | 0 | 86.02 | 0 | 46.27 | 0 | OK | Ground clear controls. | 257 | 46.27 | 132.29
17779 | TIN-INTERP | Interpolated Ground | 113464.14 | 5.24 | 88.08 | 0 | 34.92 | 0 | OK | Ground clear controls. | 257 | 34.92 | 123
17780 | TIN-INTERP | Interpolated Ground | 113464.31 | 5.66 | 88.32 | 0 | 23.27 | 0 | OK | Ground clear controls. | 257 | 28.36 | 111.59
17781 | TIN-INTERP | Interpolated Ground | 113464.49 | 7.16 | 88.85 | 0 | 28.36 | 0 | OK | Ground clear controls. | 257 | 28.36 | 117.21
17782 | TIN-INTERP | Interpolated Ground | 113488.31 | 5.01 | 92.32 | 0 | 33.15 | 0 | OK | Ground clear controls. | 258 | 62.34 | 125.47
17783 | TIN-INTERP | Interpolated Ground | 113488.38 | 6.92 | 92.43 | 0 | 27.24 | 0 | OK | Ground clear controls. | 258 | 62.34 | 119.67
17784 | TIN-INTERP | Interpolated Ground | 113488.43 | 5.42 | 92.34 | 0 | 21.83 | 0 | OK | Ground clear controls. | 258 | 62.34 | 114.17
17785 | TIN-INTERP | Interpolated Ground | 113488.52 | -5.39 | 91.1 | 0 | 23.08 | 0 | OK | Ground clear controls. | 258 | 62.34 | 114.18
17786 | TIN-INTERP | Interpolated Ground | 113488.53 | -6.89 | 90.8 | 0 | 28.87 | 0 | OK | Ground clear controls. | 258 | 62.34 | 119.67
17787 | TIN-INTERP | Interpolated Ground | 113488.56 | -0.02 | 91.83 | 0 | 42.64 | 0 | OK | Ground clear controls. | 258 | 62.34 | 134.47
17788 | TIN-INTERP | Interpolated Ground | 113488.61 | -4.98 | 91.18 | 0 | 34.29 | 0 | OK | Ground clear controls. | 258 | 62.34 | 125.47
17789 | TIN-INTERP | Interpolated Ground | 113528.31 | 4.86 | 82.94 | 0 | 30.14 | 0 | OK | Ground clear controls. | 258 | 62.34 | 113.08
17790 | TIN-INTERP | Interpolated Ground | 113528.38 | 6.78 | 82.23 | 0 | 25.18 | 0 | OK | Ground clear controls. | 258 | 62.34 | 107.41
17791 | TIN-INTERP | Interpolated Ground | 113528.43 | 5.28 | 82.73 | 0 | 19.05 | 0 | OK | Ground clear controls. | 258 | 62.34 | 101.78
17792 | TIN-INTERP | Interpolated Ground | 113528.52 | -5.33 | 84.8 | 0 | 16.96 | 0 | OK | Ground clear controls. | 258 | 62.34 | 101.76
17793 | TIN-INTERP | Interpolated Ground | 113528.53 | -6.82 | 84.97 | 0 | 22.44 | 0 | OK | Ground clear controls. | 258 | 62.34 | 107.41
17794 | TIN-INTERP | Interpolated Ground | 113528.56 | -0.02 | 83.81 | 0 | 38.32 | 0 | OK | Ground clear controls. | 258 | 62.34 | 122.13
17795 | TIN-INTERP | Interpolated Ground | 113528.61 | -4.89 | 84.75 | 0 | 28.47 | 0 | OK | Ground clear controls. | 258 | 62.34 | 113.22
17796 | TIN-INTERP | Interpolated Ground | 113568.31 | 4.72 | 68.64 | 0 | 33.05 | 0 | OK | Ground clear controls. | 258 | 62.34 | 101.69
17797 | TIN-INTERP | Interpolated Ground | 113568.38 | 6.64 | 67.92 | 0 | 28.19 | 0 | OK | Ground clear controls. | 258 | 62.34 | 96.11
17798 | TIN-INTERP | Interpolated Ground | 113568.43 | 5.14 | 68.48 | 0 | 21.91 | 0 | OK | Ground clear controls. | 258 | 62.34 | 90.39
17799 | TIN-INTERP | Interpolated Ground | 113568.52 | -5.26 | 71.25 | 0 | 19.12 | 0 | OK | Ground clear controls. | 258 | 62.34 | 90.37
17800 | TIN-INTERP | Interpolated Ground | 113568.53 | -6.74 | 71.04 | 0 | 25.08 | 0 | OK | Ground clear controls. | 258 | 62.34 | 96.12
17801 | TIN-INTERP | Interpolated Ground | 113568.56 | -0.01 | 70.07 | 0 | 40.63 | 0 | OK | Ground clear controls. | 258 | 62.34 | 110.7
17802 | TIN-INTERP | Interpolated Ground | 113568.61 | -4.8 | 71.27 | 0 | 30.65 | 0 | OK | Ground clear controls. | 258 | 62.34 | 101.92
17803 | TIN-INTERP | Interpolated Ground | 113608.31 | 4.57 | 44.29 | 0 | 46.99 | 0 | OK | Ground clear controls. | 258 | 62.34 | 91.28
17804 | TIN-INTERP | Interpolated Ground | 113608.38 | 6.51 | 44.29 | 0 | 41.48 | 0 | OK | Ground clear controls. | 258 | 62.34 | 85.77
17805 | TIN-INTERP | Interpolated Ground | 113608.43 | 5.01 | 44.23 | 0 | 35.78 | 0 | OK | Ground clear controls. | 258 | 62.34 | 80.01
17806 | TIN-INTERP | Interpolated Ground | 113608.52 | -5.19 | 48.26 | 0 | 31.73 | 0 | OK | Ground clear controls. | 258 | 62.34 | 79.99
17807 | TIN-INTERP | Interpolated Ground | 113608.53 | -6.67 | 48.68 | 0 | 37.14 | 0 | OK | Ground clear controls. | 258 | 62.34 | 85.82
17808 | TIN-INTERP | Interpolated Ground | 113608.56 | -0.01 | 46.5 | 0 | 53.7 | 0 | OK | Ground clear controls. | 258 | 62.34 | 100.2
17809 | TIN-INTERP | Interpolated Ground | 113608.61 | -4.71 | 48.12 | 0 | 43.47 | 0 | OK | Ground clear controls. | 258 | 62.34 | 91.59
17810 | TIN-INTERP | Interpolated Ground | 113648.31 | 4.42 | 27.09 | 0 | 54.77 | 0 | OK | Ground clear controls. | 258 | 62.34 | 81.86
17811 | TIN-INTERP | Interpolated Ground | 113648.38 | 6.37 | 26.63 | 0 | 49.76 | 0 | OK | Ground clear controls. | 258 | 62.34 | 76.39
17812 | TIN-INTERP | Interpolated Ground | 113648.43 | 4.87 | 26.95 | 0 | 43.68 | 0 | OK | Ground clear controls. | 258 | 62.34 | 70.63
17813 | TIN-INTERP | Interpolated Ground | 113648.52 | -5.12 | 29.01 | 0 | 41.62 | 0 | OK | Ground clear controls. | 258 | 62.34 | 70.63
17814 | TIN-INTERP | Interpolated Ground | 113648.53 | -6.59 | 29 | 0 | 47.46 | 0 | OK | Ground clear controls. | 258 | 62.34 | 76.46
17815 | TIN-INTERP | Interpolated Ground | 113648.56 | -0.01 | 28.26 | 0 | 62.34 | 0 | OK | Ground clear controls. | 258 | 62.34 | 90.6
17816 | TIN-INTERP | Interpolated Ground | 113648.61 | -4.62 | 28.95 | 0 | 53.25 | 0 | OK | Ground clear controls. | 258 | 58.08 | 82.2
17817 | TIN-INTERP | Interpolated Ground | 113688.31 | 4.27 | 23.9 | 0 | 49.53 | 0 | OK | Ground clear controls. | 258 | 58.08 | 73.43
17818 | TIN-INTERP | Interpolated Ground | 113688.38 | 6.23 | 23.91 | 0 | 44.06 | 0 | OK | Ground clear controls. | 258 | 58.08 | 67.97
17819 | TIN-INTERP | Interpolated Ground | 113688.43 | 4.73 | 23.97 | 0 | 38.26 | 0 | OK | Ground clear controls. | 258 | 58.08 | 62.23
17820 | TIN-INTERP | Interpolated Ground | 113688.52 | -5.05 | 24.14 | 0 | 38.13 | 0 | OK | Ground clear controls. | 258 | 58.08 | 62.27
17821 | TIN-INTERP | Interpolated Ground | 113688.53 | -6.52 | 24.11 | 0 | 43.96 | 0 | OK | Ground clear controls. | 258 | 58.08 | 68.07
17822 | TIN-INTERP | Interpolated Ground | 113688.56 | -0.01 | 23.83 | 0 | 58.08 | 0 | OK | Ground clear controls. | 258 | 58.08 | 81.91
17823 | TIN-INTERP | Interpolated Ground | 113688.61 | -4.52 | 24.12 | 0 | 49.63 | 0 | OK | Ground clear controls. | 258 | 49.63 | 73.75
17824 | TIN-INTERP | Interpolated Ground | 113728.31 | 4.12 | 25.12 | 0 | 40.85 | 0 | OK | Ground clear controls. | 258 | 49.43 | 65.97
17825 | TIN-INTERP | Interpolated Ground | 113728.38 | 6.1 | 25.36 | 0 | 35.12 | 0 | OK | Ground clear controls. | 258 | 49.43 | 60.48
17826 | TIN-INTERP | Interpolated Ground | 113728.43 | 4.59 | 25.1 | 0 | 29.72 | 0 | OK | Ground clear controls. | 258 | 49.43 | 54.82
17827 | TIN-INTERP | Interpolated Ground | 113728.52 | -4.98 | 24.38 | 0 | 30.53 | 0 | OK | Ground clear controls. | 258 | 49.43 | 54.91
17828 | TIN-INTERP | Interpolated Ground | 113728.53 | -6.44 | 24.31 | 0 | 36.34 | 0 | OK | Ground clear controls. | 258 | 49.43 | 60.65
17829 | TIN-INTERP | Interpolated Ground | 113728.56 | 0 | 24.69 | 0 | 49.43 | 0 | OK | Ground clear controls. | 258 | 49.43 | 74.12
17830 | TIN-INTERP | Interpolated Ground | 113728.61 | -4.43 | 24.33 | 0 | 41.92 | 0 | OK | Ground clear controls. | 258 | 43.22 | 66.25
17831 | TIN-INTERP | Interpolated Ground | 113768.31 | 3.97 | 24.05 | 0 | 35.43 | 0 | OK | Ground clear controls. | 258 | 43.22 | 59.48
17832 | TIN-INTERP | Interpolated Ground | 113768.38 | 5.96 | 24.05 | 0 | 29.89 | 0 | OK | Ground clear controls. | 258 | 43.22 | 53.94
17833 | TIN-INTERP | Interpolated Ground | 113768.43 | 4.46 | 24.06 | 0 | 24.33 | 0 | OK | Ground clear controls. | 258 | 43.22 | 48.39
17834 | TIN-INTERP | Interpolated Ground | 113768.52 | -4.91 | 24.02 | 0 | 24.53 | 0 | OK | Ground clear controls. | 258 | 43.22 | 48.55
17835 | TIN-INTERP | Interpolated Ground | 113768.53 | -6.37 | 24 | 0 | 30.17 | 0 | OK | Ground clear controls. | 258 | 43.22 | 54.17
17836 | TIN-INTERP | Interpolated Ground | 113768.56 | 0 | 24.01 | 0 | 43.22 | 0 | OK | Ground clear controls. | 258 | 43.22 | 67.23
17837 | TIN-INTERP | Interpolated Ground | 113768.61 | -4.34 | 24.02 | 0 | 35.66 | 0 | OK | Ground clear controls. | 258 | 35.66 | 59.68
17838 | TIN-INTERP | Interpolated Ground | 113787.86 | 0 | 24.65 | 0 | 39.57 | 0 | OK | Ground clear controls. | 259 | 39.57 | 64.22
17839 | TIN-INTERP | Interpolated Ground | 113792.7 | -2.87 | 24.09 | 0 | 31.9 | 0 | OK | Ground clear controls. | 259 | 31.9 | 55.99
17840 | TIN-INTERP | Interpolated Ground | 113793.2 | -3.12 | 24.02 | 0 | 26.64 | 0 | OK | Ground clear controls. | 259 | 31.8 | 50.66
17841 | TIN-INTERP | Interpolated Ground | 113793.62 | -3.62 | 23.93 | 0 | 21.45 | 0 | OK | Ground clear controls. | 259 | 31.8 | 45.38
17842 | TIN-INTERP | Interpolated Ground | 113827.52 | -5.18 | 24.34 | 0 | 23.5 | 0 | OK | Ground clear controls. | 259 | 31.8 | 47.84
17843 | TIN-INTERP | Interpolated Ground | 113832.43 | 1.73 | 24.36 | 0 | 19.72 | 0 | OK | Ground clear controls. | 259 | 31.8 | 44.08
17844 | TIN-INTERP | Interpolated Ground | 113833.16 | -1.36 | 24.4 | 0 | 17.55 | 0 | OK | Ground clear controls. | 259 | 31.8 | 41.95
17845 | TIN-INTERP | Interpolated Ground | 113833.61 | -4.52 | 24.36 | 0 | 15.69 | 0 | OK | Ground clear controls. | 259 | 31.8 | 40.05
17846 | TIN-INTERP | Interpolated Ground | 114364.15 | 2.52 | 24.01 | 0 | 31.8 | 0 | OK | Ground clear controls. | 259 | 31.8 | 55.81
17847 | TIN-INTERP | Interpolated Ground | 114364.47 | 2.99 | 24.02 | 0 | 20.65 | 0 | OK | Ground clear controls. | 259 | 26.25 | 44.67
17848 | TIN-INTERP | Interpolated Ground | 114365.94 | 3.39 | 23.99 | 0 | 26.25 | 0 | OK | Ground clear controls. | 259 | 26.25 | 50.24
17849 | TIN-INTERP | Interpolated Ground | 114904.94 | -3.81 | 371.89 | 0 | 27 | 0 | OK | Ground clear controls. | WRK2 S/S | 35.4 | 398.89
17850 | TIN-INTERP | Interpolated Ground | 114905.15 | -3.82 | 371.92 | 0 | 21.66 | 0 | OK | Ground clear controls. | WRK2 S/S | 35.4 | 393.58
17851 | TIN-INTERP | Interpolated Ground | 114905.55 | -4.06 | 371.7 | 0 | 35.4 | 0 | OK | Ground clear controls. | WRK2 S/S | 35.4 | 407.1
17852 | TIN-INTERP | Interpolated Ground | 114940.73 | -4.77 | 369.08 | 0 | 22.84 | 0 | OK | Ground clear controls. | WRK2 S/S | 22.84 | 391.92
17853 | TIN-INTERP | Interpolated Ground | 114944.93 | -4.55 | 369.22 | 0 | 17.82 | 0 | OK | Ground clear controls. | WRK2 S/S | 17.82 | 387.04
17854 | TIN-INTERP | Interpolated Ground | 114945.06 | 2.15 | 369.26 | 0 | 14.59 | 0 | OK | Ground clear controls. | WRK2 S/S | 16.02 | 383.85
17855 | TIN-INTERP | Interpolated Ground | 114945.07 | -1.24 | 369.34 | 0 | 16.02 | 0 | OK | Ground clear controls. | WRK2 S/S | 16.02 | 385.36
17856
USER GUIDE
FOLLOWING REPORT SETTINGS SHALL BE ADOPTED - WEATHER CASE SHALL BE MINIMUM TEMPERATURE - STILL AIR

## Ref (hidden)
FROM AS/NZS 1170.2 table 3.1 and 3.2
DIRECTION MULTIPLIERS MD
|  | WIND DIRECTION | [7 empty] | REGIONAL
|  | N | NE | E | SE | S | SW | W | NW | V1000
WIND REGION | A1 | 0.9 | 0.8 | 0.8 | 0.8 | 0.85 | 0.95 | 1 | 0.95 | 46
| A2 | 0.8 | 0.8 | 0.8 | 0.95 | 0.9 | 0.95 | 1 | 0.95 | 46
| A3 | 0.85 | 0.8 | 0.8 | 0.8 | 0.8 | 0.85 | 0.9 | 1 | 46
| A4 | 0.9 | 0.85 | 0.9 | 0.9 | 0.95 | 0.95 | 0.95 | 0.9 | 46
| A5 | 1 | 0.85 | 0.8 | 0.8 | 0.85 | 0.9 | 1 | 0.95 | 46
| A6 | 0.85 | 0.95 | 1 | 0.95 | 0.85 | 0.95 | 1 | 0.95 | 46
| A7 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 1 | 1 | 46
| W | 1 | 0.95 | 0.8 | 0.9 | 1 | 1 | 0.9 | 0.95 | 53
LOOKUP TABLE - BLACK LINES SHOW EXTENTS OF LOOKUP
Formula for Conditional formatting for SRF span length check
=AL17-INDEX('Staking Table'!$K$6:$K$500,MATCH($A17,'Staking Table'!$B$6:$B$500,0),1)>0.01
[6 empty] | Values from AS/NZS 1170.2 Table 4.1 (AMDT 2) | [9 empty] | Terrain Height Multiplier (Mz,CAT)
Heights | Region / Terrain Code |  |  |  |  | Interpolated values
Z | 1 | 1.1 | 1.2 | 1.3 | 1.4 | 1.5 | 1.6 | 1.7 | 1.8 | 1.9 | 2 | 2.1 | 2.2 | 2.3 | 2.4 | 2.5 | 2.6 | 2.7 | 2.8 | 2.9 | 3 | 3.1 | 3.2 | 3.3 | 3.4 | 3.5 | 3.6 | 3.7 | 3.8 | 3.9 | 4 | C1 | C3
0 | 0.99 | 0.982 | 0.974 | 0.966 | 0.958 | 0.95 | 0.942 | 0.934 | 0.926 | 0.918 | 0.91 | 0.902 | 0.894 | 0.886 | 0.878 | 0.87 | 0.862 | 0.854 | 0.846 | 0.838 | 0.83 | 0.822 | 0.814 | 0.806 | 0.798 | 0.79 | 0.782 | 0.774 | 0.766 | 0.758 | 0.75 | 0.9 | 0.8
1 | 0.99 | 0.982 | 0.974 | 0.966 | 0.958 | 0.95 | 0.942 | 0.934 | 0.926 | 0.918 | 0.91 | 0.902 | 0.894 | 0.886 | 0.878 | 0.87 | 0.862 | 0.854 | 0.846 | 0.838 | 0.83 | 0.822 | 0.814 | 0.806 | 0.798 | 0.79 | 0.782 | 0.774 | 0.766 | 0.758 | 0.75 | 0.9 | 0.8
2 | 0.99 | 0.982 | 0.974 | 0.966 | 0.958 | 0.95 | 0.942 | 0.934 | 0.926 | 0.918 | 0.91 | 0.902 | 0.894 | 0.886 | 0.878 | 0.87 | 0.862 | 0.854 | 0.846 | 0.838 | 0.83 | 0.822 | 0.814 | 0.806 | 0.798 | 0.79 | 0.782 | 0.774 | 0.766 | 0.758 | 0.75 | 0.9 | 0.8
3 | 0.99 | 0.982 | 0.974 | 0.966 | 0.958 | 0.95 | 0.942 | 0.934 | 0.926 | 0.918 | 0.91 | 0.902 | 0.894 | 0.886 | 0.878 | 0.87 | 0.862 | 0.854 | 0.846 | 0.838 | 0.83 | 0.822 | 0.814 | 0.806 | 0.798 | 0.79 | 0.782 | 0.774 | 0.766 | 0.758 | 0.75 | 0.9 | 0.8
4 | 1.02 | 1.009 | 0.998 | 0.987 | 0.976 | 0.965 | 0.954 | 0.943 | 0.932 | 0.921 | 0.91 | 0.902 | 0.894 | 0.886 | 0.878 | 0.87 | 0.862 | 0.854 | 0.846 | 0.838 | 0.83 | 0.822 | 0.814 | 0.806 | 0.798 | 0.79 | 0.782 | 0.774 | 0.766 | 0.758 | 0.75 | 0.925 | 0.8
5 | 1.05 | 1.036 | 1.022 | 1.008 | 0.994 | 0.98 | 0.966 | 0.952 | 0.938 | 0.924 | 0.91 | 0.902 | 0.894 | 0.886 | 0.878 | 0.87 | 0.862 | 0.854 | 0.846 | 0.838 | 0.83 | 0.822 | 0.814 | 0.806 | 0.798 | 0.79 | 0.782 | 0.774 | 0.766 | 0.758 | 0.75 | 0.95 | 0.8
6 | 1.064 | 1.0504 | 1.0368 | 1.0232 | 1.0096 | 0.996 | 0.9824 | 0.9688 | 0.9552 | 0.9416 | 0.928 | 0.9182 | 0.9084 | 0.8986 | 0.8888 | 0.879 | 0.8692 | 0.8594 | 0.8496 | 0.8398 | 0.83 | 0.822 | 0.814 | 0.806 | 0.798 | 0.79 | 0.782 | 0.774 | 0.766 | 0.758 | 0.75 | 0.96 | 0.818
7 | 1.078 | 1.0648 | 1.0516 | 1.0384 | 1.0252 | 1.012 | 0.9988 | 0.9856 | 0.9724 | 0.9592 | 0.946 | 0.9344 | 0.9228 | 0.9112 | 0.8996 | 0.888 | 0.8764 | 0.8648 | 0.8532 | 0.8416 | 0.83 | 0.822 | 0.814 | 0.806 | 0.798 | 0.79 | 0.782 | 0.774 | 0.766 | 0.758 | 0.75 | 0.97 | 0.836
8 | 1.092 | 1.0792 | 1.0664 | 1.0536 | 1.0408 | 1.028 | 1.0152 | 1.0024 | 0.9896 | 0.9768 | 0.964 | 0.9506 | 0.9372 | 0.9238 | 0.9104 | 0.897 | 0.8836 | 0.8702 | 0.8568 | 0.8434 | 0.83 | 0.822 | 0.814 | 0.806 | 0.798 | 0.79 | 0.782 | 0.774 | 0.766 | 0.758 | 0.75 | 0.98 | 0.854
9 | 1.106 | 1.0936 | 1.0812 | 1.0688 | 1.0564 | 1.044 | 1.0316 | 1.0192 | 1.0068 | 0.9944 | 0.982 | 0.9668 | 0.9516 | 0.9364 | 0.9212 | 0.906 | 0.8908 | 0.8756 | 0.8604 | 0.8452 | 0.83 | 0.822 | 0.814 | 0.806 | 0.798 | 0.79 | 0.782 | 0.774 | 0.766 | 0.758 | 0.75 | 0.99 | 0.872
10 | 1.12 | 1.108 | 1.096 | 1.084 | 1.072 | 1.06 | 1.048 | 1.036 | 1.024 | 1.012 | 1 | 0.983 | 0.966 | 0.949 | 0.932 | 0.915 | 0.898 | 0.881 | 0.864 | 0.847 | 0.83 | 0.822 | 0.814 | 0.806 | 0.798 | 0.79 | 0.782 | 0.774 | 0.766 | 0.758 | 0.75 | 1 | 0.89
11 | 1.128 | 1.1162 | 1.1044 | 1.0926 | 1.0808 | 1.069 | 1.0572 | 1.0454 | 1.0336 | 1.0218 | 1.01 | 0.9932 | 0.9764 | 0.9596 | 0.9428 | 0.926 | 0.9092 | 0.8924 | 0.8756 | 0.8588 | 0.842 | 0.8328 | 0.8236 | 0.8144 | 0.8052 | 0.796 | 0.7868 | 0.7776 | 0.7684 | 0.7592 | 0.75 | 1.014 | 0.902
12 | 1.136 | 1.1244 | 1.1128 | 1.1012 | 1.0896 | 1.078 | 1.0664 | 1.0548 | 1.0432 | 1.0316 | 1.02 | 1.0034 | 0.9868 | 0.9702 | 0.9536 | 0.937 | 0.9204 | 0.9038 | 0.8872 | 0.8706 | 0.854 | 0.8436 | 0.8332 | 0.8228 | 0.8124 | 0.802 | 0.7916 | 0.7812 | 0.7708 | 0.7604 | 0.75 | 1.028 | 0.914
13 | 1.144 | 1.1326 | 1.1212 | 1.1098 | 1.0984 | 1.087 | 1.0756 | 1.0642 | 1.0528 | 1.0414 | 1.03 | 1.0136 | 0.9972 | 0.9808 | 0.9644 | 0.948 | 0.9316 | 0.9152 | 0.8988 | 0.8824 | 0.866 | 0.8544 | 0.8428 | 0.8312 | 0.8196 | 0.808 | 0.7964 | 0.7848 | 0.7732 | 0.7616 | 0.75 | 1.042 | 0.926
14 | 1.152 | 1.1408 | 1.1296 | 1.1184 | 1.1072 | 1.096 | 1.0848 | 1.0736 | 1.0624 | 1.0512 | 1.04 | 1.0238 | 1.0076 | 0.9914 | 0.9752 | 0.959 | 0.9428 | 0.9266 | 0.9104 | 0.8942 | 0.878 | 0.8652 | 0.8524 | 0.8396 | 0.8268 | 0.814 | 0.8012 | 0.7884 | 0.7756 | 0.7628 | 0.75 | 1.056 | 0.938
15 | 1.16 | 1.149 | 1.138 | 1.127 | 1.116 | 1.105 | 1.094 | 1.083 | 1.072 | 1.061 | 1.05 | 1.034 | 1.018 | 1.002 | 0.986 | 0.97 | 0.954 | 0.938 | 0.922 | 0.906 | 0.89 | 0.876 | 0.862 | 0.848 | 0.834 | 0.82 | 0.806 | 0.792 | 0.778 | 0.764 | 0.75 | 1.07 | 0.95
16 | 1.166 | 1.155 | 1.144 | 1.133 | 1.122 | 1.111 | 1.1 | 1.089 | 1.078 | 1.067 | 1.056 | 1.0404 | 1.0248 | 1.0092 | 0.9936 | 0.978 | 0.9624 | 0.9468 | 0.9312 | 0.9156 | 0.9 | 0.885 | 0.87 | 0.855 | 0.84 | 0.825 | 0.81 | 0.795 | 0.78 | 0.765 | 0.75 | 1.082 | 0.97
17 | 1.172 | 1.161 | 1.15 | 1.139 | 1.128 | 1.117 | 1.106 | 1.095 | 1.084 | 1.073 | 1.062 | 1.0468 | 1.0316 | 1.0164 | 1.0012 | 0.986 | 0.9708 | 0.9556 | 0.9404 | 0.9252 | 0.91 | 0.894 | 0.878 | 0.862 | 0.846 | 0.83 | 0.814 | 0.798 | 0.782 | 0.766 | 0.75 | 1.094 | 0.99
18 | 1.178 | 1.167 | 1.156 | 1.145 | 1.134 | 1.123 | 1.112 | 1.101 | 1.09 | 1.079 | 1.068 | 1.0532 | 1.0384 | 1.0236 | 1.0088 | 0.994 | 0.9792 | 0.9644 | 0.9496 | 0.9348 | 0.92 | 0.903 | 0.886 | 0.869 | 0.852 | 0.835 | 0.818 | 0.801 | 0.784 | 0.767 | 0.75 | 1.106 | 1.01
19 | 1.184 | 1.173 | 1.162 | 1.151 | 1.14 | 1.129 | 1.118 | 1.107 | 1.096 | 1.085 | 1.074 | 1.0596 | 1.0452 | 1.0308 | 1.0164 | 1.002 | 0.9876 | 0.9732 | 0.9588 | 0.9444 | 0.93 | 0.912 | 0.894 | 0.876 | 0.858 | 0.84 | 0.822 | 0.804 | 0.786 | 0.768 | 0.75 | 1.118 | 1.03
20 | 1.19 | 1.179 | 1.168 | 1.157 | 1.146 | 1.135 | 1.124 | 1.113 | 1.102 | 1.091 | 1.08 | 1.066 | 1.052 | 1.038 | 1.024 | 1.01 | 0.996 | 0.982 | 0.968 | 0.954 | 0.94 | 0.921 | 0.902 | 0.883 | 0.864 | 0.845 | 0.826 | 0.807 | 0.788 | 0.769 | 0.75 | 1.13 | 1.05
21 | 1.193 | 1.1821 | 1.1712 | 1.1603 | 1.1494 | 1.1385 | 1.1276 | 1.1167 | 1.1058 | 1.0949 | 1.084 | 1.0702 | 1.0564 | 1.0426 | 1.0288 | 1.015 | 1.0012 | 0.9874 | 0.9736 | 0.9598 | 0.946 | 0.9269 | 0.9078 | 0.8887 | 0.8696 | 0.8505 | 0.8314 | 0.8123 | 0.7932 | 0.7741 | 0.755 | 1.137 | 1.06
22 | 1.196 | 1.1852 | 1.1744 | 1.1636 | 1.1528 | 1.142 | 1.1312 | 1.1204 | 1.1096 | 1.0988 | 1.088 | 1.0744 | 1.0608 | 1.0472 | 1.0336 | 1.02 | 1.0064 | 0.9928 | 0.9792 | 0.9656 | 0.952 | 0.9328 | 0.9136 | 0.8944 | 0.8752 | 0.856 | 0.8368 | 0.8176 | 0.7984 | 0.7792 | 0.76 | 1.144 | 1.07
23 | 1.199 | 1.1883 | 1.1776 | 1.1669 | 1.1562 | 1.1455 | 1.1348 | 1.1241 | 1.1134 | 1.1027 | 1.092 | 1.0786 | 1.0652 | 1.0518 | 1.0384 | 1.025 | 1.0116 | 0.9982 | 0.9848 | 0.9714 | 0.958 | 0.9387 | 0.9194 | 0.9001 | 0.8808 | 0.8615 | 0.8422 | 0.8229 | 0.8036 | 0.7843 | 0.765 | 1.151 | 1.08
24 | 1.202 | 1.1914 | 1.1808 | 1.1702 | 1.1596 | 1.149 | 1.1384 | 1.1278 | 1.1172 | 1.1066 | 1.096 | 1.0828 | 1.0696 | 1.0564 | 1.0432 | 1.03 | 1.0168 | 1.0036 | 0.9904 | 0.9772 | 0.964 | 0.9446 | 0.9252 | 0.9058 | 0.8864 | 0.867 | 0.8476 | 0.8282 | 0.8088 | 0.7894 | 0.77 | 1.158 | 1.09
25 | 1.205 | 1.1945 | 1.184 | 1.1735 | 1.163 | 1.1525 | 1.142 | 1.1315 | 1.121 | 1.1105 | 1.1 | 1.087 | 1.074 | 1.061 | 1.048 | 1.035 | 1.022 | 1.009 | 0.996 | 0.983 | 0.97 | 0.9505 | 0.931 | 0.9115 | 0.892 | 0.8725 | 0.853 | 0.8335 | 0.814 | 0.7945 | 0.775 | 1.165 | 1.1
26 | 1.208 | 1.1976 | 1.1872 | 1.1768 | 1.1664 | 1.156 | 1.1456 | 1.1352 | 1.1248 | 1.1144 | 1.104 | 1.0912 | 1.0784 | 1.0656 | 1.0528 | 1.04 | 1.0272 | 1.0144 | 1.0016 | 0.9888 | 0.976 | 0.9564 | 0.9368 | 0.9172 | 0.8976 | 0.878 | 0.8584 | 0.8388 | 0.8192 | 0.7996 | 0.78 | 1.172 | 1.11
27 | 1.211 | 1.2007 | 1.1904 | 1.1801 | 1.1698 | 1.1595 | 1.1492 | 1.1389 | 1.1286 | 1.1183 | 1.108 | 1.0954 | 1.0828 | 1.0702 | 1.0576 | 1.045 | 1.0324 | 1.0198 | 1.0072 | 0.9946 | 0.982 | 0.9623 | 0.9426 | 0.9229 | 0.9032 | 0.8835 | 0.8638 | 0.8441 | 0.8244 | 0.8047 | 0.785 | 1.179 | 1.12
28 | 1.214 | 1.2038 | 1.1936 | 1.1834 | 1.1732 | 1.163 | 1.1528 | 1.1426 | 1.1324 | 1.1222 | 1.112 | 1.0996 | 1.0872 | 1.0748 | 1.0624 | 1.05 | 1.0376 | 1.0252 | 1.0128 | 1.0004 | 0.988 | 0.9682 | 0.9484 | 0.9286 | 0.9088 | 0.889 | 0.8692 | 0.8494 | 0.8296 | 0.8098 | 0.79 | 1.186 | 1.13
29 | 1.217 | 1.2069 | 1.1968 | 1.1867 | 1.1766 | 1.1665 | 1.1564 | 1.1463 | 1.1362 | 1.1261 | 1.116 | 1.1038 | 1.0916 | 1.0794 | 1.0672 | 1.055 | 1.0428 | 1.0306 | 1.0184 | 1.0062 | 0.994 | 0.9741 | 0.9542 | 0.9343 | 0.9144 | 0.8945 | 0.8746 | 0.8547 | 0.8348 | 0.8149 | 0.795 | 1.193 | 1.14
30 | 1.22 | 1.21 | 1.2 | 1.19 | 1.18 | 1.17 | 1.16 | 1.15 | 1.14 | 1.13 | 1.12 | 1.108 | 1.096 | 1.084 | 1.072 | 1.06 | 1.048 | 1.036 | 1.024 | 1.012 | 1 | 0.98 | 0.96 | 0.94 | 0.92 | 0.9 | 0.88 | 0.86 | 0.84 | 0.82 | 0.8 | 1.2 | 1.15
31 | 1.222 | 1.2122 | 1.2024 | 1.1926 | 1.1828 | 1.173 | 1.1632 | 1.1534 | 1.1436 | 1.1338 | 1.124 | 1.112 | 1.1 | 1.088 | 1.076 | 1.064 | 1.052 | 1.04 | 1.028 | 1.016 | 1.004 | 0.9841 | 0.9642 | 0.9443 | 0.9244 | 0.9045 | 0.8846 | 0.8647 | 0.8448 | 0.8249 | 0.805 | 1.205 | 1.16
32 | 1.224 | 1.2144 | 1.2048 | 1.1952 | 1.1856 | 1.176 | 1.1664 | 1.1568 | 1.1472 | 1.1376 | 1.128 | 1.116 | 1.104 | 1.092 | 1.08 | 1.068 | 1.056 | 1.044 | 1.032 | 1.02 | 1.008 | 0.9882 | 0.9684 | 0.9486 | 0.9288 | 0.909 | 0.8892 | 0.8694 | 0.8496 | 0.8298 | 0.81 | 1.21 | 1.17
33 | 1.226 | 1.2166 | 1.2072 | 1.1978 | 1.1884 | 1.179 | 1.1696 | 1.1602 | 1.1508 | 1.1414 | 1.132 | 1.12 | 1.108 | 1.096 | 1.084 | 1.072 | 1.06 | 1.048 | 1.036 | 1.024 | 1.012 | 0.9923 | 0.9726 | 0.9529 | 0.9332 | 0.9135 | 0.8938 | 0.8741 | 0.8544 | 0.8347 | 0.815 | 1.215 | 1.18
34 | 1.228 | 1.2188 | 1.2096 | 1.2004 | 1.1912 | 1.182 | 1.1728 | 1.1636 | 1.1544 | 1.1452 | 1.136 | 1.124 | 1.112 | 1.1 | 1.088 | 1.076 | 1.064 | 1.052 | 1.04 | 1.028 | 1.016 | 0.9964 | 0.9768 | 0.9572 | 0.9376 | 0.918 | 0.8984 | 0.8788 | 0.8592 | 0.8396 | 0.82 | 1.22 | 1.19
35 | 1.23 | 1.221 | 1.212 | 1.203 | 1.194 | 1.185 | 1.176 | 1.167 | 1.158 | 1.149 | 1.14 | 1.128 | 1.116 | 1.104 | 1.092 | 1.08 | 1.068 | 1.056 | 1.044 | 1.032 | 1.02 | 1.0005 | 0.981 | 0.9615 | 0.942 | 0.9225 | 0.903 | 0.8835 | 0.864 | 0.8445 | 0.825 | 1.225 | 1.2
36 | 1.232 | 1.2232 | 1.2144 | 1.2056 | 1.1968 | 1.188 | 1.1792 | 1.1704 | 1.1616 | 1.1528 | 1.144 | 1.132 | 1.12 | 1.108 | 1.096 | 1.084 | 1.072 | 1.06 | 1.048 | 1.036 | 1.024 | 1.0046 | 0.9852 | 0.9658 | 0.9464 | 0.927 | 0.9076 | 0.8882 | 0.8688 | 0.8494 | 0.83 | 1.23 | 1.21
37 | 1.234 | 1.2254 | 1.2168 | 1.2082 | 1.1996 | 1.191 | 1.1824 | 1.1738 | 1.1652 | 1.1566 | 1.148 | 1.136 | 1.124 | 1.112 | 1.1 | 1.088 | 1.076 | 1.064 | 1.052 | 1.04 | 1.028 | 1.0087 | 0.9894 | 0.9701 | 0.9508 | 0.9315 | 0.9122 | 0.8929 | 0.8736 | 0.8543 | 0.835 | 1.235 | 1.22
38 | 1.236 | 1.2276 | 1.2192 | 1.2108 | 1.2024 | 1.194 | 1.1856 | 1.1772 | 1.1688 | 1.1604 | 1.152 | 1.14 | 1.128 | 1.116 | 1.104 | 1.092 | 1.08 | 1.068 | 1.056 | 1.044 | 1.032 | 1.0128 | 0.9936 | 0.9744 | 0.9552 | 0.936 | 0.9168 | 0.8976 | 0.8784 | 0.8592 | 0.84 | 1.24 | 1.23
39 | 1.238 | 1.2298 | 1.2216 | 1.2134 | 1.2052 | 1.197 | 1.1888 | 1.1806 | 1.1724 | 1.1642 | 1.156 | 1.144 | 1.132 | 1.12 | 1.108 | 1.096 | 1.084 | 1.072 | 1.06 | 1.048 | 1.036 | 1.0169 | 0.9978 | 0.9787 | 0.9596 | 0.9405 | 0.9214 | 0.9023 | 0.8832 | 0.8641 | 0.845 | 1.245 | 1.24
40 | 1.24 | 1.232 | 1.224 | 1.216 | 1.208 | 1.2 | 1.192 | 1.184 | 1.176 | 1.168 | 1.16 | 1.148 | 1.136 | 1.124 | 1.112 | 1.1 | 1.088 | 1.076 | 1.064 | 1.052 | 1.04 | 1.021 | 1.002 | 0.983 | 0.964 | 0.945 | 0.926 | 0.907 | 0.888 | 0.869 | 0.85 | 1.25 | 1.25
41 | 1.241 | 1.2331 | 1.2252 | 1.2173 | 1.2094 | 1.2015 | 1.1936 | 1.1857 | 1.1778 | 1.1699 | 1.162 | 1.1501 | 1.1382 | 1.1263 | 1.1144 | 1.1025 | 1.0906 | 1.0787 | 1.0668 | 1.0549 | 1.043 | 1.0242 | 1.0054 | 0.9866 | 0.9678 | 0.949 | 0.9302 | 0.9114 | 0.8926 | 0.8738 | 0.855 | 1.254 | 1.254
42 | 1.242 | 1.2342 | 1.2264 | 1.2186 | 1.2108 | 1.203 | 1.1952 | 1.1874 | 1.1796 | 1.1718 | 1.164 | 1.1522 | 1.1404 | 1.1286 | 1.1168 | 1.105 | 1.0932 | 1.0814 | 1.0696 | 1.0578 | 1.046 | 1.0274 | 1.0088 | 0.9902 | 0.9716 | 0.953 | 0.9344 | 0.9158 | 0.8972 | 0.8786 | 0.86 | 1.258 | 1.258
43 | 1.243 | 1.2353 | 1.2276 | 1.2199 | 1.2122 | 1.2045 | 1.1968 | 1.1891 | 1.1814 | 1.1737 | 1.166 | 1.1543 | 1.1426 | 1.1309 | 1.1192 | 1.1075 | 1.0958 | 1.0841 | 1.0724 | 1.0607 | 1.049 | 1.0306 | 1.0122 | 0.9938 | 0.9754 | 0.957 | 0.9386 | 0.9202 | 0.9018 | 0.8834 | 0.865 | 1.262 | 1.262
44 | 1.244 | 1.2364 | 1.2288 | 1.2212 | 1.2136 | 1.206 | 1.1984 | 1.1908 | 1.1832 | 1.1756 | 1.168 | 1.1564 | 1.1448 | 1.1332 | 1.1216 | 1.11 | 1.0984 | 1.0868 | 1.0752 | 1.0636 | 1.052 | 1.0338 | 1.0156 | 0.9974 | 0.9792 | 0.961 | 0.9428 | 0.9246 | 0.9064 | 0.8882 | 0.87 | 1.266 | 1.266
45 | 1.245 | 1.2375 | 1.23 | 1.2225 | 1.215 | 1.2075 | 1.2 | 1.1925 | 1.185 | 1.1775 | 1.17 | 1.1585 | 1.147 | 1.1355 | 1.124 | 1.1125 | 1.101 | 1.0895 | 1.078 | 1.0665 | 1.055 | 1.037 | 1.019 | 1.001 | 0.983 | 0.965 | 0.947 | 0.929 | 0.911 | 0.893 | 0.875 | 1.27 | 1.27
46 | 1.246 | 1.2386 | 1.2312 | 1.2238 | 1.2164 | 1.209 | 1.2016 | 1.1942 | 1.1868 | 1.1794 | 1.172 | 1.1606 | 1.1492 | 1.1378 | 1.1264 | 1.115 | 1.1036 | 1.0922 | 1.0808 | 1.0694 | 1.058 | 1.0402 | 1.0224 | 1.0046 | 0.9868 | 0.969 | 0.9512 | 0.9334 | 0.9156 | 0.8978 | 0.88 | 1.274 | 1.274
47 | 1.247 | 1.2397 | 1.2324 | 1.2251 | 1.2178 | 1.2105 | 1.2032 | 1.1959 | 1.1886 | 1.1813 | 1.174 | 1.1627 | 1.1514 | 1.1401 | 1.1288 | 1.1175 | 1.1062 | 1.0949 | 1.0836 | 1.0723 | 1.061 | 1.0434 | 1.0258 | 1.0082 | 0.9906 | 0.973 | 0.9554 | 0.9378 | 0.9202 | 0.9026 | 0.885 | 1.278 | 1.278
48 | 1.248 | 1.2408 | 1.2336 | 1.2264 | 1.2192 | 1.212 | 1.2048 | 1.1976 | 1.1904 | 1.1832 | 1.176 | 1.1648 | 1.1536 | 1.1424 | 1.1312 | 1.12 | 1.1088 | 1.0976 | 1.0864 | 1.0752 | 1.064 | 1.0466 | 1.0292 | 1.0118 | 0.9944 | 0.977 | 0.9596 | 0.9422 | 0.9248 | 0.9074 | 0.89 | 1.282 | 1.282
49 | 1.249 | 1.2419 | 1.2348 | 1.2277 | 1.2206 | 1.2135 | 1.2064 | 1.1993 | 1.1922 | 1.1851 | 1.178 | 1.1669 | 1.1558 | 1.1447 | 1.1336 | 1.1225 | 1.1114 | 1.1003 | 1.0892 | 1.0781 | 1.067 | 1.0498 | 1.0326 | 1.0154 | 0.9982 | 0.981 | 0.9638 | 0.9466 | 0.9294 | 0.9122 | 0.895 | 1.286 | 1.286
50 | 1.25 | 1.243 | 1.236 | 1.229 | 1.222 | 1.215 | 1.208 | 1.201 | 1.194 | 1.187 | 1.18 | 1.169 | 1.158 | 1.147 | 1.136 | 1.125 | 1.114 | 1.103 | 1.092 | 1.081 | 1.07 | 1.053 | 1.036 | 1.019 | 1.002 | 0.985 | 0.968 | 0.951 | 0.934 | 0.917 | 0.9 | 1.29 | 1.29
51 | 1.2508 | 1.2439 | 1.237 | 1.23 | 1.2231 | 1.2162 | 1.2093 | 1.2024 | 1.1954 | 1.1885 | 1.1816 | 1.1706 | 1.1597 | 1.1487 | 1.1378 | 1.1268 | 1.1158 | 1.1049 | 1.0939 | 1.083 | 1.072 | 1.0551 | 1.0382 | 1.0214 | 1.0045 | 0.9876 | 0.97072 | 0.95384 | 0.93696 | 0.92008 | 0.9032 | 1.2924 | 1.2924
52 | 1.2516 | 1.2448 | 1.2379 | 1.2311 | 1.2242 | 1.2174 | 1.2106 | 1.2037 | 1.1969 | 1.19 | 1.1832 | 1.1723 | 1.1614 | 1.1504 | 1.1395 | 1.1286 | 1.1177 | 1.1068 | 1.0958 | 1.0849 | 1.074 | 1.0572 | 1.0405 | 1.0237 | 1.007 | 0.9902 | 0.97344 | 0.95668 | 0.93992 | 0.92316 | 0.9064 | 1.2948 | 1.2948
53 | 1.2524 | 1.2456 | 1.2389 | 1.2321 | 1.2254 | 1.2186 | 1.2118 | 1.2051 | 1.1983 | 1.1916 | 1.1848 | 1.1739 | 1.163 | 1.1522 | 1.1413 | 1.1304 | 1.1195 | 1.1086 | 1.0978 | 1.0869 | 1.076 | 1.0594 | 1.0427 | 1.0261 | 1.0094 | 0.9928 | 0.97616 | 0.95952 | 0.94288 | 0.92624 | 0.9096 | 1.2972 | 1.2972
54 | 1.2532 | 1.2465 | 1.2398 | 1.2332 | 1.2265 | 1.2198 | 1.2131 | 1.2064 | 1.1998 | 1.1931 | 1.1864 | 1.1756 | 1.1647 | 1.1539 | 1.143 | 1.1322 | 1.1214 | 1.1105 | 1.0997 | 1.0888 | 1.078 | 1.0615 | 1.045 | 1.0284 | 1.0119 | 0.9954 | 0.97888 | 0.96236 | 0.94584 | 0.92932 | 0.9128 | 1.2996 | 1.2996
55 | 1.254 | 1.2474 | 1.2408 | 1.2342 | 1.2276 | 1.221 | 1.2144 | 1.2078 | 1.2012 | 1.1946 | 1.188 | 1.1772 | 1.1664 | 1.1556 | 1.1448 | 1.134 | 1.1232 | 1.1124 | 1.1016 | 1.0908 | 1.08 | 1.0636 | 1.0472 | 1.0308 | 1.0144 | 0.998 | 0.9816 | 0.9652 | 0.9488 | 0.9324 | 0.916 | 1.302 | 1.302
56 | 1.2548 | 1.2483 | 1.2418 | 1.2352 | 1.2287 | 1.2222 | 1.2157 | 1.2092 | 1.2026 | 1.1961 | 1.1896 | 1.1788 | 1.1681 | 1.1573 | 1.1466 | 1.1358 | 1.125 | 1.1143 | 1.1035 | 1.0928 | 1.082 | 1.0657 | 1.0494 | 1.0332 | 1.0169 | 1.0006 | 0.98432 | 0.96804 | 0.95176 | 0.93548 | 0.9192 | 1.3044 | 1.3044
57 | 1.2556 | 1.2492 | 1.2427 | 1.2363 | 1.2298 | 1.2234 | 1.217 | 1.2105 | 1.2041 | 1.1976 | 1.1912 | 1.1805 | 1.1698 | 1.159 | 1.1483 | 1.1376 | 1.1269 | 1.1162 | 1.1054 | 1.0947 | 1.084 | 1.0678 | 1.0517 | 1.0355 | 1.0194 | 1.0032 | 0.98704 | 0.97088 | 0.95472 | 0.93856 | 0.9224 | 1.3068 | 1.3068
58 | 1.2564 | 1.25 | 1.2437 | 1.2373 | 1.231 | 1.2246 | 1.2182 | 1.2119 | 1.2055 | 1.1992 | 1.1928 | 1.1821 | 1.1714 | 1.1608 | 1.1501 | 1.1394 | 1.1287 | 1.118 | 1.1074 | 1.0967 | 1.086 | 1.07 | 1.0539 | 1.0379 | 1.0218 | 1.0058 | 0.98976 | 0.97372 | 0.95768 | 0.94164 | 0.9256 | 1.3092 | 1.3092
59 | 1.2572 | 1.2509 | 1.2446 | 1.2384 | 1.2321 | 1.2258 | 1.2195 | 1.2132 | 1.207 | 1.2007 | 1.1944 | 1.1838 | 1.1731 | 1.1625 | 1.1518 | 1.1412 | 1.1306 | 1.1199 | 1.1093 | 1.0986 | 1.088 | 1.0721 | 1.0562 | 1.0402 | 1.0243 | 1.0084 | 0.99248 | 0.97656 | 0.96064 | 0.94472 | 0.9288 | 1.3116 | 1.3116
60 | 1.258 | 1.2518 | 1.2456 | 1.2394 | 1.2332 | 1.227 | 1.2208 | 1.2146 | 1.2084 | 1.2022 | 1.196 | 1.1854 | 1.1748 | 1.1642 | 1.1536 | 1.143 | 1.1324 | 1.1218 | 1.1112 | 1.1006 | 1.09 | 1.0742 | 1.0584 | 1.0426 | 1.0268 | 1.011 | 0.9952 | 0.9794 | 0.9636 | 0.9478 | 0.932 | 1.314 | 1.314
61 | 1.2588 | 1.2527 | 1.2466 | 1.2404 | 1.2343 | 1.2282 | 1.2221 | 1.216 | 1.2098 | 1.2037 | 1.1976 | 1.187 | 1.1765 | 1.1659 | 1.1554 | 1.1448 | 1.1342 | 1.1237 | 1.1131 | 1.1026 | 1.092 | 1.0763 | 1.0606 | 1.045 | 1.0293 | 1.0136 | 0.99792 | 0.98224 | 0.96656 | 0.95088 | 0.9352 | 1.3164 | 1.3164
62 | 1.2596 | 1.2536 | 1.2475 | 1.2415 | 1.2354 | 1.2294 | 1.2234 | 1.2173 | 1.2113 | 1.2052 | 1.1992 | 1.1887 | 1.1782 | 1.1676 | 1.1571 | 1.1466 | 1.1361 | 1.1256 | 1.115 | 1.1045 | 1.094 | 1.0784 | 1.0629 | 1.0473 | 1.0318 | 1.0162 | 1.0006 | 0.98508 | 0.96952 | 0.95396 | 0.9384 | 1.3188 | 1.3188
63 | 1.2604 | 1.2544 | 1.2485 | 1.2425 | 1.2366 | 1.2306 | 1.2246 | 1.2187 | 1.2127 | 1.2068 | 1.2008 | 1.1903 | 1.1798 | 1.1694 | 1.1589 | 1.1484 | 1.1379 | 1.1274 | 1.117 | 1.1065 | 1.096 | 1.0806 | 1.0651 | 1.0497 | 1.0342 | 1.0188 | 1.0034 | 0.98792 | 0.97248 | 0.95704 | 0.9416 | 1.3212 | 1.3212
64 | 1.2612 | 1.2553 | 1.2494 | 1.2436 | 1.2377 | 1.2318 | 1.2259 | 1.22 | 1.2142 | 1.2083 | 1.2024 | 1.192 | 1.1815 | 1.1711 | 1.1606 | 1.1502 | 1.1398 | 1.1293 | 1.1189 | 1.1084 | 1.098 | 1.0827 | 1.0674 | 1.052 | 1.0367 | 1.0214 | 1.0061 | 0.99076 | 0.97544 | 0.96012 | 0.9448 | 1.3236 | 1.3236
65 | 1.262 | 1.2562 | 1.2504 | 1.2446 | 1.2388 | 1.233 | 1.2272 | 1.2214 | 1.2156 | 1.2098 | 1.204 | 1.1936 | 1.1832 | 1.1728 | 1.1624 | 1.152 | 1.1416 | 1.1312 | 1.1208 | 1.1104 | 1.1 | 1.0848 | 1.0696 | 1.0544 | 1.0392 | 1.024 | 1.0088 | 0.9936 | 0.9784 | 0.9632 | 0.948 | 1.326 | 1.326
66 | 1.2628 | 1.2571 | 1.2514 | 1.2456 | 1.2399 | 1.2342 | 1.2285 | 1.2228 | 1.217 | 1.2113 | 1.2056 | 1.1952 | 1.1849 | 1.1745 | 1.1642 | 1.1538 | 1.1434 | 1.1331 | 1.1227 | 1.1124 | 1.102 | 1.0869 | 1.0718 | 1.0568 | 1.0417 | 1.0266 | 1.0115 | 0.99644 | 0.98136 | 0.96628 | 0.9512 | 1.3284 | 1.3284
67 | 1.2636 | 1.258 | 1.2523 | 1.2467 | 1.241 | 1.2354 | 1.2298 | 1.2241 | 1.2185 | 1.2128 | 1.2072 | 1.1969 | 1.1866 | 1.1762 | 1.1659 | 1.1556 | 1.1453 | 1.135 | 1.1246 | 1.1143 | 1.104 | 1.089 | 1.0741 | 1.0591 | 1.0442 | 1.0292 | 1.0142 | 0.99928 | 0.98432 | 0.96936 | 0.9544 | 1.3308 | 1.3308
68 | 1.2644 | 1.2588 | 1.2533 | 1.2477 | 1.2422 | 1.2366 | 1.231 | 1.2255 | 1.2199 | 1.2144 | 1.2088 | 1.1985 | 1.1882 | 1.178 | 1.1677 | 1.1574 | 1.1471 | 1.1368 | 1.1266 | 1.1163 | 1.106 | 1.0912 | 1.0763 | 1.0615 | 1.0466 | 1.0318 | 1.017 | 1.0021 | 0.98728 | 0.97244 | 0.9576 | 1.3332 | 1.3332
69 | 1.2652 | 1.2597 | 1.2542 | 1.2488 | 1.2433 | 1.2378 | 1.2323 | 1.2268 | 1.2214 | 1.2159 | 1.2104 | 1.2002 | 1.1899 | 1.1797 | 1.1694 | 1.1592 | 1.149 | 1.1387 | 1.1285 | 1.1182 | 1.108 | 1.0933 | 1.0786 | 1.0638 | 1.0491 | 1.0344 | 1.0197 | 1.005 | 0.99024 | 0.97552 | 0.9608 | 1.3356 | 1.3356
70 | 1.266 | 1.2606 | 1.2552 | 1.2498 | 1.2444 | 1.239 | 1.2336 | 1.2282 | 1.2228 | 1.2174 | 1.212 | 1.2018 | 1.1916 | 1.1814 | 1.1712 | 1.161 | 1.1508 | 1.1406 | 1.1304 | 1.1202 | 1.11 | 1.0954 | 1.0808 | 1.0662 | 1.0516 | 1.037 | 1.0224 | 1.0078 | 0.9932 | 0.9786 | 0.964 | 1.338 | 1.338
71 | 1.2668 | 1.2615 | 1.2562 | 1.2508 | 1.2455 | 1.2402 | 1.2349 | 1.2296 | 1.2242 | 1.2189 | 1.2136 | 1.2034 | 1.1933 | 1.1831 | 1.173 | 1.1628 | 1.1526 | 1.1425 | 1.1323 | 1.1222 | 1.112 | 1.0975 | 1.083 | 1.0686 | 1.0541 | 1.0396 | 1.0251 | 1.0106 | 0.99616 | 0.98168 | 0.9672 | 1.3404 | 1.3404
72 | 1.2676 | 1.2624 | 1.2571 | 1.2519 | 1.2466 | 1.2414 | 1.2362 | 1.2309 | 1.2257 | 1.2204 | 1.2152 | 1.2051 | 1.195 | 1.1848 | 1.1747 | 1.1646 | 1.1545 | 1.1444 | 1.1342 | 1.1241 | 1.114 | 1.0996 | 1.0853 | 1.0709 | 1.0566 | 1.0422 | 1.0278 | 1.0135 | 0.99912 | 0.98476 | 0.9704 | 1.3428 | 1.3428
73 | 1.2684 | 1.2632 | 1.2581 | 1.2529 | 1.2478 | 1.2426 | 1.2374 | 1.2323 | 1.2271 | 1.222 | 1.2168 | 1.2067 | 1.1966 | 1.1866 | 1.1765 | 1.1664 | 1.1563 | 1.1462 | 1.1362 | 1.1261 | 1.116 | 1.1018 | 1.0875 | 1.0733 | 1.059 | 1.0448 | 1.0306 | 1.0163 | 1.0021 | 0.98784 | 0.9736 | 1.3452 | 1.3452
74 | 1.2692 | 1.2641 | 1.259 | 1.254 | 1.2489 | 1.2438 | 1.2387 | 1.2336 | 1.2286 | 1.2235 | 1.2184 | 1.2084 | 1.1983 | 1.1883 | 1.1782 | 1.1682 | 1.1582 | 1.1481 | 1.1381 | 1.128 | 1.118 | 1.1039 | 1.0898 | 1.0756 | 1.0615 | 1.0474 | 1.0333 | 1.0192 | 1.005 | 0.99092 | 0.9768 | 1.3476 | 1.3476
75 | 1.27 | 1.265 | 1.26 | 1.255 | 1.25 | 1.245 | 1.24 | 1.235 | 1.23 | 1.225 | 1.22 | 1.21 | 1.2 | 1.19 | 1.18 | 1.17 | 1.16 | 1.15 | 1.14 | 1.13 | 1.12 | 1.106 | 1.092 | 1.078 | 1.064 | 1.05 | 1.036 | 1.022 | 1.008 | 0.994 | 0.98 | 1.35 | 1.35
76 | 1.2708 | 1.2658 | 1.2608 | 1.2558 | 1.2508 | 1.2458 | 1.2408 | 1.2358 | 1.2308 | 1.2258 | 1.2208 | 1.2109 | 1.201 | 1.191 | 1.1811 | 1.1712 | 1.1613 | 1.1514 | 1.1414 | 1.1315 | 1.1216 | 1.1076 | 1.0937 | 1.0797 | 1.0658 | 1.0518 | 1.0378 | 1.0239 | 1.0099 | 0.99596 | 0.982 | 1.352 | 1.352
77 | 1.2716 | 1.2666 | 1.2616 | 1.2566 | 1.2516 | 1.2466 | 1.2416 | 1.2366 | 1.2316 | 1.2266 | 1.2216 | 1.2118 | 1.2019 | 1.1921 | 1.1822 | 1.1724 | 1.1626 | 1.1527 | 1.1429 | 1.133 | 1.1232 | 1.1093 | 1.0954 | 1.0814 | 1.0675 | 1.0536 | 1.0397 | 1.0258 | 1.0118 | 0.99792 | 0.984 | 1.354 | 1.354
78 | 1.2724 | 1.2674 | 1.2624 | 1.2574 | 1.2524 | 1.2474 | 1.2424 | 1.2374 | 1.2324 | 1.2274 | 1.2224 | 1.2126 | 1.2029 | 1.1931 | 1.1834 | 1.1736 | 1.1638 | 1.1541 | 1.1443 | 1.1346 | 1.1248 | 1.1109 | 1.097 | 1.0832 | 1.0693 | 1.0554 | 1.0415 | 1.0276 | 1.0138 | 0.99988 | 0.986 | 1.356 | 1.356
79 | 1.2732 | 1.2682 | 1.2632 | 1.2582 | 1.2532 | 1.2482 | 1.2432 | 1.2382 | 1.2332 | 1.2282 | 1.2232 | 1.2135 | 1.2038 | 1.1942 | 1.1845 | 1.1748 | 1.1651 | 1.1554 | 1.1458 | 1.1361 | 1.1264 | 1.1126 | 1.0987 | 1.0849 | 1.071 | 1.0572 | 1.0434 | 1.0295 | 1.0157 | 1.0018 | 0.988 | 1.358 | 1.358
80 | 1.274 | 1.269 | 1.264 | 1.259 | 1.254 | 1.249 | 1.244 | 1.239 | 1.234 | 1.229 | 1.224 | 1.2144 | 1.2048 | 1.1952 | 1.1856 | 1.176 | 1.1664 | 1.1568 | 1.1472 | 1.1376 | 1.128 | 1.1142 | 1.1004 | 1.0866 | 1.0728 | 1.059 | 1.0452 | 1.0314 | 1.0176 | 1.0038 | 0.99 | 1.36 | 1.36
81 | 1.2748 | 1.2698 | 1.2648 | 1.2598 | 1.2548 | 1.2498 | 1.2448 | 1.2398 | 1.2348 | 1.2298 | 1.2248 | 1.2153 | 1.2058 | 1.1962 | 1.1867 | 1.1772 | 1.1677 | 1.1582 | 1.1486 | 1.1391 | 1.1296 | 1.1158 | 1.1021 | 1.0883 | 1.0746 | 1.0608 | 1.047 | 1.0333 | 1.0195 | 1.0058 | 0.992 | 1.362 | 1.362
82 | 1.2756 | 1.2706 | 1.2656 | 1.2606 | 1.2556 | 1.2506 | 1.2456 | 1.2406 | 1.2356 | 1.2306 | 1.2256 | 1.2162 | 1.2067 | 1.1973 | 1.1878 | 1.1784 | 1.169 | 1.1595 | 1.1501 | 1.1406 | 1.1312 | 1.1175 | 1.1038 | 1.09 | 1.0763 | 1.0626 | 1.0489 | 1.0352 | 1.0214 | 1.0077 | 0.994 | 1.364 | 1.364
83 | 1.2764 | 1.2714 | 1.2664 | 1.2614 | 1.2564 | 1.2514 | 1.2464 | 1.2414 | 1.2364 | 1.2314 | 1.2264 | 1.217 | 1.2077 | 1.1983 | 1.189 | 1.1796 | 1.1702 | 1.1609 | 1.1515 | 1.1422 | 1.1328 | 1.1191 | 1.1054 | 1.0918 | 1.0781 | 1.0644 | 1.0507 | 1.037 | 1.0234 | 1.0097 | 0.996 | 1.366 | 1.366
84 | 1.2772 | 1.2722 | 1.2672 | 1.2622 | 1.2572 | 1.2522 | 1.2472 | 1.2422 | 1.2372 | 1.2322 | 1.2272 | 1.2179 | 1.2086 | 1.1994 | 1.1901 | 1.1808 | 1.1715 | 1.1622 | 1.153 | 1.1437 | 1.1344 | 1.1208 | 1.1071 | 1.0935 | 1.0798 | 1.0662 | 1.0526 | 1.0389 | 1.0253 | 1.0116 | 0.998 | 1.368 | 1.368
85 | 1.278 | 1.273 | 1.268 | 1.263 | 1.258 | 1.253 | 1.248 | 1.243 | 1.238 | 1.233 | 1.228 | 1.2188 | 1.2096 | 1.2004 | 1.1912 | 1.182 | 1.1728 | 1.1636 | 1.1544 | 1.1452 | 1.136 | 1.1224 | 1.1088 | 1.0952 | 1.0816 | 1.068 | 1.0544 | 1.0408 | 1.0272 | 1.0136 | 1 | 1.37 | 1.37
86 | 1.2788 | 1.2738 | 1.2688 | 1.2638 | 1.2588 | 1.2538 | 1.2488 | 1.2438 | 1.2388 | 1.2338 | 1.2288 | 1.2197 | 1.2106 | 1.2014 | 1.1923 | 1.1832 | 1.1741 | 1.165 | 1.1558 | 1.1467 | 1.1376 | 1.124 | 1.1105 | 1.0969 | 1.0834 | 1.0698 | 1.0562 | 1.0427 | 1.0291 | 1.0156 | 1.002 | 1.372 | 1.372
87 | 1.2796 | 1.2746 | 1.2696 | 1.2646 | 1.2596 | 1.2546 | 1.2496 | 1.2446 | 1.2396 | 1.2346 | 1.2296 | 1.2206 | 1.2115 | 1.2025 | 1.1934 | 1.1844 | 1.1754 | 1.1663 | 1.1573 | 1.1482 | 1.1392 | 1.1257 | 1.1122 | 1.0986 | 1.0851 | 1.0716 | 1.0581 | 1.0446 | 1.031 | 1.0175 | 1.004 | 1.374 | 1.374
88 | 1.2804 | 1.2754 | 1.2704 | 1.2654 | 1.2604 | 1.2554 | 1.2504 | 1.2454 | 1.2404 | 1.2354 | 1.2304 | 1.2214 | 1.2125 | 1.2035 | 1.1946 | 1.1856 | 1.1766 | 1.1677 | 1.1587 | 1.1498 | 1.1408 | 1.1273 | 1.1138 | 1.1004 | 1.0869 | 1.0734 | 1.0599 | 1.0464 | 1.033 | 1.0195 | 1.006 | 1.376 | 1.376
89 | 1.2812 | 1.2762 | 1.2712 | 1.2662 | 1.2612 | 1.2562 | 1.2512 | 1.2462 | 1.2412 | 1.2362 | 1.2312 | 1.2223 | 1.2134 | 1.2046 | 1.1957 | 1.1868 | 1.1779 | 1.169 | 1.1602 | 1.1513 | 1.1424 | 1.129 | 1.1155 | 1.1021 | 1.0886 | 1.0752 | 1.0618 | 1.0483 | 1.0349 | 1.0214 | 1.008 | 1.378 | 1.378
90 | 1.282 | 1.277 | 1.272 | 1.267 | 1.262 | 1.257 | 1.252 | 1.247 | 1.242 | 1.237 | 1.232 | 1.2232 | 1.2144 | 1.2056 | 1.1968 | 1.188 | 1.1792 | 1.1704 | 1.1616 | 1.1528 | 1.144 | 1.1306 | 1.1172 | 1.1038 | 1.0904 | 1.077 | 1.0636 | 1.0502 | 1.0368 | 1.0234 | 1.01 | 1.38 | 1.38
91 | 1.2828 | 1.2778 | 1.2728 | 1.2678 | 1.2628 | 1.2578 | 1.2528 | 1.2478 | 1.2428 | 1.2378 | 1.2328 | 1.2241 | 1.2154 | 1.2066 | 1.1979 | 1.1892 | 1.1805 | 1.1718 | 1.163 | 1.1543 | 1.1456 | 1.1322 | 1.1189 | 1.1055 | 1.0922 | 1.0788 | 1.0654 | 1.0521 | 1.0387 | 1.0254 | 1.012 | 1.382 | 1.382
92 | 1.2836 | 1.2786 | 1.2736 | 1.2686 | 1.2636 | 1.2586 | 1.2536 | 1.2486 | 1.2436 | 1.2386 | 1.2336 | 1.225 | 1.2163 | 1.2077 | 1.199 | 1.1904 | 1.1818 | 1.1731 | 1.1645 | 1.1558 | 1.1472 | 1.1339 | 1.1206 | 1.1072 | 1.0939 | 1.0806 | 1.0673 | 1.054 | 1.0406 | 1.0273 | 1.014 | 1.384 | 1.384
93 | 1.2844 | 1.2794 | 1.2744 | 1.2694 | 1.2644 | 1.2594 | 1.2544 | 1.2494 | 1.2444 | 1.2394 | 1.2344 | 1.2258 | 1.2173 | 1.2087 | 1.2002 | 1.1916 | 1.183 | 1.1745 | 1.1659 | 1.1574 | 1.1488 | 1.1355 | 1.1222 | 1.109 | 1.0957 | 1.0824 | 1.0691 | 1.0558 | 1.0426 | 1.0293 | 1.016 | 1.386 | 1.386
94 | 1.2852 | 1.2802 | 1.2752 | 1.2702 | 1.2652 | 1.2602 | 1.2552 | 1.2502 | 1.2452 | 1.2402 | 1.2352 | 1.2267 | 1.2182 | 1.2098 | 1.2013 | 1.1928 | 1.1843 | 1.1758 | 1.1674 | 1.1589 | 1.1504 | 1.1372 | 1.1239 | 1.1107 | 1.0974 | 1.0842 | 1.071 | 1.0577 | 1.0445 | 1.0312 | 1.018 | 1.388 | 1.388
95 | 1.286 | 1.281 | 1.276 | 1.271 | 1.266 | 1.261 | 1.256 | 1.251 | 1.246 | 1.241 | 1.236 | 1.2276 | 1.2192 | 1.2108 | 1.2024 | 1.194 | 1.1856 | 1.1772 | 1.1688 | 1.1604 | 1.152 | 1.1388 | 1.1256 | 1.1124 | 1.0992 | 1.086 | 1.0728 | 1.0596 | 1.0464 | 1.0332 | 1.02 | 1.39 | 1.39
96 | 1.2868 | 1.2818 | 1.2768 | 1.2718 | 1.2668 | 1.2618 | 1.2568 | 1.2518 | 1.2468 | 1.2418 | 1.2368 | 1.2285 | 1.2202 | 1.2118 | 1.2035 | 1.1952 | 1.1869 | 1.1786 | 1.1702 | 1.1619 | 1.1536 | 1.1404 | 1.1273 | 1.1141 | 1.101 | 1.0878 | 1.0746 | 1.0615 | 1.0483 | 1.0352 | 1.022 | 1.392 | 1.392
97 | 1.2876 | 1.2826 | 1.2776 | 1.2726 | 1.2676 | 1.2626 | 1.2576 | 1.2526 | 1.2476 | 1.2426 | 1.2376 | 1.2294 | 1.2211 | 1.2129 | 1.2046 | 1.1964 | 1.1882 | 1.1799 | 1.1717 | 1.1634 | 1.1552 | 1.1421 | 1.129 | 1.1158 | 1.1027 | 1.0896 | 1.0765 | 1.0634 | 1.0502 | 1.0371 | 1.024 | 1.394 | 1.394
98 | 1.2884 | 1.2834 | 1.2784 | 1.2734 | 1.2684 | 1.2634 | 1.2584 | 1.2534 | 1.2484 | 1.2434 | 1.2384 | 1.2302 | 1.2221 | 1.2139 | 1.2058 | 1.1976 | 1.1894 | 1.1813 | 1.1731 | 1.165 | 1.1568 | 1.1437 | 1.1306 | 1.1176 | 1.1045 | 1.0914 | 1.0783 | 1.0652 | 1.0522 | 1.0391 | 1.026 | 1.396 | 1.396
99 | 1.2892 | 1.2842 | 1.2792 | 1.2742 | 1.2692 | 1.2642 | 1.2592 | 1.2542 | 1.2492 | 1.2442 | 1.2392 | 1.2311 | 1.223 | 1.215 | 1.2069 | 1.1988 | 1.1907 | 1.1826 | 1.1746 | 1.1665 | 1.1584 | 1.1454 | 1.1323 | 1.1193 | 1.1062 | 1.0932 | 1.0802 | 1.0671 | 1.0541 | 1.041 | 1.028 | 1.398 | 1.398
100 | 1.29 | 1.285 | 1.28 | 1.275 | 1.27 | 1.265 | 1.26 | 1.255 | 1.25 | 1.245 | 1.24 | 1.232 | 1.224 | 1.216 | 1.208 | 1.2 | 1.192 | 1.184 | 1.176 | 1.168 | 1.16 | 1.147 | 1.134 | 1.121 | 1.108 | 1.095 | 1.082 | 1.069 | 1.056 | 1.043 | 1.03 | 1.4 | 1.4
101 | 1.2904 | 1.2854 | 1.2804 | 1.2755 | 1.2705 | 1.2655 | 1.2605 | 1.2555 | 1.2506 | 1.2456 | 1.2406 | 1.2326 | 1.2247 | 1.2167 | 1.2088 | 1.2008 | 1.1928 | 1.1849 | 1.1769 | 1.169 | 1.161 | 1.1481 | 1.1351 | 1.1222 | 1.1092 | 1.0963 | 1.0834 | 1.0704 | 1.0575 | 1.0445 | 1.0316 | 1.4 | 1.4
102 | 1.2908 | 1.2858 | 1.2809 | 1.2759 | 1.271 | 1.266 | 1.261 | 1.2561 | 1.2511 | 1.2462 | 1.2412 | 1.2333 | 1.2254 | 1.2174 | 1.2095 | 1.2016 | 1.1937 | 1.1858 | 1.1778 | 1.1699 | 1.162 | 1.1491 | 1.1362 | 1.1234 | 1.1105 | 1.0976 | 1.0847 | 1.0718 | 1.059 | 1.0461 | 1.0332 | 1.4 | 1.4
103 | 1.2912 | 1.2863 | 1.2813 | 1.2764 | 1.2714 | 1.2665 | 1.2616 | 1.2566 | 1.2517 | 1.2467 | 1.2418 | 1.2339 | 1.226 | 1.2182 | 1.2103 | 1.2024 | 1.1945 | 1.1866 | 1.1788 | 1.1709 | 1.163 | 1.1502 | 1.1374 | 1.1245 | 1.1117 | 1.0989 | 1.0861 | 1.0733 | 1.0604 | 1.0476 | 1.0348 | 1.4 | 1.4
104 | 1.2916 | 1.2867 | 1.2818 | 1.2768 | 1.2719 | 1.267 | 1.2621 | 1.2572 | 1.2522 | 1.2473 | 1.2424 | 1.2346 | 1.2267 | 1.2189 | 1.211 | 1.2032 | 1.1954 | 1.1875 | 1.1797 | 1.1718 | 1.164 | 1.1512 | 1.1385 | 1.1257 | 1.113 | 1.1002 | 1.0874 | 1.0747 | 1.0619 | 1.0492 | 1.0364 | 1.4 | 1.4
105 | 1.292 | 1.2871 | 1.2822 | 1.2773 | 1.2724 | 1.2675 | 1.2626 | 1.2577 | 1.2528 | 1.2479 | 1.243 | 1.2352 | 1.2274 | 1.2196 | 1.2118 | 1.204 | 1.1962 | 1.1884 | 1.1806 | 1.1728 | 1.165 | 1.1523 | 1.1396 | 1.1269 | 1.1142 | 1.1015 | 1.0888 | 1.0761 | 1.0634 | 1.0507 | 1.038 | 1.4 | 1.4
106 | 1.2924 | 1.2875 | 1.2826 | 1.2778 | 1.2729 | 1.268 | 1.2631 | 1.2582 | 1.2534 | 1.2485 | 1.2436 | 1.2358 | 1.2281 | 1.2203 | 1.2126 | 1.2048 | 1.197 | 1.1893 | 1.1815 | 1.1738 | 1.166 | 1.1534 | 1.1407 | 1.1281 | 1.1154 | 1.1028 | 1.0902 | 1.0775 | 1.0649 | 1.0522 | 1.0396 | 1.4 | 1.4
107 | 1.2928 | 1.2879 | 1.2831 | 1.2782 | 1.2734 | 1.2685 | 1.2636 | 1.2588 | 1.2539 | 1.2491 | 1.2442 | 1.2365 | 1.2288 | 1.221 | 1.2133 | 1.2056 | 1.1979 | 1.1902 | 1.1824 | 1.1747 | 1.167 | 1.1544 | 1.1418 | 1.1293 | 1.1167 | 1.1041 | 1.0915 | 1.0789 | 1.0664 | 1.0538 | 1.0412 | 1.4 | 1.4
108 | 1.2932 | 1.2884 | 1.2835 | 1.2787 | 1.2738 | 1.269 | 1.2642 | 1.2593 | 1.2545 | 1.2496 | 1.2448 | 1.2371 | 1.2294 | 1.2218 | 1.2141 | 1.2064 | 1.1987 | 1.191 | 1.1834 | 1.1757 | 1.168 | 1.1555 | 1.143 | 1.1304 | 1.1179 | 1.1054 | 1.0929 | 1.0804 | 1.0678 | 1.0553 | 1.0428 | 1.4 | 1.4
109 | 1.2936 | 1.2888 | 1.284 | 1.2791 | 1.2743 | 1.2695 | 1.2647 | 1.2599 | 1.255 | 1.2502 | 1.2454 | 1.2378 | 1.2301 | 1.2225 | 1.2148 | 1.2072 | 1.1996 | 1.1919 | 1.1843 | 1.1766 | 1.169 | 1.1565 | 1.1441 | 1.1316 | 1.1192 | 1.1067 | 1.0942 | 1.0818 | 1.0693 | 1.0569 | 1.0444 | 1.4 | 1.4
110 | 1.294 | 1.2892 | 1.2844 | 1.2796 | 1.2748 | 1.27 | 1.2652 | 1.2604 | 1.2556 | 1.2508 | 1.246 | 1.2384 | 1.2308 | 1.2232 | 1.2156 | 1.208 | 1.2004 | 1.1928 | 1.1852 | 1.1776 | 1.17 | 1.1576 | 1.1452 | 1.1328 | 1.1204 | 1.108 | 1.0956 | 1.0832 | 1.0708 | 1.0584 | 1.046 | 1.4 | 1.4
111 | 1.2944 | 1.2896 | 1.2848 | 1.2801 | 1.2753 | 1.2705 | 1.2657 | 1.2609 | 1.2562 | 1.2514 | 1.2466 | 1.239 | 1.2315 | 1.2239 | 1.2164 | 1.2088 | 1.2012 | 1.1937 | 1.1861 | 1.1786 | 1.171 | 1.1587 | 1.1463 | 1.134 | 1.1216 | 1.1093 | 1.097 | 1.0846 | 1.0723 | 1.0599 | 1.0476 | 1.4 | 1.4
112 | 1.2948 | 1.29 | 1.2853 | 1.2805 | 1.2758 | 1.271 | 1.2662 | 1.2615 | 1.2567 | 1.252 | 1.2472 | 1.2397 | 1.2322 | 1.2246 | 1.2171 | 1.2096 | 1.2021 | 1.1946 | 1.187 | 1.1795 | 1.172 | 1.1597 | 1.1474 | 1.1352 | 1.1229 | 1.1106 | 1.0983 | 1.086 | 1.0738 | 1.0615 | 1.0492 | 1.4 | 1.4
113 | 1.2952 | 1.2905 | 1.2857 | 1.281 | 1.2762 | 1.2715 | 1.2668 | 1.262 | 1.2573 | 1.2525 | 1.2478 | 1.2403 | 1.2328 | 1.2254 | 1.2179 | 1.2104 | 1.2029 | 1.1954 | 1.188 | 1.1805 | 1.173 | 1.1608 | 1.1486 | 1.1363 | 1.1241 | 1.1119 | 1.0997 | 1.0875 | 1.0752 | 1.063 | 1.0508 | 1.4 | 1.4
114 | 1.2956 | 1.2909 | 1.2862 | 1.2814 | 1.2767 | 1.272 | 1.2673 | 1.2626 | 1.2578 | 1.2531 | 1.2484 | 1.241 | 1.2335 | 1.2261 | 1.2186 | 1.2112 | 1.2038 | 1.1963 | 1.1889 | 1.1814 | 1.174 | 1.1618 | 1.1497 | 1.1375 | 1.1254 | 1.1132 | 1.101 | 1.0889 | 1.0767 | 1.0646 | 1.0524 | 1.4 | 1.4
115 | 1.296 | 1.2913 | 1.2866 | 1.2819 | 1.2772 | 1.2725 | 1.2678 | 1.2631 | 1.2584 | 1.2537 | 1.249 | 1.2416 | 1.2342 | 1.2268 | 1.2194 | 1.212 | 1.2046 | 1.1972 | 1.1898 | 1.1824 | 1.175 | 1.1629 | 1.1508 | 1.1387 | 1.1266 | 1.1145 | 1.1024 | 1.0903 | 1.0782 | 1.0661 | 1.054 | 1.4 | 1.4
116 | 1.2964 | 1.2917 | 1.287 | 1.2824 | 1.2777 | 1.273 | 1.2683 | 1.2636 | 1.259 | 1.2543 | 1.2496 | 1.2422 | 1.2349 | 1.2275 | 1.2202 | 1.2128 | 1.2054 | 1.1981 | 1.1907 | 1.1834 | 1.176 | 1.164 | 1.1519 | 1.1399 | 1.1278 | 1.1158 | 1.1038 | 1.0917 | 1.0797 | 1.0676 | 1.0556 | 1.4 | 1.4
117 | 1.2968 | 1.2921 | 1.2875 | 1.2828 | 1.2782 | 1.2735 | 1.2688 | 1.2642 | 1.2595 | 1.2549 | 1.2502 | 1.2429 | 1.2356 | 1.2282 | 1.2209 | 1.2136 | 1.2063 | 1.199 | 1.1916 | 1.1843 | 1.177 | 1.165 | 1.153 | 1.1411 | 1.1291 | 1.1171 | 1.1051 | 1.0931 | 1.0812 | 1.0692 | 1.0572 | 1.4 | 1.4
118 | 1.2972 | 1.2926 | 1.2879 | 1.2833 | 1.2786 | 1.274 | 1.2694 | 1.2647 | 1.2601 | 1.2554 | 1.2508 | 1.2435 | 1.2362 | 1.229 | 1.2217 | 1.2144 | 1.2071 | 1.1998 | 1.1926 | 1.1853 | 1.178 | 1.1661 | 1.1542 | 1.1422 | 1.1303 | 1.1184 | 1.1065 | 1.0946 | 1.0826 | 1.0707 | 1.0588 | 1.4 | 1.4
119 | 1.2976 | 1.293 | 1.2884 | 1.2837 | 1.2791 | 1.2745 | 1.2699 | 1.2653 | 1.2606 | 1.256 | 1.2514 | 1.2442 | 1.2369 | 1.2297 | 1.2224 | 1.2152 | 1.208 | 1.2007 | 1.1935 | 1.1862 | 1.179 | 1.1671 | 1.1553 | 1.1434 | 1.1316 | 1.1197 | 1.1078 | 1.096 | 1.0841 | 1.0723 | 1.0604 | 1.4 | 1.4
120 | 1.298 | 1.2934 | 1.2888 | 1.2842 | 1.2796 | 1.275 | 1.2704 | 1.2658 | 1.2612 | 1.2566 | 1.252 | 1.2448 | 1.2376 | 1.2304 | 1.2232 | 1.216 | 1.2088 | 1.2016 | 1.1944 | 1.1872 | 1.18 | 1.1682 | 1.1564 | 1.1446 | 1.1328 | 1.121 | 1.1092 | 1.0974 | 1.0856 | 1.0738 | 1.062 | 1.4 | 1.4
121 | 1.2984 | 1.2938 | 1.2892 | 1.2847 | 1.2801 | 1.2755 | 1.2709 | 1.2663 | 1.2618 | 1.2572 | 1.2526 | 1.2454 | 1.2383 | 1.2311 | 1.224 | 1.2168 | 1.2096 | 1.2025 | 1.1953 | 1.1882 | 1.181 | 1.1693 | 1.1575 | 1.1458 | 1.134 | 1.1223 | 1.1106 | 1.0988 | 1.0871 | 1.0753 | 1.0636 | 1.4 | 1.4
122 | 1.2988 | 1.2942 | 1.2897 | 1.2851 | 1.2806 | 1.276 | 1.2714 | 1.2669 | 1.2623 | 1.2578 | 1.2532 | 1.2461 | 1.239 | 1.2318 | 1.2247 | 1.2176 | 1.2105 | 1.2034 | 1.1962 | 1.1891 | 1.182 | 1.1703 | 1.1586 | 1.147 | 1.1353 | 1.1236 | 1.1119 | 1.1002 | 1.0886 | 1.0769 | 1.0652 | 1.4 | 1.4
123 | 1.2992 | 1.2947 | 1.2901 | 1.2856 | 1.281 | 1.2765 | 1.272 | 1.2674 | 1.2629 | 1.2583 | 1.2538 | 1.2467 | 1.2396 | 1.2326 | 1.2255 | 1.2184 | 1.2113 | 1.2042 | 1.1972 | 1.1901 | 1.183 | 1.1714 | 1.1598 | 1.1481 | 1.1365 | 1.1249 | 1.1133 | 1.1017 | 1.09 | 1.0784 | 1.0668 | 1.4 | 1.4
124 | 1.2996 | 1.2951 | 1.2906 | 1.286 | 1.2815 | 1.277 | 1.2725 | 1.268 | 1.2634 | 1.2589 | 1.2544 | 1.2474 | 1.2403 | 1.2333 | 1.2262 | 1.2192 | 1.2122 | 1.2051 | 1.1981 | 1.191 | 1.184 | 1.1724 | 1.1609 | 1.1493 | 1.1378 | 1.1262 | 1.1146 | 1.1031 | 1.0915 | 1.08 | 1.0684 | 1.4 | 1.4
125 | 1.3 | 1.2955 | 1.291 | 1.2865 | 1.282 | 1.2775 | 1.273 | 1.2685 | 1.264 | 1.2595 | 1.255 | 1.248 | 1.241 | 1.234 | 1.227 | 1.22 | 1.213 | 1.206 | 1.199 | 1.192 | 1.185 | 1.1735 | 1.162 | 1.1505 | 1.139 | 1.1275 | 1.116 | 1.1045 | 1.093 | 1.0815 | 1.07 | 1.4 | 1.4
126 | 1.3004 | 1.2959 | 1.2914 | 1.287 | 1.2825 | 1.278 | 1.2735 | 1.269 | 1.2646 | 1.2601 | 1.2556 | 1.2486 | 1.2417 | 1.2347 | 1.2278 | 1.2208 | 1.2138 | 1.2069 | 1.1999 | 1.193 | 1.186 | 1.1746 | 1.1631 | 1.1517 | 1.1402 | 1.1288 | 1.1174 | 1.1059 | 1.0945 | 1.083 | 1.0716 | 1.4 | 1.4
127 | 1.3008 | 1.2963 | 1.2919 | 1.2874 | 1.283 | 1.2785 | 1.274 | 1.2696 | 1.2651 | 1.2607 | 1.2562 | 1.2493 | 1.2424 | 1.2354 | 1.2285 | 1.2216 | 1.2147 | 1.2078 | 1.2008 | 1.1939 | 1.187 | 1.1756 | 1.1642 | 1.1529 | 1.1415 | 1.1301 | 1.1187 | 1.1073 | 1.096 | 1.0846 | 1.0732 | 1.4 | 1.4
128 | 1.3012 | 1.2968 | 1.2923 | 1.2879 | 1.2834 | 1.279 | 1.2746 | 1.2701 | 1.2657 | 1.2612 | 1.2568 | 1.2499 | 1.243 | 1.2362 | 1.2293 | 1.2224 | 1.2155 | 1.2086 | 1.2018 | 1.1949 | 1.188 | 1.1767 | 1.1654 | 1.154 | 1.1427 | 1.1314 | 1.1201 | 1.1088 | 1.0974 | 1.0861 | 1.0748 | 1.4 | 1.4
129 | 1.3016 | 1.2972 | 1.2928 | 1.2883 | 1.2839 | 1.2795 | 1.2751 | 1.2707 | 1.2662 | 1.2618 | 1.2574 | 1.2506 | 1.2437 | 1.2369 | 1.23 | 1.2232 | 1.2164 | 1.2095 | 1.2027 | 1.1958 | 1.189 | 1.1777 | 1.1665 | 1.1552 | 1.144 | 1.1327 | 1.1214 | 1.1102 | 1.0989 | 1.0877 | 1.0764 | 1.4 | 1.4
130 | 1.302 | 1.2976 | 1.2932 | 1.2888 | 1.2844 | 1.28 | 1.2756 | 1.2712 | 1.2668 | 1.2624 | 1.258 | 1.2512 | 1.2444 | 1.2376 | 1.2308 | 1.224 | 1.2172 | 1.2104 | 1.2036 | 1.1968 | 1.19 | 1.1788 | 1.1676 | 1.1564 | 1.1452 | 1.134 | 1.1228 | 1.1116 | 1.1004 | 1.0892 | 1.078 | 1.4 | 1.4
131 | 1.3024 | 1.298 | 1.2936 | 1.2893 | 1.2849 | 1.2805 | 1.2761 | 1.2717 | 1.2674 | 1.263 | 1.2586 | 1.2518 | 1.2451 | 1.2383 | 1.2316 | 1.2248 | 1.218 | 1.2113 | 1.2045 | 1.1978 | 1.191 | 1.1799 | 1.1687 | 1.1576 | 1.1464 | 1.1353 | 1.1242 | 1.113 | 1.1019 | 1.0907 | 1.0796 | 1.4 | 1.4
132 | 1.3028 | 1.2984 | 1.2941 | 1.2897 | 1.2854 | 1.281 | 1.2766 | 1.2723 | 1.2679 | 1.2636 | 1.2592 | 1.2525 | 1.2458 | 1.239 | 1.2323 | 1.2256 | 1.2189 | 1.2122 | 1.2054 | 1.1987 | 1.192 | 1.1809 | 1.1698 | 1.1588 | 1.1477 | 1.1366 | 1.1255 | 1.1144 | 1.1034 | 1.0923 | 1.0812 | 1.4 | 1.4
133 | 1.3032 | 1.2989 | 1.2945 | 1.2902 | 1.2858 | 1.2815 | 1.2772 | 1.2728 | 1.2685 | 1.2641 | 1.2598 | 1.2531 | 1.2464 | 1.2398 | 1.2331 | 1.2264 | 1.2197 | 1.213 | 1.2064 | 1.1997 | 1.193 | 1.182 | 1.171 | 1.1599 | 1.1489 | 1.1379 | 1.1269 | 1.1159 | 1.1048 | 1.0938 | 1.0828 | 1.4 | 1.4
134 | 1.3036 | 1.2993 | 1.295 | 1.2906 | 1.2863 | 1.282 | 1.2777 | 1.2734 | 1.269 | 1.2647 | 1.2604 | 1.2538 | 1.2471 | 1.2405 | 1.2338 | 1.2272 | 1.2206 | 1.2139 | 1.2073 | 1.2006 | 1.194 | 1.183 | 1.1721 | 1.1611 | 1.1502 | 1.1392 | 1.1282 | 1.1173 | 1.1063 | 1.0954 | 1.0844 | 1.4 | 1.4
135 | 1.304 | 1.2997 | 1.2954 | 1.2911 | 1.2868 | 1.2825 | 1.2782 | 1.2739 | 1.2696 | 1.2653 | 1.261 | 1.2544 | 1.2478 | 1.2412 | 1.2346 | 1.228 | 1.2214 | 1.2148 | 1.2082 | 1.2016 | 1.195 | 1.1841 | 1.1732 | 1.1623 | 1.1514 | 1.1405 | 1.1296 | 1.1187 | 1.1078 | 1.0969 | 1.086 | 1.4 | 1.4
136 | 1.3044 | 1.3001 | 1.2958 | 1.2916 | 1.2873 | 1.283 | 1.2787 | 1.2744 | 1.2702 | 1.2659 | 1.2616 | 1.255 | 1.2485 | 1.2419 | 1.2354 | 1.2288 | 1.2222 | 1.2157 | 1.2091 | 1.2026 | 1.196 | 1.1852 | 1.1743 | 1.1635 | 1.1526 | 1.1418 | 1.131 | 1.1201 | 1.1093 | 1.0984 | 1.0876 | 1.4 | 1.4
137 | 1.3048 | 1.3005 | 1.2963 | 1.292 | 1.2878 | 1.2835 | 1.2792 | 1.275 | 1.2707 | 1.2665 | 1.2622 | 1.2557 | 1.2492 | 1.2426 | 1.2361 | 1.2296 | 1.2231 | 1.2166 | 1.21 | 1.2035 | 1.197 | 1.1862 | 1.1754 | 1.1647 | 1.1539 | 1.1431 | 1.1323 | 1.1215 | 1.1108 | 1.1 | 1.0892 | 1.4 | 1.4
138 | 1.3052 | 1.301 | 1.2967 | 1.2925 | 1.2882 | 1.284 | 1.2798 | 1.2755 | 1.2713 | 1.267 | 1.2628 | 1.2563 | 1.2498 | 1.2434 | 1.2369 | 1.2304 | 1.2239 | 1.2174 | 1.211 | 1.2045 | 1.198 | 1.1873 | 1.1766 | 1.1658 | 1.1551 | 1.1444 | 1.1337 | 1.123 | 1.1122 | 1.1015 | 1.0908 | 1.4 | 1.4
139 | 1.3056 | 1.3014 | 1.2972 | 1.2929 | 1.2887 | 1.2845 | 1.2803 | 1.2761 | 1.2718 | 1.2676 | 1.2634 | 1.257 | 1.2505 | 1.2441 | 1.2376 | 1.2312 | 1.2248 | 1.2183 | 1.2119 | 1.2054 | 1.199 | 1.1883 | 1.1777 | 1.167 | 1.1564 | 1.1457 | 1.135 | 1.1244 | 1.1137 | 1.1031 | 1.0924 | 1.4 | 1.4
140 | 1.306 | 1.3018 | 1.2976 | 1.2934 | 1.2892 | 1.285 | 1.2808 | 1.2766 | 1.2724 | 1.2682 | 1.264 | 1.2576 | 1.2512 | 1.2448 | 1.2384 | 1.232 | 1.2256 | 1.2192 | 1.2128 | 1.2064 | 1.2 | 1.1894 | 1.1788 | 1.1682 | 1.1576 | 1.147 | 1.1364 | 1.1258 | 1.1152 | 1.1046 | 1.094 | 1.4 | 1.4
141 | 1.3064 | 1.3022 | 1.298 | 1.2939 | 1.2897 | 1.2855 | 1.2813 | 1.2771 | 1.273 | 1.2688 | 1.2646 | 1.2582 | 1.2519 | 1.2455 | 1.2392 | 1.2328 | 1.2264 | 1.2201 | 1.2137 | 1.2074 | 1.201 | 1.1905 | 1.1799 | 1.1694 | 1.1588 | 1.1483 | 1.1378 | 1.1272 | 1.1167 | 1.1061 | 1.0956 | 1.4 | 1.4
142 | 1.3068 | 1.3026 | 1.2985 | 1.2943 | 1.2902 | 1.286 | 1.2818 | 1.2777 | 1.2735 | 1.2694 | 1.2652 | 1.2589 | 1.2526 | 1.2462 | 1.2399 | 1.2336 | 1.2273 | 1.221 | 1.2146 | 1.2083 | 1.202 | 1.1915 | 1.181 | 1.1706 | 1.1601 | 1.1496 | 1.1391 | 1.1286 | 1.1182 | 1.1077 | 1.0972 | 1.4 | 1.4
143 | 1.3072 | 1.3031 | 1.2989 | 1.2948 | 1.2906 | 1.2865 | 1.2824 | 1.2782 | 1.2741 | 1.2699 | 1.2658 | 1.2595 | 1.2532 | 1.247 | 1.2407 | 1.2344 | 1.2281 | 1.2218 | 1.2156 | 1.2093 | 1.203 | 1.1926 | 1.1822 | 1.1717 | 1.1613 | 1.1509 | 1.1405 | 1.1301 | 1.1196 | 1.1092 | 1.0988 | 1.4 | 1.4
144 | 1.3076 | 1.3035 | 1.2994 | 1.2952 | 1.2911 | 1.287 | 1.2829 | 1.2788 | 1.2746 | 1.2705 | 1.2664 | 1.2602 | 1.2539 | 1.2477 | 1.2414 | 1.2352 | 1.229 | 1.2227 | 1.2165 | 1.2102 | 1.204 | 1.1936 | 1.1833 | 1.1729 | 1.1626 | 1.1522 | 1.1418 | 1.1315 | 1.1211 | 1.1108 | 1.1004 | 1.4 | 1.4
145 | 1.308 | 1.3039 | 1.2998 | 1.2957 | 1.2916 | 1.2875 | 1.2834 | 1.2793 | 1.2752 | 1.2711 | 1.267 | 1.2608 | 1.2546 | 1.2484 | 1.2422 | 1.236 | 1.2298 | 1.2236 | 1.2174 | 1.2112 | 1.205 | 1.1947 | 1.1844 | 1.1741 | 1.1638 | 1.1535 | 1.1432 | 1.1329 | 1.1226 | 1.1123 | 1.102 | 1.4 | 1.4
146 | 1.3084 | 1.3043 | 1.3002 | 1.2962 | 1.2921 | 1.288 | 1.2839 | 1.2798 | 1.2758 | 1.2717 | 1.2676 | 1.2614 | 1.2553 | 1.2491 | 1.243 | 1.2368 | 1.2306 | 1.2245 | 1.2183 | 1.2122 | 1.206 | 1.1958 | 1.1855 | 1.1753 | 1.165 | 1.1548 | 1.1446 | 1.1343 | 1.1241 | 1.1138 | 1.1036 | 1.4 | 1.4
147 | 1.3088 | 1.3047 | 1.3007 | 1.2966 | 1.2926 | 1.2885 | 1.2844 | 1.2804 | 1.2763 | 1.2723 | 1.2682 | 1.2621 | 1.256 | 1.2498 | 1.2437 | 1.2376 | 1.2315 | 1.2254 | 1.2192 | 1.2131 | 1.207 | 1.1968 | 1.1866 | 1.1765 | 1.1663 | 1.1561 | 1.1459 | 1.1357 | 1.1256 | 1.1154 | 1.1052 | 1.4 | 1.4
148 | 1.3092 | 1.3052 | 1.3011 | 1.2971 | 1.293 | 1.289 | 1.285 | 1.2809 | 1.2769 | 1.2728 | 1.2688 | 1.2627 | 1.2566 | 1.2506 | 1.2445 | 1.2384 | 1.2323 | 1.2262 | 1.2202 | 1.2141 | 1.208 | 1.1979 | 1.1878 | 1.1776 | 1.1675 | 1.1574 | 1.1473 | 1.1372 | 1.127 | 1.1169 | 1.1068 | 1.4 | 1.4
149 | 1.3096 | 1.3056 | 1.3016 | 1.2975 | 1.2935 | 1.2895 | 1.2855 | 1.2815 | 1.2774 | 1.2734 | 1.2694 | 1.2634 | 1.2573 | 1.2513 | 1.2452 | 1.2392 | 1.2332 | 1.2271 | 1.2211 | 1.215 | 1.209 | 1.1989 | 1.1889 | 1.1788 | 1.1688 | 1.1587 | 1.1486 | 1.1386 | 1.1285 | 1.1185 | 1.1084 | 1.4 | 1.4
150 | 1.31 | 1.306 | 1.302 | 1.298 | 1.294 | 1.29 | 1.286 | 1.282 | 1.278 | 1.274 | 1.27 | 1.264 | 1.258 | 1.252 | 1.246 | 1.24 | 1.234 | 1.228 | 1.222 | 1.216 | 1.21 | 1.2 | 1.19 | 1.18 | 1.17 | 1.16 | 1.15 | 1.14 | 1.13 | 1.12 | 1.11 | 1.4 | 1.4
151 | 1.2838 | 1.2799 | 1.276 | 1.272 | 1.2681 | 1.2642 | 1.2603 | 1.2564 | 1.2524 | 1.2485 | 1.2446 | 1.2387 | 1.2328 | 1.227 | 1.2211 | 1.2152 | 1.2093 | 1.2034 | 1.1976 | 1.1917 | 1.1858 | 1.176 | 1.1662 | 1.1564 | 1.1466 | 1.1368 | 1.127 | 1.1172 | 1.1074 | 1.0976 | 1.0878 | 1.372 | 1.372
152 | 1.2576 | 1.2538 | 1.2499 | 1.2461 | 1.2422 | 1.2384 | 1.2346 | 1.2307 | 1.2269 | 1.223 | 1.2192 | 1.2134 | 1.2077 | 1.2019 | 1.1962 | 1.1904 | 1.1846 | 1.1789 | 1.1731 | 1.1674 | 1.1616 | 1.152 | 1.1424 | 1.1328 | 1.1232 | 1.1136 | 1.104 | 1.0944 | 1.0848 | 1.0752 | 1.0656 | 1.344 | 1.344
153 | 1.2314 | 1.2276 | 1.2239 | 1.2201 | 1.2164 | 1.2126 | 1.2088 | 1.2051 | 1.2013 | 1.1976 | 1.1938 | 1.1882 | 1.1825 | 1.1769 | 1.1712 | 1.1656 | 1.16 | 1.1543 | 1.1487 | 1.143 | 1.1374 | 1.128 | 1.1186 | 1.1092 | 1.0998 | 1.0904 | 1.081 | 1.0716 | 1.0622 | 1.0528 | 1.0434 | 1.316 | 1.316
154 | 1.2052 | 1.2015 | 1.1978 | 1.1942 | 1.1905 | 1.1868 | 1.1831 | 1.1794 | 1.1758 | 1.1721 | 1.1684 | 1.1629 | 1.1574 | 1.1518 | 1.1463 | 1.1408 | 1.1353 | 1.1298 | 1.1242 | 1.1187 | 1.1132 | 1.104 | 1.0948 | 1.0856 | 1.0764 | 1.0672 | 1.058 | 1.0488 | 1.0396 | 1.0304 | 1.0212 | 1.288 | 1.288
155 | 1.179 | 1.1754 | 1.1718 | 1.1682 | 1.1646 | 1.161 | 1.1574 | 1.1538 | 1.1502 | 1.1466 | 1.143 | 1.1376 | 1.1322 | 1.1268 | 1.1214 | 1.116 | 1.1106 | 1.1052 | 1.0998 | 1.0944 | 1.089 | 1.08 | 1.071 | 1.062 | 1.053 | 1.044 | 1.035 | 1.026 | 1.017 | 1.008 | 0.999 | 1.26 | 1.26
156 | 1.1528 | 1.1493 | 1.1458 | 1.1422 | 1.1387 | 1.1352 | 1.1317 | 1.1282 | 1.1246 | 1.1211 | 1.1176 | 1.1123 | 1.107 | 1.1018 | 1.0965 | 1.0912 | 1.0859 | 1.0806 | 1.0754 | 1.0701 | 1.0648 | 1.056 | 1.0472 | 1.0384 | 1.0296 | 1.0208 | 1.012 | 1.0032 | 0.9944 | 0.9856 | 0.9768 | 1.232 | 1.232
157 | 1.1266 | 1.1232 | 1.1197 | 1.1163 | 1.1128 | 1.1094 | 1.106 | 1.1025 | 1.0991 | 1.0956 | 1.0922 | 1.087 | 1.0819 | 1.0767 | 1.0716 | 1.0664 | 1.0612 | 1.0561 | 1.0509 | 1.0458 | 1.0406 | 1.032 | 1.0234 | 1.0148 | 1.0062 | 0.9976 | 0.989 | 0.9804 | 0.9718 | 0.9632 | 0.9546 | 1.204 | 1.204
158 | 1.1004 | 1.097 | 1.0937 | 1.0903 | 1.087 | 1.0836 | 1.0802 | 1.0769 | 1.0735 | 1.0702 | 1.0668 | 1.0618 | 1.0567 | 1.0517 | 1.0466 | 1.0416 | 1.0366 | 1.0315 | 1.0265 | 1.0214 | 1.0164 | 1.008 | 0.9996 | 0.9912 | 0.9828 | 0.9744 | 0.966 | 0.9576 | 0.9492 | 0.9408 | 0.9324 | 1.176 | 1.176
159 | 1.0742 | 1.0709 | 1.0676 | 1.0644 | 1.0611 | 1.0578 | 1.0545 | 1.0512 | 1.048 | 1.0447 | 1.0414 | 1.0365 | 1.0316 | 1.0266 | 1.0217 | 1.0168 | 1.0119 | 1.007 | 1.002 | 0.99712 | 0.9922 | 0.984 | 0.9758 | 0.9676 | 0.9594 | 0.9512 | 0.943 | 0.9348 | 0.9266 | 0.9184 | 0.9102 | 1.148 | 1.148
160 | 1.048 | 1.0448 | 1.0416 | 1.0384 | 1.0352 | 1.032 | 1.0288 | 1.0256 | 1.0224 | 1.0192 | 1.016 | 1.0112 | 1.0064 | 1.0016 | 0.9968 | 0.992 | 0.9872 | 0.9824 | 0.9776 | 0.9728 | 0.968 | 0.96 | 0.952 | 0.944 | 0.936 | 0.928 | 0.92 | 0.912 | 0.904 | 0.896 | 0.888 | 1.12 | 1.12
161 | 1.0218 | 1.0187 | 1.0156 | 1.0124 | 1.0093 | 1.0062 | 1.0031 | 0.99996 | 0.99684 | 0.99372 | 0.9906 | 0.98592 | 0.98124 | 0.97656 | 0.97188 | 0.9672 | 0.96252 | 0.95784 | 0.95316 | 0.94848 | 0.9438 | 0.936 | 0.9282 | 0.9204 | 0.9126 | 0.9048 | 0.897 | 0.8892 | 0.8814 | 0.8736 | 0.8658 | 1.092 | 1.092
162 | 0.9956 | 0.99256 | 0.98952 | 0.98648 | 0.98344 | 0.9804 | 0.97736 | 0.97432 | 0.97128 | 0.96824 | 0.9652 | 0.96064 | 0.95608 | 0.95152 | 0.94696 | 0.9424 | 0.93784 | 0.93328 | 0.92872 | 0.92416 | 0.9196 | 0.912 | 0.9044 | 0.8968 | 0.8892 | 0.8816 | 0.874 | 0.8664 | 0.8588 | 0.8512 | 0.8436 | 1.064 | 1.064
163 | 0.9694 | 0.96644 | 0.96348 | 0.96052 | 0.95756 | 0.9546 | 0.95164 | 0.94868 | 0.94572 | 0.94276 | 0.9398 | 0.93536 | 0.93092 | 0.92648 | 0.92204 | 0.9176 | 0.91316 | 0.90872 | 0.90428 | 0.89984 | 0.8954 | 0.888 | 0.8806 | 0.8732 | 0.8658 | 0.8584 | 0.851 | 0.8436 | 0.8362 | 0.8288 | 0.8214 | 1.036 | 1.036
164 | 0.9432 | 0.94032 | 0.93744 | 0.93456 | 0.93168 | 0.9288 | 0.92592 | 0.92304 | 0.92016 | 0.91728 | 0.9144 | 0.91008 | 0.90576 | 0.90144 | 0.89712 | 0.8928 | 0.88848 | 0.88416 | 0.87984 | 0.87552 | 0.8712 | 0.864 | 0.8568 | 0.8496 | 0.8424 | 0.8352 | 0.828 | 0.8208 | 0.8136 | 0.8064 | 0.7992 | 1.008 | 1.008
165 | 0.917 | 0.9142 | 0.9114 | 0.9086 | 0.9058 | 0.903 | 0.9002 | 0.8974 | 0.8946 | 0.8918 | 0.889 | 0.8848 | 0.8806 | 0.8764 | 0.8722 | 0.868 | 0.8638 | 0.8596 | 0.8554 | 0.8512 | 0.847 | 0.84 | 0.833 | 0.826 | 0.819 | 0.812 | 0.805 | 0.798 | 0.791 | 0.784 | 0.777 | 0.98 | 0.98
166 | 0.8908 | 0.88808 | 0.88536 | 0.88264 | 0.87992 | 0.8772 | 0.87448 | 0.87176 | 0.86904 | 0.86632 | 0.8636 | 0.85952 | 0.85544 | 0.85136 | 0.84728 | 0.8432 | 0.83912 | 0.83504 | 0.83096 | 0.82688 | 0.8228 | 0.816 | 0.8092 | 0.8024 | 0.7956 | 0.7888 | 0.782 | 0.7752 | 0.7684 | 0.7616 | 0.7548 | 0.952 | 0.952
167 | 0.8646 | 0.86196 | 0.85932 | 0.85668 | 0.85404 | 0.8514 | 0.84876 | 0.84612 | 0.84348 | 0.84084 | 0.8382 | 0.83424 | 0.83028 | 0.82632 | 0.82236 | 0.8184 | 0.81444 | 0.81048 | 0.80652 | 0.80256 | 0.7986 | 0.792 | 0.7854 | 0.7788 | 0.7722 | 0.7656 | 0.759 | 0.7524 | 0.7458 | 0.7392 | 0.7326 | 0.924 | 0.924
168 | 0.8384 | 0.83584 | 0.83328 | 0.83072 | 0.82816 | 0.8256 | 0.82304 | 0.82048 | 0.81792 | 0.81536 | 0.8128 | 0.80896 | 0.80512 | 0.80128 | 0.79744 | 0.7936 | 0.78976 | 0.78592 | 0.78208 | 0.77824 | 0.7744 | 0.768 | 0.7616 | 0.7552 | 0.7488 | 0.7424 | 0.736 | 0.7296 | 0.7232 | 0.7168 | 0.7104 | 0.896 | 0.896
169 | 0.8122 | 0.80972 | 0.80724 | 0.80476 | 0.80228 | 0.7998 | 0.79732 | 0.79484 | 0.79236 | 0.78988 | 0.7874 | 0.78368 | 0.77996 | 0.77624 | 0.77252 | 0.7688 | 0.76508 | 0.76136 | 0.75764 | 0.75392 | 0.7502 | 0.744 | 0.7378 | 0.7316 | 0.7254 | 0.7192 | 0.713 | 0.7068 | 0.7006 | 0.6944 | 0.6882 | 0.868 | 0.868
170 | 0.786 | 0.7836 | 0.7812 | 0.7788 | 0.7764 | 0.774 | 0.7716 | 0.7692 | 0.7668 | 0.7644 | 0.762 | 0.7584 | 0.7548 | 0.7512 | 0.7476 | 0.744 | 0.7404 | 0.7368 | 0.7332 | 0.7296 | 0.726 | 0.72 | 0.714 | 0.708 | 0.702 | 0.696 | 0.69 | 0.684 | 0.678 | 0.672 | 0.666 | 0.84 | 0.84
171 | 0.7598 | 0.75748 | 0.75516 | 0.75284 | 0.75052 | 0.7482 | 0.74588 | 0.74356 | 0.74124 | 0.73892 | 0.7366 | 0.73312 | 0.72964 | 0.72616 | 0.72268 | 0.7192 | 0.71572 | 0.71224 | 0.70876 | 0.70528 | 0.7018 | 0.696 | 0.6902 | 0.6844 | 0.6786 | 0.6728 | 0.667 | 0.6612 | 0.6554 | 0.6496 | 0.6438 | 0.812 | 0.812
172 | 0.7336 | 0.73136 | 0.72912 | 0.72688 | 0.72464 | 0.7224 | 0.72016 | 0.71792 | 0.71568 | 0.71344 | 0.7112 | 0.70784 | 0.70448 | 0.70112 | 0.69776 | 0.6944 | 0.69104 | 0.68768 | 0.68432 | 0.68096 | 0.6776 | 0.672 | 0.6664 | 0.6608 | 0.6552 | 0.6496 | 0.644 | 0.6384 | 0.6328 | 0.6272 | 0.6216 | 0.784 | 0.784
173 | 0.7074 | 0.70524 | 0.70308 | 0.70092 | 0.69876 | 0.6966 | 0.69444 | 0.69228 | 0.69012 | 0.68796 | 0.6858 | 0.68256 | 0.67932 | 0.67608 | 0.67284 | 0.6696 | 0.66636 | 0.66312 | 0.65988 | 0.65664 | 0.6534 | 0.648 | 0.6426 | 0.6372 | 0.6318 | 0.6264 | 0.621 | 0.6156 | 0.6102 | 0.6048 | 0.5994 | 0.756 | 0.756
174 | 0.6812 | 0.67912 | 0.67704 | 0.67496 | 0.67288 | 0.6708 | 0.66872 | 0.66664 | 0.66456 | 0.66248 | 0.6604 | 0.65728 | 0.65416 | 0.65104 | 0.64792 | 0.6448 | 0.64168 | 0.63856 | 0.63544 | 0.63232 | 0.6292 | 0.624 | 0.6188 | 0.6136 | 0.6084 | 0.6032 | 0.598 | 0.5928 | 0.5876 | 0.5824 | 0.5772 | 0.728 | 0.728
175 | 0.655 | 0.653 | 0.651 | 0.649 | 0.647 | 0.645 | 0.643 | 0.641 | 0.639 | 0.637 | 0.635 | 0.632 | 0.629 | 0.626 | 0.623 | 0.62 | 0.617 | 0.614 | 0.611 | 0.608 | 0.605 | 0.6 | 0.595 | 0.59 | 0.585 | 0.58 | 0.575 | 0.57 | 0.565 | 0.56 | 0.555 | 0.7 | 0.7
176 | 0.6288 | 0.62688 | 0.62496 | 0.62304 | 0.62112 | 0.6192 | 0.61728 | 0.61536 | 0.61344 | 0.61152 | 0.6096 | 0.60672 | 0.60384 | 0.60096 | 0.59808 | 0.5952 | 0.59232 | 0.58944 | 0.58656 | 0.58368 | 0.5808 | 0.576 | 0.5712 | 0.5664 | 0.5616 | 0.5568 | 0.552 | 0.5472 | 0.5424 | 0.5376 | 0.5328 | 0.672 | 0.672
177 | 0.6026 | 0.60076 | 0.59892 | 0.59708 | 0.59524 | 0.5934 | 0.59156 | 0.58972 | 0.58788 | 0.58604 | 0.5842 | 0.58144 | 0.57868 | 0.57592 | 0.57316 | 0.5704 | 0.56764 | 0.56488 | 0.56212 | 0.55936 | 0.5566 | 0.552 | 0.5474 | 0.5428 | 0.5382 | 0.5336 | 0.529 | 0.5244 | 0.5198 | 0.5152 | 0.5106 | 0.644 | 0.644
178 | 0.5764 | 0.57464 | 0.57288 | 0.57112 | 0.56936 | 0.5676 | 0.56584 | 0.56408 | 0.56232 | 0.56056 | 0.5588 | 0.55616 | 0.55352 | 0.55088 | 0.54824 | 0.5456 | 0.54296 | 0.54032 | 0.53768 | 0.53504 | 0.5324 | 0.528 | 0.5236 | 0.5192 | 0.5148 | 0.5104 | 0.506 | 0.5016 | 0.4972 | 0.4928 | 0.4884 | 0.616 | 0.616
179 | 0.5502 | 0.54852 | 0.54684 | 0.54516 | 0.54348 | 0.5418 | 0.54012 | 0.53844 | 0.53676 | 0.53508 | 0.5334 | 0.53088 | 0.52836 | 0.52584 | 0.52332 | 0.5208 | 0.51828 | 0.51576 | 0.51324 | 0.51072 | 0.5082 | 0.504 | 0.4998 | 0.4956 | 0.4914 | 0.4872 | 0.483 | 0.4788 | 0.4746 | 0.4704 | 0.4662 | 0.588 | 0.588
180 | 0.524 | 0.5224 | 0.5208 | 0.5192 | 0.5176 | 0.516 | 0.5144 | 0.5128 | 0.5112 | 0.5096 | 0.508 | 0.5056 | 0.5032 | 0.5008 | 0.4984 | 0.496 | 0.4936 | 0.4912 | 0.4888 | 0.4864 | 0.484 | 0.48 | 0.476 | 0.472 | 0.468 | 0.464 | 0.46 | 0.456 | 0.452 | 0.448 | 0.444 | 0.56 | 0.56
181 | 0.4978 | 0.49628 | 0.49476 | 0.49324 | 0.49172 | 0.4902 | 0.48868 | 0.48716 | 0.48564 | 0.48412 | 0.4826 | 0.48032 | 0.47804 | 0.47576 | 0.47348 | 0.4712 | 0.46892 | 0.46664 | 0.46436 | 0.46208 | 0.4598 | 0.456 | 0.4522 | 0.4484 | 0.4446 | 0.4408 | 0.437 | 0.4332 | 0.4294 | 0.4256 | 0.4218 | 0.532 | 0.532
182 | 0.4716 | 0.47016 | 0.46872 | 0.46728 | 0.46584 | 0.4644 | 0.46296 | 0.46152 | 0.46008 | 0.45864 | 0.4572 | 0.45504 | 0.45288 | 0.45072 | 0.44856 | 0.4464 | 0.44424 | 0.44208 | 0.43992 | 0.43776 | 0.4356 | 0.432 | 0.4284 | 0.4248 | 0.4212 | 0.4176 | 0.414 | 0.4104 | 0.4068 | 0.4032 | 0.3996 | 0.504 | 0.504
183 | 0.4454 | 0.44404 | 0.44268 | 0.44132 | 0.43996 | 0.4386 | 0.43724 | 0.43588 | 0.43452 | 0.43316 | 0.4318 | 0.42976 | 0.42772 | 0.42568 | 0.42364 | 0.4216 | 0.41956 | 0.41752 | 0.41548 | 0.41344 | 0.4114 | 0.408 | 0.4046 | 0.4012 | 0.3978 | 0.3944 | 0.391 | 0.3876 | 0.3842 | 0.3808 | 0.3774 | 0.476 | 0.476
184 | 0.4192 | 0.41792 | 0.41664 | 0.41536 | 0.41408 | 0.4128 | 0.41152 | 0.41024 | 0.40896 | 0.40768 | 0.4064 | 0.40448 | 0.40256 | 0.40064 | 0.39872 | 0.3968 | 0.39488 | 0.39296 | 0.39104 | 0.38912 | 0.3872 | 0.384 | 0.3808 | 0.3776 | 0.3744 | 0.3712 | 0.368 | 0.3648 | 0.3616 | 0.3584 | 0.3552 | 0.448 | 0.448
185 | 0.393 | 0.3918 | 0.3906 | 0.3894 | 0.3882 | 0.387 | 0.3858 | 0.3846 | 0.3834 | 0.3822 | 0.381 | 0.3792 | 0.3774 | 0.3756 | 0.3738 | 0.372 | 0.3702 | 0.3684 | 0.3666 | 0.3648 | 0.363 | 0.36 | 0.357 | 0.354 | 0.351 | 0.348 | 0.345 | 0.342 | 0.339 | 0.336 | 0.333 | 0.42 | 0.42
186 | 0.3668 | 0.36568 | 0.36456 | 0.36344 | 0.36232 | 0.3612 | 0.36008 | 0.35896 | 0.35784 | 0.35672 | 0.3556 | 0.35392 | 0.35224 | 0.35056 | 0.34888 | 0.3472 | 0.34552 | 0.34384 | 0.34216 | 0.34048 | 0.3388 | 0.336 | 0.3332 | 0.3304 | 0.3276 | 0.3248 | 0.322 | 0.3192 | 0.3164 | 0.3136 | 0.3108 | 0.392 | 0.392
187 | 0.3406 | 0.33956 | 0.33852 | 0.33748 | 0.33644 | 0.3354 | 0.33436 | 0.33332 | 0.33228 | 0.33124 | 0.3302 | 0.32864 | 0.32708 | 0.32552 | 0.32396 | 0.3224 | 0.32084 | 0.31928 | 0.31772 | 0.31616 | 0.3146 | 0.312 | 0.3094 | 0.3068 | 0.3042 | 0.3016 | 0.299 | 0.2964 | 0.2938 | 0.2912 | 0.2886 | 0.364 | 0.364
188 | 0.3144 | 0.31344 | 0.31248 | 0.31152 | 0.31056 | 0.3096 | 0.30864 | 0.30768 | 0.30672 | 0.30576 | 0.3048 | 0.30336 | 0.30192 | 0.30048 | 0.29904 | 0.2976 | 0.29616 | 0.29472 | 0.29328 | 0.29184 | 0.2904 | 0.288 | 0.2856 | 0.2832 | 0.2808 | 0.2784 | 0.276 | 0.2736 | 0.2712 | 0.2688 | 0.2664 | 0.336 | 0.336
189 | 0.2882 | 0.28732 | 0.28644 | 0.28556 | 0.28468 | 0.2838 | 0.28292 | 0.28204 | 0.28116 | 0.28028 | 0.2794 | 0.27808 | 0.27676 | 0.27544 | 0.27412 | 0.2728 | 0.27148 | 0.27016 | 0.26884 | 0.26752 | 0.2662 | 0.264 | 0.2618 | 0.2596 | 0.2574 | 0.2552 | 0.253 | 0.2508 | 0.2486 | 0.2464 | 0.2442 | 0.308 | 0.308
190 | 0.262 | 0.2612 | 0.2604 | 0.2596 | 0.2588 | 0.258 | 0.2572 | 0.2564 | 0.2556 | 0.2548 | 0.254 | 0.2528 | 0.2516 | 0.2504 | 0.2492 | 0.248 | 0.2468 | 0.2456 | 0.2444 | 0.2432 | 0.242 | 0.24 | 0.238 | 0.236 | 0.234 | 0.232 | 0.23 | 0.228 | 0.226 | 0.224 | 0.222 | 0.28 | 0.28
191 | 0.2358 | 0.23508 | 0.23436 | 0.23364 | 0.23292 | 0.2322 | 0.23148 | 0.23076 | 0.23004 | 0.22932 | 0.2286 | 0.22752 | 0.22644 | 0.22536 | 0.22428 | 0.2232 | 0.22212 | 0.22104 | 0.21996 | 0.21888 | 0.2178 | 0.216 | 0.2142 | 0.2124 | 0.2106 | 0.2088 | 0.207 | 0.2052 | 0.2034 | 0.2016 | 0.1998 | 0.252 | 0.252
192 | 0.2096 | 0.20896 | 0.20832 | 0.20768 | 0.20704 | 0.2064 | 0.20576 | 0.20512 | 0.20448 | 0.20384 | 0.2032 | 0.20224 | 0.20128 | 0.20032 | 0.19936 | 0.1984 | 0.19744 | 0.19648 | 0.19552 | 0.19456 | 0.1936 | 0.192 | 0.1904 | 0.1888 | 0.1872 | 0.1856 | 0.184 | 0.1824 | 0.1808 | 0.1792 | 0.1776 | 0.224 | 0.224
193 | 0.1834 | 0.18284 | 0.18228 | 0.18172 | 0.18116 | 0.1806 | 0.18004 | 0.17948 | 0.17892 | 0.17836 | 0.1778 | 0.17696 | 0.17612 | 0.17528 | 0.17444 | 0.1736 | 0.17276 | 0.17192 | 0.17108 | 0.17024 | 0.1694 | 0.168 | 0.1666 | 0.1652 | 0.1638 | 0.1624 | 0.161 | 0.1596 | 0.1582 | 0.1568 | 0.1554 | 0.196 | 0.196
194 | 0.1572 | 0.15672 | 0.15624 | 0.15576 | 0.15528 | 0.1548 | 0.15432 | 0.15384 | 0.15336 | 0.15288 | 0.1524 | 0.15168 | 0.15096 | 0.15024 | 0.14952 | 0.1488 | 0.14808 | 0.14736 | 0.14664 | 0.14592 | 0.1452 | 0.144 | 0.1428 | 0.1416 | 0.1404 | 0.1392 | 0.138 | 0.1368 | 0.1356 | 0.1344 | 0.1332 | 0.168 | 0.168
195 | 0.131 | 0.1306 | 0.1302 | 0.1298 | 0.1294 | 0.129 | 0.1286 | 0.1282 | 0.1278 | 0.1274 | 0.127 | 0.1264 | 0.1258 | 0.1252 | 0.1246 | 0.124 | 0.1234 | 0.1228 | 0.1222 | 0.1216 | 0.121 | 0.12 | 0.119 | 0.118 | 0.117 | 0.116 | 0.115 | 0.114 | 0.113 | 0.112 | 0.111 | 0.14 | 0.14
196 | 0.1048 | 0.10448 | 0.10416 | 0.10384 | 0.10352 | 0.1032 | 0.10288 | 0.10256 | 0.10224 | 0.10192 | 0.1016 | 0.10112 | 0.10064 | 0.10016 | 0.09968 | 0.0992 | 0.09872 | 0.09824 | 0.09776 | 0.09728 | 0.0968 | 0.096 | 0.0952 | 0.0944 | 0.0936 | 0.0928 | 0.092 | 0.0912 | 0.0904 | 0.0896 | 0.0888 | 0.112 | 0.112
USER GUIDE