## instructions and notes
Transpower Oil Containment Calculator - V00.8
General
- inputs are green
- calculated outputs are orange
- only use copy-paste-special-values, don't drag data as this destroys the named ranges in the workbook.
Relative Levels
- these only need to be relative to each other. They are used only to calculate the effective secondary storage volume in the bunds
NIWA HIRDS
- download HIRDS data in CSV format, open in Excel and copy-paste-special-values into this workbook.
- will add instructions, notes and revision history here after basic design is reviewed

## calculator - V00.8
Transpower Oil Containment Calculator - V00.8
Project | XXX TXX
Calculator | [7 empty] | Notes
Oil Plate Separator processing rate | 1.5 | 3 | 4.5 | 6 | 10 | 20 | m3/hour
Catchment area | 820.6 | 820.6 | 820.6 | 820.6 | 820.6 | 820.6 | m2
Max expected rainwater accumulation | 291.5258 | 234.798 | 216.798 | 198.798 | 150.798 | 93.7578 | m3 | max calculated across entire HIRDS data arrays for nominal and 1° climate change
320.6784 | 55 | 55 | 55 | 55 | 55 | 55 | m3
Required containment tank volume | 320.6784 | 258.2778 | 238.4778 | 218.6778 | 165.8778 | 103.1336 | m3 | volume between cut-on level of OPS pump and tank high level alarm. Includes error allowance
Expect value of time when tank is not empty
- hours per year | 687.6663 | 239.6596 | 114.7258 | 69.9909 | 24.4141 | 7.3403 | hours | equivalent to expected annual pump running hours
- % of time | 7.85% | 2.736% | 1.31% | 0.799% | 0.2787% | 0.08379% | %
Effective secondary storage volume in bunds | 337 | 337 | 337 | 337 | 337 | 337 | m3 | additional volume available in connected connected bunds if containment tank becomes full (e.g. rainfull outside HIRDS data or OPS pump fails)
Buffer against oil escape during worst rainstorm | 89.79% | 105.4% | 111.7% | 118.9% | 144.4% | 195.9% | % | % additional volume offered by bunds over what is required for largest volume of oil plus max expected rainwater accumulation]
Design Factors
Error allowance for bunded area measurements | 10%
Error allowance for tank as-built volume | 10%
Bunded areas and oil volume (including prudent future allowance)
| Oil (m3) | Area (m2) |  | Relative Levels (m)
Name | Largest single volume in bund | Bunded | Exclusion (e.g. tx area) | Floor | Top of bund wall
T12 | 55 | 150 | 15 | 0 | 0.5
T13 | 55 | 150 | 15 | 0 | 0.5
T11 | 55 | 150 | 15 | 0 | 0.5
T14 | 55 | 150 | 15 | 0 | 0.5
T13 Old | 42 | 140 | 12 | 0 | 0.5
OPS bund | 0 | 6 | 0 | 0 | 0.5
NIWA High Intensity Rainfall Design System (HIRDS) - hirds.niwa.co.nz (depth-duration-freq results)
Duration
|  |  | 0.16667 | 0.33333 | 0.5 | 1 | 2 | 6 | 12 | 24 | 48 | 72 | (hours)
Data Set (mm) | ARI (years) | AEP | 10m | 20m | 30m | 60m | 2h | 6h | 12h | 24h | 48h | 72h
Rainfall depths - nominal | 1.58 | 0.633 | 9.34 | 14.1 | 17.9 | 26.2 | 37.5 | 62.4 | 82.5 | 105 | 128 | 140
| 2 | 0.5 | 10.3 | 15.6 | 19.7 | 28.9 | 41.3 | 68.7 | 90.7 | 115 | 140 | 154
| 5 | 0.2 | 13.7 | 20.7 | 26.2 | 38.3 | 54.7 | 90.7 | 119 | 151 | 184 | 202
| 10 | 0.1 | 16.4 | 24.7 | 31.1 | 45.5 | 64.8 | 107 | 141 | 179 | 217 | 238
| 20 | 0.05 | 19.2 | 28.8 | 36.3 | 53 | 75.5 | 125 | 164 | 207 | 251 | 275
| 30 | 0.033 | 20.9 | 31.4 | 39.5 | 57.6 | 82.1 | 135 | 178 | 225 | 272 | 298
| 40 | 0.025 | 22.1 | 33.2 | 41.9 | 61 | 86.8 | 143 | 188 | 237 | 287 | 314
| 50 | 0.02 | 23.1 | 34.7 | 43.7 | 63.7 | 90.5 | 149 | 196 | 247 | 299 | 327
| 60 | 0.017 | 23.9 | 35.9 | 45.2 | 65.9 | 93.6 | 154 | 202 | 255 | 309 | 338
| 80 | 0.013 | 25.2 | 37.9 | 47.7 | 69.4 | 98.6 | 162 | 213 | 268 | 324 | 355
| 100 | 0.01 | 26.3 | 39.4 | 49.6 | 72.2 | 103 | 168 | 221 | 278 | 336 | 368
Rainfall depths - 1° climate change | 1.58 | 0.633 | 10.7 | 16.2 | 20.4 | 30 | 42.6 | 69.5 | 90.5 | 114 | 137 | 149
| 2 | 0.5 | 11.8 | 17.9 | 22.6 | 33.1 | 47.2 | 76.9 | 100 | 125 | 151 | 164
| 5 | 0.2 | 15.9 | 24 | 30.2 | 44.2 | 62.8 | 102 | 133 | 166 | 199 | 217
| 10 | 0.1 | 19 | 28.6 | 36 | 52.7 | 74.7 | 121 | 157 | 196 | 235 | 256
| 20 | 0.05 | 22.3 | 33.5 | 42.2 | 61.6 | 87.2 | 141 | 183 | 228 | 273 | 297
| 30 | 0.033 | 24.3 | 36.5 | 45.9 | 67 | 94.9 | 154 | 199 | 247 | 296 | 322
| 40 | 0.025 | 25.7 | 38.6 | 48.6 | 70.9 | 100 | 163 | 210 | 261 | 312 | 340
| 50 | 0.02 | 26.9 | 40.4 | 50.8 | 74.1 | 105 | 170 | 219 | 272 | 326 | 354
| 60 | 0.017 | 27.8 | 41.8 | 52.6 | 76.6 | 108 | 175 | 227 | 281 | 336 | 366
| 80 | 0.012 | 29.4 | 44.1 | 55.5 | 80.8 | 114 | 185 | 238 | 296 | 354 | 384
| 100 | 0.01 | 30.6 | 45.9 | 57.7 | 84 | 119 | 192 | 248 | 307 | 367 | 399
Standard errors | 1.58 | 0.633 | 1.1 | 1.5 | 1.7 | 2.5 | 3.4 | 6.4 | 9.5 | 3.5 | 6.9 | 6.8
| 2 | 0.5 | 1.2 | 1.6 | 1.8 | 2.7 | 3.7 | 7.1 | 10 | 3.7 | 7.5 | 7.4
| 5 | 0.2 | 1.8 | 2.5 | 2.8 | 3.9 | 5.6 | 9.6 | 14 | 6.2 | 11 | 11
| 10 | 0.1 | 2.3 | 3.4 | 4 | 5.3 | 7.6 | 12 | 18 | 9.3 | 15 | 16
| 20 | 0.05 | 3.1 | 4.6 | 5.5 | 7.3 | 10 | 16 | 22 | 14 | 20 | 22
| 30 | 0.033 | 3.6 | 5.5 | 6.7 | 8.9 | 13 | 18 | 26 | 17 | 24 | 26
| 40 | 0.025 | 4 | 6.2 | 7.6 | 10 | 14 | 21 | 29 | 19 | 27 | 30
| 50 | 0.02 | 4.4 | 6.8 | 8.4 | 11 | 16 | 22 | 31 | 22 | 29 | 33
| 60 | 0.017 | 4.8 | 7.3 | 9.1 | 12 | 17 | 24 | 34 | 23 | 31 | 35
| 80 | 0.013 | 5.3 | 8.3 | 10 | 14 | 20 | 27 | 37 | 27 | 35 | 40
| 100 | 0.01 | 5.8 | 9.1 | 11 | 16 | 22 | 30 | 41 | 29 | 38 | 43
Coordinate system | NZMG
Easting | 2759532
Northing | 6098783