## 0. Revision History
In Bund Oil Containment Calculator - Revision History
Revision | EC | Descripton | Design | Date | Check | Date | Approved | Date
1 | AECOM | First Issue | JD | 5.25 | IG/TC | 5.25 | AB | 5.25
2
3
4
5

## 1. Read Me
In-Bund Oil Containment Sump and OPS Sizing Spreadsheet
Introduction
This spreadsheet is designed to assist designers in selecting an appropriate sump volume and OPS rate for in-bund oil containment systems. It should be used in accordance with Transpower design standard DS 54.01. Instructions for using this spreadsheet are provided in the flowchart below, and a worked example is available in Tab 4.
How to use this spreadsheet
The flowchart below outlines the process for using this spreadsheet. Definitions for input parameters can be found in Tab 2, along with design boundaries such as OPS rate options, minimum buffer volumes, maximum practicable sump depth, and maximum bund collection areas. Once the inputs are entered and the calculation is performed, Tab 3 should be saved as a PDF and submitted to the Transpower project manager and project engineer for review.

## 2. Definitions
Definitions
Term | Unit | Description
Transformer Bund Surface Area | m2 | The total surface area of the transformer bund which rainfall will be captured. This includes part of the bund wall if there is an inwards chamfer where rainfall would runoff into the bund.
Transformer Bund Surface Area Excluding Transformer | m2 | The total surface area of the bund, minus the footprint occupied by the transformer.
Buffer Volume | L | The total bund volume between the top of the transformer embedded pates and the OPS cut in float switch, serving as additional containment capacity. Refer Figure 1.
NIWA HIRDS Data | mm | High Intensity Rainfall Design System (HIRDS) data used for estimating extreme rainfall events at a given location. Data can be downloaded from https://hirds.niwa.co.nz/. Detailed instructions below.
Sump Volume | L | The total usable volume within the sump (between the OPS float switch cut-in and cut-out levels). The volume below the OPS cut in level generally contains effluent to keep the pump primed, and therefore is not considered in this definition.
OPS Processing Rate | m3/hr | The rate at which the oil plate separator processes effluent.
Design Boundaries
Sump Size |  | The maximum practicable sump depth is 3 meters below the finished switchyard level, for a typical sump length and width of 1.2 meters.
OPS Rate |  | MACSEP OPS units come in standard sizes of 1.5, 3, 4.5 and 6 m3/hr, typically sufficient for most sites, though extreme weather regions may require larger units or deeper sumps.
Catchment Area |  | Bunds with surface areas over 175m² in high-rainfall regions may become impractical for achieving appropriate sump and OPS rates.
Figures
Figure 1 - Buffer Volume
Downloading HIRDS Data
Step 1 - Navigate to the HIRDS website. Go to https://hirds.niwa.co.nz/ and select a site on the map.
Step 2 - Generate the report. Click Generate Report, ensuring the Depth-Duration-Frequency option is selected.
Step 3 - Download the spreadsheet. Click Spreadsheet Download, then open the CSV file.
Step 4 - Extract the required data. Scroll to the bottom and copy the RCP8.5 (2081-2100) data into Tab 3 of this spreadsheet.

## 3. Calculation
Project Information
FMIS Code: |  | IP_XX_XX_XX
Description: |  | Enter project description here
Revision |  | Design | Date | Check | Date | Approved | Date | TP Approved | Date
-1 |  | XX | XX.XX | XX | XX.XX | XX | XX.XX | XX | XX
-2
-3
-4
-5
Inputs (Definitions provided in Tab 2)
Bund Area {m^2} | [6 empty] | Input Cells
OPS Rate {m^3/hr} | [6 empty] | Calculated Cells
Sump Volume {L} | [6 empty] | Notes 1. Hidden cells between columns M and V contain explanations. 2. Hidden rows between 34 and 116 contain intermediate calculation steps. 3. Hidden rows between 6 and 12 contain extra revision lines.
Buffer Volume {L}
Bund Area Excluding Transformer {m^2}
Rainfall depths {mm} :: RCP8.5 for the period 2081-2100 |  |  |  |  | Refer blue cells below
NIWA HIRDS Rainfall Depths - This the total rainfall expected in the time period given NOT the rate per hour in over that time
| Hours | 0.16667 | 0.33333 | 0.5 | 1 | 2 | 6 | 12 | 24 | 48 | 72
ARI | AEP | 10m | 20m | 30m | 1h | 2h | 6h | 12h | 24h | 48h | 72h
1.58 | 0.633
2 | 0.5
5 | 0.2
10 | 0.1
20 | 0.05
30 | 0.033
40 | 0.025
50 | 0.02
60 | 0.017
80 | 0.013
100 | 0.01
Calculation
Litres of rain captured in the bund and sump
| Hours | 0.16667 | 0.33333 | 0.5 | 1 | 2 | 6 | 12 | 24 | 48 | 72
ARI | AEP | 10m | 20m | 30m | 1h | 2h | 6h | 12h | 24h | 48h | 72h
1.58 | 0.633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 0.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 | 0.025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60 | 0.017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80 | 0.013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Litres above Tx base without processing
| Hours | 0.16667 | 0.33333 | 0.5 | 1 | 2 | 6 | 12 | 24 | 48 | 72
ARI | AEP | 10m | 20m | 30m | 1h | 2h | 6h | 12h | 24h | 48h | 72h
1.58 | 0.633
2 | 0.5
5 | 0.2
10 | 0.1
20 | 0.05
30 | 0.033
40 | 0.025
50 | 0.02
60 | 0.017
80 | 0.013
100 | 0.01
Processing rate required to empty bund excluding the sump
| Hours | 0.16667 | 0.33333 | 0.5 | 1 | 2 | 6 | 12 | 24 | 48 | 72
ARI | AEP | 10m | 20m | 30m | 1h | 2h | 6h | 12h | 24h | 48h | 72h
1.58 | 0.633
2 | 0.5
5 | 0.2
10 | 0.1
20 | 0.05
30 | 0.033
40 | 0.025
50 | 0.02
60 | 0.017
80 | 0.013
100 | 0.01
Unprocessed Residual Rate
| Hours | 0.16667 | 0.33333 | 0.5 | 1 | 2 | 6 | 12 | 24 | 48 | 72
ARI | AEP | 10m | 20m | 30m | 1h | 2h | 6h | 12h | 24h | 48h | 72h
1.58 | 0.633
2 | 0.5
5 | 0.2
10 | 0.1
20 | 0.05
30 | 0.033
40 | 0.025
50 | 0.02
60 | 0.017
80 | 0.013
100 | 0.01
Leftover volume of rain captured above ideal flat foundation (inundation)
| Hours | 0.16667 | 0.33333 | 0.5 | 1 | 2 | 6 | 12 | 24 | 48 | 72
ARI | AEP | 10m | 20m | 30m | 1h | 2h | 6h | 12h | 24h | 48h | 72h
1.58 | 0.633
2 | 0.5
5 | 0.2
10 | 0.1
20 | 0.05
30 | 0.033
40 | 0.025
50 | 0.02
60 | 0.017
80 | 0.013
100 | 0.01
Outputs
Leftover mm of rain above transformer base
| Hours | 0.16667 | 0.33333 | 0.5 | 1 | 2 | 6 | 12 | 24 | 48 | 72
ARI | AEP | 10m | 20m | 30m | 1h | 2h | 6h | 12h | 24h | 48h | 72h
1.58 | 0.633
2 | 0.5
5 | 0.2
10 | 0.1
20 | 0.05
30 | 0.033
40 | 0.025
50 | 0.02
60 | 0.017
80 | 0.013
100 | 0.01
Red cells indicate theoretical idealised level of inundation (mm above transfomer base). Engineer to review

## 4. Worked Example
Project Information
FMIS Code: |  | IP_XX_XX_XX
Description: |  | Example using INV T7 Approx Geometry
Revision |  | Design | Date | Check | Date | Approved | Date | TP Approved | Date
-1 |  | JD | 5.25 | IG | 5.25 | AB | 5.25 | XX | XX
-2
-3
-4
-5
Inputs (Definitions provided in Tab 2)
Bund Area {m^2} |  |  |  |  | 168 |  | Input Cells
OPS Rate {m^3/hr} |  |  |  |  | 1500 |  | Calculated Cells
Sump Volume {L} |  |  |  |  | 1264 |  | Notes 1. Hidden cells between columns M and V contain explanations. 2. Hidden rows between 34 and 116 contain intermediate calculation steps. 3. Hidden rows between 6 and 12 contain extra revision lines.
Buffer Volume {L} |  |  |  |  | 5803
Bund Area Excluding Transformer {m^2} |  |  |  |  | 142
Rainfall depths {mm} :: RCP8.5 for the period 2081-2100 |  |  |  |  | Refer blue cells below
NIWA HIRDS Rainfall Depths - This the total rainfall expected in the time period given NOT the rate per hour in over that time
| Hours | 0.16667 | 0.33333 | 0.5 | 1 | 2 | 6 | 12 | 24 | 48 | 72
ARI | AEP | 10m | 20m | 30m | 1h | 2h | 6h | 12h | 24h | 48h | 72h
1.58 | 0.633 | 4.63 | 6.35 | 7.63 | 10.4 | 14.1 | 22.8 | 30.6 | 41.2 | 55.3 | 65.5
2 | 0.5 | 5.24 | 7.13 | 8.54 | 11.6 | 15.7 | 25 | 33.4 | 44.7 | 59.6 | 70.4
5 | 0.2 | 7.54 | 10.1 | 12 | 16 | 21.2 | 32.9 | 43.2 | 56.7 | 74.3 | 87
10 | 0.1 | 9.53 | 12.6 | 14.8 | 19.6 | 25.7 | 39.1 | 50.8 | 65.8 | 85.3 | 99.2
20 | 0.05 | 11.9 | 15.5 | 18.1 | 23.6 | 30.7 | 45.9 | 59 | 75.5 | 96.8 | 112
30 | 0.033 | 13.4 | 17.4 | 20.3 | 26.3 | 33.9 | 50.3 | 64.1 | 81.6 | 104 | 120
40 | 0.025 | 14.6 | 18.9 | 22 | 28.3 | 36.3 | 53.5 | 67.9 | 86.1 | 109 | 125
50 | 0.02 | 15.6 | 20.1 | 23.3 | 30 | 38.3 | 56.1 | 71 | 89.6 | 113 | 130
60 | 0.017 | 16.5 | 21.2 | 24.5 | 31.4 | 40 | 58.3 | 73.6 | 92.6 | 117 | 133
80 | 0.013 | 17.9 | 22.9 | 26.4 | 33.7 | 42.8 | 61.9 | 77.7 | 97.4 | 122 | 139
100 | 0.01 | 19.1 | 24.3 | 28 | 35.6 | 45 | 64.8 | 81.1 | 101 | 126 | 144
Calculation
Litres of rain captured in the bund and sump
| Hours | 0.16667 | 0.33333 | 0.5 | 1 | 2 | 6 | 12 | 24 | 48 | 72
ARI | AEP | 10m | 20m | 30m | 1h | 2h | 6h | 12h | 24h | 48h | 72h
1.58 | 0.633 | 777.84 | 1066.8 | 1281.84 | 1747.2 | 2368.8 | 3830.4 | 5140.8 | 6921.6 | 9290.4 | 11004
2 | 0.5 | 880.32 | 1197.84 | 1434.72 | 1948.8 | 2637.6 | 4200 | 5611.2 | 7509.6 | 10012.8 | 11827.2
5 | 0.2 | 1266.72 | 1696.8 | 2016 | 2688 | 3561.6 | 5527.2 | 7257.6 | 9525.6 | 12482.4 | 14616
10 | 0.1 | 1601.04 | 2116.8 | 2486.4 | 3292.8 | 4317.6 | 6568.8 | 8534.4 | 11054.4 | 14330.4 | 16665.6
20 | 0.05 | 1999.2 | 2604 | 3040.8 | 3964.8 | 5157.6 | 7711.2 | 9912 | 12684 | 16262.4 | 18816
30 | 0.033 | 2251.2 | 2923.2 | 3410.4 | 4418.4 | 5695.2 | 8450.4 | 10768.8 | 13708.8 | 17472 | 20160
40 | 0.025 | 2452.8 | 3175.2 | 3696 | 4754.4 | 6098.4 | 8988 | 11407.2 | 14464.8 | 18312 | 21000
50 | 0.02 | 2620.8 | 3376.8 | 3914.4 | 5040 | 6434.4 | 9424.8 | 11928 | 15052.8 | 18984 | 21840
60 | 0.017 | 2772 | 3561.6 | 4116 | 5275.2 | 6720 | 9794.4 | 12364.8 | 15556.8 | 19656 | 22344
80 | 0.013 | 3007.2 | 3847.2 | 4435.2 | 5661.6 | 7190.4 | 10399.2 | 13053.6 | 16363.2 | 20496 | 23352
100 | 0.01 | 3208.8 | 4082.4 | 4704 | 5980.8 | 7560 | 10886.4 | 13624.8 | 16968 | 21168 | 24192
Litres above Tx base without processing
| Hours | 0.16667 | 0.33333 | 0.5 | 1 | 2 | 6 | 12 | 24 | 48 | 72
ARI | AEP | 10m | 20m | 30m | 1h | 2h | 6h | 12h | 24h | 48h | 72h
1.58 | 0.633 | [8 empty] | 2223.4 | 3937
2 | 0.5 | [7 empty] | 442.6 | 2945.8 | 4760.2
5 | 0.2 | [6 empty] | 190.6 | 2458.6 | 5415.4 | 7549
10 | 0.1 | [6 empty] | 1467.4 | 3987.4 | 7263.4 | 9598.6
20 | 0.05 | [5 empty] | 644.2 | 2845 | 5617 | 9195.4 | 11749
30 | 0.033 | [5 empty] | 1383.4 | 3701.8 | 6641.8 | 10405 | 13093
40 | 0.025 | [5 empty] | 1921 | 4340.2 | 7397.8 | 11245 | 13933
50 | 0.02 | [5 empty] | 2357.8 | 4861 | 7985.8 | 11917 | 14773
60 | 0.017 | [5 empty] | 2727.4 | 5297.8 | 8489.8 | 12589 | 15277
80 | 0.013 |  |  |  |  | 123.4 | 3332.2 | 5986.6 | 9296.2 | 13429 | 16285
100 | 0.01 |  |  |  |  | 493 | 3819.4 | 6557.8 | 9901 | 14101 | 17125
Processing rate required to empty bund excluding the sump
| Hours | 0.16667 | 0.33333 | 0.5 | 1 | 2 | 6 | 12 | 24 | 48 | 72
ARI | AEP | 10m | 20m | 30m | 1h | 2h | 6h | 12h | 24h | 48h | 72h
1.58 | 0.633 | [8 empty] | 46.3208 | 54.6806
2 | 0.5 | [7 empty] | 18.4417 | 61.3708 | 66.1139
5 | 0.2 | [6 empty] | 15.8833 | 102.4417 | 112.8208 | 104.8472
10 | 0.1 | [6 empty] | 122.2833 | 166.1417 | 151.3208 | 133.3139
20 | 0.05 | [5 empty] | 107.3667 | 237.0833 | 234.0417 | 191.5708 | 163.1806
30 | 0.033 | [5 empty] | 230.5667 | 308.4833 | 276.7417 | 216.7708 | 181.8472
40 | 0.025 | [5 empty] | 320.1667 | 361.6833 | 308.2417 | 234.2708 | 193.5139
50 | 0.02 | [5 empty] | 392.9667 | 405.0833 | 332.7417 | 248.2708 | 205.1806
60 | 0.017 | [5 empty] | 454.5667 | 441.4833 | 353.7417 | 262.2708 | 212.1806
80 | 0.013 |  |  |  |  | 61.7 | 555.3667 | 498.8833 | 387.3417 | 279.7708 | 226.1806
100 | 0.01 |  |  |  |  | 246.5 | 636.5667 | 546.4833 | 412.5417 | 293.7708 | 237.8472
Unprocessed Residual Rate
| Hours | 0.16667 | 0.33333 | 0.5 | 1 | 2 | 6 | 12 | 24 | 48 | 72
ARI | AEP | 10m | 20m | 30m | 1h | 2h | 6h | 12h | 24h | 48h | 72h
1.58 | 0.633
2 | 0.5
5 | 0.2
10 | 0.1
20 | 0.05
30 | 0.033
40 | 0.025
50 | 0.02
60 | 0.017
80 | 0.013
100 | 0.01
Leftover volume of rain captured above ideal flat foundation (inundation)
| Hours | 0.16667 | 0.33333 | 0.5 | 1 | 2 | 6 | 12 | 24 | 48 | 72
ARI | AEP | 10m | 20m | 30m | 1h | 2h | 6h | 12h | 24h | 48h | 72h
1.58 | 0.633
2 | 0.5
5 | 0.2
10 | 0.1
20 | 0.05
30 | 0.033
40 | 0.025
50 | 0.02
60 | 0.017
80 | 0.013
100 | 0.01
Outputs
Leftover mm of rain above transformer base
| Hours | 0.16667 | 0.33333 | 0.5 | 1 | 2 | 6 | 12 | 24 | 48 | 72
ARI | AEP | 10m | 20m | 30m | 1h | 2h | 6h | 12h | 24h | 48h | 72h
1.58 | 0.633
2 | 0.5
5 | 0.2
10 | 0.1
20 | 0.05
30 | 0.033
40 | 0.025
50 | 0.02
60 | 0.017
80 | 0.013
100 | 0.01
Red cells indicate theoretical idealised level of inundation (mm above transfomer base). Engineer to review