## Introduction
Introduction to Asset Owner Checksheet
Purpose of this document:
This document aims to provide a standard checksheet for Asset Owners to perform a self-assessment and record how Code compliance has been met. Final compliance is an assessment completed during the closeout phase of the project.
Objective:
1. Before the closeout phase (starting in the initiation phase), the Asset Owner to identify all Code clauses that they must comply with. This will allow the Asset Owners to become aware of the Code obligations which the System Operator will assess compliance against at the end of their project. Clarifying Code obligations early will support timely progress of the commissioning generation process.
2. During the closeout phase, the Asset Owner to select evidence and provide comment that proves compliance with each Code clause. Find below some advice for what information to include with the main types of evidence.
| Source type | Critical information demonstrating compliance
| Report | Report name, section, page number, table number (if applicable).
| Registry | Confirmation that you have checked the information is correct or has been updated.
| Agreement | Confirmation that the agreement is signed/complete; where this agreement is stored or who it was emailed to and when.
| Email | Email date, person addressed, indication about which part of the email addresses the clause.
3. During the closeout phase, the System Operator will perform a compliance assessment using the information provided by the Asset Owner. If the information is vague or unclear, the System Operator may request more information, which may delay the final closeout of the project.
Associated documents outlining the requirements:
1. Electricity Industry Participation Code ("The Code") available at https://www.ea.govt.nz/code-and-compliance/code/
2. Connected Asset Commissioning, Testing, and Information Standard ("CACTIS") available at https://www.ea.govt.nz/code-and-compliance/code/documents-incorporated-into-the-code/
Disclaimers:
1. The System Operator reminds the Asset Owner that it is their responsibility to familiarise themselves with the Code and the obligations that apply to their asset(s).
2. There is a short set of instructions for how to use the Code Checksheet to the right of the 'comment' column (Column E) in that tab.
3. Where there is a conflict between the Code and any System Operator documents (including this one), the Code takes precedence.
4. The Code clauses referred to in this document are extracted from the last updated version of the Code as of:
2026-07-01
2026 Transpower New Zealand

## Code Checksheet
Code Clause | Subclause or CACTIS Clause | Clause Description | Asset Owner Evidence [e.g. ACS, Connection Study etc.] | Asset Owner Comment [Where in the evidence is compliance demonstrated?]
8.17 |  | Contribution by injections to overall frequency management: Each generator (while synchronised) and the HVDC owner must at all times ensure that its assets, other than any generating units within an excluded generating station, make the maximum possible injection contribution to maintain frequency within the normal band (and to restore frequency to the normal band). Any such contribution must be assessed against the technical codes. |  |  | Instructions for Asset Owners 1. Familiarise yourself with the Code clauses in columns A, B and C. It is your responsibility to identify which ones apply to your asset and then demonstrate compliance with each. 2. For each Code clause, select the best source of evidence that demonstrates your compliance from the drop-down menu in each cell of column D. If you want to feature multiple sources of evidence, simply mention the other(s) in the comment column (Column E). 3. For some of the clauses, you may not be able to provide explicit evidence - for those, the drop-down menu asks that you acknowledge the clause and then provide a comment in the cell next to it to explain it. 4. Send your completed sheet for review to the System Operator to prompt them to start their review. They will reach out with a report once they have assessed your evidence. Tips: a. Open this document in the desktop version of Microsoft Excel. b. Fill in evidence throughout the Commissioning and Closeout phases to keep on track with your compliance requirements. c. If a Code requirement doesn't apply to your asset, simply select 'Not Applicable' from the drop-down menu. d. Consult the example sheet provided in the tab at the bottom toolbar for an idea of the level of detail the System Operator expects from you.
8.19 |  | Contributions to frequency support in under-frequency events:
8.19 (1) |  | Subject to subclause (3), each generator must at all times ensure that, while connected, its assets, other than any excluded generating stations, contribute to supporting frequency by remaining synchronised, ensuring that each of its generating units can and does, at a minimum, sustain pre-event output―
8.19 (1) | (a) | at all times when the frequency is above 47.5 Hertz; and
8.19 (1) | (b) | for at least 120 seconds when the frequency is 47.5 Hertz; and
8.19 (1) | (c) | for at least 20 seconds when the frequency is 47.3 Hertz; and
8.19 (1) | (d) | for at least 5 seconds when the frequency is 47.1 Hertz; and
8.19 (1) | (e) | for at least 0.1 seconds when the frequency is 47.0 Hertz; and
8.19 (1) | (f) | at any frequencies between those specified in paragraphs (b) to (e) for times derived by linear interpolation.
8.19 (2) |  | If the inherent characteristics and design of a generator's generating unit are such that it is reasonably able to operate beyond the above requirements, the generator must declare such capabilities in accordance with clause 2(5) of Technical Code A of Schedule 8.3.
8.19 (3) |  | Each South Island generator must ensure that each of its assets, other than excluded generating units, remains synchronised, and can and do, at a minimum, sustain pre-event output―
8.19 (3) | (a) | at all times when the frequency is above 47 Hertz; and
8.19 (3) | (b) | for 30 seconds if the frequency falls below 47 Hertz but not below 45 Hertz.
8.22 |  | Voltage Range AOPOs
8.22 | (2) | Each generator with a point of connection to the grid must at all times ensure that its assets are capable of being operated, and do operate, when the grid is operated within the range of voltages set out in subclause (1).
8.23 |  | Voltage support AOPOs for grid-connected generating stations
8.23 |  | Each generator with a point of connection to the grid must at all times ensure that its assets―
8.23 | (a) | when the voltage at its grid injection point is within the applicable range of nominal voltage, are capable of exporting (over excited) when synchronised and made available for dispatch by the system operator, a minimum net reactive power which is 50% of the maximum continuous MW output power as measured at the following generating unit terminals:
8.23 | (b) | when the voltage at its grid injection point is within the applicable range of nominal voltage, are capable of importing (under excited) when synchronised and made available for dispatch by the system operator, a minimum net reactive power which is 33% of the maximum continuous MW output power as measured at the generating unit terminals as set out below:
8.23 | (c) | when synchronised, continuously operate in a manner that supports voltage and voltage stability on the grid in compliance with the technical codes.
8.23A |  | Voltage support AOPOs for embedded generating stations
8.23A | (1) | Unless agreed otherwise with the distributor who operates the local network, each embedded generator must ensure that each embedded generating station it owns or operates to which clause 5(2A) of Technical Code A applies is, when synchronised with the local network, at all times capable of―
8.23A | (a) | when the voltage at the embedded generating station’s point of connection to the local network is within the applicable range of nominal voltage in the table (see the Code), exporting a minimum reactive power of 33% of the maximum continuous MW output power of the embedded generating station, as measured at the embedded generating station’s point of connection to the local network:
8.23A | (b) | when the voltage at the embedded generating station’s point of connection to the local network is within the applicable range of nominal voltage in the table (see the Code), importing a minimum reactive power of 33% of the maximum continuous MW output power of the embedded generating station, as measured at the embedded generating station’s point of connection to the local network:
8.25 | (3) | Each asset owner and each purchaser must provide communication facilities that comply with the technical codes or otherwise as the system operator reasonably requests, to assist the system operator in planning to comply, and complying, with its principal performance obligations and achieving the dispatch objective.
8.25A |  | Fault Ride Through
8.25A | (1) | Each generator must ensure that each of its assets, when electrically connected to a network, is capable of remaining stable and electrically connected when the grid's lowest line-to-line voltage is within the no-trip zone shaded and marked "No-trip zone" in Figure 8.1 (for an asset in the North Island) or Figure 8.2 (for an asset in the South Island) for the period of 6 seconds immediately following the commencement of a zero impedance three-phase short circuit fault, or an unbalanced short circuit fault, on any part of the grid at 110 kV or 220 kV in the island in which the asset is connected
8.25A | (2) | Each generator must ensure that each of its assets, when electrically connected to a network, is capable of remaining stable and electrically connected when the highest line-to-line voltage at Haywards 220 kV bus (for an asset in the North Island) or Benmore 220 kV bus (for an asset in the South Island) is within the no-trip zone shaded and marked "No-trip zone" in Figure 8.3 for the period of 1 second immediately following the commencement of a trip of the HVDC link
8.25A | (3) | Whether a generator is complying with subclause (2) must be determined using power system analysis that uses (a) study cases provided by the relevant grid owner; and (b) relevant system assumptions provided by the system operator.
8.25A | (4) | A generator is not required to comply with subclause (1) in respect of an asset in the event of a fault of a type described in subclause (1) if the asset becomes isolated from the grid as a result of the fault.
8.25A | (5) | A generating unit need not comply with subclause (1) to the extent that it is complying with a special protection scheme approved by the system operator.
8.25B | (1) | Each generator must ensure that each of its generating units generates reactive current to oppose the change in its terminal voltage without exceeding the maximum transient reactive current specified in the generator's asset capability statement for the period of 6 seconds immediately following the commencement of a fault on the grid of a type described in clause 8.25A(1)
8.25B | (2) | Each generator must ensure that each of its generating units provides active power output relative to pre-fault active power output at least in proportion to the grid voltage at the grid injection point for the period of 6 seconds immediately following the clearance of a fault on the grid of a type described in clause 8.25A(1).
8.25B | (3) | Subclause (2) does not apply to a wind generating station if there has been a reduction in the intermittent wind power source during the 6 seconds following the commencement of the fault.
Use of additional equipment
8.25C | (a) to (c ) | A generator may comply with clause 8.25A in relation to a generating station by (a) ensuring that the performance of generating units that comprise the generating station comply; or (b) installing additional equipment within the generating station; or (c) a combination of the methods described in paragraphs (a) and (b).
8.25D |  | Application
Clauses 8.25A and 8.25B do not apply (a) to a wind generating station when it operates at less than 5% of rated MW; or (b) to any asset at an excluded generating station.
Sch 8.3 TC A 2 |  | General requirements
Sch 8.3 TC A 2 | (5) (a) to (b) | Each asset owner must provide the system operator with an asset capability statement in accordance with the connected asset commissioning, testing and information standard (a) for each asset that is― (i) proposed to be connected, or is connected to, or forms part of the grid; or (ii) proposed to be connected, or is connected directly or indirectly to a local network; and (b) for each asset, where the asset owner is a generator, that (i) forms part or all of a generating station with a capacity equal to or greater than the threshold specified in clause 8.21(1) at the point of connection to the network; or (ii) forms part or all of a generating unit with a capacity equal to or greater than the threshold specified in clause 8.21(2) at the point of connection to the network.
Sch 8.3 TC A 2 | (6) | Each asset owner must provide a commissioning plan or test plan in accordance with to the system operator in compliance with the connected asset commissioning, testing and information standard
Sch 8.3 TC A 2 | (10) | Each asset owner must―
Sch 8.3 TC A 2 | (10) (a) | carry out connection studies for each asset, in accordance with the connected asset commissioning, testing and information standard; and
Sch 8.3 TC A 2 | (10) (b) | provide connection study reports, including modelling information, to the system operator in compliance with the connected asset commissioning, testing and information standard.; and
Sch 8.3 TC A 2 | (10) (c) | ensure that modelling information is provided to the system operator in compliance with the connected asset commissioning, testing and information standard; and
Sch 8.3 TC A 2 | (10) (d) | provide a model to the system operator in compliance with the connected asset commissioning, testing and information standard that can be used for the network models in clause 8.25A(3)(a).
CACTIS | 5.22 | If the asset owner modifies any of the control system settings for the asset during or after commissioning, the asset owner must notify the system operator and the fault ride through studies must be repeated with the new control system settings.
Sch 8.3 TC A 3 |  | Requirements for asset information
Sch 8.3 TC A 3 | (1) | In accordance with clause 8.25(4), the following information is required by the system operator to assist it to plan to comply, and to comply, with its principal performance obligations:
Sch 8.3 TC A 3 | (1) (a) | sufficient information must be exchanged between the system operator and the asset owner to ensure that both fully understand the implications of any changes to the asset capability statement or of any proposed connection of the relevant assets to the grid or to the local network. This information must be exchanged in accordance with a timetable agreed to by the system operator and the asset owner:
Sch 8.3 TC A 3 | (1) (b) | if reasonably requested by the system operator, the asset owner must provide sufficient information to the system operator to demonstrate the compliance of the asset owner's assets with the asset owner performance obligations and the technical codes.
Sch 8.3 TC A 4 |  | Requirements for the grid and a grid interface
Sch 8.3 TC A 4 | (1) | Each asset owner and grid owner must co-operate with the system operator to ensure that protection systems on both sides of a grid interface, which include main protection systems and back up protection systems, are co-ordinated so that a faulted asset is disconnected by the main protection system first and the other assets are not prematurely disconnected.
Sch 8.3 TC A 4 | (2) | A proposed grid interface, including the settings of any associated protection system, must be agreed between the relevant asset owner and the system operator before being implemented.
Sch 8.3 TC A 4 | (3) | Each asset owner must ensure that sufficient circuit breakers are provided for its assets so that each of its assets is able to be disconnected totally from the grid whenever a fault occurs within the asset.
Sch 8.3 TC A 4 | (4) | Each asset owner must ensure that it provides protection systems for its assets that are connected to, or form part of, the grid. Each asset owner must also ensure that as a minimum requirement―
Sch 8.3 TC A 4 | (4) (a) | such protection systems support the system operator in planning to comply, and complying, with the principal performance obligations and are designed, commissioned and maintained, and settings are applied, to achieve the following performance in a reliable manner: (i) disconnect any faulted asset in minimum practical time (taking into account selectivity margins and industry best design practice) and minimum disruption to the operation of the grid or other assets: (ii) be selective when operating, so that the minimum amount of assets are disconnected: (iii) as far as reasonably practicable, preserve power system stability; and
Sch 8.3 TC A 4 | (4) (b) | it provides duplicated main protection systems for each of its assets at voltages of 220 kV a.c. or above, other than busbars; and
Sch 8.3 TC A 4 | (4) (c) | it provides, for each of its 220 kV a.c. busbars― (i) a single main protection system and a back up protection system; or (ii) if the performance of its back up protection system does not meet the requirements of paragraph (a), a duplicated main protection system; and
Sch 8.3 TC A 4 | (4) (d) | it provides duplicated main protection systems for each of its busbars at voltages above 220 kV a.c; and
Sch 8.3 TC A 4 | (4) (e) | it designs, tests and maintains its main protection systems at voltages of 220 kV a.c. or above in accordance with the requirements set out in Appendix A; and
Sch 8.3 TC A 4 | (4) (f) | it provides a circuit breaker failure protection system, that need not be duplicated, for each circuit breaker at voltages of 220 kV a.c. or above. Circuit breaker duplication is not required; and
Sch 8.3 TC A 4 | (4) (g) | protection system design for a connection of assets to the grid at lower voltages must be similar to existing design practice in adjacent connections of assets to ensure coordination of protection systems.
Sch 8.3 TC A 4 | (5) (a) | At a point of connection to the grid― an asset owner, other than a grid owner, must provide a means of checking synchronisation before the switching of assets if it is possible that such switching may result in connection of parts of the New Zealand electric power system that are not synchronised;
Sch 8.3 TC A 5 |  | Specific requirements for generators
Sch 8.3 TC A 5 | (1) | Each generator must ensure that―
Sch 8.3 TC A 5 | (1) (a) | each of its generating units, and its associated control systems,― (i) supports the system operator to plan to comply, and to comply, with the principal performance obligations; and (ii) is able to synchronise at a stable frequency within the frequency range stated in the asset capability statement for that asset; and
Sch 8.3 TC A 5 | (1) (b) | the rate of change in the output of any of its generating units does not adversely affect the system operator's ability to plan to comply, and to comply, with the principal performance obligations. The rate of change must be adjustable to allow for changes in grid conditions; and
Sch 8.3 TC A 5 | (1) (c) | each of its generating units has a speed governor and/or frequency control system that― (i) provides stable performance with adequate damping; and (ii) has an adjustable droop over the range of 1% to 7%; and (iii) does not adversely affect the operation of the grid because of any of its non-linear characteristics; and (iv) operates with a dead band not exceeding the greater of: (A) ±0.1 Hertz; or (B) the inherent dead band of the generating unit, as agreed with the system operator acting reasonably; and
Sch 8.3 TC A 5 | (1) (d) | appropriate speed governor and/or frequency control system settings to be applied before commencing system tests for a generating unit are agreed between the system operator and the generator. The performance of the generating unit is then assessed by measurements from system tests and final settings are then applied to the generating unit before making it ready for service after those final settings are agreed between the system operator and the generator. An asset owner must not change speed governor and/or frequency control system settings without system operator approval.
Sch 8.3 TC A 5 | (1A) | For a generator with a generating unit that has electrically connected to a network prior to the commencement of the [name of the amending instrument], the requirement in subclause (1)(c)(iv) only applies from the time of the next periodic test of the generating unit carried out in accordance with Appendix B of Technical Code A following the commencement of the [name of the amending instrument].
Sch 8.3 TC A 5 | (1AB) | The requirement in subclause 1(c)(iv) does not apply to generating units for which geothermal heat is the primary power source.
Sch 8.3 TC A 5 | (2) | Each generator must ensure that each of its generating units connected to the grid is equipped with―
Sch 8.3 TC A 5 | (2) (a) | have a voltage control system with a voltage set point that is adjustable over the range of voltage set out in clause 8.23 and operates continuously in the voltage control mode when synchronised; and
Sch 8.3 TC A 5 | (2) (b) | in order to meet the asset owner performance obligations, ensure that each of its generating units is equipped with either― (i) a connection transformer with an appropriate range of taps on each transformer together with an on-load tap-changer; or (ii) assets to give a dynamic performance equivalent to those required by subparagraph (i).
Sch 8.3 TC A 5 | (2A) | Each embedded generator must at all times ensure that each of its embedded generating stations connected to a local network is equipped with, and operates when the conditions specified in subclause (2B) apply, a voltage control system that enables the embedded generating station to export or import reactive power through the embedded generating station’s point of connection to the local network so as to regulate voltage at the embedded generating station’s point of connection to the local network.
Sch 8.3 TC A 5 | (2B) | The conditions that apply under subclause (2A) are that the embedded generating station—
Sch 8.3 TC A 5 | (2B) (a) | electrically connects to the local network at the nominal voltage of the electrical busbar— (i) at which a grid owner has agreed to provide services to the local network owner; and (ii) that is electrically closest to the embedded generating station; and
Sch 8.3 TC A 5 | (2B) (b) | has a maximum continuous MW output power of 10 MW or more.
Sch 8.3 TC A 5 | (2C) | Subclause (2A) only applies in respect of an embedded generating station—
Sch 8.3 TC A 5 | (2C) (a) | if the distributor who operates the local network has not directed the embedded generator to operate the embedded generating station in an alternative voltage control mode (such as constant reactive power or constant power factor) for the purpose of enabling the distributor to operate the local network in accordance with good electricity industry practice; and
Sch 8.3 TC A 5 | (2C) (b) | that, if first electrically connected to a local network before 1 July 2027, is able to comply, without modification, with all the requirements in subclause (2A) and in clause 8.23A.
Sch 8.3 TC A 5 | (2D) | Subclause (2C) (b) ceases to apply in respect of an embedded generating station from the date—
Sch 8.3 TC A 5 | (2D) (a) | a modification is made to the embedded generating station that means it is able to comply with all the requirements in subclause (2A) and clause 8.23A; or
Sch 8.3 TC A 5 | (2D) (b) | the embedded generating station's maximum continuous MW output power increases by 5 MW or more above its maximum continuous MW output power immediately before 1 July 2027.
Sch 8.3 TC A 5 | (2E) | Each embedded generator must update the asset capability statement for an embedded generating station to―
Sch 8.3 TC A 5 | (2E) (a) | explain the extent to which the embedded generating station complies with the requirements of subclause (2A), where that subclause applies; and
Sch 8.3 TC A 5 | (2E) (b) | record any direction given in respect of the embedded generating station under subclause (2C) (a)
Sch 8.3 TC A 5 | (2F) | When preparing the information required under subclause (2E), an embedded generator is not required to undertake and provide power system studies that are additional to the power system studies the embedded generator must undertake for, and provide to, the distributor who operates the local network to which the embedded generating station is connected.
Sch 8.3 TC A 5 | (3) | If the output of more than 1 generating unit is controlled by a common control system, the generator must ensure that―
Sch 8.3 TC A 5 | (3) (a) | the common control system does not adversely affect the ability of the system operator to plan to comply, and to comply, with the principal performance obligations; and
Sch 8.3 TC A 5 | (3) (b) | the combined output from the generating units performs as though it were from 1 generating unit; and
Sch 8.3 TC A 5 | (3) (c) | the control system does not degrade the individual performance of any one generating unit.
Sch 8.3 TC A 5 | (4) | Each generator and grid owner must ensure that each of its assets is capable of operating under the voltage imbalance conditions stated in clause 4.9 of the Connection Code and, when operated within the limits stated in its asset capability statement, does not―
Sch 8.3 TC A 5 | (4) (a) | contribute unbalanced phase currents into the grid; or
Sch 8.3 TC A 5 | (4) (b) | aggravate any current imbalance that may occur on the grid.
Sch 8.3 TC A 5 | (5) | At some points of connection, a generator must ensure that its generating units have both main protection systems and back-up protection systems for nearby faults on the grid, if the necessity for, and the method of providing, such protection systems is agreed between the system operator and the generator.
Sch 8.3 TC A 8 |  | Records, tests and inspections
Sch 8.3 TC A 8 | (1) | Each asset owner must arrange for, and retain, records for each of its assets to demonstrate that the assets comply with the asset owner performance obligations and this technical code.
Sch 8.3 TC A 8 | (2) | In addition to the requirements for commissioning or testing in clause 2(6) to (8), each asset owner must carry out periodic testing of its assets and automatic under-frequency load shedding systems in accordance with Appendix B.
Sch 8.3 TC A 8 | (3) | If the system operator advises an asset owner that it reasonably believes that an asset may not comply with an asset owner performance obligation or this technical code, the asset owner must―
Sch 8.3 TC A 8 | (3) (a) | as soon as practicable, but no later than 30 days after receiving a written request, advise the system operator of its remedial or test plan for the assets; and
Sch 8.3 TC A 8 | (3) (b) | as soon as reasonably practicable undertake any remedial action or testing of its assets in accordance with its plan advised to the system operator in paragraph (a). The system operator may require such testing or remedial action to be undertaken in the presence of a system operator representative.
Sch 8.3 TC A 8 | (4) | Each asset owner must, at the request of the system operator, provide access to records of the performance or testing of an asset and access to inspect an asset.
CACTIS | Chapter 4 | Modelling requirements
CACTIS | 4.6 | Ensure M2 PowerFactory model(s) submitted as mandated in this chapter.
CACTIS | 4.6 | Ensure M2 TSAT model(s) submitted as mandated in this chapter.
CACTIS | 4.6 | Ensure M2 PSCAD model(s) submitted as mandated in this chapter.
CACTIS | Chapter 8 | General requirements for operational communications
CACTIS | 8.5 | Each voice or electronic communication between the system operator and an asset owner must be logged by the system operator and the asset owner. Unless otherwise agreed between the system operator and the asset owner, every voice instruction must be repeated back by the person receiving the instruction and confirmed by the person giving the instruction before the instruction is actioned.
CACTIS | 8.6 | The system operator and each asset owner must nominate and advise each other of the preferred points of contact and the alternative points of contact to be used by the system operator and the asset owner. Each asset owner must also nominate and advise the system operator of the person to receive instructions and formal notices as set out in Technical Code B of Schedule 8.3 of the Code. The preferred points of contact must include those to be used when the system operator instructs the asset owner, when the system operator sends formal notices to the asset owner and when the asset owner contacts the system operator. The alternative points of contact must be used only if the preferred points of contact are not available.
CACTIS | 8.7 | The grid owner and each other asset owner must nominate and advise each other of the preferred points of contact and the alternative points of contact to be used by the grid owner and the other asset owner for the purpose of communications regarding the availability of the grid owner’s data transmission communications. The alternative points of contact must only be used if the preferred points of contact are not available.
CACTIS |  | Specific requirements for voice communication
CACTIS | 8.8 | Each asset owner must have in place a primary means of communicating by voice between the control room of the asset owner and the system operator. The primary means of voice communication must use either―
CACTIS | 8.8 (a) | the grid owner’s speech network; or
CACTIS | 8.8 (b) | a widely available public switched telephone network that operates in real time and in full duplex mode.
CACTIS | 8.9 | Each asset owner must have in place a backup means of communicating by voice between the control room of the asset owner and the system operator. The backup means of voice communication―
CACTIS | 8.9 (a) | must be approved by the system operator (such approval not to be unreasonably withheld); and
CACTIS | 8.9 (b) | may include, but is not limited to, satellite phone or cellular phone; and
CACTIS | 8.9 (c) | may be used only if the primary means of voice communication described in paragraph 8.8 is unavailable or otherwise with the agreement of the system operator.
CACTIS | 8.10 | An asset owner who has a control room with, at any time, operational control of more than 299 MW of injection, offtake, or power flow must have 2 or more back up means of voice communication between the control room of the asset owner and the system operator, each of which must meet the requirements of paragraph 8.9.
CACTIS |  | Specific requirements for document transmission communication
CACTIS | 8.11 | Each asset owner must transmit information between its control room and the system operator in writing.
CACTIS | 8.12 | Despite paragraph 8.11, an asset owner may request the system operator to approve an alternative primary means of transmitting a document (such approval not to be unreasonably withheld).
CACTIS | 8.13 | Each asset owner must have in place a backup means of transmitting a document. The backup means of document transmission communication―
CACTIS | 8.13 (a) | must be approved by the system operator (such approval not to be unreasonably withheld); and
CACTIS | 8.13 (b) | may include, but is not limited to, voice communication or email; and
CACTIS | 8.13 (c) | may only be used if the primary means of document transmission described in paragraph 8.11 or 8.12 is unavailable or otherwise with the agreement of the system operator.
CACTIS |  | Specific requirements for data transmission communication
CACTIS | 8.14 | Each asset owner (other than a grid owner) must have in place―
CACTIS | 8.14 (a) | a primary means of transmitting data between the assets of the asset owner and a SCADA remote terminal unit of a grid owner; or
CACTIS | 8.14 (b) | if approved by the system operator (such approval not to be unreasonably withheld), a primary means of transmitting data between the assets of the asset owner and the system operator.
CACTIS | 8.16 | An asset owner must have in place a backup means of transmitting data for each type of indication and measurement specified in paragraph 8.23. The backup means of data transmission communication―
CACTIS | 8.16 (a) | must be approved by the system operator (such approval not to be unreasonably withheld); and
CACTIS | 8.16 (b) | may include, but is not limited to, use of voice communication or document transmission communication; and
CACTIS | 8.16 (c) | may only be used if the primary means of data transmission communication described in paragraph 8.14 or 8.15 is unavailable or otherwise with the agreement of the system operator.
CACTIS | 8.17 | Each asset owner must use reasonable endeavours to ensure that the primary means of communication described in paragraphs 8.8, 8.9, 8.12, 8.14 and 8.15 is available continuously.
CACTIS | 8.18 | If the primary means of communication described in paragraphs 8.8, 8.9, 8.12, 8.14 and 8.15 is unavailable, an asset owner must use reasonable endeavours to restore availability of the primary means of communication as soon as practicable.
CACTIS | 8.20 | Each asset owner must provide the relevant indications and measurements shown in the Required Indications and Measurements (in CACTIS starting at paragraph 8.23) to the system operator, in accordance with paragraphs 8.14 to 8.16. The system operator may require the asset owner to provide additional information if, in the reasonable opinion of the system operator, such information is required for the system operator to plan to comply, and to comply, with its principal performance obligations.
CACTIS | 8.21 | An asset owner must use reasonable endeavours to ensure that the accuracy of the measurements it provides to the system operator in accordance with paragraph 8.20 complies with the Required Indications and Measurements section (in CACTIS, starting at paragraph 8.23).
CACTIS | 8.22 | Each indication and measurement provided in accordance with paragraph 8.20 must be updated at the grid owner’s SCADA remote terminal or the system operator’s interface unit at least once every 8 seconds when provided by the primary means of data transmission communications.
CACTIS | 8.23 | A generator, grid owner, and connected asset owner must provide the indications and measurements listed in Table A (see CACTIS) and to the extent applicable, provide the indications and measurements listed in Tables B-J (see CACTIS).
CACTIS | Chapter 9 | High Speed Data Requirements
CACTIS | 9.3 | An asset owner must install a high-speed monitor at each of its generating stations and provide event data from the high-speed monitor to the system operator for post-event analysis and routine testing requirements in accordance with Chapter 7 (of CACTIS).
CACTIS | 9.4 | The asset owner must submit high-speed monitor data to the system operator in either a csv, ascii, or COMTRADE format.
CACTIS | 9.5 | High-speed monitor data must include the values listed in Table K below.
CACTIS | 9.6 | High-speed monitor data recording must be triggered according to Table L (see CACTIS) and must be global positioning system time stamped and recorded as follows: (a) pre-trigger, 10 seconds (b) post-trigger, 120 seconds; (c) at a resolution of 20 milliseconds or better
Sch 8.3 TC A AppA 1 |  | General requirements
Sch 8.3 TC A AppA 1 |  | An asset owner must design, test and maintain all main protection systems at voltages of 220 kV a.c. or above to conform to electricity industry standards and practices as they are reasonably and ordinarily applied by a skilled and experienced asset owner to current installations at voltages of 220 kV a.c. or above in the New Zealand context.
Sch 8.3 TC A AppA 2 |  | Specific requirements for main protection systems
Sch 8.3 TC A AppA 2 |  | Main protection systems at voltages of 220 kV a.c. or above must meet the requirements set out below:
Sch 8.3 TC A AppA 2 | (a) | either test blocks or both test switches and test terminals must be provided:
Sch 8.3 TC A AppA 2 | (b) | the eletrical continuity of fused protection circuits, including d.c. and voltage transformer circuits must be supervised:
Sch 8.3 TC A AppA 2 | (c) | the electrical continuity of circuit breaker trip ciruits must be supervised.
Sch 8.3 TC A AppA 3 |  | Specific requirements for duplicated main protection systems
Sch 8.3 TC A AppA 3 |  | Duplicated main protection systems (the 2 components of which are referred to in this appendix as main 1 protection and main 2 protection) at voltages of 220 kV a.c. or above must meet the requirements set out below:
Sch 8.3 TC A AppA 3 | (a) | duplicated main protection systems must be designed with sufficient coverage and probability of detection that if any or all parts of 1 main protection system fail, the other main protection system electrically disconnects a faulted asset before a back up protection system initiates the electrical disconnection of other non-faulted assets:
Sch 8.3 TC A AppA 3 | (b) | the d.c. supply to duplicated main protection systems must consist of 2 independent station batteries, each with its own charger, supervision, and with a capacity and carry over duty to cover charger failure until repair and restoration. Station batteries may only feed a common primary d.c busbar provided that the busbar is insulated and isolated from earth:
Sch 8.3 TC A AppA 3 | (c) | the d.c supply to each duplicated main protection system must be independently fused at the primary d.c. busbar:
Sch 8.3 TC A AppA 3 | (d) | the manufacturer of main 1 protection must not be the same as the manufacturer of main 2 protection, unless one protection uses different measurement principles from the other:
Sch 8.3 TC A AppA 3 | (e) | the current transformer core (or an equivalent instrument) and the cabling associated with that current transformer core or equivalent instrument (as the case may be) used for main 1 protection must be independent from that used for main 2 protection:
Sch 8.3 TC A AppA 3 | (f) | if a voltage transformer supply is required for main 1 or main 2 protection-
Sch 8.3 TC A AppA 3 | (f) (i) | the supply must be fused at the voltage transformer; and
Sch 8.3 TC A AppA 3 | (f) (ii) | the supply for main 1 protection must use an independent fuse and cable from those used for main 2 protection:
Sch 8.3 TC A AppA 3 | (g) | main 1 protection must use, in each of the circuit breakers tripped by that main 1 protection, an independent trip coil from that used for main 2 protection:
Sch 8.3 TC A AppA 3 | (h) | if protection signalling is used, main 1 protection must use a signal channel over an independent bearer on a different route from that used for main 2 protection:
Sch 8.3 TC A AppA 3 | (i) | main 1 protection cabling must be segreated from main 2 protection cabling in a manner that minimised the risk of common mode failure of main 1 and 2 protection and minimises the number of connections in any protection circuit.
Sch 8.3 TC A AppA 4 |  | Existing equipment
Sch 8.3 TC A AppA 4 |  | Despite clauses 1 and 3-
Sch 8.3 TC A AppA 4 | (a) | a current transformer comissioned before 31 May 2007 is not required to comply with clause 3(e) until the current transformer is replaced; and
Sch 8.3 TC A AppA 4 | (b) | a circuit breaker commissioned before 31 May 2007, if not designed to incorporate a second trip coil, is not required comply with clause 3(g) until the current circuit breaker is replaced; and
Sch 8.3 TC A AppA 4 | (c) | cabling commissioned before 31 May 2007, if not designed to be segregated, is not required to comply with the segreation requirements of clause 3(i) until the cabling is replaced.

## Dropdown ref for Checksheet (hidden)
Column1
Model Validation Report
Protection Settings Report
System Operator Connection Studies
Asset Capability Statement (ACS)
Control Parameters
Protection Coordination Agreement
Agreement of Governor Settings
GL-PC-437 Realtime Telephone Directory
ICCP Communication Infrastructure
Compliance by dispensation or equivalence
ICCP Dataset
Code Commissioning Plan
Engineering Methodology
Distributor Agreement Documentation
Not Applicable/Not Required
Other (explain in comment)

## Example
Clause | Subclause | Clause Description | Asset Owner Evidence [e.g. ACS, Connection Study etc.] | Asset Owner Comment [Where in the evidence is compliance demonstrated?]
8.17 |  | Contribution by injections to overall frequency management: Each generator (while synchronised) and the HVDC owner must at all times ensure that its assets, other than any generating units within an excluded generating station, make the maximum possible injection contribution to maintain frequency within the normal band (and to restore frequency to the normal band). Any such contribution must be assessed against the technical codes. | Control Parameters | Control parameters are outlined in page 10, in table 2 of the model validation report. | This Is an example of how
8.19 |  | Contributions to frequency support in under-frequency events:
8.19 (1) |  | Subject to subclause (3), each generator must at all times ensure that, while connected, its assets, other than any excluded generating stations, contribute to supporting frequency by remaining synchronised, ensuring that each of its generating units can and does, at a minimum, sustain pre-event output―
8.19 (1) | (a) | at all times when the frequency is above 47.5 Hertz; and | Protection Coordination Report | Under Frequency settings are outlined in section 5.5.2.3 Underfrequency (UF(DefT)) in the protection coordination report.
8.19 (1) | (b) | for at least 120 seconds when the frequency is 47.5 Hertz; and | Protection Coordination Report | Under Frequency settings are outlined in section 5.5.2.3 Underfrequency (UF(DefT)) in the protection coordination report.
8.19 (1) | (c) | for at least 20 seconds when the frequency is 47.3 Hertz; and | Protection Coordination Report | Under Frequency settings are outlined in section 5.5.2.3 Underfrequency (UF(DefT)) in the protection coordination report.
8.19 (1) | (d) | for at least 5 seconds when the frequency is 47.1 Hertz; and | Protection Coordination Report | Under Frequency settings are outlined in section 5.5.2.3 Underfrequency (UF(DefT)) in the protection coordination report.
8.19 (1) | (e) | for at least 0.1 seconds when the frequency is 47.0 Hertz; and | Protection Coordination Report | Under Frequency settings are outlined in section 5.5.2.3 Underfrequency (UF(DefT)) in the protection coordination report.
8.19 (1) | (f) | at any frequencies between those specified in paragraphs (b) to (e) for times derived by linear interpolation. | Acknowledged (provide supporting notes in comments) | The relay works in in discreet steps which covers the points that are linearly extrapolated.
8.19 (2) |  | If the inherent characteristics and design of a generator's generating unit are such that it is reasonably able to operate beyond the above requirements, the generator must declare such capabilities in accordance with clause 2(5) of Technical Code A of Schedule 8.3. | Asset Capability Statement (ACS) | The general specification of the V-ABC XX MW generator can be found under the attachments on ACS under Manufacturer Specification. Page 5, Table 9-4 outlines the operating envelope w.r.t frequency for the WTG connected to the grid i.e. nominal frequency (Hz), frequency gradient (Hz/sec) and Table 9-5 outlines the minimum and maximum operating frequency, mechanical deadbands and inherent frequency deadband range.
8.19 (3) |  | Each South Island generator must ensure that each of its assets, other than excluded generating units, remains synchronised, and can and do, at a minimum, sustain pre-event output―
8.19 (3) | (a) | at all times when the frequency is above 47 Hertz; and | Not Applicable/Not Required | NI Connected Asset
8.19 (3) | (b) | for 30 seconds if the frequency falls below 47 Hertz but not below 45 Hertz. | Not Applicable/Not Required | NI Connected Asset
8.22 |  | Voltage Range AOPOs
8.22 | (2) | Each generator with a point of connection to the grid must at all times ensure that its assets are capable of being operated, and do operate, when the grid is operated within the range of voltages set out in subclause (1). | Protection Coordination Report | Pg 19 of the protection coordination report (attached to the ACS) shows the Under voltage setting of the generator in section 5.5.2.1. Model Validation Report: During the Open Circuit test, the generator was subjected to it's voltage rage capability determine its saturation curve. The results for this test can be found in Appendix A, Pg 32 of the model validation report. ACS: The manufacturer specification document ("Manufacturer Specification - V-XYZ - 4MW") is attached to the ACS also shows the inherent capability of the generator to operate between +-15% which proves the capability to operate within the specified ranges in the code. This can be seen in Table 7, on page 6.
8.23 |  | Voltage support AOPOs
8.23 |  | Each generator with a point of connection to the grid must at all times ensure that its assets―
8.23 | (a) | when the voltage at its grid injection point is within the applicable range of nominal voltage, are capable of exporting (over excited) when synchronised and made available for dispatch by the system operator, a minimum net reactive power which is 50% of the maximum continuous MW output power as measured at the following generating unit terminals: | Model Validation Report | In the model validation report, the generator capability test shows the PQ capability of the generator. This can be seen on Pg 13 of the model validation report (Attached to the ACS). The generator capability curve is uploaded as an attachment to the ACS ("Gen_Cap_Curve.pdf").
8.23 | (b) | when the voltage at its grid injection point is within the applicable range of nominal voltage, are capable of importing (under excited) when synchronised and made available for dispatch by the system operator, a minimum net reactive power which is 33% of the maximum continuous MW output power as measured at the generating unit terminals as set out below: | Model Validation Report | In the model validation report, the generator capability test shows the PQ capability of the generator. This can be seen on Pg 13 of the model validation report (Attached to the ACS).
8.23 | (c) | when synchronised, continuously operate in a manner that supports voltage and voltage stability on the grid in compliance with the technical codes. | Acknowledged (provide supporting notes in comments) | This is noted, the small voltage disturbance test shows that the machine responds to stabilise the voltage. It is expected to continuously operate stably. The information in the technical codes will provide evidence that the generators voltage control system operate in a stable manner.
8.25 | (3) | Each asset owner and each purchaser must provide communication facilities that comply with the technical codes or otherwise as the system operator reasonably requests, to assist the system operator in planning to comply, and complying, with its principal performance obligations and achieving the dispatch objective. | Other (explain in comment) | This is proven in the technical codes.
8.25A |  | Fault Ride Through
8.25A | (1) | Each generator must ensure that each of its assets, when electrically connected to a network, is capable of remaining stable and electrically connected when the grid's lowest line-to-line voltage is within the no-trip zone shaded and marked "No-trip zone" in Figure 8.1 (for an asset in the North Island) or Figure 8.2 (for an asset in the South Island) for the period of 6 seconds immediately following the commencement of a zero impedance three-phase short circuit fault, or an unbalanced short circuit fault, on any part of the grid at 110 kV or 220 kV in the island in which the asset is connected | System Operator Connection Studies | The fault ride through report ("FRT_STUDIES.pdf") and power system study files ("FRT_Models.pfd") are uploaded as an attachment in the ACS. These studies prove that the generator can ride through faults and remain connected within the fault ride through envelope. The results can be seen in pgs 4-6.
8.25A | (2) | Each generator must ensure that each of its assets, when electrically connected to a network, is capable of remaining stable and electrically connected when the highest line-to-line voltage at Haywards 220 kV bus (for an asset in the North Island) or Benmore 220 kV bus (for an asset in the South Island) is within the no-trip zone shaded and marked "No-trip zone" in Figure 8.3 for the period of 1 second immediately following the commencement of a trip of the HVDC link | System Operator Connection Studies | The fault ride through report ("FRT_STUDIES.pdf") and power system study files ("FRT_Models.pfd") are uploaded as an attachment in the ACS. These studies prove that the generator can ride through faults and remain connected within the fault ride through envelope. The results can be seen in pgs 4-6.
8.25A | (3) | Whether a generator is complying with subclause (2) must be determined using power system analysis that uses (a) study cases provided by the relevant grid owner; and (b) relevant system assumptions provided by the system operator. | System Operator Connection Studies | The fault ride through report ("FRT_STUDIES.pdf") and power system study files ("FRT_Models.pfd") are uploaded as an attachment in the ACS.
8.25A | (4) | A generator is not required to comply with subclause (1) in respect of an asset in the event of a fault of a type described in subclause (1) if the asset becomes isolated from the grid as a result of the fault. | Acknowledged (provide supporting notes in comments) | This is noted.
8.25A | (5) | A generating unit need not comply with subclause (1) to the extent that it is complying with a special protection scheme approved by the system operator. | Acknowledged (provide supporting notes in comments) | This is noted. Generating Station XX does not have an SPS approved by the System Operator.
8.25B | (1) | Each generator must ensure that each of its generating units generates reactive current to oppose the change in its terminal voltage without exceeding the maximum transient reactive current specified in the generator's asset capability statement for the period of 6 seconds immediately following the commencement of a fault on the grid of a type described in clause 8.25A(1) | Model Validation Report | The small voltage disturbance test shows that the machine responds to oppose the change in voltage. This test can be found in "Gen Model Validation Report.pdf" in section 5.2.1 on page 17. The report is uploaded to the ACS.
8.25B | (2) | Each generator must ensure that each of its generating units provides active power output relative to pre-fault active power output at least in proportion to the grid voltage at the grid injection point for the period of 6 seconds immediately following the clearance of a fault on the grid of a type described in clause 8.25A(1).
8.25B | (3) | Subclause (2) does not apply to a wind generating station if there has been a reduction in the intermittent wind power source during the 6 seconds following the commencement of the fault. | Not Applicable | Gen XX is synchronous
Use of additional equipment
8.25C | (a) to (c ) | A generator may comply with clause 8.25A in relation to a generating station by (a) ensuring that the performance of generating units that comprise the generating station comply; or (b) installing additional equipment within the generating station; or (c) a combination of the methods described in paragraphs (a) and (b).
8.25D |  | Application
Clauses 8.25A and 8.25B do not apply (a) to a wind generating station when it operates at less than 5% of rated MW; or (b) to any asset at an excluded generating station.
Sch 8.3 TC A 2 |  | General requirements
Sch 8.3 TC A 2 | (5) | Each asset owner must provide the system operator with an asset capability statement in the form from time to time published by the system operator for each asset that is proposed to be connected, or is connected to, or forms part of the grid. The asset capability statement must―
Sch 8.3 TC A 2 | (5) (a) | include all information reasonably requested by the system operator so as to allow the system operator to determine the limitations in the operation of the asset that the system operator needs to know for the safe and efficient operation of the grid; and
Sch 8.3 TC A 2 | (5) (b) | include any modelling data for the planning studies, as reasonably requested by the system operator; and
Sch 8.3 TC A 2 | (5) (c) | be updated and reissued to the system operator as information and design development progresses through the study, design, manufacture, testing and commissioning phases; and
Sch 8.3 TC A 2 | (5) (d) | be complete and up to date before the commissioning of the asset; and
Sch 8.3 TC A 2 | (5) (e) | be complete and up to date at all times while the asset is connected to, or forms part of, the grid.
Sch 8.3 TC A 3 |  | Requirements for asset information
Sch 8.3 TC A 3 | (1) | In accordance with clause 8.25(4), the following information is required by the system operator to assist it to plan to comply, and to comply, with its principal performance obligations:
Sch 8.3 TC A 3 | (1) (a) | sufficient information must be exchanged between the system operator and the asset owner to ensure that both fully understand the implications of any changes to the asset capability statement or of any proposed connection of the relevant assets to the grid or to the local network. This information must be exchanged in accordance with a timetable agreed to by the system operator and the asset owner:
Sch 8.3 TC A 3 | (1) (b) | if reasonably requested by the system operator, the asset owner must provide sufficient information to the system operator to demonstrate the compliance of the asset owner's assets with the asset owner performance obligations and the technical codes.
Sch 8.3 TC A 4 |  | Requirements for the grid and a grid interface
Sch 8.3 TC A 4 | (1) | Each asset owner and grid owner must co-operate with the system operator to ensure that protection systems on both sides of a grid interface, which include main protection systems and back up protection systems, are co-ordinated so that a faulted asset is disconnected by the main protection system first and the other assets are not prematurely disconnected. | Protection Coordination Agreement | The Protection Coordination Agreement is uploaded to the ACS.
Sch 8.3 TC A 4 | (2) | A proposed grid interface, including the settings of any associated protection system, must be agreed between the relevant asset owner and the system operator before being implemented. | Protection Coordination Agreement | The Protection Coordination Agreement is uploaded to the ACS.
Sch 8.3 TC A 4 | (3) | Each asset owner must ensure that sufficient circuit breakers are provided for its assets so that each of its assets is able to be disconnected totally from the grid whenever a fault occurs within the asset. | Protection Coordination Agreement | The Protection Coordination Agreement is uploaded to the ACS.
Sch 8.3 TC A 4 | (4) | Each asset owner must ensure that it provides protection systems for its assets that are connected to, or form part of, the grid. Each asset owner must also ensure that as a minimum requirement―
Sch 8.3 TC A 4 | (4) (a) | such protection systems support the system operator in planning to comply, and complying, with the principal performance obligations and are designed, commissioned and maintained, and settings are applied, to achieve the following performance in a reliable manner: (i) disconnect any faulted asset in minimum practical time (taking into account selectivity margins and industry best design practice) and minimum disruption to the operation of the grid or other assets: (ii) be selective when operating, so that the minimum amount of assets are disconnected: (iii) as far as reasonably practicable, preserve power system stability; and
Sch 8.3 TC A 4 | (4) (b) | it provides duplicated main protection systems for each of its assets at voltages of 220 kV a.c. or above, other than busbars; and
Sch 8.3 TC A 4 | (4) (c) | it provides, for each of its 220 kV a.c. busbars― (i) a single main protection system and a back up protection system; or (ii) if the performance of its back up protection system does not meet the requirements of paragraph (a), a duplicated main protection system; and
Sch 8.3 TC A 4 | (4) (d) | it provides duplicated main protection systems for each of its busbars at voltages above 220 kV a.c; and
Sch 8.3 TC A 4 | (4) (e) | it designs, tests and maintains its main protection systems at voltages of 220 kV a.c. or above in accordance with the requirements set out in Appendix A; and
Sch 8.3 TC A 4 | (4) (f) | it provides a circuit breaker failure protection system, that need not be duplicated, for each circuit breaker at voltages of 220 kV a.c. or above. Circuit breaker duplication is not required; and
Sch 8.3 TC A 4 | (4) (g) | protection system design for a connection of assets to the grid at lower voltages must be similar to existing design practice in adjacent connections of assets to ensure coordination of protection systems.
Sch 8.3 TC A 4 | (5) (a) | At a point of connection― an asset owner, other than a grid owner, must provide a means of checking synchronisation before the switching of assets if it is possible that such switching may result in connection of parts of the New Zealand electric power system that are not synchronised;
Sch 8.3 TC A 5 |  | Specific requirements for generators
Sch 8.3 TC A 5 | (1) | Each generator must ensure that―
Sch 8.3 TC A 5 | (1) (a) | each of its generating units, and its associated control systems,― (i) supports the system operator to plan to comply, and to comply, with the principal performance obligations; and (ii) is able to synchronise at a stable frequency within the frequency range stated in the asset capability statement for that asset; and
Sch 8.3 TC A 5 | (1) (b) | the rate of change in the output of any of its generating units does not adversely affect the system operator's ability to plan to comply, and to comply, with the principal performance obligations. The rate of change must be adjustable to allow for changes in grid conditions; and
Sch 8.3 TC A 5 | (1) (c) | each of its generating units has a speed governor that― (i) provides stable performance with adequate damping; and (ii) has an adjustable droop over the range of 1% to 7%; and (iii) does not adversely affect the operation of the grid because of any of its non-linear characteristics; and
Sch 8.3 TC A 5 | (1) (d) | appropriate speed governor settings to be applied before commencing system tests for a generating unit are agreed between the system operator and the generator. The performance of the generating unit is then assessed by measurements from system tests and final settings are then applied to the generating unit before making it ready for service after those final settings are agreed between the system operator and the generator. An asset owner must not change speed governor settings without system operator approval. | Agreement of Governor Settings | The agreement of the governor settings can be found in the ACS as an attachment.
Sch 8.3 TC A 5 | (2) | Each grid-connected generator must―
Sch 8.3 TC A 5 | (2) (a) | have an excitation and voltage control system with a voltage set point that is adjustable over the range of voltage set out in clause 8.23 and operates continuously in the voltage control mode when synchronised; and
Sch 8.3 TC A 5 | (2) (b) | in order to meet the asset owner performance obligations, ensure that each of its generating units is equipped with either― (i) a connection transformer with an appropriate range of taps on each transformer together with an on-load tap-changer; or (ii) assets to give a dynamic performance equivalent to those required by subparagraph (i).
Sch 8.3 TC A 5 | (3) | If the output of more than 1 generating unit is controlled by a common control system, the generator must ensure that―
Sch 8.3 TC A 5 | (3) (a) | the common control system does not adversely affect the ability of the system operator to plan to comply, and to comply, with the principal performance obligations; and
Sch 8.3 TC A 5 | (3) (b) | the combined output from the generating units performs as though it were from 1 generating unit; and
Sch 8.3 TC A 5 | (3) (c) | the control system does not degrade the individual performance of any one generating unit.
Sch 8.3 TC A 5 | (4) | Each generator and grid owner must ensure that each of its assets is capable of operating under the voltage imbalance conditions stated in clause 4.9 of the Connection Code and, when operated within the limits stated in its asset capability statement, does not―
Sch 8.3 TC A 5 | (4) (a) | contribute unbalanced phase currents into the grid; or
Sch 8.3 TC A 5 | (4) (b) | aggravate any current imbalance that may occur on the grid.
Sch 8.3 TC A 5 | (5) | At some points of connection, a generator must ensure that its generating units have both main protection systems and back-up protection systems for nearby faults on the grid, if the necessity for, and the method of providing, such protection systems is agreed between the system operator and the generator.
Sch 8.3 TC A 8 |  | Records, tests and inspections
Sch 8.3 TC A 8 | (1) | Each asset owner must arrange for, and retain, records for each of its assets to demonstrate that the assets comply with the asset owner performance obligations and this technical code.
Sch 8.3 TC A 8 | (2) | In addition to the requirements for commissioning or testing in clause 2(6) to (8), each asset owner must carry out periodic testing of its assets and automatic under-frequency load shedding systems in accordance with Appendix B.
Sch 8.3 TC A 8 | (3) | If the system operator advises an asset owner that it reasonably believes that an asset may not comply with an asset owner performance obligation or this technical code, the asset owner must―
Sch 8.3 TC A 8 | (3) (a) | as soon as practicable, but no later than 30 days after receiving a written request, advise the system operator of its remedial or test plan for the assets; and
Sch 8.3 TC A 8 | (3) (b) | as soon as reasonably practicable undertake any remedial action or testing of its assets in accordance with its plan advised to the system operator in paragraph (a). The system operator may require such testing or remedial action to be undertaken in the presence of a system operator representative.
Sch 8.3 TC A 8 | (4) | Each asset owner must, at the request of the system operator, provide access to records of the performance or testing of an asset and access to inspect an asset.
Sch 8.3 TC C 2 |  | Application - This technical code applies to all asset owners except for excluded generating stations
Sch 8.3 TC C 3 |  | General requirements for operational communications
Sch 8.3 TC C 3 | (1) | Each voice or electronic communication between the system operator and an asset owner must be logged by the system operator and the asset owner. Unless otherwise agreed between the system operator and the asset owner, every voice instruction must be repeated back by the person receiving the instruction and confirmed by the person giving the instruction before the instruction is actioned. | GL-PC-437 Realtime Telephone Directory | The contacts were checked and remain unchanged.
Sch 8.3 TC C 3 | (2) | The system operator and each asset owner must nominate and advise each other of the preferred points of contact and the alternative points of contact to be used by the system operator and the asset owner. Each asset owner must also nominate and advise the system operator of the person to receive instructions and formal notices as set out in Technical Code B. The preferred points of contact must include those to be used when the system operator instructs the asset owner, when the system operator sends formal notices to the asset owner and when the asset owner contacts the system operator. The alternative points of contact must be used only if the preferred points of contact are not available. | GL-PC-437 Realtime Telephone Directory | The contacts were checked and updated.
Sch 8.3 TC C 3 | (3) | The grid owner and each other asset owner must nominate and advise each other of the preferred points of contact and the alternative points of contact to be used by the grid owner and the other asset owner for the purpose of communications regarding the availability of the grid owner’s data transmission communications. The alternative points of contact must only be used if the preferred points of contact are not available. | GL-PC-437 Realtime Telephone Directory | Details have been checked and are correct.
Sch 8.3 TC C 4 |  | Specific requirements for voice communication
Sch 8.3 TC C 4 | (1) | Each asset owner must have in place a primary means of communicating by voice between the control room of the asset owner and the system operator. The primary means of voice communication must use either―
Sch 8.3 TC C 4 | (1) (a) | the grid owner’s speech network; or
Sch 8.3 TC C 4 | (1) (b) | a widely available public switched telephone network that operates in real time and in full duplex mode.
Sch 8.3 TC C 4 | (2) | Each asset owner must have in place a backup means of communicating by voice between the control room of the asset owner and the system operator. The backup means of voice communication―
Sch 8.3 TC C 4 | (2) (a) | must be approved by the system operator (such approval not to be unreasonably withheld); and
Sch 8.3 TC C 4 | (2) (b) | may include, but is not limited to, satellite phone or cellular phone; and
Sch 8.3 TC C 4 | (2) (c) | may be used only if the primary means of voice communication described in subclause (1) is unavailable or otherwise with the agreement of the system operator. | Other (explain in comment) | Acknowledged, no action
Sch 8.3 TC C 4 | (3) | An asset owner who has a control room with, at any time, operational control of more than 299 MW of injection, offtake, or power flow must have 2 or more back up means of voice communication between the control room of the asset owner and the system operator, each of which must meet the requirements of subclause (2).
Sch 8.3 TC C 5 |  | Specific requirements for document transmission communication
Sch 8.3 TC C 5 | (1) | Each asset owner must transmit information between its control room and the system operator in writing.
Sch 8.3 TC C 5 | (2) | An asset owner may request the system operator to approve an alternative primary means of transmitting a document (such approval not to be unreasonably withheld).
Sch 8.3 TC C 5 | (3) | Each asset owner must have in place a backup means of transmitting a document. The backup means of document transmission communication―
Sch 8.3 TC C 5 | (3) (a) | must be approved by the system operator (such approval not to be unreasonably withheld); and
Sch 8.3 TC C 5 | (3) (b) | may include, but is not limited to, voice communication or email; and
Sch 8.3 TC C 5 | (3) (c) | may only be used if the primary means of document transmission described in subclause (1) or (2) is unavailable or otherwise with the agreement of the system operator.
Sch 8.3 TC C 6 |  | Specific requirements for data transmission communication
Sch 8.3 TC C 6 | (1) | Each asset owner (other than a grid owner) must have in place―
Sch 8.3 TC C 6 | (1) (a) | a primary means of transmitting data between the assets of the asset owner and a SCADA remote terminal unit of a grid owner; or | ICCP Communication Infrastructure | Company XX currently has an existing ICCP connection between Company XX and Transpower. The end to end infrastructure is confirmed to have a primary and backup means of transmitting data. See email ("RE: ICCP Infrastructure - confirmed.msg") which is uploaded to the ACS.
Sch 8.3 TC C 6 | (1) (b) | if approved by the system operator (such approval not to be unreasonably withheld), a primary means of transmitting data between the assets of the asset owner and the system operator.
Sch 8.3 TC C 6 | (3) | Each asset owner must have in place a backup means of transmitting data for each type of indication and measurement specified in Appendix A of this technical code. The backup means of data transmission communication―
Sch 8.3 TC C 6 | (3) (a) | must be approved by the system operator (such approval not to be unreasonably withheld); and
Sch 8.3 TC C 6 | (3) (b) | may include, but is not limited to, use of voice communication or document transmission communication; and
Sch 8.3 TC C 6 | (3) (c) | may only be used if the primary means of data transmission communication described in subclause (1) or (2) is unavailable or otherwise with the agreement of the system operator.
Sch 8.3 TC C 7 | (1) | Each asset owner must use reasonable endeavours to ensure that the primary means of communication described in clauses 4(1), 5(1) or (2), and 6(1) or (2) is available continuously.
Sch 8.3 TC C 7 | (2) | If the primary means of communication described in clauses 4(1), 5(1) or (2), and 6(1) or (2) is unavailable, an asset owner must use reasonable endeavours to restore availability of the primary means of communication as soon as practicable.
Sch 8.3 TC C 9 | (1) | Each asset owner must provide the relevant indications and measurements shown in Appendix A to the system operator, in accordance with clause 6. The system operator may require the asset owner to provide additional information if, in the reasonable opinion of the system operator, such information is required for the system operator to plan to comply, and to comply, with its principal performance obligations. | ICCP Dataset | The final dataset is in the updated Data Transmission Agreement, as part of the appendix. Signed copy sent to Jane Doe at Customer Solutions.
Sch 8.3 TC C 9 | (2) | The asset owner must use reasonable endeavours to ensure that the accuracy of the measurements it provides to the system operator in accordance with subclause (1) complies with Appendix A. | ICCP Dataset | The email provided on the 21st of Dec 2021, send to John Doe, indicates that the accuracy of the measurements. A comparison document in the attachments on the ACS ("Indications.pdf") show the indications and onsite measurements meet the accuracy requirements in the Code.
Sch 8.3 TC C 9 | (3) | Each indication and measurement provided in accordance with subclause (1) must be updated at the grid owner’s SCADA remote terminal or the system operator’s interface unit at least once every 8 seconds when provided by the primary means of data transmission communications. | ICCP Dataset | An email sent on 21 Dec 2021 to John Doe confirms that this requirement was tested and performing as expected.
Column1
Model Validation Report
Protection Coordination Report
System Operator Connection Studies
Asset Capability Statement (ACS)
Control Parameters
Protection Coordination Agreement
Agreement of Governor Settings
GL-PC-437 Realtime Telephone Directory
ICCP Communication Infrastructure
ICCP Dataset
Not Applicable/Not Required
Other (explain in comment)
This is an EXAMPLE to show what level of information the System Operator requires. We provide this as an indication only; your sources may differ.
Note that our example mentions fewer Code clauses than the checksheet in order to showcase a range of evidence you might use.
Use examples relevant to your asset.
You are responsible for meeting your obligations in the Code.

## Revision History
Revision | Revised on | Revised by | Reviewed by | Description
1 | 2024-12-12 | Ivani Molver, Cris Cucerzan | Engineering Assurance Team | Updated user interface.
2 | 2024-12-18 | Ivani Molver, Cris Cucerzan | Engineering Assurance Team | Finalised user interface and example sheet.
3 | 2025-02-07 | Ivani Molver | Cris Cucerzan | Added revision history.
4 | 2025-05-27 | Ivani Molver |  | 1. Added Tech Code A AppA. 2. Updated clauses to match latest release of the Code.
5 | 2026-06-26 | Cris Cucerzan |  | 1. Added Voltage and Frequency Changes based on March 2026 EA Decision Papers