## Front Page - Contents
Date Updated | 2025-09-26
Tab | Contents
Demand Assumptions | Monthly demand assumptions for ERC and SSTs
Supply Assumptions | Generation supply assumptions for ERCs and SSTs
Planned Generator Outages | Outages used in the ERCs
HVDC Assumptions | HVDC Restrictions in Transfer for ERCs and SSTs
Thermal Fuel Generation | Aggregated thermal generation from the ERCs

## Demand Assumptions
Date | NI Demand | SI Demand
2025-02-01 | 463.3472 | 202.0639 | Notes - The values shown are weekly averages (GWh) for North and South Islands. - These South Island demand values do not include demand at the NZAS Tiwai site.
2025-03-01 | 460.6065 | 189.6411
2025-04-01 | 476.5992 | 196.4801
2025-05-01 | 503.0794 | 206.6595
2025-06-01 | 544.145 | 215.1477
2025-07-01 | 552.2563 | 212.0768
2025-08-01 | 545.83 | 208.193
2025-09-01 | 519.0017 | 200.5808
2025-10-01 | 484.5469 | 194.0658
2025-11-01 | 466.6935 | 193.9238
2025-12-01 | 452.6835 | 186.6144
2026-01-01 | 456.2506 | 193.863
2026-02-01 | 469.0787 | 199.6999
2026-03-01 | 466.1621 | 187.1835
2026-04-01 | 483.2025 | 193.8396
2026-05-01 | 510.8862 | 204.7602
2026-06-01 | 549.1436 | 216.2581
2026-07-01 | 556.9542 | 214.5165
2026-08-01 | 550.5201 | 210.9461
2026-09-01 | 523.9902 | 203.2285
2026-10-01 | 488.4377 | 197.1009
2026-11-01 | 470.4879 | 195.4108
2026-12-01 | 456.3736 | 188.8745
2027-01-01 | 463.0543 | 197.1586
2027-02-01 | 475.6149 | 203.8537
2027-03-01 | 473.3869 | 190.5422
2027-04-01 | 505.8947 | 203.5173
2027-05-01 | 533.0779 | 214.7405
2027-06-01 | 572.3643 | 225.9025
2027-07-01 | 555.766 | 214.2729
2027-08-01 | 549.1786 | 212.0739
2027-09-01 | 523.105 | 203.949
2027-10-01 | 487.3366 | 197.9467
2027-11-01 | 471.1085 | 195.3413

## Supply Assumptions
Generator | Capacity (MW) | Generation profile | Island | Fuel Type | Indicative Commissioning Date (calendar quarter) | Commissioning completion date | Decommissioning Date | Comments
Clandeboye Solar Farm | 27 | Profiled output | SI | Solar | 2026 Q3
Kaiwaikawe | 77 | Based on historical wind sequences / Profiled output | NI | Wind | 2026 Q3
Ruakaka Solar Farm | 130 | Profiled output | NI | Solar | 2026 Q4
Kowhai Park Solar Farm | 170 | Profiled output | SI | Solar | 2026 Q3
Huntly Battery | 102 | Profiled output | NI | Battery | 2026 Q2
Kaiwera Downs 2 | 152 | Based on historical wind sequences / Profiled output | SI | Wind | 2026 Q2
Tauhei Solar Farm | 150 | Profiled output | NI | Solar | 2026 Q2
Edgecumbe Solar Farm (FNSF) | 27 | Profiled output | NI | Solar | 2026 Q1
Glenbrook Battery | 100 | Profiled output | NI | Battery | 2025 Q4
Ngatamariki (new unit) | 54 | Profiled output | NI | Geothermal | 2025 Q4
Taiohi Solar Farm | 22 | Profiled output | NI | Solar | 2025 Q4
TOPP2 | 55 | Profiled output | NI | Geothermal | 2025 Q4
Whitianga Solar Farm | 23 | Profiled output | NI | Solar | 2025 Q4
GDS Papareireiā | 17 | Profiled output | NI | Solar | 2025 Q4
Twin Rivers solar Farm | 25 | Profiled output | NI | Solar | 2025 Q4
Te Herenga o Te Ra Solar Farm Waiotahi | 31 | Profile output | NI | Solar |  | 2025-07-25
Pukenui Solar Farm | 17 | Profiled output | NI | Solar |  | 2025-06-16
RUK Battery | 100 | Profiled output | NI | Battery |  | 2025-05-31
Lauriston | 52 | Profiled output | SI | Solar |  | 2025-02-10
Ruawai Solar Farm | 14 | Profiled output | NI | Solar |  | 2024-12-19
Te Huka Unit 3 | 50 | Profiled output | NI | Geothermal |  | 2024-12-16
Tauhara | 174 | Profiled output | NI | Geothermal |  | 2024-05-15
Rotohiko | 33 | Profiled output | NI | Battery
Glenbrook | 74 | Profiled output | NI | Co-generation
Kapuni | 25 | Profiled output | NI | Co-generation
Kinleith | 28 | Profiled output | NI | Co-generation
Kiwi Cogen/Whareroa | 70 | Profiled output | NI | Co-generation
Kawerau | 104 | Profiled output | NI | Geothermal
Kawerau Onepu | 60 | Profiled output | NI | Geothermal |  |  |  | Includes both Cogen (TA2 & TA3), and Geothermal (KA24 and TOPP1) generators
Mokai | 112 | Profiled output | NI | Geothermal
Nga Awa Purua | 135 | Profiled output | NI | Geothermal
Ngatamariki | 83.2 | Profiled output | NI | Geothermal
Ngawha 2 | 26 | Profiled output | NI | Geothermal
Ngawha B | 31.5 | Profiled output | NI | Geothermal
Ohaaki | 40 | Profiled output | NI | Geothermal
Poihipi | 55 | Profiled output | NI | Geothermal
Rotokawa | 34.5 | Profiled output | NI | Geothermal
Te Ahi O Maui | 24 | Profiled output | NI | Geothermal
Te Huka | 28 | Profiled output | NI | Geothermal
Te Mihi | 166 | Profiled output | NI | Geothermal
Wairakei | 132 | Profiled output | NI | Geothermal
Aniwhenua | 25 | Profiled output | NI | Hydro
Arapuni | 192 | Based on historical inflow sequences | NI | Hydro
Aratiatia | 78 | Based on historical inflow sequences | NI | Hydro
Argyle/Branch | 11 | Profiled output | SI | Hydro
Atiamuri | 74 | Based on historical inflow sequences | NI | Hydro
Aviemore | 220 | Based on historical inflow sequences | SI | Hydro
Benmore | 540 | Based on historical inflow sequences | SI | Hydro
Clyde | 432 | Based on historical inflow sequences | SI | Hydro
Cobb | 32 | Based on historical inflow sequences | SI | Hydro
Coleridge | 39 | Based on historical inflow sequences | SI | Hydro
Dillmans/Kumera | 10 | Profiled output | SI | Hydro
Highbank | 26.8 | Profiled output | SI | Hydro
Kaimai | 38 | Profiled output | NI | Hydro
Kaitawa | 36 | Based on historical inflow sequences | NI | Hydro
Karapiro | 96 | Based on historical inflow sequences | NI | Hydro
Manapouri | 800 | Based on historical inflow sequences | SI | Hydro
Mangahao | 42 | Profiled output | NI | Hydro
Maraetai | 352 | Based on historical inflow sequences | NI | Hydro
Matahina | 80 | Based on historical inflow sequences | NI | Hydro
Ohakuri | 106 | Based on historical inflow sequences | NI | Hydro
Ohau A | 264 | Based on historical inflow sequences | SI | Hydro |  |  |  | Output constrained a low Pukaki lake levels due to low flow rates
Ohau B | 212 | Based on historical inflow sequences | SI | Hydro
Ohau C | 212 | Based on historical inflow sequences | SI | Hydro
Patea | 32 | Profiled output | NI | Hydro
Patearoa/Paerau | 12 | Profiled output | SI | Hydro
Piripaua | 44 | Based on historical inflow sequences | NI | Hydro
Rangipo | 120 | Based on historical inflow sequences | NI | Hydro
Roxburgh | 320 | Based on historical inflow sequences | SI | Hydro
Tekapo A | 30 | Based on historical inflow sequences | SI | Hydro
Tekapo B | 154 | Based on historical inflow sequences | SI | Hydro
Tokaanu | 240 | Based on historical inflow sequences | NI | Hydro
Tuai | 59 | Based on historical inflow sequences | NI | Hydro
Waipapa | 54 | Based on historical inflow sequences | NI | Hydro
Waipori | 83.6 | Profiled output | SI | Hydro
Waitaki | 105 | Based on historical inflow sequences | SI | Hydro
Whakamaru | 118 | Based on historical inflow sequences | NI | Hydro
Wheao | 24 | Profiled output | NI | Hydro
Kaitaia Solar Farm | 23 | Profiled output | NI | Solar
Rangitaiki Solar Farm Edgecumbe | 21 | Profiled output | NI | Solar
Huntly Rankines | 720 | Fully Dispatch (- forced outages) | NI | Thermal |  |  |  | Unit capacity of 240 MW
Huntly Unit 5 | 385 | Fully Dispatch (- forced outages) | NI | Thermal
Huntly Unit 6 | 45 | Fully Dispatch (- forced outages) | NI | Thermal
Junction Road | 100 | Fully Dispatch (- forced outages) | NI | Thermal
Mckee Peaker | 95 | Fully Dispatch (- forced outages) | NI | Thermal
Stratford Peakers | 200 | Fully Dispatch (- forced outages) | NI | Thermal
Taranaki Combined Cycle | 377 | Fully Dispatch (- forced outages) | NI | Thermal |  |  | 2026-01-01
Whirinaki | 155 | Fully Dispatch (- forced outages) | NI | Thermal |  |  |  | Limited by fuel constraint to 60 GWh per year
Harapaki | 176 | Based on historical wind sequences / Profiled output | NI | Wind
Kaiwera Downs | 43 | Based on historical wind sequences / Profiled output | SI | Wind
Mahinerangi | 36 | Profiled output | SI | Wind
Mill Creek | 60 | Based on historical wind sequences / Profiled output | NI | Wind
Tararua I, II & III | 161 | Based on historical wind sequences / Profiled output | NI | Wind
Te Apiti | 90 | Based on historical wind sequences / Profiled output | NI | Wind
Te Rere Hau | 48.5 | Based on historical wind sequences / Profiled output | NI | Wind
Te Uku | 67 | Based on historical wind sequences / Profiled output | NI | Wind
Turitea North | 119 | Based on historical wind sequences / Profiled output | NI | Wind
Turitea South | 103 | Based on historical wind sequences / Profiled output | NI | Wind
Waipipi | 133 | Based on historical wind sequences / Profiled output | NI | Wind
Westwind | 142 | Based on historical wind sequences / Profiled output | NI | Wind
White Hill | 58 | Profiled output | SI | Wind

## HVDC Assumptions
Standard Assumptions
| Maximum North (Sent) | 1000MW
| Maximum South (Sent) | 550MW
Planned Outages
| HVDC Flow Direction | Limit (MW) | Start Date | End Date
|  | 500 | 2026-02-19 05:00 | 2026-02-22 22:00
|  | 300 | 2026-02-21 05:00 | 2026-03-02 22:00
|  | 300 | 2027-02-18 05:00 | 2027-02-21 22:00
|  | 500 | 2027-02-20 05:00 | 2027-02-23 22:00

## Planned Generator Outages
Plant | De-rating (MW) | Start | End | Description of Change
Highbank/Montalto | 21 | 21/09/2025 | 31/07/2026 | New/Adjusted
Highbank/Montalto | 26.8 | 01/09/2025 | 21/09/2025 | No change
Huntly Rankines | 240 | 12/09/2025 | 11/10/2025 | No change
Huntly Rankines | 240 | 12/10/2025 | 24/10/2025 | No change
Huntly Rankines | 240 | 01/01/2026 | 31/08/2027 | New/Adjusted
Huntly Rankines | 240 | 01/09/2025 | 07/09/2025 | New/Adjusted
Huntly Unit 5 | 385 | 31/10/2025 | 24/11/2025 | No change
Huntly Unit 6 | 45 | 04/10/2025 | 17/10/2025 | No change
Junction Road | 50 | 22/11/2025 | 24/11/2025 | New/Adjusted
Junction Road | 100 | 24/11/2025 | 28/11/2025 | New/Adjusted
Kawerau | 3 | 01/09/2025 | 03/09/2025 | New/Adjusted
Kawerau | 3 | 03/09/2025 | 05/09/2025 | New/Adjusted
Kinleith | 32 | 01/09/2025 | 17/11/2025 | No change
Kumara/Dillmans/Duffers | 10 | 29/09/2025 | 20/10/2025 | No change
McKee | 50 | 09/10/2025 | 17/10/2025 | No change
McKee | 50 | 03/10/2025 | 08/10/2025 | New/Adjusted
Mokai | 4.5 | 10/11/2025 | 24/11/2025 | New/Adjusted
Mokai | 7.5 | 17/09/2025 | 17/10/2025 | New/Adjusted
Nga Awa Purua | 135 | 02/11/2025 | 28/11/2025 | No change
Ngatamariki | 84.8 | 07/10/2025 | 09/10/2025 | No change
Patea | 11 | 10/11/2025 | 14/11/2025 | New/Adjusted
Patea | 11 | 06/10/2025 | 24/10/2025 | No change
Patea | 11 | 03/11/2025 | 07/11/2025 | New/Adjusted
Poihipi | 24 | 15/09/2025 | 19/09/2025 | New/Adjusted
Poihipi | 37 | 02/09/2025 | 03/09/2025 | New/Adjusted
Rangipo | 70 | 29/03/2026 | 12/04/2026 | No change
Rangipo | 70 | 01/09/2025 | 19/09/2025 | No change
Rangipo | 70 | 22/02/2026 | 29/03/2026 | No change
Rangipo | 70 | 09/12/2025 | 06/02/2026 | No change
Rangipo | 70 | 13/10/2025 | 09/12/2025 | No change
Rangipo | 120 | 19/09/2025 | 13/10/2025 | No change
Rangipo | 120 | 06/02/2026 | 22/02/2026 | No change
Rotokawa | 9.4 | 02/11/2025 | 29/11/2025 | New/Adjusted
Stratford Peakers | 100 | 24/11/2025 | 28/11/2025 | New/Adjusted
Stratford Peakers | 190 | 29/11/2025 | 05/12/2025 | New/Adjusted
TCC | 20 | 01/09/2025 | 31/12/2025 | New/Adjusted
TCC | 330 | 01/01/2026 | 31/08/2027 | New/Adjusted
Tauhara A | 24 | 22/11/2025 | 23/11/2025 | New/Adjusted
Tauhara B | 15 | 29/11/2025 | 03/12/2025 | New/Adjusted
Tauhara B | 159 | 02/11/2025 | 29/11/2025 | New/Adjusted
Te Apiti | 22.2 | 12/09/2025 | 15/09/2025 | New/Adjusted
Te Apiti | 22.2 | 19/09/2025 | 22/09/2025 | New/Adjusted
Te Apiti | 22.2 | 26/09/2025 | 28/11/2025 | New/Adjusted
Te Apiti | 22.2 | 05/09/2025 | 08/09/2025 | New/Adjusted
Te Huka 3 | 52 | 15/02/2026 | 17/03/2026 | No change
Te Huka 3 | 52 | 07/10/2025 | 08/10/2025 | New/Adjusted
Te Mihi | 3 | 06/11/2025 | 20/11/2025 | New/Adjusted
Te Mihi | 3 | 20/11/2025 | 04/12/2025 | New/Adjusted
Te Mihi | 3 | 03/11/2025 | 06/11/2025 | New/Adjusted
Te Mihi | 8 | 11/09/2025 | 15/09/2025 | New/Adjusted
Te Mihi | 8 | 19/09/2025 | 25/09/2025 | New/Adjusted
Te Mihi | 8 | 25/09/2025 | 26/09/2025 | New/Adjusted
Te Mihi | 166 | 15/09/2025 | 19/09/2025 | New/Adjusted
Te Rapa | 42 | 01/09/2025 | 31/08/2027 | New/Adjusted
Tekapo A | 30 | 14/09/2025 | 20/09/2025 | No change
Tekapo B | 154 | 14/09/2025 | 18/09/2025 | New/Adjusted
Wairakei incl. binary | 33 | 08/10/2025 | 14/10/2025 | No change
Wairakei incl. binary | 33 | 29/10/2025 | 22/01/2026 | New/Adjusted
Wairakei incl. binary | 33 | 01/09/2025 | 23/09/2025 | New/Adjusted
Wairakei incl. binary | 33 | 23/09/2025 | 25/09/2025 | New/Adjusted
Wairakei incl. binary | 33 | 24/01/2026 | 28/02/2026 | No change
Wairakei incl. binary | 33 | 15/10/2025 | 29/10/2025 | New/Adjusted
Wairakei incl. binary | 33 | 25/09/2025 | 30/09/2025 | No change
Wairakei incl. binary | 33 | 07/04/2026 | 31/08/2027 | New/Adjusted
Wairakei incl. binary | 33 | 30/09/2025 | 07/10/2025 | New/Adjusted
Wairakei incl. binary | 63 | 14/10/2025 | 15/10/2025 | No change
Wairakei incl. binary | 63 | 22/03/2026 | 31/03/2026 | New/Adjusted
Wairakei incl. binary | 63 | 01/03/2026 | 08/03/2026 | No change
Wairakei incl. binary | 63 | 07/10/2025 | 08/10/2025 | New/Adjusted
Wairakei incl. binary | 70 | 08/03/2026 | 18/03/2026 | New/Adjusted
West Wind | 48.3 | 01/09/2025 | 10/10/2025 | No change
Whirinaki | 52 | 01/08/2025 | 05/08/2025 | New/Adjusted
Whitehill | 12 | 01/08/2025 | 04/08/2025 | New/Adjusted
Whitehill | 14 | 29/08/2025 | 01/09/2025 | New/Adjusted
Whitehill | 14 | 08/08/2025 | 11/08/2025 | New/Adjusted
Whitehill | 14 | 15/08/2025 | 18/08/2025 | New/Adjusted
Whitehill | 14 | 22/08/2025 | 25/08/2025 | New/Adjusted

## Thermal Generation Assumptions
| Modelled Month | Approximate Coal and Gas Generation (GWh)
| Sep-25 | 722.6558 | [1] There is a small amount of variation in the modelling of thermal fuel consumption based on the hydro sequence being modelled, and the ERC month being assessed. These figures are representative samples of thermal fuel generation in the ERC model.
| Oct-25 | 700.4429
| Nov-25 | 694.3632
| Dec-25 | 670.9271
| Jan-26 | 557.4568
| Feb-26 | 438.8034
| Mar-26 | 502.8455
| Apr-26 | 432.9841
| May-26 | 416.9253
| Jun-26 | 346.681
| Jul-26 | 380.1092
| Aug-26 | 380.7256
| Sep-26 | 322.7906
| Oct-26 | 360.3312
| Nov-26 | 325.8858
| Dec-26 | 343.6387
| Jan-27 | 322.9223
| Feb-27 | 276.2357
| Mar-27 | 323.0078
| Apr-27 | 312.8542
| May-27 | 312.8381
| Jun-27 | 301.5796
| Jul-27 | 317.3689
| Aug-27 | 317.1104
Thermal deratings
For this month thermal deratings have been applied to the basecase. These can be found in the update log.