## Manual Constraints
Manual Constraints
Constraint Name | Type | Term 1 |  | Term 2 |  | Term 3 |  | Term 4 |  | Term 5 |  | Term 6 |  | Term 7 |  | Term 8 |  | Term 9 |  | Term 10 |  | Term 11 |  | Term 12 |  | Term 13 | Term 14 | Term 15 | Temperature | RHS | Purpose | Equation | istar1 | istar2 | istar3 | istar4 | istar5 | istar6 | istar7 | istar8 | istar9 | istar10 | istar11 | istar12 | istar13 | istar14 | istar15 | istarEnd | iplus2 | iplus3 | iplus4 | iplus5 | iplus6 | iplus7 | iplus8 | iplus9 | iplus10 | iplus11 | iplus12 | iplus13 | iplus14 | iplus15 | iplusEnd
Branch Constraints - Outage
ARI_HAM_1_Branch_W_O_1 | Outage | +1.00* | ARI_HAM1.1 | [25 empty] | 20 | 58 | The effect of this constraint is to manage flows through Arapuni - Hamilton 1 circuit pre contingent to prevent Arapuni Runback scheme operation in steady state during certain outage scenarios. The limit is set at 95% of the rating of the circuit. | 1.00 * ARI_HAM1.1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ARI_HAM_2_Branch_W_O_1 | Outage | +1.00* | ARI_HAM2.1 | [25 empty] | 20 | 58 | The effect of this constraint is to manage flows through Arapuni - Hamilton 2 circuit pre contingent to prevent Arapuni runback scheme operation in steady state during certain outage scenarios. The limit is set at 95% of the rating of the circuit. | 1.00 * ARI_HAM2.1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ARI_HAM_1_Branch_M_O_1 | Outage | +1.00* | ARI_HAM1.1 | [25 empty] | 25 | 52 | The effect of this constraint is to manage flows through Arapuni - Hamilton 1 circuit to avoid ARI Runback scheme operation in steady state. The limit is set at 95% of the rating of the circuit. | 1.00 * ARI_HAM1.1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ARI_HAM_2_Branch_M_O_1 | Outage | +1.00* | ARI_HAM2.1 | [25 empty] | 25 | 52 | The effect of this constraint is to manage flows through Arapuni - Hamilton 2 circuit to avoid ARI Runback scheme operation in steady state. The limit is set at 95% of the rating of the circuit. | 1.00 * ARI_HAM2.1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ARI_HAM_1_Branch_S_O_1 | Outage | +1.00* | ARI_HAM1.1 | [25 empty] | 30 | 47 | The effect of this constraint is to manage flows through Arapuni - Hamilton 1 circuit pre contingent to prevent Arapuni Runback scheme operation in steady state. The limit is set at 95% of the rating of the circuit. | 1.00 * ARI_HAM1.1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ARI_HAM_2_Branch_S_O_1 | Outage | +1.00* | ARI_HAM2.1 | [25 empty] | 30 | 47 | The effect of this constraint is to manage flows through Arapuni - Hamilton 2 circuit pre contingent to prevent Arapuni Runback scheme operation in steady state. The limit is set at 95% of the rating of the circuit. | 1.00 * ARI_HAM2.1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HAM_KPO_1_M_O_2A | Outage | -1.0* | HAM_KPO2.1 | [25 empty] | 25 | 37 | The effect of this constraint is to manage flows through the Hamilton Karapiro circuit 2 for a contingency of a Karapiro generator unit when Hamilton Karapiro circuit 1 is out of service. | -1.0 * HAM_KPO2.1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HAM_KPO_1_S_O_2A | Outage | -1.0* | HAM_KPO2.1 | [25 empty] | 30 | 34 | The effect of this constraint is to manage flows through the Hamilton Karapiro circuit 2 for a contingency of a Karapiro generator unit when Hamilton Karapiro circuit 1 is out of service. | -1.0 * HAM_KPO2.1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HAM_KPO_1_W_O_2A | Outage | -1.0* | HAM_KPO2.1 | [25 empty] | 20 | 51 | The effect of this constraint is to manage flows through the Hamilton Karapiro circuit 2 for a contingency of a Karapiro generator unit when Hamilton Karapiro circuit 1 is out of service. | -1.0 * HAM_KPO2.1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HAM_KPO_2_M_O_2A | Outage | -1.0* | HAM_KPO1.1 | [25 empty] | 25 | 37 | The effect of this constraint is to manage flows through the Hamilton Karapiro circuit 1 for a contingency of a Karapiro generator unit when Hamilton Karapiro circuit 2 is out of service. | -1.0 * HAM_KPO1.1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HAM_KPO_2_S_O_2A | Outage | -1.0* | HAM_KPO1.1 | [25 empty] | 30 | 34 | The effect of this constraint is to manage flows through the Hamilton Karapiro circuit 1 for a contingency of a Karapiro generator unit when Hamilton Karapiro circuit 2 is out of service. | -1.0 * HAM_KPO1.1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HAM_KPO_2_W_O_2A | Outage | -1.0* | HAM_KPO1.1 | [25 empty] | 20 | 51 | The effect of this constraint is to manage flows through the Hamilton Karapiro circuit 1 for a contingency of a Karapiro generator unit when Hamilton Karapiro circuit 2 is out of service. | -1.0 * HAM_KPO1.1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RDF_T4_O_1 | Outage | -1* | RDF_T5.M5 | [26 empty] | 237 | The effect of this constraint is to manage flows through Redclyffe-T5 during an outage of Redclyffe-T4A and T4B with low Tuai generation. This constraint prevents Redclyffe-T5's load from exceeding 249 MVA, which is Redclyffe-T5's protection limit. The limit is modeled on the MV winding of T5. | -1 * RDF_T5.M5 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RDF_T5_W_O_1 | Outage | +1* | RDF_T4A.T4A | +1* | RDF_T4B.T4B | [23 empty] | 20 | 208 | The effect of this constraint is to manage flows through Redclyffe-T4AB during an outage of Redclyffe-T5 with low Tuai generation. | 1 * RDF_T4A.T4A + 1 * RDF_T4B.T4B | 3 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0
RDF_T5_M_O_1 | Outage | +1* | RDF_T4A.T4A | +1* | RDF_T4B.T4B | [23 empty] | 25 | 196 | The effect of this constraint is to manage flows through Redclyffe-T4AB during an outage of Redclyffe-T5 with low Tuai generation. | 1 * RDF_T4A.T4A + 1 * RDF_T4B.T4B | 3 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0
RDF_T5_S_O_1 | Outage | +1* | RDF_T4A.T4A | +1* | RDF_T4B.T4B | [23 empty] | 30 | 196 | The effect of this constraint is to manage flows through Redclyffe-T4AB during an outage of Redclyffe-T5 with low Tuai generation. | 1 * RDF_T4A.T4A + 1 * RDF_T4B.T4B | 3 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0
BPE_WDV_1_Branch_M_O_1A | Outage | -1* | BPE_WDV2.1 | [25 empty] | 25 | 58 | The effect of this constraint is to manage flows through Bunnythorpe-Woodville-2 pre-contingently to prevent the operation of the Bunnythorpe -Woodville Circuit Overload Scheme in steady state during outages of Bunnythorpe-Woodville-1, with or without a split between Woodville and Masterton. The constraint reduces the loading on the circuit to below 291A, which is the Shoulder Operational Limit of the scheme. The Shoulder Nominal Trip Setting of the scheme is 300A. | -1 * BPE_WDV2.1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BPE_WDV_1_Branch_S_O_1A | Outage | -1* | BPE_WDV2.1 | [25 empty] | 30 | 58 | The effect of this constraint is to manage flows through Bunnythorpe-Woodville-2 pre-contingently to prevent the operation of the Bunnythorpe -Woodville Circuit Overload Scheme in steady state during outages of Bunnythorpe-Woodville-1, with or without a split between Woodville and Masterton. The constraint reduces the loading on the circuit to below 291A, which is the Summer Operational Limit of the scheme. The Summer Nominal Trip Setting of the scheme is 300A. | -1 * BPE_WDV2.1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BPE_WDV_1_Branch_W_O_1A | Outage | -1* | BPE_WDV2.1 | [25 empty] | 20 | 68 | The effect of this constraint is to manage flows through Bunnythorpe-Woodville-2 pre-contingently to prevent the operation of the Bunnythorpe -Woodville Circuit Overload Scheme in steady state during outages of Bunnythorpe-Woodville-1, with or without a split between Woodville and Masterton. The constraint reduces the loading on the circuit to below 340A, which is the Winter Operational Limit of the scheme. The Winter Nominal Trip Setting of the scheme is 350A. | -1 * BPE_WDV2.1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BPE_WDV_2_Branch_M_O_1A | Outage | -1* | BPE_WDV1.1 | [25 empty] | 25 | 58 | The effect of this constraint is to manage flows through Bunnythorpe-Woodville-1 pre-contingently to prevent the operation of the Bunnythorpe -Woodville Circuit Overload Scheme in steady state during outages of Bunnythorpe-Woodville-2, with or without a split between Woodville and Masterton. The constraint reduces the loading on the circuit to below 291A, which is the Shoulder Operational Limit of the scheme. The Shoulder Nominal Trip Setting of the scheme is 300A. | -1 * BPE_WDV1.1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BPE_WDV_2_Branch_S_O_1A | Outage | -1* | BPE_WDV1.1 | [25 empty] | 30 | 58 | The effect of this constraint is to manage flows through Bunnythorpe-Woodville-1 pre-contingently to prevent the operation of the Bunnythorpe -Woodville Circuit Overload Scheme in steady state during outages of Bunnythorpe-Woodville-2, with or without a split between Woodville and Masterton. The constraint reduces the loading on the circuit to below 291A, which is the Summer Operational Limit of the scheme. The Summer Nominal Trip Setting of the scheme is 300A. | -1 * BPE_WDV1.1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BPE_WDV_2_Branch_W_O_1A | Outage | -1* | BPE_WDV1.1 | [25 empty] | 20 | 68 | The effect of this constraint is to manage flows through Bunnythorpe-Woodville-1 pre-contingently to prevent the operation of the Bunnythorpe -Woodville Circuit Overload Scheme in steady state during outages of Bunnythorpe-Woodville-2, with or without a split between Woodville and Masterton. The constraint reduces the loading on the circuit to below 340A, which is the Winter Operational Limit of the scheme. The Winter Nominal Trip Setting of the scheme is 350A. | -1 * BPE_WDV1.1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HWA_SFD_1_S_O_2 | Outage | -1* | WGN_WVY1.1 | [25 empty] | 30 | 153 | The effect of this constraint is to manage flows through the Wanganui-Waverley-1 circuit during high Patea, Whareroa and Waipipi generation and / or low Hawera, Waverley and Whareroa load when the Hawera-Stratford-1 is out of service to avoid steady-state thermal overload. | -1 *WGN_WVY1.1
HWA_SFD_1_M_O_2 | Outage | -1* | WGN_WVY1.1 | [25 empty] | 25 | 159 | The effect of this constraint is to manage flows through the Wanganui-Waverley-1 circuit during high Patea, Whareroa and Waipipi generation and / or low Hawera, Waverley and Whareroa load when the Hawera-Stratford-1 is out of service to avoid steady-state thermal overload. | -1 *WGN_WVY1.1
HWA_SFD_1_W_O_2 | Outage | -1* | WGN_WVY1.1 | [25 empty] | 20 | 165 | The effect of this constraint is to manage flows through the Wanganui-Waverley-1 circuit during high Patea, Whareroa and Waipipi generation and / or low Hawera, Waverley and Whareroa load when the Hawera-Stratford-1 is out of service to avoid steady-state thermal overload. | -1 *WGN_WVY1.1
Stability Constraints - Outage
COL_OTI_2orCLH_COLorAPS_CLHorAPS_OTI_STABILITY_O_1 | Outage | -1* | COL_OTI1.1 | +1* | COL_OTI2.1 | +1* | DOB_GYM.1 | [22 empty] | 18 | The effect of this constraint is to manage flows through the Coleridge-Otira 1 circuit during an outage of the Coleridge-Otira 2 circuit or through the Coleridge-Otira 2 circuit during an outage of any segment of the Coleridge-Otira 1 circuit for a contingency of the Dobson-Greymouth circuit during periods of high Grid Zone 12 load and low generation by bringing on Kumara generation to avoid voltage instability occurring. | -1 * COL_OTI1.1 + 1 * COL_OTI2.1 + 1 * DOB_GYM.1
COL_HOR_2&3_O_1A_z | Outage | +1* | COL_OTI2.1 | -1* | COL_OTI1.1 | [24 empty] | 12 | The effect of this constraint is to limit generation from Coleridge Power Station for voltage stability reasons when Coleridge-Hororata 2 and 3 are out of service. | 1 * COL_OTI2.1 + -1 * COL_OTI1.1 | 3 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 0
CYD_ROX_1_or_2_STABILITY_O_1 | Outage | +1* | CYD_ROX1.1 | +1* | LIV_NSY.1 | +1* | CYD_ROX2.1 | [22 empty] | 570 | The effect of this constraint is to manage flows through Clyde-Roxburgh-1, Clyde-Roxburgh-2 and Livingstone-Naseby for a contingency on either Clyde-Roxburgh-1 or Clyde-Roxburgh-2 circuits during an outage of Clyde-Roxburgh-2 or Clyde-Roxburgh-1 circuits with high GZ14 import to avoid voltage collapse. | 1 * CYD_ROX1.1 + 1 * LIV_NSY.1 + 1 * CYD_ROX2.1 | 3 | 20 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 32 | 0 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 0
HWA_SFD_1_STABILITY_O_1 | Outage | -1* | HWA_WVY1.1 | [26 empty] | 30 | The effect of this constraint is to manage flows through Hawera_Waverly during Low Patea generation and/or no Whareroa generation when Hawera_Stratford is out of service.This constraint assists with precontingent voltage management at Hawera and covers for a loss of Bunnythorpe Wanganui 1or 2. | -1 * HWA_WVY1.1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ISL_KIK1_or_2_or_3_TOP_SOUTH_ISLAND_STABILITY_O_1A | Outage | -1* | ISL_KIK3.2 | +1* | ISL_KIK1.1 | -1* | ISL_KIK2.2 | [22 empty] | 266 | The effect of this constraint is to manage flows through the Islington-Kikiwa-1, 2 and 3 circuits for a contingency of either of the two remaining in service circuits during low Nelson area generation and / or high Nelson area load, when 1 of the 3 circuits is on outage to avoid voltage instability. | -1 * ISL_KIK3.2 + 1 * ISL_KIK1.1 + -1 * ISL_KIK2.2 | 4 | 21 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 34 | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0
ISL_TKB_1_or_TKB_TWZ_1_STABILITY_O_1B | Outage | -1* | ASB_TIM_TWZ2.3 | +1* | LIV_NWD1.1 | -1* | ASB_TIM_TWZ1.3 | [22 empty] | 1150 | The effect of this constraint is to manage flows through Ashburton-Timaru-Twizel 1 and 2 and Livingstone-Norwood for a contingency of one of these 220kV circuits when Islington - Tekapo B or Tekapo B - Twizel 1 is out of service. This is to ensure voltage stability limits are not exceeded during periods when load in the Upper South Island is high | -1 * ASB_TIM_TWZ2.3 + 1 * LIV_NWD1.1 + -1 * ASB_TIM_TWZ1.3 | 4 | 25 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 38 | 0 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 0
MAN_NMA_1_or_2_MAN_INTERTRIP_DISABLED_O_1 | Outage | +1* | MAN_NMA1.1 | +1* | MAN_NMA2.1 | +1* | MAN_NMA3.1 | -1* | INV_MAN.1 | [20 empty] | 775 | The effect of this constraint is to manage flows through Manapouri North Makarewa 1 or 2,Manapouri-North Makarewa-3 and Invercargill-Manapouri-2 for a contingency of Manapouri North Makarewa 2 or 1 when Manapouri North Makarewa 1 or 2 is out of service for stability reasons when Manapouri Intertrip is Disabled. | 1 * MAN_NMA1.1 + 1 * MAN_NMA2.1 + 1 * MAN_NMA3.1 + -1 * INV_MAN.1 | 3 | 20 | 37 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 33 | 50 | 0 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 0
WELLINGTON_STABILITY_MGM_MST_1_or_MGM_WDV_1_O_1D | Outage | +1* | BPE_PRM_HAY1.1 | +1* | BPE_PRM_HAY2.1 | -1* | HAY_WIL_LTN1.1 | - 1* | HAY_WIL_LTN2.1 | [20 empty] | 1091 | The effect of this constraint is to manage flows through Bunnythorpe-Paraparaumu-Haywards-1 and 2, and Haywards-Wilton-Linton-1 and 2 circuits for a contingency of one of the circuits during high HVDC south transfer to avoid voltage collapse when Mangamaire-Masterton-1 or Mangamaire-Woodville-1 is out of service or a split is in place between Woodville and Masterton. | 1 * BPE_PRM_HAY1.1 + 1 * BPE_PRM_HAY2.1 + -1 * HAY_WIL_LTN1.1 +- 1 * HAY_WIL_LTN2.1 | 3 | 24 | 46 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 41 | 63 | 0 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0
WEST_COAST_SPLIT_STABILITY_O_1 | Outage | -1* | COL_HOR2.1 | -1* | COL_HOR3.1 | [24 empty] | 10 | The effect of this constraint is manage voltage stability on the West Coast during low West Coast generation and high West Coast load when one of the following is out of service: Greymouth-Kumara, Dobson-Greymouth, Atarau-Dobson or Atarau-Reefton-Inangahua. | -1 * COL_HOR2.1 + -1 * COL_HOR3.1 | 4 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0
WEST_COAST_STABILITY_LOW_GENERATION_O_1 | Outage | -1* | COL_HOR2.1 | -1* | COL_HOR3.1 | [24 empty] | 10 | The effect of this constraint is manage voltage stability on the West Coast during low West Coast generation and high West Coast load. | -1 * COL_HOR2.1 + -1 * COL_HOR3.1 | 4 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0
Thermal or Static Constraints - Permanent
BPE_MTR_1_Branch_S_P_1 | Permanent | +1* | BPE_MTR1.1 | [25 empty] | 30 | 54 | The effect of this constraint is to manage flows through the Bunnythorpe-Mataroa-1 circuit. This is to prevent the Bunnythorpe-Mataroa Circuit Overload Special Protection Scheme operating in steady state under certain system conditions. | 1 * BPE_MTR1.1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BPE_MTR_1_Branch_M_P_1 | Permanent | +1* | BPE_MTR1.1 | [25 empty] | 25 | 61 | The effect of this constraint is to manage flows through the Bunnythorpe-Mataroa-1 circuit. This is to prevent the Bunnythorpe-Mataroa Circuit Overload Special Protection Scheme operating in steady state under certain system conditions. | 1 * BPE_MTR1.1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BPE_MTR_1_Branch_W_P_1 | Permanent | +1* | BPE_MTR1.1 | [25 empty] | 20 | 66 | The effect of this constraint is to manage flows through the Bunnythorpe-Mataroa-1 circuit. This is to prevent the Bunnythorpe-Mataroa Circuit Overload Special Protection Scheme operating in steady state under certain system conditions. | 1 * BPE_MTR1.1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Thermal or Static Constraints - Outage
HOR_KBY_ISL_1_M_O_1 | Outage | -1.03* | GYM_KUM.1 | +0.78* | HOR_KBY_ISL2.1 | [23 empty] | 25 | 30.9 | The effect of this constraint is to manage flows through Greymouth-Kumara for a contingency of Hororata-Kimberley-Islington-2 during high West Coast generation and low West Coast load when Hororata-Kimberley-Islington-1 is out of service. | -1.03 * GYM_KUM.1 + 0.78 * HOR_KBY_ISL2.1 | 7 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0
HOR_KBY_ISL_1_S_O_1 | Outage | -1.03* | GYM_KUM.1 | +0.79* | HOR_KBY_ISL2.1 | [23 empty] | 30 | 27.5 | The effect of this constraint is to manage flows through Greymouth-Kumara for a contingency of Hororata-Kimberley-Islington-2 during high West Coast generation and low West Coast load when Hororata-Kimberley-Islington-1 is out of service. | -1.03 * GYM_KUM.1 + 0.79 * HOR_KBY_ISL2.1 | 7 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0
HOR_KBY_ISL_1_W_O | Outage | -1.00* | GYM_KUM.1 | +0.89* | HOR_KBY_ISL2.1 | [23 empty] | 20 | 33 | The effect of this constraint is to manage flows through Greymouth_Kumara for a contingency of Hororata_Kimberley_Islington_2 during high West Coast generation and low West Coast load when Hororata_Kimberley_Islington_1 is out of service. | -1.00 * GYM_KUM.1 + 0.89 * HOR_KBY_ISL2.1 | 7 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0
HOR_KBY_ISL_2_M_O_1 | Outage | -1.03* | GYM_KUM.1 | +0.79* | HOR_KBY_ISL1.1 | [23 empty] | 25 | 30.9 | The effect of this constraint is to manage flows through Greymouth-Kumara for a contingency of Hororata-Kimberley-Islington-1 during high West Coast generation and low West Coast load when Hororata-Kimberley-Islington-2 is out of service. | -1.03 * GYM_KUM.1 + 0.79 * HOR_KBY_ISL1.1 | 7 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0
HOR_KBY_ISL_2_S_O_1 | Outage | -1.03* | GYM_KUM.1 | +0.8* | HOR_KBY_ISL1.1 | [23 empty] | 30 | 27.5 | The effect of this constraint is to manage flows through Greymouth-Kumara for a contingency of Hororata-Kimberley-Islington-1 during high West Coast generation and low West Coast load when Hororata-Kimberley-Islington-2 is out of service. | -1.03 * GYM_KUM.1 + 0.8 * HOR_KBY_ISL1.1 | 7 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0
HOR_KBY_ISL_2_W_O | Outage | -1* | GYM_KUM.1 | +0.89* | HOR_KBY_ISL1.1 | [23 empty] | 20 | 33 | The effect of this constraint is to manage flows through Greymouth_Kumara for a contingency of Hororata_Kimberley_Islington_1 during high West Coast generation and low West Coast load when Hororata_Kimberley_Islington_2 is out of service. | -1 * GYM_KUM.1 + 0.89 * HOR_KBY_ISL1.1 | 4 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 0
Stability Constraints - Permanent
GZ14_EXPORT_FREQUENCY_LIMIT_P_1 | Permanent | -1* | NSY_ROX.1 | -1* | CYD_TWZ2.1 | -1* | CYD_TWZ1.1 | [22 empty] | 2000 | The effect of this constraint is to manage flows through Clyde-Cromwell-Twizel-1 or Clyde-Cromwell-Twizel-2 or Naseby-Roxburgh for a contingency of this circuit when the other two circuits are out of service in order to avoid frequency instability. It will also be used to manage flows through Clyde-Cromwell-Twizel-1 and Clyde-Cromwell-Twizel-2 when Naseby-Roxburgh is out of service and Clyde-Cromwell-Twizel-1 and Clyde-Cromwell-Twizel-2 have been declared a double circuit contingency risk in order to avoid frequency instability. | -1 * NSY_ROX.1 + -1 * CYD_TWZ2.1 + -1 * CYD_TWZ1.1 | 4 | 21 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 34 | 0 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 0
GZ14_EXPORT_FREQUENCY_LIMIT_P_2 | Permanent | -1* | CYD_ROX1.1 | -1* | CYD_ROX2.1 | -1* | NSY_ROX.1 | [22 empty] | 2000 | The effect of this constraint is to manage flows through Clyde-Roxburgh-1 or Clyde-Roxburgh-2 or Naseby-Roxburgh for a contingency of this circuit when the other two circuits are out of service in order to avoid frequency instability. It will also be used to manage flows through Clyde-Roxburgh-1 and Clyde-Roxburgh-2 when Naseby-Roxburgh is out of service and Clyde-Roxburgh-1 and Clyde-Roxburgh-2 have been declared a double circuit contingency risk in order to avoid frequency instability. | -1 * CYD_ROX1.1 + -1 * CYD_ROX2.1 + -1 * NSY_ROX.1 | 4 | 22 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0
GZ14_IMPORT_STABILITY_P_1A | Permanent | -1* | CYD_TWZ2.2 | +1* | LIV_NSY.1 | -1* | CYD_TWZ1.2 | [22 empty] | 920 | The effect of this constraint is to manage flows through Clyde-Cromwell-Twizel 1 and 2 and Livingstone-Naseby-1 for a contingency of one of these circuits during high GZ14 import to avoid voltage collapse. | -1 * CYD_TWZ2.2 + 1 * LIV_NSY.1 + -1 * CYD_TWZ1.2 | 4 | 21 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 33 | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0
HLY_SFD_Stability_P_z | Permanent | -1* | HLY_SFD.1 | +1* | SFD_TMN1.1 | [24 empty] | 550 | To limit pre-contingency flows from SFD to HLY and SFD to TMN to set maximum stability limit for a single contingency during high Taranaki generation and high north flow. | -1 * HLY_SFD.1 + 1 * SFD_TMN1.1 | 4 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 0
MAN_INTERTRIP_DISABLED_STABILITY_P_1 | Permanent | +1* | MAN_NMA1.1 | +1* | MAN_NMA2.1 | +1* | MAN_NMA3.1 | -1* | INV_MAN.1 | [20 empty] | 845 | The effect of this constraint is to manage flows through Manapouri -North Makarewa1,Manapouri-North Makarewa2, Manapouri-North Makarewa3 and Invercargill-Manapouri 2 for a loss of one of the Manapouri North Makarewa 1 or 2 for stability reasons when the Manapouri intertrip scheme is Disabled. | 1 * MAN_NMA1.1 + 1 * MAN_NMA2.1 + 1 * MAN_NMA3.1 + -1 * INV_MAN.1 | 3 | 20 | 37 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 33 | 50 | 0 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 0
MAN_INTERTRIP_ENABLED_STABILITY_P_1 | Permanent | +1* | MAN_NMA1.1 | +1* | MAN_NMA2.1 | +1* | MAN_NMA3.1 | -1* | INV_MAN.1 | [20 empty] | 880 | The effect of this constraint is to manage flows through Manapouri -North Makarewa1,Manapouri-North Makarewa2, Manapouri-North Makarewa3 and Invercargill-Manapouri 2 for a loss of one of the Manapouri North Makarewa 1 or 2 for stability reasons when the Manapouri intertrip scheme is Enabled. | 1 * MAN_NMA1.1 + 1 * MAN_NMA2.1 + 1 * MAN_NMA3.1 + -1 * INV_MAN.1 | 3 | 20 | 37 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 33 | 50 | 0 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 0
SOUTHLAND_STABILITY_P_1D | Permanent | -1* | INV_ROX1.1 | -1* | INV_ROX2.1 | +1* | NMA_GOR_TMH1.1 | +1* | NMA_GOR_TMH2.1 | +1* | EDN_INV.1 | [18 empty] | 1000 | The effect of this constraint is to manage flows into the lower Southland region through Invercargill-Roxburgh 1 and 2, North Makarewa-Gore-Three Mile Hill 1 and 2, and Edendale-Invercargill 1 circuits to avoid voltage collapse during low Southland generation and / or high Southland load. | -1 * INV_ROX1.1 + -1 * INV_ROX2.1 + 1 * NMA_GOR_TMH1.1 + 1 * NMA_GOR_TMH2.1 + 1 * EDN_INV.1 | 4 | 22 | 39 | 60 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 56 | 77 | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0
UPPER_SOUTH_ISLAND_STABILITY_P_1C | Permanent | -1* | ASB_TIM_TWZ2.3 | -1* | ISL_TKB.1 | +1* | LIV_NWD1.1 | -1* | ASB_TIM_TWZ1.3 | [20 empty] | 1330 | The effect of this constraint is to manage flows through Ashburton-Timaru-Twizel 1 and 2, Livingstone-Norwood and Islington-Tekapo B for a contingency of one of these 220kV circuits. This is to ensure voltage stability limits are not exceeded during periods when load in the Upper South Island is high. | -1 * ASB_TIM_TWZ2.3 + -1 * ISL_TKB.1 + 1 * LIV_NWD1.1 + -1 * ASB_TIM_TWZ1.3 | 4 | 26 | 42 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 38 | 55 | 0 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 0
UPPER_NORTH_ISLAND_STABILITY_P_1H | Permanent | -1* | HLY_OHW1.1 | -1* | HLY_OHW2.1 | -1* | HLY_SFD.1 | -1* | HLY_TWH1.1 | +1* | OHW_OTA1.1 | +1* | OHW_OTA2.1 | +1* | OTA_HTU_WKM1.1 | +1* | OTA_HTU_WKM2.1 | -1* | PAK_WKM1.2 | -1* | PAK_WKM2.2 | -1* | BOB_HAM1.1 | +1* | ARI_BOB1.1 |  |  |  |  | 2500 | The effect of this constraint is to manage flows through all transmission lines into the upper North Island region, for a contingency of either the largest connected generator or a major 220kV circuit in the region, to maintain post-contingent voltage stability. | -1 * HLY_OHW1.1 + -1 * HLY_OHW2.1 + -1 * HLY_SFD.1 + -1 * HLY_TWH1.1 + 1 * OHW_OTA1.1 + 1 * OHW_OTA2.1 + 1 * OTA_HTU_WKM1.1 + 1 * OTA_HTU_WKM2.1 + -1 * PAK_WKM1.2 + -1 * PAK_WKM2.2 + -1 * BOB_HAM1.1 + 1 * ARI_BOB1.1 | 4 | 22 | 40 | 57 | 74 | 91 | 109 | 127 | 145 | 163 | 180 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 52 | 70 | 87 | 104 | 122 | 140 | 158 | 176 | 0 | 17 | 17 | 17 | 0
WELLINGTON_STABILITY_P_1E | Permanent | +1* | BPE_PRM_HAY1.1 | +1* | BPE_PRM_HAY2.1 | -1* | HAY_WIL_LTN1.1 | -1* | HAY_WIL_LTN2.1 | -1* | MGM_WDV1.1 | [18 empty] | 1500 | The effect of this constraint is to manage flows through Bunnythorpe-Paraparaumu-Haywards-1 and 2, Haywards-Wilton-Linton-1 and 2 and Mangamaire-Woodville-1 circuits during high HVDC south transfer to avoid voltage collapse. | 1 * BPE_PRM_HAY1.1 + 1 * BPE_PRM_HAY2.1 + -1 * HAY_WIL_LTN1.1 + -1 * HAY_WIL_LTN2.1 + -1 * MGM_WDV1.1 | 3 | 24 | 46 | 68 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 41 | 63 | 85 | 0 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0
Market Node Constraints
BWK1101 WPI0 MW_Min | Outage | +1* | BWK1101 WPI0 ENOF | [26 empty] | 2 | A new manual Market Node constraint has been created for use during outages in the Southland area to bring on WPI for Voltage support and GZ14 voltage stability. | 1 * BWK1101 WPI0 ENOF | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
COL0661 COL0 MW_Min | Outage | +1* | COL0661 COL0 ENOF | [26 empty] | 10 | The effect of this constraint is to manage post contingent voltages during low low generation and high load at Hororata and Kimberley 66kV when Coleridge Otira 2 and Castle-Hill Coleridge 1 are out of service | 1 * COL0661 COL0 ENOF | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HWB0331 WPI0 MW_Min | Outage | +1* | HWB0331 WPI0 ENOF | [26 empty] | 2 | A new manual Market Node constraint has been created for use during outages in the Southland area to bring on WPI for Voltage support. | 1 * HWB0331 WPI0 ENOF | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KPA1101 KPI1 MW_Min | Outage | +1* | KPA1101 KPI1 ENOF | [26 empty] | 13 | A new manual Market Node constraint has been created for use during outages in the Taranaki area to bring on KPI for Voltage support. | 1 * KPA1101 KPI1 ENOF | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KUM0661 KUM0_Min | Outage | +1* | KUM0661 KUM0 ENOF | [26 empty] | 3 | The effect of this constraint is to manage post contingent voltages at Hokitika, Kumara, Greymouth and Dobson during a West Coast split via Coleridge-Otira-1 and 2. | 1 * KUM0661 KUM0 ENOF | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MHO331 MHO0_Min | Outage | +1* | MHO0331 MHO0 ENOF | [26 empty] | 20 | A new manual Market Node constraint has been created for use during outages in the Bunnythorpe area to bring on MHO G1 for Voltage support. | 1 * MHO0331 MHO0 ENOF | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MKE1101 MKE1 MW_Min | Outage | +1* | MKE1101 MKE1 ENOF | [26 empty] | 30 | The effect of this constraint is to manage voltage stability for an extended contingent event of Stratford T9 during low generation and high load at Taranaki 110kV that has no 110kV splits in place and when Stratford T10 is out of service or vice versa. | 1 * MKE1101 MKE1 ENOF | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PTA MW_Min | Outage | +1* | HWA1101 PTA1 ENOF | +1* | HWA1101 PTA2 ENOF | +1* | HWA1101 PTA3 ENOF | [22 empty] | 9 | The effect of this constraint is to manage post contingent voltages at Hawera and Wanganui during an outage on either Bunnythorpe-Marton-Wanganui circuits. | 1 * HWA1101 PTA1 ENOF + 1 * HWA1101 PTA2 ENOF + 1 * HWA1101 PTA3 ENOF | 3 | 27 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 47 | 0 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 0
STK0661 COB0 MW_Min | Outage | +1* | STK0661 COB0 ENOF | [26 empty] | 4 | The effect of this constraint is to bring on COB for voltage support during outages in the Nelson area | 1 * STK0661 COB0 ENOF | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TKA0111 TKA1 MW_Min | Outage | +1* | TKA0111 TKA1 ENOF | [26 empty] | 15 | The effect of this constraint is to manage post contingent voltages during low generation and high load at Timaru and Temuka 110kV when Tekapo B-Twizel is out of service. | 1 * TKA0111 TKA1 ENOF | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WKA_MW_MIN | Outage | +1* | TUI1101 KTW0 ENOF | +1* | TUI1101 PRI0 ENOF | +1* | TUI1101 TUI0 ENOF | [22 empty] | 60 | The effect of this constraint is to offer an alternative operational measure to manage the post-contingent thermal and/or voltage violations in the Hawkes Bay region during outages, and when necessary. | 1 * TUI1101 KTW0 ENOF + 1 * TUI1101 PRI0 ENOF + 1 * TUI1101 TUI0 ENOF | 3 | 27 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 23 | 47 | 0 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 1
Temporary Constraints
KIN_TRK_SPLIT_W_TEMP_1 | Temporary | +1* | HAM_T9.T9 | +0.72* | HAM_T6.T6 | [23 empty] | 20 | 231 | The effect of this constraint is to manage flows through Hamilton T9 for an extended contingent event of HAM T6 during high load at GZ3 110 kV and low generation at Karapiro and Arapuni when the system split at Arapuni bus shifts to Kinleith-Tarukenga 1 & 2 circuits. | 1 * HAM_T9.T9 + 0.72 * HAM_T6.T6 | 3 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 0
Temporary Constraints - Real-time Operations
BEN_HAY_Transfer_Limit | Temporary | +1* | BEN_HAY1.1 | +1* | BEN_HAY2.1 | [24 empty] | 1200 | The purpose of this constraint is to limit transfer on the HVDC link from Benmore to Haywards on a temporary basis for certain operating conditions that require manual intervention in real-time. This constraint may be required due to a number of AC system limits that are not accounted for by the HVDC control system in automatically determining the HVDC transfer limit. Please note, these constraints will never be 100% binding but can still limit HVDC transfer. HVDC transfer will be limited when equal to the right-hand side minus the modulation risk. This is because of how these constraints are referred to within the SPD formulation, where the sum of reserve shared from the sending island (either FIR or SIR), HVDC transfer, and the modulation risk must be less than or equal to the RHS of these constraints. | 1 * BEN_HAY1.1 + 1 * BEN_HAY2.1 | 3 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 0
HAY_BEN_Transfer_Limit | Temporary | +1* | HAY_BEN1.1 | +1* | HAY_BEN2.1 | [24 empty] | 850 | The purpose of this constraint is to limit transfer on the HVDC link from Haywards to Benmore on a temporary basis for certain operating conditions that require manual intervention in real-time. This constraint may be required due to a number of AC system limits that are not accounted for by the HVDC control system in automatically determining the HVDC transfer limit. Please note, these constraints will never be 100% binding but can still limit HVDC transfer. HVDC transfer will be limited when equal to the right-hand side minus the modulation risk. This is because of how these constraints are referred to within the SPD formulation, where the sum of reserve shared from the sending island (either FIR or SIR), HVDC transfer, and the modulation risk must be less than or equal to the RHS of these constraints. | 1 * HAY_BEN1.1 + 1 * HAY_BEN2.1 | 3 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 0
Constraint Name | Type | Term 1 |  | Term 2 |  | Term 3 |  | Term 4 |  | Term 5 |  | Term 6 |  | Term 7 |  | Term 8 |  | Term 9 |  | Term 10 |  | Term 11 |  | Term 12 |  | Term 13 | Term 14 | Term 15 | Temperature | RHS | Purpose | Equation | istar1 | istar2 | istar3 | istar4 | istar5 | istar6 | istar7 | istar8 | istar9 | istar10 | istar11 | istar12 | istar13 | istar14 | istar15 | istarEnd | iplus2 | iplus3 | iplus4 | iplus5 | iplus6 | iplus7 | iplus8 | iplus9 | iplus10 | iplus11 | iplus12 | iplus13 | iplus14 | iplus15 | iplusEnd
Constraint Name | Type | Term 1 |  | Term 2 |  | Term 3 |  | Term 4 |  | Term 5 |  | Term 6 |  | Term 7 |  | Term 8 |  | Term 9 |  | Term 10 |  | Term 11 |  | Term 12 |  | Term 13 | Term 14 | Term 15 | Temperature | RHS | Purpose | Equation | istar1 | istar2 | istar3 | istar4 | istar5 | istar6 | istar7 | istar8 | istar9 | istar10 | istar11 | istar12 | istar13 | istar14 | istar15 | istarEnd | iplus2 | iplus3 | iplus4 | iplus5 | iplus6 | iplus7 | iplus8 | iplus9 | iplus10 | iplus11 | iplus12 | iplus13 | iplus14 | iplus15 | iplusEnd

## Change Log
Change | Requested by | Failover date | Date | Reason for Change
Change COB_UTK_1 to No | D O'Grady | 2011-02-23 | 2011-02-14
Change COB_STK_2 to No | D O'Grady | 2011-02-23 | 2011-02-14
Removed Branch-CTG overrides for ARI CTGS | D O'Grady |  | 2011-03-23
Change STU_TIM to Yes | D O'Grady | 2011-04-06 | 2011-03-23
Change OAM_STU_WTK2.2, 2.3 & 2.4 to Yes | D O'Grady | 2011-04-06 | 2011-03-23
Change BPE WDV 1 & 2 to Yes | D O'Grady | 2011-05-11 | 2011-04-21
Change HWA SFD 1 to Yes | D O'Grady | 2011-05-11 | 2011-04-21
Added "HWA_SFD_1_or_HWA_WVY_1_or_WGN_WVY_1_S_O_1" to the list of manual constraints. | John Prattley |  | 2012-02-20
Added "HWA_SFD_1_or_HWA_WVY_1_or_WGN_WVY_1_M_O_1" to the list of manual constraints. | John Prattley |  | 2012-03-13
Added "HWA_SFD_1_or_HWA_WVY_1_or_WGN_WVY_1_W_O_1" to the list of manual constraints. | John Prattley |  | 2012-05-10
Added "WELLINGTON_STABILITY_P_1A" to the list of manual constraints. | Philip Pidgeon |  | 2012-05-15
Removed "WELLINGTON_STABILITY_P_1A" as constraint not needed. | Philip Pidgeon |  | 2012-05-17
Changed MTI_WKM1 to No | D.O'Grady | 2012-05-30
Changed MTI_WKM2 to No | D.O'Grady | 2012-05-30
Updated "WELLINGTON_STABILITY_MGM_MST_1_or_MGM_WDV_1_O_1A" from version 1. | Philip Pidgeon |  | 2012-05-30
Added "BWK_HWB_O_1" constraint and "INV_ROX_1_or_INV_ROX_2_O_1" constraint to the list of manual constraints. | Peter Gao |  | 2012-07-04
Added ROX_T10_P_1 constraint to the list of manual constraints. | Philip Pidgeon |  | 2012-08-21
Added ISL_LIV_1&_LIV_WTK_1_W_O_1 and ROX_T10&HWB_ROX_1_or_HWB_ROX_2_O_1 constraints to the list of manual constraints. | Peter Gao |  | 2012-08-21
Superseeded "ROX_T10&HWB_ROX_1_or_HWB_ROX_2_O_1" constraint with "ROX_T10_O_1". | Shiva Pillay |  | 2012-09-04
Added ISL_T3_M_O_1 constraint to the list of manual constraints. | Peter Gao |  | 2012-11-16
Added "KAW_T13_S_P_3" and "EDG_KAW_1&EDG_KAW_1&2_O_1 constraints to the list of manual constraints. | Peter Gao |  | 2012-11-22
ROX_T10 re-rated so remove constraints: "ROX_T10_P_1, INV_ROX_1_or_INV_ROX_2_O_1, BAL_GOR_O_1, BWK_HWB_O_1, INV_T1_O_1" | Philip Pidgeon |  | 2012-11-27
Removed KAW_T13_S_P_3 and added KAW_T13_S_TEMP_2, KAW_T13_W_TEMP_2, KAW_T13_S_O_1, KAW_T12_S_O_1, EDG_KAW_1&EDG_KAW_2_W_O_1 and KAW_T13&EDG_KAW_1&2_O_1 constraints to the list of manual constraints. | Peter Gao |  | 2012-12-07
Added BPE_T1_or_BPE_T2_or_BPE_T3_S_O_1 constraint to the list of manual constraints. | Prateik Soni |  | 2012-12-14
Added RDF_TX_ECE_TEMP_1 constraint to the list of manual constraints. | Shiva Pillay |  | 2012-12-19
Removed KAW_T12_S_O_1 | D O'Grady |  | 2013-01-16
Removed KAW_T13_S_O_1 | D O'Grady |  | 2013-01-16
Removed KAW_T13&EDG_227_254_274_M_O_1 | D O'Grady |  | 2013-01-16
Removed KAW_T13&EDG_227_254_274_M_O_2 | D O'Grady |  | 2013-01-16
Removed EDG_KAW_1&EDG_KAW_2_S_O_1 | D O'Grady |  | 2013-01-16
Removed EDG_KAW_1&EDG_KAW_2_W_O_1 | D O'Grady |  | 2013-01-16
Removed EDG_KAW_1_W_O_1 | D O'Grady |  | 2013-01-16
Added KAW_T13_KAW_MAT_TRIP_ENABLED_S_P_1 | D O'Grady |  | 2013-01-16
Added KAW_T13_KAW_MAT_TRIP_ENABLED_M_P_1 | D O'Grady |  | 2013-01-16
Added KAW_T13_KAW_MAT_TRIP_ENABLED_W_P_1 | D O'Grady |  | 2013-01-16
Added KAW_T13_KAW_T12_T13_OVERLOAD_PROT_DISABLED_S_P_1 | D O'Grady |  | 2013-01-16
Added KAW_T13_KAW_T12_T13_OVERLOAD_PROT_DISABLED_M_P_1 | D O'Grady |  | 2013-01-16
Added KAW_T13_KAW_T12_T13_OVERLOAD_PROT_DISABLED_W_P_1 | D O'Grady |  | 2013-01-16
Added HWB_T4_O_1, HWB_T4_O_2 to & superseded ROX_T10_O_1 with ROX_T10_O_1A on the list of manual constraints. | John Prattley |  | 2013-01-16
Removed STK_UTK_1_S_P, STK_UTK_1_W_P, STK_UTK_1_M_P_1, MOT_STK_2_S_O, MOT_STK_2_W_O, MOT_STK_2_M_O_1 as circuit STK_UTK1.1 is now Dog conductor | Philip Pidgeon |  | 2013-01-17
Added ISL_T6_S_O_1 and ISL_T3_or_ISL_T7_S_O_1 manual constraint. | Carlo Jaminola |  | 2013-01-22
Add MOT_T5_O_1 manual constraint. | Sophia Ting |  | 2013-01-22
Added ROX_T10_O_2 manual constraint | Asher Habib |  | 2013-02-04
Added MNI_MKE_SFD1.1 and Yes for SFT monitoring | Shiva Pillay |  | 2013-02-07
Added MNI_MKE_SFD1.2 and Yes for SFT monitoring | Shiva Pillay |  | 2013-02-07
Added MNI_MKE_SFD1.3 and No for SFT monitoring | Shiva Pillay |  | 2013-02-07
Remove RDF_TX_ECE_TEMP_1 from the manual contraints. | Ravisha |  | 2013-02-12
Superseeded RDF_T3_M_O_1, with RDF_T3_M_O_1A | Ravisha |  | 2013-02-12
Superseeded RDF_T3_S_O_1, with RDF_T3_S_O_1A | Ravisha |  | 2013-02-12
Superseeded RDF_T3_W_O_1, with RDF_T3_W_O_1A | Ravisha |  | 2013-02-12
Superseeded RDF_T4_M_O_1, with RDF_T4_M_O_1A | Ravisha |  | 2013-02-12
Superseeded RDF_T4_S_O_1, with RDF_T4_S_O_1A | Ravisha |  | 2013-02-12
Superseeded RDF_T4_W_O_1, with RDF_T4_W_O_1A | Ravisha |  | 2013-02-12
Removed HWB_T4_O_1 | Shiva Pillay |  | 2013-02-13
Removed HWB_T4_O_2 | Shiva Pillay |  | 2013-02-13
Removed ROX_T10_O_1A | Shiva Pillay |  | 2013-02-13
Removed ROX_T10_O_2 | Shiva Pillay |  | 2013-02-13
Put in alphabetic order add COL_OTI stability & update Southland constraints | Philip Pidgeon |  | 2013-02-08
Removed COB_MOT_2_S_O | Achary |  | 2013-03-26
Removed COB_MOT_2_W_O | Achary |  | 2013-03-26
Removed COB_MOT_2_M_O_1 | Achary |  | 2013-03-26
Removed MOT_STK_2&MOT_T6_S_O_1 | Achary |  | 2013-03-26
Removed MOT_STK_2&MOT_T6_W_O_1 | Achary |  | 2013-03-26
Removed MOT_STK_2&MOT_T6_M_O_1 | Achary |  | 2013-03-26
Added ISL_T3_W_O_1 manual constraint | Shiva Pillay |  | 2013-05-02
Added DOB_T11.T11 =n to GZ12 | Aaron R |  | 2013-05-09
Added DOB_T11.M11 =n to GZ12 | Aaron R |  | 2013-05-09
Added DOB_T11.L11 =n to GZ12 | Aaron R |  | 2013-05-09
Added DOB_T11.M12 =n to GZ12 | Aaron R |  | 2013-05-09
Added DOB_T11.L12 =n to GZ12 | Aaron R |  | 2013-05-09
Added HWB_T4.M4 =y to GZ14 | Aaron R |  | 2013-05-09
Added HWB_T4.L4 =n to GZ14 | Aaron R |  | 2013-05-09
Added INV_T1.M1 = y to GZ14 | Aaron R |  | 2013-05-09
Added INV_T1.L1 =n to GZ14 | Aaron R |  | 2013-05-09
Added ROX_T10.M10 =y to GZ14 | Aaron R |  | 2013-05-09
Added ROX_T10.L10 =n to GZ14 | Aaron R |  | 2013-05-09
Added BRY_T7.T7 =n to GZ11 | Aaron R |  | 2013-05-09
Added BRY_T7.M7 =n to GZ11 | Aaron R |  | 2013-05-09
Added BRY_T7.L7 =n to GZ11 | Aaron R |  | 2013-05-09
Added STK_T3.M3 =y to GZ9 | Aaron R |  | 2013-05-09
Added STK_T3.L3 =n to GZ9 | Aaron R |  | 2013-05-09
Removed WKM_PPI_WRK.1 =y from GZ4 | Aaron R |  | 2013-05-10
Removed WKM_PPI_WRK.2 =y from GZ4 | Aaron R |  | 2013-05-10
Removed WKM_PPI_WRK.3 =n from GZ4 | Aaron R |  | 2013-05-10
Added THI_WKM1 =y to GZ4 | Aaron R |  | 2013-05-10
Added THI_WRK1 =y to GZ4 | Aaron R |  | 2013-05-10
Added PPI_THI1 =n to GZ4 | Aaron R |  | 2013-05-10
Added PAK_WKM1 to GZ2 | Aaron R |  | 2013-05-10
Added PAK_WKM1.1 =y to GZ2 | Aaron R |  | 2013-05-10
Added PAK_WKM1.2 =y to GZ2 | Aaron R |  | 2013-05-10
Added PAK_WKM2 to GZ2 | Aaron R |  | 2013-05-10
Added PAK_WKM2.1 =y to GZ2 | Aaron R |  | 2013-05-10
Added PAK_WKM2.2 =y to GZ2 | Aaron R |  | 2013-05-10
Removed OKI_NAP_WRK2 from GZ4 | Aaron R |  | 2013-05-10
Removed OKI_NAP_WRK2.1 =y from GZ4 | Aaron R |  | 2013-05-10
Removed OKI_NAP_WRK2.2 =y from GZ4 | Aaron R |  | 2013-05-10
Removed OKI_NAP_WRK2.3 =n from GZ4 | Aaron R |  | 2013-05-10
Added NAP_OKI2 =y to GZ4 | Aaron R |  | 2013-05-10
Added NAP_OKI2 =y to GZ4 | Aaron R |  | 2013-05-10
Removed HAM_WHU1 =n from GZ3 | Aaron R |  | 2013-05-10
Removed HAM_WHU2 =n from GZ3 | Aaron R |  | 2013-05-10
Added HAM_PAO_WHU1 to GZ3 | Aaron R |  | 2013-05-10
Added HAM_PAO_WHU1.1 =n to GZ3 | Aaron R |  | 2013-05-10
Added HAM_PAO_WHU1.2 =n to GZ3 | Aaron R |  | 2013-05-10
Added HAM_PAO_WHU1.3 =n to GZ3 | Aaron R |  | 2013-05-10
Added HAM_PAO_WHU2 to GZ3 | Aaron R |  | 2013-05-10
Added HAM_PAO_WHU2.1 =n to GZ3 | Aaron R |  | 2013-05-10
Added HAM_PAO_WHU2.2 =n to GZ3 | Aaron R |  | 2013-05-10
Added HAM_PAO_WHU2.3 =n to GZ3 | Aaron R |  | 2013-05-10
Removed MNI_SFD1 =y from GZ6 | Aaron R |  | 2013-05-10
Added MNI_MKE_SFD1 to GZ6 | Aaron R |  | 2013-05-10
Added MNI_MKE_SFD1.1 =y to GZ6 | Aaron R |  | 2013-05-10
Added MNI_MKE_SFD1.2 =y to GZ6 | Aaron R |  | 2013-05-10
Added MNI_MKE_SFD1.3 =n to GZ6 | Aaron R |  | 2013-05-10
Removed HAM_HAT1 =y from GZ3 | Aaron R |  | 2013-05-10
Removed HAM_HAT2 =y from GZ3 | Aaron R |  | 2013-05-10
Removed HAT_OHW1 =y from GZ3 | Aaron R |  | 2013-05-10
Removed HAT_OHW2 =y from GZ3 | Aaron R |  | 2013-05-10
Removed HAT_WKM1 =y from GZ3 | Aaron R |  | 2013-05-10
Removed HAT_WKM2 =y from GZ3 | Aaron R |  | 2013-05-10
Added HWB_WPIA =y to GZ14 | Aaron R |  | 2013-05-10
Added HWB_WPIB =y to GZ14 | Aaron R |  | 2013-05-10
Added HWB_WPIC =y to GZ14 | Aaron R |  | 2013-05-10
Added ALB_WRD1 =n to GZ1 | Aaron R |  | 2013-05-10
Added ALB_WRD2 =n to GZ1 | Aaron R |  | 2013-05-10
Added ALB_WRD3 =n to GZ1 | Aaron R |  | 2013-05-10
Added ALB_WRD4 =n to GZ1 | Aaron R |  | 2013-05-10
Added WRD.T1.T1 =n to GZ1 | Aaron R |  | 2013-05-10
Added WRD.T2.T2 =n to GZ1 | Aaron R |  | 2013-05-10
Added WRD.T3.T3 =n to GZ1 | Aaron R |  | 2013-05-10
Added WRD.T7.T7 =n to GZ1 | Aaron R |  | 2013-05-10
Added KIN_TRK_SPLIT_W_TEMP_1 on the list of manual constraints. | Peter Gao |  | 2013-05-13
Added BPE.T1.M1 =y to GZ7 | Sophia Ting |  | 2013-05-13
Added BPE.T1.L1 =n to GZ7 | Sophia Ting |  | 2013-05-13
Added BPE.T1.M2 =y to GZ7 | Aaron R |  | 2013-05-16
Added BPE.T1.L2 =n to GZ7 | Aaron R |  | 2013-05-16
Added BPE.T1.M3 =y to GZ7 | Aaron R |  | 2013-05-16
Added BPE.T1.L3 =n to GZ7 | Aaron R |  | 2013-05-16
Added ISL.T7.M7 =n to GZ10 | Aaron R |  | 2013-05-23
Added ISL.T7.L7 =n to GZ10 | Aaron R |  | 2013-05-23
Added PEN_STC1A =n to GZ2 | Aaron R |  | 2013-05-30
Added PEN_STC1B =n to GZ2 | Aaron R |  | 2013-05-30
Added WTK.T23.M23 =n to GZ13 | Aaron R |  | 2013-05-30
Added WTK.T23.L23 =n to GZ13 | Aaron R |  | 2013-05-30
Added WTK.T24.M24 =n to GZ13 | Aaron R |  | 2013-05-30
Added WTK.T24.L24 =n to GZ13 | Aaron R |  | 2013-05-30
Added HWB.T1.M1 =n to GZ14 | Aaron R |  | 2013-06-07
Added HWB.T1.L1 =n to GZ14 | Aaron R |  | 2013-06-07
Added HWB.T2.M2 =n to GZ14 | Aaron R |  | 2013-06-07
Added HWB.T2.L2 =n to GZ14 | Aaron R |  | 2013-06-07
Removed HOR_ISL1 =y from GZ12 | Aaron R |  | 2013-06-20
Removed HOR_ISL2 =y from GZ12 | Aaron R |  | 2013-06-20
Added HOR_KBY_ISL1 to GZ12 | Aaron R |  | 2013-06-20
Added HOR_KBY_ISL1.1 =y to GZ12 | Aaron R |  | 2013-06-20
Added HOR_KBY_ISL1.2 =y to GZ12 | Aaron R |  | 2013-06-20
Added HOR_KBY_ISL1.3 =n to GZ12 | Aaron R |  | 2013-06-20
Added HOR_KBY_ISL2 to GZ12 | Aaron R |  | 2013-06-20
Added HOR_KBY_ISL2.1 =y to GZ12 | Aaron R |  | 2013-06-20
Added HOR_KBY_ISL2.2 =y to GZ12 | Aaron R |  | 2013-06-20
Added HOR_KBY_ISL2.3 =n to GZ12 | Aaron R |  | 2013-06-20
Added KBY.T1.T1 =n to GZ12 | Aaron R |  | 2013-06-20
Added KBY.T2.T2 =n to GZ12 | Aaron R |  | 2013-06-20
Added EDG.T4.M4 =y to GZ4 | Aaron R |  | 2013-06-20
Added EDG.T4.L4 =n to GZ4 | Aaron R |  | 2013-06-20
Added EDG.T5.M5 =y to GZ4 | Aaron R |  | 2013-06-20
Added EDG.T5.L5 =n to GZ4 | Aaron R |  | 2013-06-20
Added GIS.T2.M2 =n to GZ5 | Sophia Ting |  | 2013-06-25
Added GIS.T2.L2 =n to GZ5 | Sophia Ting |  | 2013-06-25
Added GIS.T4.M4 =n to GZ5 | Sophia Ting |  | 2013-06-25
Added GIS.T4.L4 =n to GZ5 | Sophia Ting |  | 2013-06-25
Added SWN.T2.T2 =n to GZ1 | Aaron R |  | 2013-07-03
Removed KKA T1 from GZ1 | Aaron R |  | 2013-07-03
Relocated MTR T1 from GZ1 to GZ7 | Aaron R |  | 2013-07-03
Added HLY_OTA2.1 to GZ2 | Aaron R |  | 2013-07-03
Added HLY_OTA2.2 to GZ2 | Aaron R |  | 2013-07-03
Added LST_PEN1 to GZ2 | Aaron R |  | 2013-07-03
Added LST_PEN2 to GZ2 | Aaron R |  | 2013-07-03
Added LST_ROS1.1 to GZ2 | Aaron R |  | 2013-07-03
Added LST_ROS1.2 to GZ2 | Aaron R |  | 2013-07-03
Removed OTA_PAK from GZ2 | Aaron R |  | 2013-07-03
Removed OTA_PAK2 from GZ2 | Aaron R |  | 2013-07-03
Added OTA_PAK3 to GZ2 | Aaron R |  | 2013-07-03
Added OTA_PAK4 to GZ2 | Aaron R |  | 2013-07-03
Removed PAK_PEN from GZ2 | Aaron R |  | 2013-07-03
Relocated BOB T2 from GZ3 to GZ2 | Aaron R |  | 2013-07-03
Relocated BOB T3 from GZ3 to GZ2 | Aaron R |  | 2013-07-03
Relocated HLY T1 from GZ2 to GZ3 | Aaron R |  | 2013-07-03
Relocated HLY T2 from GZ2 to GZ3 | Aaron R |  | 2013-07-03
Relocated HLY T3 from GZ2 to GZ3 | Aaron R |  | 2013-07-03
Relocated HLY T4 from GZ2 to GZ3 | Aaron R |  | 2013-07-03
Relocated HLY T5 from GZ2 to GZ3 | Aaron R |  | 2013-07-03
Relocated HLY T6 from GZ2 to GZ3 | Aaron R |  | 2013-07-03
Relocated HLY T21 from GZ2 to GZ3 | Aaron R |  | 2013-07-03
Relocated HLY T22 from GZ2 to GZ3 | Aaron R |  | 2013-07-03
Relocated HLY T500 from GZ2 to GZ3 | Aaron R |  | 2013-07-03
Relocated HLY T600 from GZ2 to GZ3 | Aaron R |  | 2013-07-03
Added PAK T1 to GZ2 | Aaron R |  | 2013-07-03
Added PAK T2 to GZ2 | Aaron R |  | 2013-07-03
Added PAK T3 to GZ2 | Aaron R |  | 2013-07-03
Removed PAK T5 from GZ2 | Aaron R |  | 2013-07-03
Removed PAK T6 from GZ2 | Aaron R |  | 2013-07-03
Added PEN T5 to GZ2 | Aaron R |  | 2013-07-03
Added PEN T7 to GZ2 | Aaron R |  | 2013-07-03
Added ARI_ONG.1 to GZ3 | Aaron R |  | 2013-07-03
Added ARI_ONG.2 to GZ3 | Aaron R |  | 2013-07-03
Added ARI_ONG.3 to GZ3 | Aaron R |  | 2013-07-03
Removed EDG_KAW2 from GZ4 | Aaron R |  | 2013-07-03
Removed KAW_MAT2 from GZ4 | Aaron R |  | 2013-07-03
Added EDG_MAT2 to GZ4 | Aaron R |  | 2013-07-03
Added KAW_ONU1 to GZ4 | Aaron R |  | 2013-07-03
Added KAW_ONU2 to GZ4 | Aaron R |  | 2013-07-03
Added KAW_ONU3 to GZ4 | Aaron R |  | 2013-07-03
Added KAW_ONU4 to GZ4 | Aaron R |  | 2013-07-03
Added KIN_TRK1.1 to GZ4 | Aaron R |  | 2013-07-03
Added KIN_TRK1.2 to GZ4 | Aaron R |  | 2013-07-03
Added KIN_TRK2.1 to GZ4 | Aaron R |  | 2013-07-03
Added KIN_TRK2.2 to GZ4 | Aaron R |  | 2013-07-03
Added NAP_NTM1 to GZ4 | Aaron R |  | 2013-07-03
Removed OKI_WRK3 from GZ4 | Aaron R |  | 2013-07-03
Added WKM_TIE1 to GZ4 | Aaron R |  | 2013-07-03
Added WKM_TIE2 to GZ4 | Aaron R |  | 2013-07-03
Relocated KIN_T1A from GZ4 to GZ3 | Aaron R |  | 2013-07-03
Relocated KIN_T2 from GZ4 to GZ3 | Aaron R |  | 2013-07-03
Relocated KIN_T3A from GZ4 to GZ3 | Aaron R |  | 2013-07-03
Relocated KIN_T3B from GZ4 to GZ3 | Aaron R |  | 2013-07-03
Relocated KIN_T4 from GZ4 to GZ3 | Aaron R |  | 2013-07-03
Relocated KIN_M5 from GZ4 to GZ3 | Aaron R |  | 2013-07-03
Relocated KIN_T5 from GZ4 to GZ3 | Aaron R |  | 2013-07-03
Relocated KIN_L5 from GZ4 to GZ3 | Aaron R |  | 2013-07-03
Relocated KPO_T1 from GZ4 to GZ3 | Aaron R |  | 2013-07-03
Relocated KPO_T2 from GZ4 to GZ3 | Aaron R |  | 2013-07-03
Relocated KPO_T3 from GZ4 to GZ3 | Aaron R |  | 2013-07-03
Relocated ONG_T1 from GZ6 to GZ3 | Aaron R |  | 2013-07-03
Added TRC T1 to GZ3 | Aaron R |  | 2013-07-03
Added TRC M1 to GZ3 | Aaron R |  | 2013-07-03
Added TRC L1 to GZ3 | Aaron R |  | 2013-07-03
Added TRC T2 to GZ3 | Aaron R |  | 2013-07-03
Added TRC M2 to GZ3 | Aaron R |  | 2013-07-03
Added TRC L2 to GZ3 | Aaron R |  | 2013-07-03
Removed KAW T5 from GZ4 | Aaron R |  | 2013-07-03
Added KMO T2 to GZ4 | Aaron R |  | 2013-07-03
Added KMO T4 to GZ4 | Aaron R |  | 2013-07-03
Added NTM T1 to GZ4 | Aaron R |  | 2013-07-03
Added NTM T2 to GZ4 | Aaron R |  | 2013-07-03
Added THI T1 to GZ4 | Aaron R |  | 2013-07-03
Added THI T2 to GZ4 | Aaron R |  | 2013-07-03
Relocated BRK T1 from GZ7 to GZ6 | Aaron R |  | 2013-07-03
Relocated RPO T5 from GZ5 to GZ7 | Aaron R |  | 2013-07-03
Relocated RPO T6 from GZ5 to GZ7 | Aaron R |  | 2013-07-03
Relocated TMN T5 from GZ5 to GZ7 | Aaron R |  | 2013-07-03
Relocated TMN T8 from GZ5 to GZ7 | Aaron R |  | 2013-07-03
Relocated TNG T11from GZ5 to GZ7 | Aaron R |  | 2013-07-03
Relocated TNG T12 from GZ5 to GZ7 | Aaron R |  | 2013-07-03
Relocated TNG T2 from GZ5 to GZ7 | Aaron R |  | 2013-07-03
Relocated TNG T3 from GZ5 to GZ7 | Aaron R |  | 2013-07-03
Added MKE T1 to GZ6 | Aaron R |  | 2013-07-03
Added MKE T2 to GZ6 | Aaron R |  | 2013-07-03
Relocated NPK T1 from GZ6 to GZ7 | Aaron R |  | 2013-07-03
Removed NPL T3 from GZ6 | Aaron R |  | 2013-07-03
Relocated OKN T1 from GZ6 to GZ7 | Aaron R |  | 2013-07-03
Relocated TKU T1 from GZ6 to GZ7 | Aaron R |  | 2013-07-03
Relocated TKU T2 from GZ6 to GZ7 | Aaron R |  | 2013-07-03
Relocated TKU T3 from GZ6 to GZ7 | Aaron R |  | 2013-07-03
Relocated TKU T4 from GZ6 to GZ7 | Aaron R |  | 2013-07-03
Relocated TKU T21 from GZ6 to GZ7 | Aaron R |  | 2013-07-03
Relocated TKU T22 from GZ6 to GZ7 | Aaron R |  | 2013-07-03
Added BPE_WGN1.1 to GZ7 | Aaron R |  | 2013-07-03
Added BPE_WGN1.2 to GZ7 | Aaron R |  | 2013-07-03
Added BPE_WGN2.1 to GZ7 | Aaron R |  | 2013-07-03
Added BPE_WGN2.2 to GZ7 | Aaron R |  | 2013-07-03
Added BPE_WIL1.1 to GZ7 | Aaron R |  | 2013-07-03
Added BPE_WIL1.2 to GZ7 | Aaron R |  | 2013-07-03
Added OKN_ONG1.1 to GZ7 | Aaron R |  | 2013-07-03
Added OKN_ONG1.2 to GZ7 | Aaron R |  | 2013-07-03
Added OKN_ONG1.3 to GZ7 | Aaron R |  | 2013-07-03
Relocated LTN T2 from GZ8 to GZ7 | Aaron R |  | 2013-07-03
Relocated LTN T3 from GZ8 to GZ7 | Aaron R |  | 2013-07-03
Relocated MHO T1 from GZ8 to GZ7 | Aaron R |  | 2013-07-03
Relocated MHO T3 from GZ8 to GZ7 | Aaron R |  | 2013-07-03
Relocated MHO T4 from GZ8 to GZ7 | Aaron R |  | 2013-07-03
Relocated PNI T1 from GZ7 to GZ8 | Aaron R |  | 2013-07-03
Relocated PNI T2 from GZ7 to GZ8 | Aaron R |  | 2013-07-03
Relocated TAP T1 from GZ8 to GZ7 | Aaron R |  | 2013-07-03
Relocated TWC T1 from GZ8 to GZ7 | Aaron R |  | 2013-07-03
Relocated TWC T2 from GZ8 to GZ7 | Aaron R |  | 2013-07-03
Relocated TWF T1 from GZ8 to GZ7 | Aaron R |  | 2013-07-03
Relocated TWF T2 from GZ8 to GZ7 | Aaron R |  | 2013-07-03
Relocated WDV T1 from GZ8 to GZ7 | Aaron R |  | 2013-07-03
Relocated WDV T2 from GZ8 to GZ7 | Aaron R |  | 2013-07-03
Removed HAY M7 from GZ8 | Aaron R |  | 2013-07-03
Removed HAY L7 from GZ8 | Aaron R |  | 2013-07-03
Removed HAY M8 from GZ8 | Aaron R |  | 2013-07-03
Removed HAY L8 from GZ8 | Aaron R |  | 2013-07-03
Added HAY T24 to GZ8 | Aaron R |  | 2013-07-03
Added HAY T25 to GZ8 | Aaron R |  | 2013-07-03
Removed WIL T4 from GZ8 | Aaron R |  | 2013-07-03
Added MST_UHT1.1 to GZ8 | Aaron R |  | 2013-07-03
Added MST_UHT1.2 to GZ8 | Aaron R |  | 2013-07-03
Added MST_UHT2.1 to GZ8 | Aaron R |  | 2013-07-03
Added MST_UHT2.2 to GZ8 | Aaron R |  | 2013-07-03
Added PRM_PNI_TKR1.1 to GZ8 | Aaron R |  | 2013-07-03
Added PRM_PNI_TKR1.2 to GZ8 | Aaron R |  | 2013-07-03
Added PRM_PNI_TKR2.1 to GZ8 | Aaron R |  | 2013-07-03
Added PRM_PNI_TKR2.2 to GZ8 | Aaron R |  | 2013-07-03
Added "PEN_T10_W_O_1" constraint to the list of manual constraints. | Peter Gao |  | 2013-07-15
Added "ISL_T3_or_ISL_T7_M_O_1", "ISL_T3_or_ISL_T7_W_O_1", "ISL_T6_M_O_1" and "ISL_T6_W_O_1" constraints to the list of manual constraints. Deleted "ISL_T3_M_O_1" and "ISL_T3_W_O_1" from the list of manual constraints. | Peter Gao |  | 2013-09-10
Added RDF T3&T4 permanent constraints | Philip Pidgeon |  | 2013-11-08
Added "BPE_T1_or_BPE_T2_or_BPE_T3_S_O_1B", "BPE_T1_or_BPE_T2_or_BPE_T3_M_O_1" and "BPE_T1_or_BPE_T2_or_BPE_T3_W_O_1" constraints to the list of manual constraints. Deleted "BPE_T1_or_BPE_T2_or_BPE_T3_S_O_1" from the list of manual constraints. | Shiva Pillay |  | 2013-12-10 | Issues with "S_O_1" constraint in ACI not communicating with MS. Had to clone "S_O_1" and name that as "S_O_1B" and push it out again for the constraint to work.
Added "LIV_NSY_1_or_NSY_ROX_1_DBL_CTG_O_1" constraint to the list of manual constraints | Shiva Pillay |  | 2014-01-24
Added KMO.T2.M2 =n to GZ5 | Aaron R |  | 2014-01-31 | Converted from 2W to 3W. Modellers need to update csm to 'write constraint = no' for primary and secondary windings (as it was for the 2W transformer)
Added KMO.T2.L2 =n to GZ5 | Aaron R |  | 2014-01-31 | Converted from 2W to 3W. Modellers need to update csm to 'write constraint = no' for primary and secondary windings (as it was for the 2W transformer)
Added KMO.T4.M4 =n to GZ5 | Aaron R |  | 2014-01-31 | Converted from 2W to 3W. Modellers need to update csm to 'write constraint = no' for primary and secondary windings (as it was for the 2W transformer)
Added KMO.T4.L4 =n to GZ5 | Aaron R |  | 2014-01-31 | Converted from 2W to 3W. Modellers need to update csm to 'write constraint = no' for primary and secondary windings (as it was for the 2W transformer)
Added MDN.T5.M5 =n to GZ1 | Aaron R |  | 2014-01-31 | Converted from 2W to 3W.
Added MDN.T5.L5 =n to GZ1 | Aaron R |  | 2014-01-31 | Converted from 2W to 3W.
Added MDN.T6.M6 =n to GZ1 | Aaron R |  | 2014-01-31 | Converted from 2W to 3W.
Added MDN.T6.L6 =n to GZ1 | Aaron R |  | 2014-01-31 | Converted from 2W to 3W.
Removed DAR_MPE1 from GZ1 | Aaron R |  | 2014-01-31
Removed DAR_MPE2 from GZ1 | Aaron R |  | 2014-01-31
Removed DAR T1 from GZ1 | Aaron R |  | 2014-01-31
Removed DAR T1 from GZ1 | Aaron R |  | 2014-01-31
Removed MPE T1 from GZ1 | Aaron R |  | 2014-01-31
Removed MPE T2 from GZ1 | Aaron R |  | 2014-01-31
Removed MPE T3 from GZ1 | Aaron R |  | 2014-01-31
Removed MPE T4 from GZ1 | Aaron R |  | 2014-01-31
Added KAW T12=n | Achary |  | 2014-02-04
Added KAW T13=n | Achary |  | 2014-02-04
Added CYD_ROX_1&2_ROX_IMPORT_SCHEME_ENABLED constraints to manual constraints spreadsheet | D O'Grady |  | 2014-02-14
Added "EDG_KAW_3_S_O_1" constraint to the list of manual constraints. | Peter Gao |  | 2014-02-20
Added "EDG_KAW_3_M_O_1" & "EDG_KAW_3_W_O_1"constraints to the list of manual constraints. | Peter Gao |  | 2014-03-04
Added "HWA_SFD_1_or_HWA_WVY_1_WGN_WVY_1_S_O_1A", "HWA_SFD_1_or_HWA_WVY_1_WGN_WVY_1_M_O_1A" and "HWA_SFD_1_or_HWA_WVY_1_WGN_WVY_1_W_O_1A" constraints to the list of manual constraints. Removed "HWA_SFD_1_or_HWA_WVY_1_WGN_WVY_1_S_O_1", "HWA_SFD_1_or_HWA_WVY_1_WGN_WVY_1_M_O_1" and "HWA_SFD_1_or_HWA_WVY_1_WGN_WVY_1_W_O_1" from the list of manual constraints. | Shiva Pillay |  | 2014-03-05 | Constraints existed in ACI but not in MOI Constraints Library.
Added "NPL_T8_O_1"constraints to the list of manual constraints. | Anna Lu |  | 2014-03-20
Superseded "NPL_T8_O_1" with NPL_T8_O_1A" constraints in the list of manual constraints. | Peter Gao |  | 2014-03-25
Added "West_Coast_Split_S_O_2", "West_Coast_Split_M_O_2" & "West_Coast_Split_W_O_2" constraints to the list of manual constraints. | Peter Gao |  | 2014-03-31
Added "COB_UTK_1&COB_VT10_O_1" and "COB_STK_2&COB_VT10_O_1" constraints to the list of manual constraints. | Shiva Pillay |  | 2014-05-19
Update MTI permanent constraints to account for both ccts. | Philip Pidgeon |  | 2014-05-27 | Constraint will not bind when either MTI_WHM cct is out
Added "BOB_OTA_SPLIT_O_1" & "NPL_T8_O_2" constraints to the list of manual constraints. | Peter Gao |  | 2014-08-15
Added "AVI_WTK_1_or_LIV_WTK_1_W_O_1" constraint to the list of manual constraints. | Peter Gao |  | 2014-08-26
Replace textual equation field with data fields, remove comments from name field and place in textual purpose field | Conrad Edwards |  | 2014-09-09 | Reduce risk to FTR Manager, possibly assist customers
Added "SFD_T10_O_1A" & "SFD_T10_O_2A" constraints to the list of manual constraints. | Peter Gao |  | 2014-10-10
Updated UPPER_NORTH_ISLAND_STABILITY_P_1B to …C. Also changed sheet to handle 11 terms | Philip Pidgeon |  | 2014-10-17
Remove CYD_ROX import scheme enabled constraints | Philip Pidgeon |  | 2014-12-19
Add SFD bus outage constraint (on behalf of Kate) | Philip Pidgeon |  | 2015-02-09
Added "NPL_T8_M_O_3" constraint to the list of manual constraints | Bharti Patel |  | 2015-03-18
Added "WELLINGTON_STABILITY_P_1B" to the list of manual constraints | D O'Grady |  | 2015-04-15 | Update to branches
Added COL and TKA Market node constraints | Grant Tuffery |  | 2015-04-22 | New
Added KUM and PTA Market Node constraints | Grant Tuffery |  | 2015-05-25 | New
WELLINGTON_STABILITY_MGM_MST_1_or_MGM_WDV_1_O_1B updated and MTI 80 sec constraints removed | Philip Pidgeon |  | 2015-07-02 | Update to branches
Added MHO Market Node constraint | Ravisha Wijesinghe |  | 2015-07-16
Added HAM-KPO circuit outage constraints | Ravisha Wijesinghe |  | 2015-08-26
Added WPI into BWK market node constraint | Piyaranga Gammanpila |  | 2015-09-02
Added WPI into HWB market node constraint | Piyaranga Gammanpila |  | 2015-09-02
Modified BPE_MHO1, BPE_MHO2, MHO_T3, MHO_T4 = Yes for SFT Monitoring | Shiva Pillay |  | 2015-09-09 | Branches require monitoring.
Added KPI market node constraint. Added ARI_HAM1 & 2 brach constraints | Ravisha Wijesinghe |  | 2015-10-30
Removed UPPER_NORTH_ISLAND_STABILITY_P_1C | D O'Grady |  | 2015-11-04 | Thermal retirements
Added UPPER_NORTH_ISLAND_STABILITY_P_1D | D O'Grady |  | 2015-11-04 | Thermal retirements
Updated EDG_KAW_3 outages to include KAW_OHK_1 | Philip Pidgeon |  | 2015-11-09 | EDG_OWH name change and removed old ones
Change branch constraint names to ARI_HAM_1_Branch_W_O_1, ARI_HAM_2_Branch_W_O_1, ARI_HAM_1_Branch_M_O_1, ARI_HAM_2_Branch_M_O_1, ARI_HAM_1_Branch_S_O_1, ARI_HAM_2_Branch_S_O_1 | Piyaranga Gammanpila |  | 2015-11-17 | ARI_HAM branch constraint name changed and reworded in include ARI CB 48 'Closed' or 'Open' scenarios.
Added NPL_SFD_1_M_O_2 and NPL_SFD_2_M_O_2 | Gavin Austin |  | 2016-04-21 | New
Added NPL_SFD_1_W_O_1 | Piyaranga Gammanpila |  | 2016-05-06 | New constraint to use 1 hour rating of SFD T10 transformer
COL MN constraint RHS updated after consultation with TrustPower | Grant Tuffery |  | 2016-05-18 | Lowered to ensure less cost of constraint.
New constraint created for SFD_T10 outage | Minura Vithanage |  | 2016-05-23 | SFD_T10 outage
New manual permenant constraint NSY_ROX_1_ROX_Export_Scheme_Enabled_W_P created | Piyaranga Gammanpila |  | 2016-06-03 | Manual constraint created to manage ROX Export Scheme. SFT constraint doesn't get published until 100%.
Remove KAW_T13_KAW_MAT_TRIP_ENABLED... constraints | Philip Pidgeon |  | 2016-06-17 | SPS scheme is modelled
Added existing HOR_KBY_ISL_1_W_O constraint to this spreadsheet | Andrew Vareed |  | 2016-06-27 | Manual constraint had been created in July 2015 but had not been updated in this register.
New manual outage constraint: HOR_KBY_ISL_2_W_O | Andrew Vareed |  | 2016-06-27 | SFT constraint monitoring enabled for GYM KUM cct during a HOR ISL 2 outage - this manual constraint is only required as backup. Cloned cct 1 constraint which was already available.
Update MKE1101 MKE1 MW_Min to RHS of 45 MW | Angela Houston |  | 2016-07-26 | Request from Nova for minimum of 45 MW (one unit)
New Branch constraints for BPE_WDV_1 and 2 | Ravisha Wijesinghe |  | 2016-07-27 | Restrict generation at Te Apiti to ensure Te Apiti generation will not runback for overloading of Bunnythorpe-Woodville -2 circuit steady state when concurrent outages on Bunnythorpe-Woodville-1/2 circuit and Mangamaire split is between Woodville to Masterton.
Moved the "Branches excluded for SFT Monitoring" s/s to SO Circuit & Transformer Rating s/s | Achary |  | 2016-08-02 | To have it in one place for ease of updating
COB market node constraint added | Angela Houston |  | 2016-08-24 | Use COB for voltage support in some outage scenarios
New RDF permanent constraint added. Notes added to existing RDF permanent constraints with respect when these will be made ineffective. | Jaleel Mesbah |  | 2016-09-01 | New Grid Owner offer on the ratings of the RDF ICTs.
ISL_T6 constraints updated | Angela Houston |  | 2016-09-02 | Manual constraints had been created in May 2016 but had not been updated in this register.
Old RDF permanent constraints removed. Removed erroneous NPL_SFD_1_W_O_1. Updated workbook closing macro to get rid of error. | Jaleel Mesbah |  | 2016-09-14 | New Grid Owner offer on the ratings of the RDF ICTs. General housekeeping.
KAW_T12_T_1 added. | Jaleel Mesbah |  | 2016-09-28 | Change in rating of KAW_T12
New KAW T12 outage constraints (KAW_T12_W_O_1 and KAW_T12_O_2) added. | Andrew Vareed |  | 2016-10-03 | Required to manage the de-rating of KAW T12/T13 (60/80 respectively) due to gassing/insulation issues.
NPL_T8_O_2 and SFD_T10_O_2A removed. | Jaleel Mesbah |  | 2016-11-30 | Increase in rating of the HWA-SFD-1 circuit as part of the HWA Bus Rebuild Project makes these constraints obsolete.
Added: BPE_T1_or_BPE_T2_or_BPE_T3_S_O_1 NPL_T8_W_O_3 Removed: KAW_T13_KAW_T12_T13_OVERLOAD_PROT_DISABLED_S_P_1 KAW_T13_KAW_T12_T13_OVERLOAD_PROT_DISABLED_W_P_1 KAW_T13_KAW_T12_T13_OVERLOAD_PROT_DISABLED_M_P_1 LIV_NSY_1_or_NSY_ROX_1_DBL_CTG_O_1 HOR_ISL_1or2_&_DOB_RFN_IGH_1_O ISL_LIV&AVI_BEN_1&2_STABILITY_O_1 ATI_OHK_1_O_1 ASB_OPI_1_STABILITY_O_1 ASB_ISL_1&ASB_OPI_2_STABILITY_O_1A MAN_BLACKSTART_TEST_STABILITY_O_1 HWB_ROX_2&HWB_T4_STABILITY_O_1 ATI_OHK_1_STABILITY_O_1 PEN_T10_W_O_1 KAW_T12_O_2 KAW_T12_W_O_1 KAW_T12_T_1 KAW_T13&EDG_KAW_1&2_O_1 COB_STK_2&COB_VT10_O_1 COB_UTK_1&COB_VT10_O_1 OHK_WRK_1&KIN_TRK_SPLIT_STABILITY_O_1 OHK_WRK_1_O_1_z NSY_ROX_1_ROX_Export_Scheme_Enabled_W_P MOT_T5_O_1 | Jaleel Mesbah |  | 2016-12-06 | General review and cleanup of ACI database.
Removed: NPL_SFD_1_M_O_2 NPL_SFD_2_M_O_2 BPE_T1_or_BPE_T2_or_BPE_T3_S_O_1B BPE_T1_or_BPE_T2_or_BPE_T3_S_O_1 BPE_T1_or_BPE_T2_or_BPE_T3_M_O_1 BPE_T1_or_BPE_T2_or_BPE_T3_W_O_1 HWA_SFD_1_or_HWA_WVY_1_or_WGN_WVY_1_S_O_1A HWA_SFD_1_or_HWA_WVY_1_or_WGN_WVY_1_M_O_1A HWA_SFD_1_or_HWA_WVY_1_or_WGN_WVY_1_W_O_1A ISL_T6_S_O_1A ISL_T6_M_O_1A ISL_T6_W_O_1A ISL_T3_or_ISL_T7_S_O_1 ISL_T3_or_ISL_T7_M_O_1 ISL_T3_or_ISL_T7_W_O_1 NPL_T8_M_O_3 NPL_T8_W_O_3 NPL_T8_O_1A SFD_BUS_SPLIT_S_O_1 SFD_T10_O_1A SFD_T10_S_O_3 SFD_T10_M_O_3 SFD_T10_W_O_3 | Jaleel Mesbah |  | 2017-01-27 | SFT has been enabled for contingencies of interconnecting transformers at NPL, SFD, BPE and ISL. All interconnecting transformer ratings have been updated to the 1-hour offload rating. Change came into effect on Dec 2016.
Added: BPE_T1_or_BPE_T2_or_BPE_T3_S_O_1C BPE_T1_or_BPE_T2_or_BPE_T3_M_O_1A BPE_T1_or_BPE_T2_or_BPE_T3_W_O_1A HWA_SFD_1_or_HWA_WVY_1_or_WGN_WVY_1_S_O_1B HWA_SFD_1_or_HWA_WVY_1_or_WGN_WVY_1_M_O_1B HWA_SFD_1_or_HWA_WVY_1_or_WGN_WVY_1_W_O_1B ISL_T6_S_O_1B ISL_T6_M_O_1B ISL_T6_W_O_1B ISL_T3_or_ISL_T7_S_O_1A ISL_T3_or_ISL_T7_M_O_1A ISL_T3_or_ISL_T7_W_O_1A NPL_T8_O_1B NPL_T8_M_O_3A NPL_T8_W_O_3A SFD_BUS_SPLIT_S_O_1A SFD_BUS_SPLIT_M_O_1A SFD_T10_O_1B SFD_T10_S_O_3A SFD_T10_M_O_3A SFD_T10_W_O_3A | Jaleel Mesbah |  | 2017-02-27 | Manual constraints for the contingencies of NPL, SFD, BPE and ISL interconnecting transformers re-instated due to Market System issues with respect to SFT constraints.
Removed: ISL_T3_or_ISL_T7_S_O_1A ISL_T3_or_ISL_T7_M_O_1A ISL_T3_or_ISL_T7_W_O_1A Added: ISL_T7_S_O_1 ISL_T7_M_O_1 ISL_T7_W_O_1 ISL_T3_S_O_1 ISL_T3_M_O_1A ISL_T3_W_O_1A | Angela Houston |  | 2017-03-07 | ISL_T3 and ISL_T7 have different 1-hour ratings. This means that separate outage constraints are needed for ISL_T3 and ISL_T7 outages as the RHS would be different to reflect the 1-hour rating of the remaining interconnector
Extended the term columns to 15 to cater for larger equations. Removed: HAM_KPO_1_S_O_2 HAM_KPO_1_M_O_2 HAM_KPO_1_W_O_2 HAM_KPO_2_S_O_2 HAM_KPO_2_M_O_2 HAM_KPO_2_W_O_2 EDG_KAW_3_M_1 (duplicate entry) | Jaleel Mesbah |  | 2017-03-09 | HAM-KPO-1 or 2 outage constraints removed due to the effect of the HTI-TMU-1 circuit. Minor cleanup of the database carried out.
Removed: NPL_T8_O_1B SFD_T10_O_1B | Jaleel Mesbah |  | 2017-06-14 | Uprating of reverse rating of HWA-WVY-1 circuit makes these constraints obsolete.
Modified: BEN_HAY_Transfer_Limit HAY_BEN_Transfer_Limit | Jaleel Mesbah |  | 2017-07-07 | Updated CAN description, RHS and constraint type to reflect use by real-time operations.
Removed: BPE_T1_or_BPE_T2_or_BPE_T3_S_O_1C BPE_T1_or_BPE_T2_or_BPE_T3_M_O_1A BPE_T1_or_BPE_T2_or_BPE_T3_W_O_1A HWA_SFD_1_or_HWA_WVY_1_or_WGN_WVY_1_S_O_1B HWA_SFD_1_or_HWA_WVY_1_or_WGN_WVY_1_M_O_1B HWA_SFD_1_or_HWA_WVY_1_or_WGN_WVY_1_W_O_1B | Angela Houston |  | 2017-08-23 | Commisioning of new BPE T2 and T3
WEST_COAST_SPLIT_STABILITY_LOW_GENERATION_O_1 | Angela Houston |  | 2017-08-25 | Voltage stability constraint required on West Coast during generation shutdown
HAM_KPO_1_M_O_2A added | Angela Houston |  | 2017-09-20 | Required for outage
Added notes against BEN_HAY_Transfer_Limit and HAY_BEN_Transfer_Limit. Reordered Constraints alphabetically Added missing information in HAM_KPO_1_M_O_2A Corrected name of WEST_COAST_STABILITY_LOW_GENERATION_O_1 | Christian Jensen |  | 2018-02-12 | Clarify Market participant concerns about Transfer Limit Constraints. General Clean-Up
Added: HAM_KPO_1_M_O_2A HAM_KPO_1_S_O_2A HAM_KPO_1_W_O_2A HAM_KPO_2_M_O_2A HAM_KPO_2_S_O_2A HAM_KPO_2_W_O_2A Removed: ISL_T6_S_O_1B (Replaced by SFT Constraint) ISL_T6_M_O_1B (Replaced by SFT Constraint) ISL_T6_W_O_1B (Replaced by SFT Constraint) ISL_T7_S_O_1 (Replaced by SFT Constraint) ISL_T7_M_O_1 (Replaced by SFT Constraint) ISL_T7_W_O_1 (Replaced by SFT Constraint) ISL_T3_S_O_1 (Replaced by SFT Constraint) ISL_T3_M_O_1A (Replaced by SFT Constraint) ISL_T3_W_O_1A (Replaced by SFT Constraint) NPL_T8_M_O_3A (Replaced by SFT Constraint) NPL_T8_W_O_3A (Replaced by SFT Constraint) SFD_BUS_SPLIT_S_O_1A (Replaced by SFT Constraint) SFD_BUS_SPLIT_M_O_1A (Replaced by SFT Constraint) SFD_T10_S_O_3A (Replaced by SFT Constraint) SFD_T10_M_O_3A (Replaced by SFT Constraint) SFD_T10_W_O_3A (Replaced by SFT Constraint) AVI_WTK_1_or _LIV_WTK_1_W_O_1 (Redundant) MAN_NMA_1_or_2_MAN_INTERTRIP_ENABLED_O_1 (Redundant) Modified: MKE1101 MKE1 MW_Min (RHS reduced from 45MW to 30MW) KPA1101 KPI1 MW_Min (RHS reduced from 15MW to 13MW) | Christian Jensen |  | 2018-04-06 | 1. General Clean-Up 2. Removal of Manual Constraints replaced by SFT Constraints 3. Removal of Redundant Constraints 4. Addition of new Constraints
Added: KAW_T13_Branch_M_O_1 KAW_T13_Branch_S_O_1 KAW_T13_Branch_W_O_1 HOR_KBY_ISL_1_M_O_1 HOR_KBY_ISL_1_S_O_1 HOR_KBY_ISL_2_M_O_1 HOR_KBY_ISL_2_S_O_1 Removed: ISL_LIV_1&_LIV_WTK_1_W_O_1 (Redundant) Modified: SOUTHLAND_STABILITY_P_1A becomes SOUTHLAND_STABILITY_P_1B (NMA_TMH.1 renamed to NMA_GOR_TMH1.1) | Christian Jensen |  | 2018-05-22 | 1. Modification of existing Constraints to account for updated Branch Names 2. Removal of Redundant Constraints 3. Addition of new Constraints
Modified: SOUTHLAND_STABILITY_P_1B becomes SOUTHLAND_STABILITY_P_1C (NMA_TMH2.1 renamed to NMA_GOR_TMH2.1) | Christian Jensen |  | 2018-06-06 | Modification of existing Constraints to account for updated Branch Names
Added: EDG_KAW_3_W_O_1A EDG_KAW_3_M_O_1A EDG_KAW_3_S_O_1A Removed: EDG_KAW_3_M_1 | Christian Jensen |  | 2018-07-06 | EDG_KAW_3_M_1 rebuilt with correct naming convention and additional ratings periods added .
Added: RDF_T3_M_O_1B RDF_T3_S_O_1B RDF_T3_W_O_1B RDF_T4_M_O_1B RDF_T4_S_O_1B RDF_T4_W_O_1B Removed: RDF_T3_M_O_1A RDF_T3_S_O_1A RDF_T3_W_O_1A RDF_T4_M_O_1A RDF_T4_S_O_1A RDF_T4_W_O_1A | Nicholas Merrington | 2019-06-12 | 2019-07-09 | RDF TOPS scheme commissioned. New RDF ITC ratings for when scheme is disbaled an ITC is on outage.
ADDED: -1 * KAW_T13.T13 + -1 * KAW_T12.T12 + 1 * EDG_OWH2.1 | Sean O'Connor |  | 2018-08-02 | New constraint added to reduce KAW, MAT and ANI generation prior to switching KAW_T12 out of service
Added: KAW_T12_M_O_1 KAW_T12_S_O_1A KAW_T12_W_O_1B Removed: KAW_T12_W_O_1A | Nicholas Merrington |  | 2019-10-25 | Added Summer and Shoulder season pre-outage constraints for a KAW_T12 outage. The existing Winter season constraint replaced with updated constraint that considers KAW_T13 ratings change.
Added: KAW_T13_Branch_M_O_1B KAW_T13_Branch_S_O_1A KAW_T13_Branch_W_O_1A EDG_KAW_3_M_O_1B EDG_KAW_3_S_O_1B EDG_KAW_3_W_O_1B EDG_KAW_3_or_KAW_OHK_1_S_O_1A EDG_KAW_3_or_KAW_OHK_1_M_O_1A EDG_KAW_3_or_KAW_OHK_1_W_O_1A Removed: KAW_T13_Branch_M_O_1 KAW_T13_Branch_S_O_1 KAW_T13_Branch_W_O_1 EDG_KAW_3_M_O_1A EDG_KAW_3_S_O_1A EDG_KAW_3_W_O_1A EDG_KAW_3_or_KAW_OHK_1_S_O_1 EDG_KAW_3_or_KAW_OHK_1_M_O_1 EDG_KAW_3_or_KAW_OHK_1_W_O_1 Modified: (Purpose only) RDF_T3_M_O_1B RDF_T3_S_O_1B RDF_T3_W_O_1B RDF_T4_M_O_1B RDF_T4_S_O_1B RDF_T4_W_O_1B | Nicholas Merrington |  | 2019-11-14 | Updated several outage constraints for the KAW region. This was both a response to new KAW_T13 ratings and to be consistent with RHS of 95% of static limit.
ADDED: -1 * NSY_ROX_M_TEMP_1 | Nicholas Merrington |  | 2019-11-19 | New constraint to manage steady-state flows through NSY_ROX without triggering REOLPS.
Added: NSY_ROX_S_P_1 NSY_ROX_M_P_1 NSY_ROX_W_P_1 Removed: NSY_ROX_M_TEMP_1 | Nicholas Merrington |  | 2019-12-02 | Added new constraints to manage steady-state flows through NSY_ROX. Replace the temporary constraint.
Added: BPE_WDV_1_Branch_S_O_1 BPE_WDV_1_Branch_M_O_1 BPE_WDV_1_Branch_W_O_1 BPE_WDV_2_Branch_S_O_1 BPE_WDV_2_Branch_M_O_1 BPE_WDV_2_Branch_W_O_1 Removed: BPE_WDV_1_AND_WDV_TO_MST_SPLIT_S_O_1 BPE_WDV_1_AND_WDV_TO_MST_SPLIT_M_O_1 BPE_WDV_1_AND_WDV_TO_MST_SPLIT_W_O_1 BPE_WDV_2_AND_WDV_TO_MST_SPLIT_S_O_1 BPE_WDV_2_AND_WDV_TO_MST_SPLIT_M_O_1 BPE_WDV_2_AND_WDV_TO_MST_SPLIT_W_O_1 | Nicholas Merrington |  | 2020-01-06 | Name and description on constraints changed. This is to remove requirement that MGM split must be open.
Added: GZ14_EXPORT_FREQUENCY_LIMIT_P_1 | Minura Vithanage |  | 2020-10-16 | New constraint to manage flows through Clyde-Cromwell-Twizel-1 or Clyde-Cromwell-Twizel-2 or Naseby-Roxburgh for a contingency of this circuit when the other two circuits are out of service in order to avoid frequency instability.
Added: BPE_WDV_1_Branch_S_O_1A BPE_WDV_1_Branch_M_O_1A BPE_WDV_1_Branch_W_O_1A BPE_WDV_2_Branch_S_O_1A BPE_WDV_2_Branch_M_O_1A BPE_WDV_2_Branch_W_O_1A Removed: BPE_WDV_1_Branch_S_O_1 BPE_WDV_1_Branch_M_O_1 BPE_WDV_1_Branch_W_O_1 BPE_WDV_2_Branch_S_O_1 BPE_WDV_2_Branch_M_O_1 BPE_WDV_2_Branch_W_O_1 ARG_BLN_1_S_O_1 BOB_OTA_SPLIT_O_1 West_Coast_Split_S_O_2 West_Coast_Split_M_O_2 West_Coast_Split_W_O_2 | Minura Vithanage |  | 2020-12-15 | BPE_WDV constraints: Fixed errors in CAN description, conductor type, constraint type, background and powerflow solution results. ICT ECE constraints: Removed constraints as no longer needed after the CER in 2018.
Added: GZ14_EXPORT_FREQUENCY_LIMIT_P_2 | Minura Vithanage |  | 2020-12-22 | New constraint to manage flows through Clyde-Roxburgh-1 or Clyde-Roxburgh-2 or Naseby-Roxburgh for a contingency of this circuit when the other two circuits are out of service in order to avoid frequency instability.
Added: NSY_ROX_1_or_LIV_NSY_1_STU_SPLIT_CLOSED_S_O_1 NSY_ROX_1_or_LIV_NSY_1_STU_SPLIT_CLOSED_M_O_1 NSY_ROX_1_or_LIV_NSY_1_STU_SPLIT_CLOSED_W_O_1 | Minura Vithanage |  | 2020-12-23 | New manual constraints have been developed to manage flows through Studholme-Timaru 1 for a contingency of Aviemore-Waitaki 1 when Naseby-Roxburgh 1 or Livingstone-Naseby 1 is out of service with the system split at Studholme closed. These manual constraints are required due to SFT not building the correct constraint when the flow on a protected circuit changes direction post-contingently.
Removed: EDG_KAW_3_or_KAW_OHK_1_S_O_1A EDG_KAW_3_or_KAW_OHK_1_M_O_1A EDG_KAW_3_or_KAW_OHK_1_W_O_1A | Mark Yeomans |  | 2021-01-28 | Constraints no longer required as a new policy has been implemented to manage with application of system splits.
Removed: EDG_KAW_3_S_O_1B EDG_KAW_3_M_O_1B EDG_KAW_3_W_O_1B | Mark Yeomans |  | 2021-02-04 | Constraints no longer required as a new policy has been implemented to manage with application of system splits.
Added: KAW_T12_S_O_1B KAW_T12_M_O_1B KAW_T12_W_O_1C Removed: KAW_T12_S_O_1A KAW_T12_M_O_1A KAW_T12_W_O_1B | Mark Yeomans |  | 2021-03-24 | Fixed errors in CAN description, background, MDE, Grid configuration and assumptions. Amended the RHS values utilising 100% of the transformer rating instead of 95% as in the previous version of the constraints. In the case of the Winter constraint the constraint is now designed to ensure that the EDG_KAW COPS does not trip the remaining cct following a fault on the first cct. Uploaded powerflow solution results.
Added: COL_OTI_2orCLH_COLorAPS_CLHorAPS_OTI_STABILITY_O_1 Removed: COL_OTI_2_STABILITY_O_1 CLH_COL_OR_APS_CLH_OR_APS_OTI_STABILITY_O_1 | Mark Yeomans |  | 2021-05-31 | A new manual constraint has been built which combines the previous two. At the same time the oppurtunity was taken to update all fields and information boxes to the latest standards.
Added: ISL_KIK1_or_2_or_3_TOP_SOUTH_ISLAND_STABILITY_O_1A Removed: ISL_KIK_1_or_2_or_3_TOP_SOUTH_ISLAND_STABILITY_O_1 | Mark Yeomans |  | 2021-07-29 | Constraint reviewed and updated following changes in the available reactive equipment and revised the CAN description.
Added: SOUTHLAND_STABILITY_P_1_D Removed: SOUTHLAND_STABILITY_P_1_C | Mark Yeomans |  | 2021-07-29 | Fixed errors in CAN description, background, MDE, Grid configuration and assumptions. Constraint re-studied to provide upto date informationand values within the constarint database.
Added: HWA_SFD_1_S_O_2 HWA_SFD_1_M_O_2 HWA_SFD_1_W_O_2 | Mark Yeomans |  | 2021-08-05 | New manual constraints have been developed to manage flows through the Wanganui-Waverley 1 cct during high Patea, Whareroa and Waipipi generation and / or low Hawera, Waverley and Whareroa load when the Hawera-Stratford-1 is out of service to avoid steady-state thermal overload.
Added: KAW_T13_P_1 Removed: KAW_T13_BRANCH_S_O_1A KAW_T13_BRANCH_M_O_1B KAW_T13_BRANCH_W_O_1A | Christian Jensen |  | 2021-08-25 | A new manual constraint has been developed to manage flows through Kawerau T13 in steady state during periods of high Kawerau area 110kV generation when Kawerau T12 and either Edgecumbe - Kawerau 1 and 2 or Edgecumbe - Owhata 2 are on outage to avoid Kawerau T13 exceeding its continuous rating. This replaces the 3 seasonal BRANCH constraints which were built to utilise the seasonal cyclic rating of KAW T13
Added: WELLINGTON_STABILITY_P_1C WELLINGTON_STABILITY_MGM_MST_1_or_MGM_WDV_1_O_1C Removed: WELLINGTON_STABILITY_P_1B WELLINGTON_STABILITY_MGM_MST_1_or_MGM_WDV_1_O_1B | Christian Jensen |  | 2021-09-29 | Revised Permanent and Outage Manual Constraints have been developed to manage flows into the Wellington region under high HVDC South conditions. The changes are required due to stage 2A of the Judgeford Tee project.
Added: WELLINGTON_STABILITY_P_1D WELLINGTON_STABILITY_MGM_MST_1_or_MGM_WDV_1_O_1D Removed: WELLINGTON_STABILITY_P_1C WELLINGTON_STABILITY_MGM_MST_1_or_MGM_WDV_1_O_1C | Christian Jensen |  | 2021-10-18 | Revised Permanent and Outage Manual Constraints have been developed to manage flows into the Wellington region under high HVDC South conditions. The changes are required due to stage 2B of the Judgeford Tee project.
Added: GZ14_IMPORT_STABILITY_T_1 | Christian Jensen |  | 2022-01-28 | Added to manage emergent voltage stability issues in GZ14
Added: GZ14_IMPORT_STABILITY_P_1 Removed: GZ14_IMPORT_STABILITY_T_1 NSY_ROX_S_P_1 NSY_ROX_M_P_1 NSY_ROX_W_P_1 | Anjana Madurapperuma |  | 2022-04-08 | Added to replace GZ14 temporary constraint, and remove REOLPS related constraints due to CUWLP works decommissioning the REOLPS.
Added: GZ14_IMPORT_STABILITY_P_1A Removed: GZ14_IMPORT_STABILITY_P_1 | Anjana Madurapperuma |  | 2022-04-29 | Updated RHS due to changes with regards to Tiwai load in voltage stability assessment model.
Added: KAW_T12_S_O_1C KAW_T12_M_O_1C KAW_T12_W_O_1D Removed: KAW_T12_S_O_1B KAW_T12_M_O_1B KAW_T12_W_O_1C | Anjana Madurapperuma |  | 2022-05-10 | Updated constraints due to changes in protection settings for EDG_KAW SPS.
Removed: NSY_ROX_1_or_LIV_NSY_1_STU_SPLIT_CLOSED_S_O_1 NSY_ROX_1_or_LIV_NSY_1_STU_SPLIT_CLOSED_M_O_1 NSY_ROX_1_or_LIV_NSY_1_STU_SPLIT_CLOSED_W_O_1 | Anjana Madurapperuma |  | 2022-07-15 | SFT defect confirmed fixed, constraint no longer needed.
Added: CYD_ROX_1_or_2_STABILITY_O_1 | Anjana Madurapperuma |  | 2022-10-27 | Added to manage voltage stability in GZ14 with CYD_ROX outages.
Added: UPPER_NORTH_ISLAND_STABILITY_P_1E Removed: UPPER_NORTH_ISLAND_STABILITY_P_1D | Anjana Madurapperuma |  | 2022-12-23 | Updated equation to reflect decommissioning of BOB_HAM_2.
Removed: INV_ROX_1or2_STABILITY_O_1 | Anjana Madurapperuma |  | 2023-02-07 | Constraint no longer required, thermal limits bind first.
Added: HAM_KPO_1_S_O_3 HAM_KPO_1_W_O_3 HAM_KPO_1_M_O_3 | Yousef Rashid |  | 2023-03-06 | SFT not building constraints as intended
Added: HAM_KPO_2_S_O_3 HAM_KPO_2_W_O_3 HAM_KPO_2_M_O_3 | Yousef Rashid |  | 2023-03-10 | SFT not building constraints as intended
Updated: RDF_T3&T4_P_1 | Theo Kleynhans |  | 2023-06-29 | Due to the temporary withdrawal of the Redclyffe T3 and T4 Transformer Overload Protection Scheme, a 1 hour contingency rating of 110MVA will apply. The right hand side of the constraint changed from 129MW to 109MW.
Added: UPPER_NORTH_ISLAND_STABILITY_P_1F | Theo Kleynhans |  | 2023-08-18 | This will replace UPPER_NORTH_ISLAND_STABILITY_P_1E on 20/09/2023 while the OHW deviation is in service. The change is due to the work required on the Pakuranga-Whakamaru-1 circuit cable section. The circuit will be removed from service for an extended period and a Ohinewai deviation done to enable a new circuit from Whakamaru to Ohinewai temporarily using the existing Pakuranga-Whakamaru-1 overhead line section. The Pakuranga-Whakamaru-1 circuit thus had to be removed from the equation.
Added: UPPER_SOUTH_ISLAND_STABILITY_P_1C | Theo Kleynhans |  | 2023-08-31 | This will replace UPPER_SOUTH_ISLAND_STABILITY_P_1B on 21/09/2023. The change is due to Norwood GXP commissioning. The new station will cut into the Islington-Livingston circuit. The equation had to be updated with the new circuit name.
Added: ISL_TKB_1_or_TKB_TWZ_1_STABILITY_O_1B | Theo Kleynhans |  | 2023-09-08 | This will replace ISL_TKB_1_or_TKB_TWZ_1_STABILITY_O_1A. The change is due to Norwood GXP commissioning. The new station will cut into the Islington-Livingston circuit. The equation had to be updated with the new circuit name.
Removed: ISL_TKB_1_or_TKB_TWZ_1_STABILITY_O_1A | Theo Kleynhans |  | 2023-09-22 | This was superceded by ISL_TKB_1_or_TKB_TWZ_1_STABILITY_O_1B. The change is due to Norwood GXP commissioning. The new station will cut into the Islington-Livingston circuit. The equation had to be updated with the new circuit name.
Removed: UPPER_SOUTH_ISLAND_STABILITY_P_1B | Theo Kleynhans |  | 2023-09-22 | This was superceded by UPPER_SOUTH_ISLAND_STABILITY_P_1C on 21/09/2023. The change is due to Norwood GXP commissioning. The new station will cut into the Islington-Livingston circuit. The equation had to be updated with the new circuit name.
Removed: ASB_BRY_1_or_ASB_ISL_STABILITY_O_1B | Theo Kleynhans |  | 2023-09-22 | Outage Constraint removed. The permanent stability constraint UPPER_SOUTH_ISLAND_STABILITY_P_1C will be used for these outages with an adjusted right-hand side.
Removed: ASB_ISL_1&ASB_TIM_TWZ_2_STABILITY_O_1 | Theo Kleynhans |  | 2023-09-22 | Outage Constraint removed. The permanent stability constraint UPPER_SOUTH_ISLAND_STABILITY_P_1C will be used for these outages with an adjusted right-hand side.
Removed: ASB_TIM_TWZ_1_or_ASB_TIM_TWZ_2_STABILITY_O_1B | Theo Kleynhans |  | 2023-09-22 | Outage Constraint removed. The permanent stability constraint UPPER_SOUTH_ISLAND_STABILITY_P_1C will be used for these outages with an adjusted right-hand side.
Removed: BRY_ISL_1_STABILITY_O_1A | Theo Kleynhans |  | 2023-09-22 | Outage Constraint removed. The permanent stability constraint UPPER_SOUTH_ISLAND_STABILITY_P_1C will be used for these outages with an adjusted right-hand side.
Removed: ISL_TKB_or_ISL_LIV_STABILITY_O_1B | Theo Kleynhans |  | 2023-09-22 | Outage Constraint removed. The permanent stability constraint UPPER_SOUTH_ISLAND_STABILITY_P_1C will be used for these outages with an adjusted right-hand side.
Updated: RDF_T3&T4_P_1 | Theo Kleynhans |  | 2023-09-27 | The Grid owner has re-offered the Redclyffe T3 and T4 Transformer Overload Protection Scheme. The right hand side of the constraint changed from 109MW to 129MW.
Removed: UPPER_NORTH_ISLAND_STABILITY_P_1E | Theo Kleynhans |  | 2023-11-24 | This was replace by UPPER_NORTH_ISLAND_STABILITY_P_1F on 20/09/2023 while the OHW deviation is in service. The change is due to the work required on the Pakuranga-Whakamaru-1 circuit cable section.
Removed: HAM_KPO_1_S_O_3 | Theo Kleynhans |  | 2023-11-28 | SFT has been updated and is now building these constraints. These manual constraints have been deactivated.
Removed: HAM_KPO_1_W_O_3 | Theo Kleynhans |  | 2023-11-28 | SFT has been updated and is now building these constraints. These manual constraints have been deactivated.
Removed: HAM_KPO_1_M_O_3 | Theo Kleynhans |  | 2023-11-28 | SFT has been updated and is now building these constraints. These manual constraints have been deactivated.
Removed: HAM_KPO_2_S_O_3 | Theo Kleynhans |  | 2023-11-28 | SFT has been updated and is now building these constraints. These manual constraints have been deactivated.
Removed: HAM_KPO_2_W_O_3 | Theo Kleynhans |  | 2023-11-28 | SFT has been updated and is now building these constraints. These manual constraints have been deactivated.
Removed: HAM_KPO_2_M_O_3 | Theo Kleynhans |  | 2023-11-28 | SFT has been updated and is now building these constraints. These manual constraints have been deactivated.
Added: UPPER_NORTH_ISLAND_STABILITY_P_1G | Anna Lu |  | 2024-03-11 | This will replace UPPER_NORTH_ISLAND_STABILITY_P_1F on 18/04/2024. The change is due to the recommissioning of PAK_WKM_1. As a part of the Ohinewai Temporary Bypass Project (or the Ohinewai Deviation Project), the PAK_WKM_1 circuit, which has been removed from service since September 2023, will be recommissioned and returned to service on 18/04/2024.
Added: WKA_MW_MIN | Anna Lu |  | 2024-05-22 | The WKA_MW_MIN constraint is already available in the market system. The constraint has been added to the register to support outage planning.
Removed: KAW_T13_P_1 KAW_T12_S_O_1C KAW_T12_M_O_1C KAW_T12_W_O_1D | Anna Lu |  | 2024-08-15 | The existing KAW T12 and T13 manual constraints will be deactivated after the decommissioning of the KAW T13 interconnecting transformer. The tentative decommissioning date is 06/09/2024. The tentative commissioning date of the new KAW T14 interconnecting transformer is 21/09/2024.
Added: BPE_MTR_1_Branch_S_P_1 BPE_MTR_1_Branch_M_P_1 BPE_MTR_1_Branch_W_P_1 | Conor Lawrence |  | 2024-10-22 | A new permanent branch constraint was added to manage flows through the Bunnythorpe-Mataroa-1 circuit. This was added to prevent the Bunnythorpe-Mataroa Circuit Overload Protection Scheme operating in steady state during certain system conditions.
Removed: UPPER_NORTH_ISLAND_STABILITY_P_1G Added: UPPER_NORTH_ISLAND_STABILITY_P_1H | Conor Lawrence |  | 2025-03-04 | UPPER_NORTH_ISLAND_STABILITY_P_1G was replaced with UPPER_NORTH_ISLAND_STABILITY_P_1H. As part of the new HTU GXP project, OTA_WKM_1 and OTA_WKM_2 were renamed as OTA_HTU_WKM_1 and OTA_HTU_WKM_2 respectively. The constraint's equation was updated with the new circuit names.
Removed: RDF_T3&T4_P_1 Added: RDF_T4&T5_T_1A | Conor Lawrence |  | 2025-07-02 | A new temporary static constraint was added to manage flows through RDF_T4 and RDF_T5. This was added for the temporary configuration during the RDF upgrade substation project, with RDF_T3 removed from service, RDF_T4 and RDF_T5 operating in parallel, and the RDF TOPS unavailable. The RHS is set to maintain flows below the 15 minute rating of RDF_T4. This replace the permanent constraint RDF_T3&T4_P_1
Removed: RDF_T3_M_O_1B RDF_T3_S_O_1B RDF_T3_W_O_1B RDF_T4_M_O_1B RDF_T4_M_O_1B RDF_T4_M_O_1B | Theo Kleynhans |  | 2025-08-22 | The existing RDF_T3 and RDF_T4 are being double banked as T4A and T4B to create a new RDF_T4. This will run with the new RDF_T5 transformer. Thus these outage constraints are removed and replaced by new ones.
Added: RDF_T4_O_1 | Theo Kleynhans |  | 2025-08-22 | New outage constraint to to manage flows through Redclyffe-T5 during an outage of Redclyffe-T4A and T4B with low Tuai generation. This constraint prevents Redclyffe-T5's load from exceeding 249 MVA, which is Redclyffe-T5's protection limit.
Added: RDF_T5_W_O_1 RDF_T5_M_O_1 RDF_T5_S_O_1 Removed: RDF_T4&T5_T_1A | Conor Lawrence |  | 2025-09-26 | Three new seasonal outage constraints were added to manage flows through both RDF_T4A & T4B during an outage of RDF_T5 during low Tuai generation. The temporary static constraint that managed flows through RDF_T4 & T5 was removed because the temporary configuration had ended.
Added: WELLINGTON_STABILITY_P_1E Removed: WELLINGTON_STABILITY_P_1D | Jenin George |  | 2025-11-18 | The existing wellington stability constraint was modified to have a higher RHS. The previous RHS was found to be binding in real time even when VSAT was less than 75%.