## Index
ON
Hazardous Substances Register Index
Click hyperlink to goto that page.
1 |  | Instructions
2 |  | Revision Management
3 |  | Revision History
4 |  | Data Capture
5 |  | HSR Summary Data (Site HSR Register)
Useful Links
safety@transpower.co.nz
www.transpower.co.nz
Hazardous Substances (Classes 1 to 5 Controls) Regulations 2001
Hazardous Substances (Classes 1 to 5 Controls) Regulations 2001 - Schedule 3
Section 2 - Quantities of flammable substance that activate Approved Handler requirements
Section 4 - Quantities of class 2, 3, and 4 substances that activate Location Certificate requirements
Worksafe NZ
Person in Charge
Approved Handlers
Test Certificates

## Instructions (hidden)
Hazardous Substances Register |  |  |  | Back to INDEX
Introduction
A Hazardous Substances Register (HSR) is required under the Hazardous Substances & New Organisms Act. All hazardous substances on site must be recorded in this register. The HSR is a listing of all products identified as dangerous or hazardous, used or stored at a facility. The HSR is used in: > Identifying dangerous or hazardous products used or stored on-site > Providing basic data to assist in sourcing Material Safety Data Sheets > Providing information to relevant authorities on hazardous substances on-site. The HSR must be accessible to: > All employees and contractors > Relevant public authorities > Emergency services. The process for the establishment and maintenance of Hazaradous Substances Registers can be found in Transpower Standard TP.AG 47.19 Safety, health and environmental product safety stewardship.
Establishing and Maintaining the Hazardous Substances Register
The process for the establishment and maintenance of Hazaradous Substances Registers can be found in Transpower Standard TP.AG 47.19 Safety, health and environmental product safety stewardship. The key process steps are:
Section 1 | Record the following information at the top of the 'Data Capture Sheet': A - Enter the Name of the inspector the Date and the Time that the site inspection was completed. B - Ensure the Site Code, Name and Contract Group are correct. C - Check that the Emergency Response Plan flipchart is available and easily accessible and that it is current. Update as required. Change to YES once this has been done. D - Check that the MSDS are available and current. There is a set of generic MSDS in the Site Register and the latest updates of these are all available on the Transpower Website. Refer to section 5 below for more MSDS information. Change to YES once this is done.
Section 2 | Record the following information to the right near the top of the 'Data Capture Sheet': Spaces have been provided for these. A - HSNO Responsibilities for the site, such as: Person in Charge Approved Handler(s) B - HSNO Certification details for the site are current, including where relevant: Location Certificate (renewed annually; certification is required for locations where the thresholds quantities for defined Class 1 - 5 hazardous substances are exceeded, for example Haywards and Warehouses) Stationary Container Certificate(s) (new tanks must be certified before use and existing tanks recertified every 5 years. Certificates are required for above ground oil storage tanks > 5,000 L capacity or diesel tanks connected to a burner or a stationary internal combustion engine with a capacity of more than 500 L) Approved Handler/s Certificate(s) (these are issued to individuals and are valid for 5 years) Secondary Containment Certificate(s) (these are currently not required) C - Hazardous Substances Data is updated and correct for the site. This refers to the data in section 3 below.
Click here to send e-mail | Ensure that copies of any issued certificates for the site and for the Approved Handler/s are placed in the Site Register's Hazardous Substances Information section. There is a five year rolling program for the Site Certification inspections of all Transpower Sites and the dates for these can be confirmed by Transpower's Safety and Health Manager. Use email link at left.
Section 3 | Record the following information on the 'Data Capture Sheet' from row 9 onwards. NOTE - Items with these hazardous substance diamonds must be noted. A list of the Product Codes is here also for reference.
Column specific data is described here: Col B - Product Code - selected from the dropdown list Col C - Product Name - only required if not described in the product code Col D - Manufacturer/Supplier - if known Col E - UN Class No. from Container - if available Col F - MSDS available - "Yes" or "No" (applicable for new HS types identified) Col G - Location on Site - area where equipment is or Eq name Col H - this column is hidden and is used by the automated process Col I - Quantity of Hazardous Substance in litres or kilograms Col J - Container type - Note the container type and size (e.g. 1 x 200 litre steel drum, or 3 x 1.25 litre plastic bottle) Col K - Opened inside? - "open", "closed" or "occasional" - a can or drum with a cap/lid would be occasional Col L - Bunded? - "Yes", "No" or "NA" - "NA" is for equipment where this is irrelevant ie Prot'n, or DIS/ES Col M - Comments - for any notes/comments you wish to permanently record about this item.
Section 4 | Note A - The location of the hazardous substance, if it is stored in several associated items of equipment, can be grouped into areas, ie "33kv Switchyard" to make identifying where the Hazardous Substance is a little easier. Detail each equipment item and associated Hazardous Substance thereafter. See Grouping example below. B - The quantity of the dangerous good on-site and in each piece of equipment in some cases will be difficult to accurately quantify. Please provide an educated estimate (e.g. '150' litres, or '20' kgs, etc.) in these cases. C - The quantity values in column 'I' are automatically summed (by product code) and transferred to the 'HSR Summary Data' sheet.
Section 5 | Material Safety Data Sheets (MSDSs) should be stored in a central location, the Site Register has been selected as the appropriate place for this. A generic set of MSDSs was placed on each site after the initial site surveys were carried out and they should always be readily available to people working at the location. MSDSs provide important information about the substances people are working with and the hazards associated with those substances. MSDSs also provide information to others handling the substance, e.g. in storage and transport. The information given on an MSDS allows users to: • Use substances correctly and safely; • Understand safety recommendations and the rationale for these recommendations; • Be aware of the consequences of failure to follow these recommendations; • Recognise symptoms of overexposure; and • Know how to respond to emergency situations.
Undertaking an Annual Review
Section 6 | Undertake an annual review of the Hazardous Substances Register (HSR) to ensure that the: A - HSNO Responsibilities are correct for the site. Refer to requirements in section 2 above. B - HSNO Certification details are correct. Refer to the requirements in section 2 above. C - Hazardous Substance Data is updated and correct for the site. This refers to the data in section 3 above. NOTE there should be a copy of the certificates in the Site Register's Hazardous Substance Information section. There is a 5 year rolling program for the certification inspections of all Transpower Sites and the dates for these can be confirmed on the Transpower Contractors/ Consultants website. Use email link below and left.
Click here to send e-mail | Notify Transpower's Safety & Health Group by email of any newly identified hazardous substances stored or used on site, for which there is no electronic MSDS available on the Transpower Contractors/ Consultants website; and update the Hazardous Substances Register accordingly.
Click here to access Transpower website | Electronic copies of the following are available on the Transpower Contractors/ Consultants website http://www.transpower.co.nz/ for you to download: > Product Safety Stewardship Standard TP.AG 47.19 > Site Hazardous Substances Registers (for your location) > Material Data Safety Sheets (MSDS) > Emergency Response Plans Flip Chart > Certification Inspection Schedule > Test Certificates (Location and Stationary Container) > Erma Quick Guides
Instructions for Data Entry
Step 1 | Move the cursor onto the cell into which you require to enter data.
Step 2 | Type in the necessary information, and hit the [Enter] key when complete.
Step 3 | In the 'Product Name' key, enter either the manuafacturer's/ supplier's marketing name for the product, or its common name.
Step 4 | In the 'Other Names' field, enter alternatives under which the substance may be known as (e.g. Diesel is also known as ADO).
Step 5 | Location on Site', this is where the substance is stored on site. Each location should develop its own code for storage locations on site, this location code will enable all substances stored in the same area to be readily identified by using the 'in-built' data filter function.
Step 6 | MSDS Location - where the hard copies are kept.
Step 7 | Hazard Class': Substances should be classified as detailed in Transport of Dangerous Goods Standard as to whether they are Class 3.1, 3.2 etc.
Step 8 | 'UN No.'; Enter the United Nations Number for the substance in question, normally detailed on MSDS's.
Step 9 | Enter any comments which may be of local benefit, e.g.. supplier's name.
Step 10 | There are 3 miscellaneous categories (X1 - Misc… to X3 - Misc…) for various different types of misc substances.
Please don't use any Substance types other than those in the dropdown list in the Product Code column - Column B
Note: | If you have any misc substances please look up their Hazard Classification from on the product or the MSDS and apply an 'x' in the respective row/column (L28-R30) on the HSR Summary Data sheet. If unsure contact SafetyServices@transpower.co.nz
Data Filter
If you have a large number of hazardous materials stored on site, then quickly locating their storage location may be difficult. The 'Hazardous Substances Register' has a built in 'Data Filter' to enable the quick selection of relevant data. To use this feature, follow these steps:
Step 1 | Click your mouse onto the ▼ located in the header box of the item of interest. | ß | located in the header box of the item of interest.
Step 2 | From the dropdown menu that appears (alphabetically sorted), selected the item or criteria required
Step 3 | The database will automatically filter out the substances that meet the criteria selected. To narrow a
search further, additional filters can be applied to additional header columns.
Step 4 | Re-click mouse onto the ▼ and select 'All' from the dropdown menu/s to reset your database. | ß | and select 'All' from the dropdown menu to reset your database.
Print Instructions

## List (hidden)
Product Codes
Bunding?
A - Asbestos | A
BR - Battery Acid - Replenishment | BR | Yes
BS - Battery Acid - Sealed | BS | No
BV - Battery Acid - Vented | BV | N/A
C - Cobalt Chloride | C
D - Diesel | D
H - Hydrogen | H
G - Gas (not listed) | G
Ga - Oxygen | Ga
Gb - Acetylene | Gb
Gc - Nitrogen | Gc
Gd - Carbon Dioxide | Gd
K - Cleaning Solutions | K
Ke/T - Kerosine or Turpentine | Ke/T
L - Lubricating Oils | L
M - Mercury | M
N - Ammonia | N
O - Insulating Oil | O
P - Polychlorinated Biphenyls | P
S - Sulphur Hexaflouride | S
Su - Sulphur | Su
V - Solvents (General) | V
X1 - Miscellaneous | X1
X2 - Miscellaneous | X2
X3 - Miscellaneous | X3

## Revision Management (hidden)
Back to INDEX
HSR Revision Management
HSR Revision
The Hazardous Substance Registers (HSRs) are .xls spreadsheets and all conform to a standard naming convention.
ie "HSNO-XXX-RevX.xls"
The 'XXX' refers to the standard site abbreiviations as detailed in TP.AG 10.11 - ie INV, BPE, TMN etc
The 'X' in RevX refers to the revision number - ie Rev3 (first issued version's revision number)
These file names need to stay in this format as the master database (managed and maintained by Transpower) looks for the files named in this way for the extraction of the relevant data.
The Current Revision
The most current revision of the HSR spreadsheets are held by Transpower in a secure area on their network. A copy of these will always be available for download on the Contractor's/Consultant's area of their website. The current revision will change once the Transpower Safety & Health Manager receives and approves an updated HSR from the contractor and updates the NZ database.
Obtaining and returning the latest HSR
1 | The current versions of the HSRs will be available for download from the Contractors/Consultants area of Transpowers Website. They will be sorted into Contract Groups and will be stored as .zip files for downloading convenience and speed. Note - they will be available for download by anyone who has access to this area of the Website so contractors will need to ensure they manage this part of the process carefully to avoid duplication errors.
2 | Once downloaded please refer to the instructions and then carry out the site HS reviews and update the data on the 'Data Capture Sheet'.
Once the HS review is complete and the HS Register has been updated please ensure you update the HSR History sheet and resave the HSR with it's new revision number. This will be the next number after the downloaded version's number - ie downloaded Rev3 therefore new version is Rev4.
| After you have done this please print the HSR Summary sheet for inclusion in the Hazardous Substances section of the site registers kept on site. This should replace the existing register. | Email link
| When completed email it back to the Safety & Health team at Transpower using the email address safetyservices@transpower.co.nz - see link to right -> | safetyservices@transpower.co.nz
The SafetyServices team at Transpower will update the master database and upload the new revision of that HSR to the Contractor's/Consultant's area of the website. This updated file will then becomes the new current HSR revision and is available for download.

## Revision History (hidden)
Back to INDEX
HSR Revision History
Please document the activities/changes that were undertaken/made for this revision. Please note that this revision once accepted by Transpower's Safety & Health Team will be updated onto the Transpower Website with the new revision no. for example:-
eg | Rev6 | 2009-07-05 | Annual HS survey and documentation updates carried out as per service specification. Completed by Jo Bloggs
History
| Rev No. | Date | Details
| Rev1 | 2005-10-04 | Initial site survey to determine quantities and types of HS on site
| Rev2 | 2006-06-01 | Modifications of HSNO Register spreadsheets to detail HS to be removed from sites (ie no non essential item to be kept on site)
| Rev3 | 2008-09-01 | Modifications to Register spreadsheet to allow for auto data extraction to master database. Addition of certification details information and relevant persons with site responsibilities. Addition of Sign calculation code to enable contractors to determine and effect sign updating if HS changes necessitate this. Updates to Instructions Addition of Index, Revision Management information sheet and Revision History sheet
| Rev4 | 2008-11-20 | Added mods to fix auto save before exit function.
| Rev5 | 22/01/2009 | Updates applied to Instructions and associated information
| Rev6 | 2011-03-18 | Code Mods required to comply with Excel 2007
| Rev16 | 2016-01-13 | Annual HS survey and documentation updates carried out as per service specification.
| Rev17 | 2017-01-09 | Annual HS survey and documentation updates carried out as per service specification.
| Rev18 | 2018-01-09 | Annual HS survey and documentation updates carried out as per service specification.

## Data Capture Sheet
General Data
Name of Inspector: | L. Grant |  | Site Name: | OAM | Oamaru |  | SS3 |  | This site requires a Location Certificate?
Date of inspection: | 2025-01-08 |  | Emergency Response Plan Flip Chart Available and Current (yes/no)?: |  |  |  | Yes |  | No |  |  | HSNO Responsibilities |  | Name | Company | Function/Role | Approved Handler | Certificate
Time of inspection: | 12:00 |  | MSDS Available and Current (yes/no)?: (In Site Register) |  |  |  | Yes |  | Click here for Info. | [7 empty] | Certificate No. | Expiry Date
[12 empty] | 1 | Person in Charge | Duncan Ormandy | Omexom | Supervisor | - | 2029-09-03
[12 empty] | 2 | Approved Handler 1 | Jason Walker | Omexom | Electrician | - | 2029-09-03
[12 empty] | 3 | Approved Handler 2 | Carl Carlson | Omexom | Maintainer | - | 2029-09-03
Product Code | Product Name - if not described in Code | Manufacturer or Supplier Name | UN Class number on container | Material Safety Data Sheet available? For new HS identified | Location on Site |  | Estimated values are in Red Quantity (Kg/Lts) | Container Type | Open container inside? Closed Occasional Open | Bunded Y/N/NA | Comments | HSNO Certification Details
BS - Battery Acid - Sealed | 12TD150F | Genesis |  |  | 48v DC Power Supply 1 (P19) | BS | 80 |  |  | No | 8x Batteries in panel - 46kg each | Required? | Certification Type? | Site |  |  | Certificate No. | Expiry date
BS - Battery Acid - Sealed | 12TD150F | Genesis |  |  | 48v DC Power Supply 2 (P9) | BS | 80 |  |  | No | 8x Batteries in panel - 46kg each | No | Location Certificate | OAM - Oamaru - SS3
BS - Battery Acid - Sealed | GP50G09 | Absolyte |  |  | Station Battery Bank 1 | BS | 1600 |  |  | No | 54 * batteries in Battery Room | No | Stationary Container Certificate/s
BS - Battery Acid - Sealed | 12TM-200 | Enersys |  |  | Station Battery Bank 2 | BS | 1944 |  |  | No | 54 * batteries in Battery Room | Stationary Container Certification (if required)
[12 empty] | Item | Type | Description | HS Type | Capacity | Certificate No. | Expiry date | Bunded OK?
S - Sulphur Hexaflouride |  |  |  |  | CB 252 | S | 0.252 |  |  | No |  | 1 | Stationary Container 1
S - Sulphur Hexaflouride |  |  |  |  | CB 312 | S | 0.252 |  |  | No |  | 2 | Stationary Container 2
[12 empty] | 3 | Stationary Container 3
O - Insulating Oil |  |  |  |  | LST 1 | O | 780 |  |  | No |  | 4 | Stationary Container 4
O - Insulating Oil |  |  |  |  | LST 2 | O | 1000 |  |  | No |  | 5 | Stationary Container 5
O - Insulating Oil |  |  |  |  | T1 | O | 23150 |  |  | Yes |  | 6 | Stationary Container 6
O - Insulating Oil |  |  |  |  | T2 | O | 23150 |  |  | Yes |  | 7 | Stationary Container 7
[12 empty] | 8 | Stationary Container 8
O - Insulating Oil |  |  |  |  | VT 3 | O | 195 |  |  | No |  | 9 | Stationary Container 9
O - Insulating Oil |  |  |  |  | VT 4 | O | 476 |  |  | No |  | 10 | Stationary Container 10
S - Sulphur Hexaflouride |  |  |  |  | CB 82 | S | 38 |  |  | No
S - Sulphur Hexaflouride |  |  |  |  | CB 62 | S | 38 |  |  | No
Note on Q7: Enter N/A if not required
Note on Q13: Leave blank if not required
Note on R7: Leave blank if not required
Note on R13: Leave blank if not required
Note on S7: Leave blank if not required
Note on S13: Leave blank if not required
Note on T5: Enter N/A if not required
Note on T7: Leave blank if not required
Note on T9: Leave blank if not required
Note on T13: Leave blank if not required
Note on U5: Leave blank if not required
Note on U7: Leave blank if not required
Note on U9: Leave blank if not required
Note on U13: Leave blank if not required
A= Asbestos; BR= Battery Acid (replenishment); BS= Battery Acid (sealed); BV= Battery Acid (vented); C = Cobalt Chloride; D= Diesel; H= Hydrogen; G=Gas; K= Cleaning Solutions; L= Lubricating Oils; M= Mercury; N= Ammonia; O=Oil; P= Polychlorinated Biphenyls; S = Sulphur hexafluoride; V= Solvents (general); X= Miscellaneous

## HSR Summary Data
| Hazardous Substances Register - Summary Sheet | [7 empty] | Quantity Values |  | 2.2, 3, 6, 8, 9, |  |  |  | DoubleClick to update Sign Type & Quantity Values
| Site Name: | Oamaru | OAM | SS3 | Date of Inspection: | 2025-01-08 |  | Surveyed by | Previous | Current
| MSDS Available: | Yes | Emergency Response Plan on site: |  |  | Yes |  | L. Grant
Product Code | Product Name | Other Names | UN No. | UN Class. | Hazard Classification. | Quantity (Litres or Kgs) | Lts or Kgs | Comment | 2017-01-09 | 2018-01-09 | 2.1 | 2.2 | 3 | 4.1 | 5 | 6 | 8 | 9
S | Sulphur Hexafluoride | SF6; Sulphur fluoride | 1080 | 2.2 | Non Hazardous | 76.504 | Kgs | CAS 2551-62-4; Liquified, non-flammable, odourless gas. Much denser than air (5.1). Ozone depleting chemical. | 76.504 | 76.504 |  | x
M | Mercury |  | 2809 | 8 | 6.1B; 6.5B; 6.8A; 6.9A; 8.1A; 9.1A; 9.2B; 9.3A | 0 | Ltrs | CAS 7439-97-6; Silvery corrosive and harmful liquid. Evolves toxic vapours. Forms explosive compounds with amonia, amines and acetylene. Amalgamates with some metals. | 0 | 0
H | Hydrogen |  | 1049 | 2.1 | 2.1.1A | 0 | Kgs | CAS 1333-74-0; Flammable odourless gas. Significantly less dense than air (0.07). If a leak occurs, high pressure jet of gas may catch fire and burn with a colourless flame. Identify if only in existing sealed equipment. | 0 | 0
P | Polychlorinated Biphenyls | PCB's | 2315 | 9 | 6.8A, 6.9A and 9.1A | 0 | Ltrs | CAS 11097-69-1; Harmful by ingestion and skin contact. Possible carcinogen, environmental pollutant. Identify if only in existing sealed equipment. | 0 | 0
A | Asbestos |  | 2212 | 9 | 9 | 0 |  | CAS 1332-21-4; Mineral fibres of varying length. Non combustible. Inhalation of the dust of asbestos fibres is dangerous (carcinogen) and therfore exposure to the dust should be avoided at all times. Always preevent the generation of asbestos dust. Crocidolite (blue asbestos) should be regarded as the most hazardous type of asbestos. | 0 | 0
BR | Battery Acid (replenishment) | Sulphuric Acid | 1830 | 8 | 6.1D; 6.7A; 6.9A; 8.1A; 8.2B; 8.3A; 9.1D | 0 | Ltrs | CAS 7664-93-9; Colourless, oily liquid, density up to 1.840 kg/L. In the presence of moisture highly corrosive to most metals. Include the quantity of acid used for battery 'top-up' . | 0 | 0
BS | Battery Acid (sealed units) | Sulphuric Acid | 1830 | 8 | 6.1D; 6.7A; 6.9A; 8.1A; 8.2B; 8.3A; 9.1D | 3704 | Ltrs | CAS 7664-93-9; Colourless, oily liquid, density up to 1.840 kg/L. In the presence of moisture highly corrosive to most metals. | 352 | 1415.5 | [5 empty] | x | x | x
BV | Battery Acid (vented units) | Sulphuric Acid | 1830 | 8 | 6.1D; 6.7A; 6.9A; 8.1A; 8.2B; 8.3A; 9.1D | 0 | Ltrs | CAS 7664-93-9; Colourless, oily liquid, density up to 1.840 kg/L. In the presence of moisture highly corrosive to most metals. | 0 | 0
N | Ammonia Solution |  | 2672 | 8 | 8 | 0 | Ltrs | CAS 7664-41-7; Flammable; Corrosive | 0 | 0
O | Insulating Oil | Naphthenic Oil; Crude Oil - Low Flammability |  |  | 3.1D; 6.1E; 6.3B; 6.7B; 9.1C | 48751 | Ltrs | CAS 8002-05-9; Identify if only in existing sealed equipment. | 48751 | 48751 |  |  | x |  |  | x |  | x
D | Diesel Oil | Automotive gas oil ADO | 1202 |  | 3.1D; 6.1E; 6.3B; 6.7B; 9.1B | 0 | Ltrs | Detail storage quantity and container type (tank or drum) | 0 | 0
Ke/T | Kerosine Turpentine |  | 1223 1299 | 3 | 3.1C; 6.1E; 6.3B; 9.1B | 0 | Ltrs | Identify if only in closed containers. CAS 9005-90-7; Mixture of resin and volatile oil. Immiscible with water. | 0 | 0
Su | Sulphur |  | 1350 | 4.1 | 4.1.1B;6.4A | 0 | Kgs | CAS 7704-34-9; Dry powdered form of solid; Flammable | 0 | 0
C | Cobalt Chloride | CoCl2; Cobalt | 3089 | 4.1 | 4.1.1B; 6.4A; 6.5A ;6.5B; 6.7B; 6.8B; 6.9A | 0 | Kgs | CAS 7440-48-4; Metal powder, flammable, N.O.S. | 0 | 0
K | Cleaning Solutions |  |  |  |  | 0 | Ltrs |  | 0 | 0
L | Lubricating Oils |  |  |  |  | 0 | Ltrs | General lubricating oils used in miscellaneous equipment on site. | 0 | 0
V | Solvents (General) | Flammable Solvents, not otherwise stated (N.O.S) |  | 3 | 3.1B; 6.4A; 9.1D | 0 | Ltrs |  | 0 | 0
G | Gas General (not listed below) |  |  |  |  | 0 | Ltrs |  | 0 | 0
Ga | Oxygen Bottle(s) |  | 1072 | 2.2; 5.1 | 5.1.2A | 0 | Kgs | CAS 7782-44-7; Non-flammable, odourless gas. Strong supporter of combustion. Slightly denser than air (1.1). Combustible materials impregnated with oxygen may ignite readily. | 0 | 0
Gb | Acetylene Bottle(s) |  | 1001 | 2.1 | 2.1.1A | 0 | Kgs | CAS 74-86-2; Flammable, disolved gas with slight odour. Less dense than air (0.907). Contained in cylinders containing a solvent, usually acetone, and a porous mass. Rough handling and exposure to local heating should be avoided. Results of such rough handling or heating may be delayed explosion. Empty cylinders must be treated the same as full cylinders. | 0 | 0
Gc | Nitrogen Bottle(s) |  | 1066 | 2.2 | 2.2 | 0 | Kgs | CAS 7727-37-9; Non-flammable, non toxic and odourless gas. It is a simply asphixiant and in sufficient quantities can displace the oxygen levels to below those necessary to sustain life. | 0 | 0
Gd | Carbon Dioxide | Carbonic acid anhydride; Carbonic anhydride; Dry ice | 1013 | 2.2 | 2.2 | 0 | Ltrs | CAS 124-38-9; Compressed, liquified, non-flammable gas. Denser than air (1.5). | 0 | 0
Other chemical products on-site > 5 litres: (List hazardous chemical name below and add quantities and container types only as above)
X1 | X1 - Miscellaneous |  | … | … | … | 0 |  |  | 0 | 0
X2 | X2 - Miscellaneous |  | … | … | … | 0 |  |  | 0 | 0
X3 | X3 - Miscellaneous |  | … | … | … | 0 |  |  | 0 | 0
[5 empty] | Note 0 |  | Used at HVDC sites for cleaning Mercury Arc Valves
[5 empty] | Note 1 |  | Items identified by this colour shouldn't be kept on an unmanned site!
HSNO Responsibilities |  |  |  |  | Note 2 |  | Items identified by this colour should be removed and replaced with an alternative product.
Item | Type | Name | Role | Certificate No. | Expiry Date
1 | Person in Charge | Duncan Ormandy | Supervisor | - | 2029-09-03 |  |  | Sign F, HS Classes 2.2, 3, 6, 8, 9,
2 | Approved Handler 1 | Jason Walker | Electrician | - | 2029-09-03
3 | Approved Handler 2 | Carl Carlson | Maintainer | - | 2029-09-03 |  |  |  | Hazardous Substances Register - Summary Sheet
F
Location Certification |  | If required
| Required | Site |  | Certificate No. | Expiry Date
| No | OAM - Oamaru - SS3 |  | 0 | 0
[10 empty] | Site name |  |  | Code |  | Group
Stationary Container Certification |  |  |  | Required? | No |  |  |  | Oamaru |  |  |  | OAM |  | SS3
Item | Type | Description |  | Certificate No. | Expiry | Bund OK? |  |  | Surveyed on |  |  |  | 2025-01-08
1 | Stationary Container 1 |  |  | 0 | 0 | 0
2 | Stationary Container 2 |  |  | 0 | 0 | 0 |  |  | HSR Revision |  | HSNO-OAM-Rev 25.xls
3 | Stationary Container 3 |  |  | 0 | 0 | 0
4 | Stationary Container 4 |  |  | 0 | 0 | 0
5 | Stationary Container 5 |  |  | 0 | 0 | 0
6 | Stationary Container 6 |  |  | 0 | 0 | 0
7 | Stationary Container 7 |  |  | 0 | 0 | 0
8 | Stationary Container 8 |  |  | 0 | 0 | 0 |  | Note - The actual sign layout may differ from the image above.
9 | Stationary Container 9 |  |  | 0 | 0 | 0
10 | Stationary Container 10 |  |  | 0 | 0 | 0