## List (hidden)
AD
KT
Not started | LW
In progress | RT
In first review | HM
In second review | DF
Complete | ADT
HP
LS
MSR
MS
DLS
JC
LB
TR
JW
AF
RK
KP
SJ
JM
IM
GC
Pending audit sign off
Pending reconfirmation

## CoverSheet
Transpower Information Disclosure Schedules F1-7a, G1-8, SO1
| Disclosure Year (year ended) | 2025-06-30
Prepared and Published on 24 October 2025

## Directors' certificate
Directors' Certificate - October 2025

## Table of Contents
TRANSPOWER INFORMATION DISCLOSURE
Table of Contents
Compliance
| Directors' Certificate | Transpower-inserted tab
| Assurance Report | Transpower-inserted tab
Financial Information
F1 | Value of the Regulatory Asset Base (RAB Roll Forward)
F2 | Operating Expenditure (Opex): Actual
F3 | Base Capital Expenditure (Base Capex): Actual Commissioned
F4 | Comparison of Forecasts for Opex and base Capex Commissioning
F5 | Major Capital Expenditure (Major Capex)
F6 | Regulated Revenue
TP1 | ROI and profit calculations required by paragraphs 8.6 to 8.13 | Transpower-inserted tab
TP2 | Major project costs required by paragraph 8.19.1 | Transpower-inserted tab
TP3 | Major project timing required by paragraph 8.19.2 | Transpower-inserted tab
TP4 | Fully commissioned project details required by paragraph 8.20 | Transpower-inserted tab
TP5 | Related party transactions | Transpower-inserted tab
TP6 | Investment contracts | Transpower-inserted tab
Grid Management Information
G1 | Transmission System Statistics
G2 | Grid Demand and Injection
G3 | Grid Exit Point (GXP) Connection Capacity and Demand (Actual and Forecast)
G4 | Quality of Supply: Grid Outputs and Performance Measures
G5 | Quality of Supply: Interconnection Assets
System Operator
SO1 | System Operator

## Assurance report
Assurance Report - October 2025
.

## F1. RAB
[10 empty] | Transpower |  | Disclosure Date |  | 2025-10-24
SCHEDULE F1: VALUE OF THE REGULATORY ASSET BASE (RAB ROLL FORWARD) | [11 empty] | Disclosure Year (year ended) |  | 2025-06-30
Disclosure of line items required from disclosure year 2026 onward are specified in column U. The opening balance of the RAB has been adjusted to bring it in line with the RAB balance in the Annual Compliance Statements. The Commission's decision to allow IDC cap revenue reductions to be subtracted off depreciation means that the ID and ACS RAB's will be aligned going forward. https://comcom.govt.nz/__data/assets/pdf_file/0020/363152/Information-Disclosure-Transpower-Amendment-Determination-2024-Final-Decision-Reasons-Paper-13-November-2024.pdf Clause 2.83 align IPP RAB with ID RAB
ref
5 | F1(i): Value of Regulatory Asset Base (RAB Roll Forward)
6 | [7 empty] | RAB | RAB | RAB | RAB | RAB
7 | [7 empty] | CY-4 | CY-3 | CY-2 | CY-1 | CY
8 | [7 empty] | ($M) | ($M) | ($M) | ($M) | ($M)
9 |  |  | Opening RAB value (excl ACA) |  |  |  |  | 4839141597.7351 | 4864216474.6736 | 4882848062.6986 | 4956466525.2144 | 5050212277.4996 |  |  | Opening balance adjustment | 20930228.6648
10 |  | plus | Value of found assets |  |  |  |  | 0 | 0 | 0 | 0 | 0
11 |  | less | Value of disposed assets |  |  |  |  | 9524636.402 | 8994642.09 | 7467082.173 | 3060788.84 | 3678767.98
12 |  | less | Value of lost assets |  |  |  |  | 0 | 0 | 0 | 0 | 0
13 |  | less | Total depreciation |  |  |  |  | 255608864.9384 | 247604830.2337 | 250836346.7763 | 255632095.5696 | 267645223.8333
14 |  | plus | Total Value of commissioned assets (including acquired assets and costs incurred after an asset is first commissioned) |  |  |  |  | 294848300.5629 | 275231060.3487 | 331921891.4651 | 331508408.0299 | 445510163.2116
15 |  | plus | Adjustment to opening RAB resulting from change in cost allocation |  |  |  |  | 0 | 0 | 0 | 0 | 0
16 |  |  | Closing RAB value |  |  |  |  | 4868856396.9576 | 4882848062.6986 | 4956466525.2144 | 5029282048.8347 | 5224398448.8979
17
18 |  | plus | Opening RAB of Anticipatory Connection Assets (ACA)
19 |  |  | Opening RAB value including Anticipatory Connection Assets (ACA) | [8 empty] | 5050212277.4996
20 |  |  | Value of commissioned ACA |  |  |  |  | 0 | 0 | 0 | 0 | 0
21
22 | F1(ii): Unallocated Regulatory Asset Base
23 | [7 empty] | Unallocated RAB | Unallocated RAB | Unallocated RAB | Unallocated RAB | Unallocated RAB
24 | [7 empty] | CY-4 | CY-3 | CY-2 | CY-1 | CY
25 | [7 empty] | ($M) | ($M) | ($M) | ($M) | ($M) |  |  | Unallocated includes system operator asset and depreciation
26 |  |  | Unallocated opening RAB value |  |  |  |  | 4872791125.4897 | 4910918248.5235 | 4933005584.1313 | 5009056431.4634 | 5094097471.8646 |  |  | Opening balance adjustment | 20873724.8231
27 |  | plus | Found assets |  |  |  |  | 0 | 0 | 0 | 0 | 0
28 |  | less | Asset disposals |  |  |  |  | 9524636.402 | 8994642.09 | 7467082.173 | 3060788.84 | 3678767.98
29 |  | less | Lost Assets |  |  |  |  | 0 | 0 | 0 | 0 | 0
30 |  | less | Total depreciation |  |  |  |  | 266199644.7247 | 259858758.6909 | 264897147.1428 | 270196924.7519 | 280572164.3518
31 |  | plus | Assets commissioned |  |  |  |  | 318560131.3429 | 290940736.3887 | 348415076.648 | 337425029.1699 | 451496639.6366
32 |  |  | Unallocated closing RAB value |  |  |  |  | 4915626975.7059 | 4933005584.1313 | 5009056431.4634 | 5073223747.0415 | 5261343179.1694
33
34 |  |  | Result of cost allocation ratio (opening values) |  |  |  |  | 99.31% | 99.05% | 98.98% | 98.95% | 99.14%
35
36 | F1(iii): Calculation of Revaluation Rate and Revaluation of Assets
37
38 |  |  | CPI4 | [8 empty] | 0 | From 30/6/2026 |  | Required from disclosure year 2026
39 |  |  | CPI4-4 | [8 empty] | 0 | From 30/6/2026 |  | Required from disclosure year 2026
40 |  |  | Revaluation rate (%) | [8 empty] | 0%
41
42 | [8 empty] | Unallocated RAB ($000) |  | RAB ($000)
43 |  |  |  | Total opening RAB value |  |  |  |  | 5094097471.8646 |  | 5050212277.4996 |  |  |  | Required from disclosure year 2026
44 |  | less |  | Opening value of assets with nil physical life, and disposed and lost assets |  |  |  |  | 0 |  | 0 |  |  |  | Required from disclosure year 2026
45
46 |  |  |  | Total opening RAB value adjusted for fully depreciated, disposed and lost assets |  |  |  |  | 5094097471.8646 |  | 5050212277.4996 |  |  |  | Required from disclosure year 2026
47
48 |  |  | Total revaluations | [5 empty] | 0 |  | 0 |  |  |  | Required from disclosure year 2026
49
50
51 | F1(iv): Disclosure by Asset Category
52 |  |  |  |  | HVAC Substations | HVAC Lines and Transmission cables | HVDC Substations and Submarine cables | HVDC Lines | Easements | Intangibles | IST | Business Support | Pseudo Assets | Total
53 |  |  |  |  | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M)
54 |  |  | Opening RAB value (CY) |  | 1780394351.294 | 2057132226.8675 | 394749812.8053 | 101555152.6785 | 300722488.1399 | 49384353.0462 | 205040236.8961 | 96405651.6083 | 43897775.7712 | 5050212277.7717
55 | plus |  | Found assets |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56 | less |  | Asset disposals |  | 1154155.54 | 1954375.24 | 0 | 38381.55 | 0 | 67584 | 1041172.42 | -576900.77 | 0 | 3678767.98
57 | less |  | Lost Assets |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58 | less |  | Total depreciation |  | 79749834.0312 | 87510276.4084 | 25108470.4016 | 4803164.3912 | 580471.21 | 20859812.3868 | 18413572.663 | 28624268.9478 | 1995353.3933 | 267645223.8333
59 | plus |  | Total Assets commissioned |  | 191922196.9651 | 136604206.23 | 32199072.2 | 3590023.9 | 4.8021e-09 | 19809664.5726 | 18896818.4419 | 42488180.902 | 0 | 445510163.2116
60 | less |  | Adjustment to opening RAB resulting from change in cost allocation | [10 empty] | 0
61 |  |  | Closing RAB value (CY) |  | 1891412558.6878 | 2104271781.449 | 401840414.6036 | 100303630.6373 | 300142016.9299 | 48266621.232 | 204482310.255 | 110846464.3326 | 41902422.3779 | 5224398449.1701
62
63 | plus |  | Opening RAB value of Anticipatory Connection Assets (ACA)
64 |  |  | Opening RAB value including Anticipatory Connection Assets (ACA) |  | 1780394351.294 | 2057132226.8675 | 394749812.8053 | 101555152.6785 | 300722488.1399 | 49384353.0462 | 205040236.8961 | 96405651.6083 | 43897775.7712 | 5050212277.7717 | Required from disclosure year 2026
65 |  |  | Commissioned ACA |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Required from disclosure year 2026
66
67
68 | F1(v): Found Assets
69 |  |  |  |  | HVAC Substations | HVAC Lines and Transmission cables | HVDC Substations and Submarine cables | HVDC Lines | Easements | Intangibles | IST | Business Support | Pseudo Assets | Total
70 |  |  |  |  | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M)
71 |  |  |  | RAB value (CY) | [9 empty] | 0
72 |  |  |  | Unallocated RAB value (CY) | [9 empty] | 0
73
74 | F1(vi): Asset Disposals
75 |  |  |  |  | HVAC Substations | HVAC Lines and Transmission cables | HVDC Substations and Submarine cables | HVDC Lines | Easements | Intangibles | IST | Business Support | Pseudo Assets | Total
76 |  |  |  |  | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M)
77 |  |  |  | RAB Asset Sales - Related Party (CY) | [9 empty] | 0
78 |  |  |  | RAB Asset Sales - Regulated Supplier (CY) | [9 empty] | 0
79 |  |  |  | RAB Asset Sales - Other (CY) | [9 empty] | 0
80 |  |  |  | RAB Asset Disposals (CY) | 1154155.54 | 1954375.24 | 0 | 38381.55 | 0 | 67584 | 1041172.42 | -576900.77 | 0 | 3678767.98
81 |  |  |  | Unallocated RAB Asset Sales - Related party (CY) | [9 empty] | 0
82 |  |  |  | Unallocated RAB Asset Sales - Regulated Supplier (CY) | [9 empty] | 0
83 |  |  |  | Unallocated RAB Asset Sales - Other (CY) | [9 empty] | 0
84 |  |  |  | Unallocated RAB Asset Disposals (CY) | 1154155.54 | 1954375.24 | 0 | 38381.55 | 0 | 67584 | 1041172.42 | -576900.77 | 0 | 3678767.98
85
86 | F1(vii): Lost Assets
87 |  |  |  |  | HVAC Substations | HVAC Lines and Transmission cables | HVDC Substations and Submarine cables | HVDC Lines | Easements | Intangibles | IST | Business Support | Pseudo Assets | Total
88 |  |  |  |  | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M)
89 |  |  |  | RAB value (CY) | [9 empty] | 0
90 |  |  |  | Unallocated RAB value (CY) | [9 empty] | 0
91
92 | F1(viii): Depreciation
93 |  |  |  |  | HVAC Substations | HVAC Lines and Transmission cables | HVDC Substations and Submarine cables | HVDC Lines | Easements | Intangibles | IST | Business Support | Pseudo Assets | Total
94 |  |  |  |  | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M)
95 |  |  |  | Depreciation and impairment on the RAB (CY) | 79749834.0312 | 87510276.4084 | 25108470.4016 | 4803164.3912 | 580471.21 | 20859812.3868 | 18413572.663 | 28624268.9478 | 1995353.3933 | 267645223.8333
96 |  |  |  | Depreciation and impairment on the unallocated RAB (CY) | 79749834.0312 | 87510276.4084 | 25108470.4016 | 4803164.3912 | 580471.21 | 33786752.9052 | 18413572.663 | 28624268.9478 | 1995353.3933 | 280572164.3518
97
98
99 | F1(ix): Value of Commissioned Assets
100 |  |  |  |  | HVAC Substations | HVAC Lines and Transmission cables | HVDC Substations and Submarine cables | HVDC Lines | Easements | Intangibles | IST | Business Support | Pseudo Assets | Total
101 |  |  |  |  | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M)
102 |  |  |  | RAB value (CY) | 191922196.9651 | 136604206.23 | 32199072.2 | 3590023.9 | 4.8021e-09 | 19809664.5726 | 18896818.4419 | 42488180.902 | 0 | 445510163.2116
103 |  |  |  | Unallocated RAB value (CY) | 191922196.9651 | 136604206.23 | 32199072.2 | 3590023.9 | 4.8021e-09 | 25796140.9976 | 18896818.4419 | 42488180.902 | 0 | 451496639.6366
104
105
106
107 | F1(x): Anticipatory Connection Assets (ACA)
108 | [5 empty] | New investment contracts | Unit
109 |  | New investment contract - total capacity |  |  |  | 0 | (MW)
110 |  | New investment contract - ACA capacity |  |  |  | 0 | (MW) | [7 empty] | Required from disclosure year 2026
111 |  | Percentage of anticipatory capacity |  |  |  |  | (%) | [7 empty] | Required from disclosure year 2026
112 | [14 empty] | Required from disclosure year 2026
113 |  | New investment contract costs |  |  |  | 152860673.48 | ($M)
114 |  | New investment contract cost allocated to ACA |  |  |  | 0 | ($M) | [7 empty] | Required from disclosure year 2026
115 |  | Percentage of cost allocated to ACA |  |  |  | 0% | (%) | [7 empty] | Required from disclosure year 2026
116 | [14 empty] | Required from disclosure year 2026
117

## F2.Opex
[5 empty] | Transpower |  | Disclosure Date |  | 2025-10-24
SCHEDULE F2: OPERATING EXPENDITURE (OPEX): ACTUAL | [6 empty] | Disclosure Year (year ended) |  | 2025-06-30
Disclosure of line items required and not required from disclosure year 2026 onward are specified in column N.
ref
5 | F2(i): Operating Expenditure (Actual Totals)
6 |  |  |  |  | CY-4 | CY-3 | CY-2 | CY-1 | CY
7 |  |  |  |  | ($M) | ($M) | ($M) | ($M) | ($M)
8 |  | Grid - maintenance projects |  |  | 0 | 0 | 0 | 0 | 0
9 |  | Grid - routine maintenance |  |  | 0 | 0 | 0 | 0 | 0
10 |  | IST - grid |  |  | 0 | 0 | 0 | 0 | 0
11 |  | IST - business support |  |  | 0 | 0 | 0 | 0 | 0
12 |  | Corporate |  |  | 0 | 0 | 0 | 0 | 0
13
14 |  | Grid maintenance |  |  | 110949507.76 | 107816842.63 | 133531615.7329 | 131116662.604 | 140066409.58
15 |  | ICT |  |  | 30780842.0831 | 38168116.0929 | 40962389.4729 | 45893699.5484 | 50768700.1301
16 |  | Asset Management & Operations |  |  | 66798333.6924 | 65398707.9534 | 72474796.2246 | 77986279.4156 | 87587487.2681
17 |  | Business Support |  |  | 42116951.3515 | 45441541.1037 | 55085948.0555 | 59628018.5463 | 63787820.2521
18 |  | Insurance |  |  | 18713017.07 | 22154277.9 | 26547466.96 | 30086222.1 | 32216912.76
19 |  | Total operating expenditure (includes TPM CY $1.7m) |  |  | 269358651.957 | 278979485.68 | 328602216.4458 | 344710882.2143 | 374427329.9902
20
21 |  | Comprising:
22 |  | HVAC operating expenditure |  |  | 243199816.3426 | 249948011.3196 | 294711672.393 | 306477315.2979 | 331954464.7181 | Not required from disclosure year 2026
23 |  | HVDC operating expenditure |  |  | 26158835.6144 | 29031438.0637 | 33858476.9728 | 38233566.6864 | 42467646.1422 | Not required from disclosure year 2026
24 |  | * Excluding the cost of capitalised operating leases (CY-1 $11.2 million, CY $11.8 million).
25 | F2(ii): Operating Expenditure (Actual Details)
26 |  |  |  |  | CY-4 | CY-3 | CY-2 | CY-1 | CY
27 |  |  |  |  | ($M) | ($M) | ($M) | ($M) | ($M)
28 |  | Grid | Maintenance Projects - Transmission | TL Tower | 0 | 0 | 0 | 0 | 0 |  | Old format - RT (explained to CC we will hide these rows)
29 |  | Grid | Maintenance Projects - Transmission | TL Conductor | 0 | 0 | 0 | 0 | 0 |  | Old format - RT (explained to CC we will hide these rows)
30 |  | Grid | Maintenance Projects - Transmission | TL Foundation | 0 | 0 | 0 | 0 | 0 |  | Old format - RT (explained to CC we will hide these rows)
31 |  | Grid | Maintenance Projects - Transmission | TL Insulators | 0 | 0 | 0 | 0 | 0 |  | Old format - RT (explained to CC we will hide these rows)
32 |  | Grid | Maintenance Projects - Transmission | TL Pole | 0 | 0 | 0 | 0 | 0 |  | Old format - RT (explained to CC we will hide these rows)
33 |  | Grid | Maintenance Projects - Transmission | TL Access | 0 | 0 | 0 | 0 | 0 |  | Old format - RT (explained to CC we will hide these rows)
34 |  | Grid | Maintenance Projects - AC Stations | ACS Buildings & Grounds | 0 | 0 | 0 | 0 | 0 |  | Old format - RT (explained to CC we will hide these rows)
35 |  | Grid | Maintenance Projects - AC Stations | ACS Power Transformers | 0 | 0 | 0 | 0 | 0 |  | Old format - RT (explained to CC we will hide these rows)
36 |  | Grid | Maintenance Projects - AC Stations | ACS Outdoor Circuit Breakers | 0 | 0 | 0 | 0 | 0 |  | Old format - RT (explained to CC we will hide these rows)
37 |  | Grid | Maintenance Projects - AC Stations | ACS Indoor Switchgear | 0 | 0 | 0 | 0 | 0 |  | Old format - RT (explained to CC we will hide these rows)
38 |  | Grid | Maintenance Projects - HVDC Stations | HVDC | 0 | 0 | 0 | 0 | 0 |  | Old format - RT (explained to CC we will hide these rows)
39 |  | Grid | Maintenance Projects - Other | MP Other | 0 | 0 | 0 | 0 | 0 |  | Old format - RT (explained to CC we will hide these rows)
40 |  | Total grid - maintenance projects |  |  | 0 | 0 | 0 | 0 | 0
41
42 |  | Grid | Routine Maintenance | RM Stations | 0 | 0 | 0 | 0 | 0 |  | Old format - RT (explained to CC we will hide these rows)
43 |  | Grid | Routine Maintenance | RM Transmission Lines | 0 | 0 | 0 | 0 | 0 |  | Old format - RT (explained to CC we will hide these rows)
44 |  | Grid | Routine Maintenance | RM HVDC | 0 | 0 | 0 | 0 | 0 |  | Old format - RT (explained to CC we will hide these rows)
45 |  | Grid | Routine Maintenance | RM Operating | 0 | 0 | 0 | 0 | 0 |  | Old format - RT (explained to CC we will hide these rows)
46 |  | Grid | Routine Maintenance | RM Training | 0 | 0 | 0 | 0 | 0 |  | Old format - RT (explained to CC we will hide these rows)
47 |  | Grid | Routine Maintenance | RM Contractor Transition | 0 | 0 | 0 | 0 | 0 |  | Old format - RT (explained to CC we will hide these rows)
48 |  | Total grid - routine maintenance |  |  | 0 | 0 | 0 | 0 | 0
49
50 |  | IST ICT Grid | IST ICT Grid | IT Asset Management | 0 | 0 | 0 | 0 | 0 |  | Old format - RT (explained to CC we will hide these rows)
51 |  | IST ICT Grid | IST ICT Grid | IT Transmission System Plan | 0 | 0 | 0 | 0 | 0 |  | Old format - RT (explained to CC we will hide these rows)
52 |  | IST ICT Grid | IST ICT Grid | IT Telecommunications Services | 0 | 0 | 0 | 0 | 0 |  | Old format - RT (explained to CC we will hide these rows)
53 |  | IST ICT Grid | IST ICT Grid | IT Network Services | 0 | 0 | 0 | 0 | 0 |  | Old format - RT (explained to CC we will hide these rows)
54 |  | Total IST - grid |  |  | 0 | 0 | 0 | 0 | 0
55
56 |  | IST Business Support | IST Business Support | IT Corporate services | 0 | 0 | 0 | 0 | 0 |  | Old format - RT (explained to CC we will hide these rows)
57 |  | IST Business Support | IST Business Support | IT ICT Shared Services | 0 | 0 | 0 | 0 | 0 |  | Old format - RT (explained to CC we will hide these rows)
58 |  | IST Business Support | IST Business Support | IT Security Services | 0 | 0 | 0 | 0 | 0 |  | Old format - RT (explained to CC we will hide these rows)
59 |  | Total IST - business support |  |  | 0 | 0 | 0 | 0 | 0
60
61 |  | Corporate | Corporate | CS Departmental Corporate | [6 empty] | Old format - RT (explained to CC we will hide these rows)
62 |  | Corporate | Corporate | CS Departmental Grid | [6 empty] | Old format - RT (explained to CC we will hide these rows)
63 |  | Corporate | Corporate | Grid Operating Services Costs (GOS) | [6 empty] | Old format - RT (explained to CC we will hide these rows)
64 |  | Corporate | Corporate | Reseach and Development (R&D) | [6 empty] | Old format - RT (explained to CC we will hide these rows)
65 |  | Corporate | Corporate | Investigations | [6 empty] | Old format - RT (explained to CC we will hide these rows)
66 |  | Corporate | Corporate | Insurance | [6 empty] | Old format - RT (explained to CC we will hide these rows)
67 |  | Corporate | Corporate | Ancillary Services | [6 empty] | Old format - RT (explained to CC we will hide these rows)
68 |  | Total Corporate |  |  | 0 | 0 | 0 | 0 | 0
69
70
71 |  | Grid maintenance | Grid maintenance | Preventive Maintenance | 40431729.1948 | 38780206.2535 | 44322559.6173 | 51363958.8087 | 49747927.3945
72 |  | Grid maintenance | Grid maintenance | Predictive Maintenance | 66155939.9352 | 63667881.8965 | 83568838.3356 | 71875776.3353 | 82766497.0755
73 |  | Grid maintenance | Grid maintenance | Corrective Maintenance | 3778438.99 | 4756041.55 | 4870033.59 | 6838899.04 | 6505954.67
74 |  | Grid maintenance | Grid maintenance | Proactive Maintenance | 583399.64 | 612712.93 | 770184.19 | 1038028.42 | 1046030.44
75 |  | Grid maintenance | Grid maintenance | Resilience |  |  |  |  | 0 | Required from disclosure year 2026
76 |  | Total - Grid maintenance |  |  | 110949507.76 | 107816842.63 | 133531615.7329 | 131116662.604 | 140066409.58
77
78 |  | ICT | ICT | ICT Opex | 30780842.0831 | 38168116.0929 | 40962389.4729 | 45893699.5484 | 50768700.1301 | Required from disclosure year 2026
79 |  | ICT | ICT | ICT Software as a Service |  |  |  |  | 0 | Required from disclosure year 2026
80 |  | Total - ICT |  |  | 30780842.0831 | 38168116.0929 | 40962389.4729 | 45893699.5484 | 50768700.1301
81
82 |  | Asset Management & Operations | Asset Management & Operations | Asset Management & Operations | 66798333.6924 | 65398707.9534 | 72474796.2246 | 77986279.4156 | 87587487.2681 | Required from disclosure year 2026
83 |  | Asset Management & Operations | Asset Management & Operations | Sustainability |  |  |  |  | 0 | Required from disclosure year 2026
84 |  | Total - Asset Management & Operations |  |  | 66798333.6924 | 65398707.9534 | 72474796.2246 | 77986279.4156 | 87587487.2681
85
86 |  | Business Support | Business Support | Business Support | 42116951.3515 | 45441541.1037 | 55085948.0555 | 59628018.5463 | 63787820.2521
87
88 |  | Insurance | Insurance | Insurance | 18713017.07 | 22154277.9 | 26547466.96 | 30086222.1 | 32216912.76
89
90
91 | F2(iii): Network Divestiture Expenditure
92 |  |  |  |  | CY-4 | CY-3 | CY-2 | CY-1 | CY
93 |  |  |  |  | ($M) | ($M) | ($M) | ($M) | ($M)
94 |  | Network divestiture expenses |  |  | 0 | 0 | 0 | 0 | 0
95
96 | F2(iv): Other Disclosures
97 |  |  |  |  | CY-4 | CY-3 | CY-2 | CY-1 | CY
98 |  |  |  |  | ($M) | ($M) | ($M) | ($M) | ($M)
99 |  | Third party insurance allowance |  |  | 0 | 0 | 0 | 0 | 0 | From 2026
100 |  | Self-insurance allowance |  |  | 16277974 | 17800223.6949 | 19610840.8584 | 21135822.2023 | 22324331.0621 | (only one line in old Template - unless finance reporting can do this split, we may leave it on this line)
101
102

## F3. Base Capex
[5 empty] | Transpower |  | Disclosure Date |  | 2025-10-24
SCHEDULE F3: BASE CAPITAL EXPENDITURE (BASE CAPEX): ACTUAL COMMISSIONED | [6 empty] | Disclosure Year (year ended) |  | 2025-06-30
Line items not required from disclosure year 2026 onward are specified in column M.
ref |  | Schedule F3 was reported as Commissioned Assets up until 2024. This schedule reports Capex values from 2025 onwards which is consistent with the 2024 Information Disclosure Review Final Decision on F4(ii)
5 | F3(i): Base Capex (Actual Commissioned Totals up to 2024 and 2025 Capex) |  |  |  | Commissioned | Commissioned | Commissioned | Commissioned | SPEND basis
6 |  |  |  |  | CY-4 | CY-3 | CY-2 | CY-1 | CY
7 |  |  |  |  | ($M) | ($M) | ($M) | ($M) | ($M)
8 |  | Grid - refurbishment and replacement |  |  | 205655027.4 | 176025394.64 | 210824205.44 | 241832966.76 | 348936574.68
9 |  | Grid - enhancement and development |  |  | 15288759 | 7115716 | 21873281 | 47076178.02 | 47822321
10 |  | IST |  |  | 25439233.16 | 28253820.82 | 21841730.74 | 22392572.08 | 47587019.13
11 |  | Business support |  |  | 3880413 | 17324445 | 3860306.837 | 9741593.5442 | 9582106
12 |  | Total base capex commissioned |  |  | 250263432.56 | 228719376.46 | 258399524.017 | 321043310.4042 | 453928020.81
13
14 |  | Comprising:
15 |  | HVAC base capex commissioned / Spend basis |  |  | 239003103.11 | 221738914.595 | 245085445.687 | 294962841.4042 | 407310699.31 | Not required from disclosure year 2026
16 |  | HVDC base capex commissioned / Spend basis |  |  | 11260329.45 | 6980461.865 | 13314078.33 | 26080469 | 46617321.5 | Not required from disclosure year 2026
17
18 | F3(ii): Base Capex (Actual Commissioned Totals up to 2024 and 2025 Capex) |  |  |  | Commissioned | Commissioned | Commissioned | Commissioned | SPEND basis
19 |  |  |  |  | CY-4 | CY-3 | CY-2 | CY-1 | CY
20 |  |  |  |  | ($M) | ($M) | ($M) | ($M) | ($M)
21 |  | Grid refurbishment and replacement | AC Stations | ACS Power Transformers | 27153562 | 10568565 | 25083339 | 6854812 | 33191462
22 |  | Grid refurbishment and replacement | AC Stations | ACS Outdoor to Indoor Conv | 26340361 | 33445865 | 4386357 | 3014162 | 1795688
23 |  | Grid refurbishment and replacement | AC Stations | ACS Buildings & Grounds-Seismic | 0 | 0 | 0 | 0 | 0
24 |  | Grid refurbishment and replacement | AC Stations | ACS Buildings & Grounds | 5459697.4 | 5125842.64 | 9860131.44 | 14096915.76 | 48463912.68
25 |  | Grid refurbishment and replacement | AC Stations | ACS Outdoor Circuit Breakers | 6041727 | 1257850 | 469458 | 203297 | 1440364
26 |  | Grid refurbishment and replacement | AC Stations | ACS Indoor Switchgear | 322908 | 7932259 | 11571151 | 6945099 | 16513010
27 |  | Grid refurbishment and replacement | AC Stations | ACS Capacitors and Reactors | 0 | 0 | 3555159 | 757795 | 718668
28 |  | Grid refurbishment and replacement | AC Stations | ACS Structures & Buswork | 1277211 | 13476 | 192990 | 219566 | 4031968
29 |  | Grid refurbishment and replacement | AC Stations | ACS Instrument Transformers | 4789345 | 2948897 | 1888745 | 1852274 | 2904788
30 |  | Grid refurbishment and replacement | AC Stations | ACS Disconnectors & E/S | 6584464 | 926142 | 3497 | 0 | 2558001
31 |  | Grid refurbishment and replacement | AC Stations | ACS Other Station Equipment | 2572690 | 799253 | 14238209 | 8882619 | 6254533
32 |  | Grid refurbishment and replacement | AC Stations | ACS Power Cables | 265148 | 12209 | 5890693 | 4109811 | 30671176
33 |  | Grid refurbishment and replacement | AC Stations | ACS Dynamic Reactive | 37517 | 1772238 | 3563655 | 6087002 | 5684479
34 |  | Grid refurbishment and replacement | Protection and Metering | SA Metering | 562046 | 227160 | 67455 | 4648758 | 1868163
35 |  | Grid refurbishment and replacement | Protection and Metering | SA BZ Protection | 5710073 | 4286435 | 4992306 | 6153707 | 10697535
36 |  | Grid refurbishment and replacement | Protection and Metering | SA Line Protection | 8142226 | 11222622 | 2965856 | 6269628 | 7089970
37 |  | Grid refurbishment and replacement | Protection and Metering | SA Transformer Protection | 8280263 | 814121 | 1505527 | 3949958 | 3700653
38 |  | Grid refurbishment and replacement | Protection and Metering | SA Batteries & DC Systems | 4706489 | 1898869 | 4660068 | 2615864 | 3583167
39 |  | Grid refurbishment and replacement | Protection and Metering | SA Feeder Protection | 2050830 | 3421893 | 1839267 | 4369033 | 2196741
40 |  | Grid refurbishment and replacement | Protection and Metering | SA Substation Mgmt Systems | 16535669 | 12484480 | 12765257 | 16330294 | 8673551
41 |  | Grid refurbishment and replacement | Protection and Metering | SA Special Protection Schemes | 16731 | -21742 | 634976 | 841541 | 700396
42 |  | Grid refurbishment and replacement | HVDC Stations | HVDC | 2896645 | 2259803 | 8151077 | 21453047 | 24601589
43 |  | Grid refurbishment and replacement | Transmission Lines | TL Paint | 45173487 | 38879163 | 43566111 | 56277714 | 55702469
44 |  | Grid refurbishment and replacement | Transmission Lines | TL Tower | 4476857 | 15329 | 4050412 | 9248928 | 16813227
45 |  | Grid refurbishment and replacement | Transmission Lines | TL Foundation | 14514 | 4282499 | 3526657 | 7191313 | 17639445
46 |  | Grid refurbishment and replacement | Transmission Lines | TL Grillage | 6227997 | 6815811 | 5693106 | 10688687 | 9074071
47 |  | Grid refurbishment and replacement | Transmission Lines | TL Conductor | 12092716 | 11242023 | 24764385 | 15756868 | 10475871
48 |  | Grid refurbishment and replacement | Transmission Lines | TL Pole | 4486539 | 9614996 | 7869126 | 8745147 | 13564950
49 |  | Grid refurbishment and replacement | Transmission Lines | TL Insulators | 3144854 | 2635922 | 2425272 | 6115445 | 6651104
50 |  | Grid refurbishment and replacement | Transmission Lines | TL Access | 292461 | 1143414 | 643963 | 8153682 | 1675623
51 |  | Total grid refurbishment and replacement |  |  | 205655027.4 | 176025394.64 | 210824205.44 | 241832966.76 | 348936574.68
52
53 |  | Grid enhancment and development | Corridor Management program |  | 340214 | 200036 | 610858 | 0 | 1372219
54 |  | Grid enhancment and development | CP_SNI_AC_00_00 BPE CPK WIL Fire Protection |  | 138956 | 5460 | 0 | -8450 | 0
55 |  | Grid enhancment and development | CP_CST_94_00_00 CST 33kV Outdoor to Indoor Conversion |  | 130317 | 111891 | 19436 | 0 | 0
56 |  | Grid enhancment and development | CP_TIM_64_00_00 Timaru Region capacity Upgrade - Build |  | 4225 | 0 | 0 | 0 | 0
57 |  | Grid enhancment and development | CP_MTR_69_00_00 MTR 110kV SPS (BPE-MTR) Overload Protection Scheme |  | -3 | 0 | 0 | 0 | 0
58 |  | Grid enhancment and development | CP_HLY_64_00_00 HLY HILP Relay Room Constraints- build |  | 38642 | 0 | 0 | 0 | 0
59 |  | Grid enhancment and development | CP_NPL_51_00_00 SFD 2nd Interconnector Bld |  | 1066389 | 50763 | 1956 | 0 | 0
60 |  | Grid enhancment and development | CP_VSA_08_00_00 Waikato and UNI Voltage Management - Shunt Capacitors Stage 1 - HAM & OHW Capacitors |  | 11876178 | 227127 | 298517 | 0 | 0
61 |  | Grid enhancment and development | CP_VSI_AT_00_00 USI High Voltage Management - Build |  | 1086 | 0 | 0 | 0 | 0
62 |  | Grid enhancment and development | CP_OTA_PE_00_00 OTA T4 Replacement and OTA T2 Decommissioning |  | 382357 | 0 | 0 | 0 | 0
63 |  | Grid enhancment and development | CP_VAC_59_00_00 BHL-PAK Cable Joint Replacement |  | 1195691 | 0 | 0 | 0 | 0
64 |  | Grid enhancment and development | CP_VSI_62_00_00 USI Reliability Solution - Stage 2 - Investigation |  | 0 | 488266 | 0 | 0 | 0
65 |  | Grid enhancment and development | CP_HTI_87_00_00 HTI Voltage Constraints - Build TMU Cap Banks |  | 0 | 5130581 | 149237 | 512837 | 54084
66 |  | Grid enhancment and development | CP_RDF_FB_00_00 RDF T3 & T4 Protection Limit SPS pre-contingency loading increased to 160 MVA |  | 0 | 413619 | 13787 | 0 | 0
67 |  | Grid enhancment and development | CP_AVI_66_00_00 AVI-BEN A SPS North Flow |  | 0 | 389509 | 0 | 0 | 0
68 |  | Grid enhancment and development | CP_VTN_13_00_00 BOB 220/110kV Interconnection Transformer - Capex Investigation |  | 0 |  | 2172712 | 0 | 0
69 |  | Grid enhancment and development | CP_VTL_85_00_00 Wairakei Ring transmission capacity - Build - Reactor |  | 0 |  | 5401828 | 167160 | 133073
70 |  | Grid enhancment and development | CP_VTL_95_00_00 NPL-SFD A & CST-NPL A lines junction capex investigation |  | 0 |  | 826853 | 0 | 0
71 |  | Grid enhancment and development | CP_VTL_96_00_00 CST-SFD A Permanent Junction |  | 0 |  | 2946938 | 183926 | 0
72 |  | Grid enhancment and development | CP_TPR_00J_0_00 Digital Substation PAC Inception - initial capital investigation |  | 0 |  | 4194928 | 0 | 0
73 |  | Grid enhancment and development | CP_ISL_01K_0_00 USI High voltage management, ISL Reactor- Install |  | 0 |  | 123726 | 606709 | 0
74 |  | Grid enhancment and development | CP_ISL_001_0_00 USI High voltage management, ISL Reactor - Cap Inv |  | 0 |  | 2906416 | 0 | 0
75 |  | Grid enhancment and development | CP_ISL_002_0_00 USI High voltage management, ISL Reactor- Build |  | 0 |  | 1789552 | 0 | 0
76 |  | Grid enhancment and development | CP_RA1_026_0_00 HEN-MPE A 0160 Slip Deviation Cyclone Gabrielle |  | 0 |  | 416537 | 543617 | 0
77 |  | Grid enhancment and development | CP_VNN_27_00_00 UNI High Voltage Management - Build |  | 0 | 0 | 0 | 14444930 | 602270
78 |  | Grid enhancment and development | CP_TIM_00U_0_00 TIM Voltage Stability ICT Pre-purchase & Build |  | 0 | 0 | 0 | 10058247 | 2017627
79 |  | Grid enhancment and development | CP_OHW_00F_0_00 OHW Deviation Build |  | 0 | 0 | 0 | 7679343 | 0
80 |  | Grid enhancment and development | CP_627_13_00_00 OTA PEN C Line Deviation and Protection (CAPEX) |  | 0 | 0 | 0 | 2093225 | 0
81 |  | Grid enhancment and development | CP_SWN_007_0_00 SWN Generator exit - Build |  | 0 | 0 | 0 | 2195508 | 0
82 |  | Grid enhancment and development | CP_VLT_00_00_00 Lichfield-Kinleith A reconductoring - Build |  | 0 | 0 | 0 | 1585859 | 157344
83 |  | Grid enhancment and development | CP_TIM_DB_00_00 TIM voltage support - Capex Investigation |  | 0 | 0 | 0 | 482740 | 0
84 |  | Grid enhancment and development | CP_810_22_00_00 Connection of WMG-WPT A at ORO tee due to WPT substation decommissioning |  | 0 | 0 | 0 | 320765 | 0
85 |  | Grid enhancment and development | CP_811_29_00_00 IGH-WPT B Connection at ORO tee due to WPT Substation decommissioning |  | 0 | 0 | 0 | 464137 | 0
86 |  | Grid enhancment and development | CP_VTL_BD_00_00 WPT ORO lines junctn capex inv |  | 0 | 0 | 0 | 250393 | 0
87 |  | Grid enhancment and development | CP_VAR_1A3_0_00 22/23 U/C Capex Design Project |  | 0 | 0 | 0 | 917127 | 0
88 |  | Grid enhancment and development | CP_VAR_1FZ_0_00 Ohinewai Diversion Inv |  | 0 | 0 | 0 | 711761 | 0
89 |  | Grid enhancment and development | CP_VTL_DK_00_00 National Vegetation |  | 0 | 0 | 0 | 394317 | 0
90 |  | Grid enhancment and development | CP_KAW_FS_00_00 Kawerau interconnection capacity- Build |  | 0 | 0 | 0 | 0 | 895268
91 |  | Grid enhancment and development | CP_KAW_006_0_00 Kawerau interconnection capacity- Cap Inv |  | 0 | 0 | 0 | 0 | 2577
92 |  | Grid enhancment and development | CP_VNI_35_00_00 AOVCS UNI RPC changes Cap Inv |  | 0 | 0 | 0 | 0 | -5420
93 |  | Grid enhancment and development | CP_651_001_0_00 BHL-OTA Cable Route Designation Extension |  | 0 | 0 | 0 | 0 | 114340
94 |  | Grid enhancment and development | CP_VTL_79_00_00 Arapuni-Kinleith-Tarukenga transmission capacity - Capex Investigation |  | 0 | 0 | 0 | 0 | 3711
95 |  | Grid enhancment and development | CP_HAM_OR_00_00 Bussing ARI-BOB at Hamilton - Capex Investigation |  | 0 | 0 | 0 | 0 | 261820
96 |  | Grid enhancment and development | CP_VSI_AQ_00_00 USI Transmission Capacity - Capex Investigation |  | 0 | 0 | 0 | 0 | 1245609
97 |  | Grid enhancment and development | CP_RDF_EV_00_00 RDF interconnecting capacity - build |  | 0 | 0 | 0 | 0 | 11030255
98 |  | Grid enhancment and development | CP_TPR_00G_0_00 Substation Digital PAC - Inception 2, Development 1 and 2 |  | 0 | 0 | 0 | 0 | 1143997
99 |  | Grid enhancment and development | CP_SFD_00U_0_00 Whareroa Electrification (Ohangai GXP) Transpower Build |  | 0 | 0 | 0 | 0 | 97430
100 |  | Grid enhancment and development | CP_792_006_0_00 BEN-HAY-A Cross-arm Design and Replacements |  | 0 | 0 | 0 | 0 | 140711
101 |  | Grid enhancment and development | CP_EDG_00Y_0_00 EDG 220/110 kV interconnecting transformer - Cap Inv |  | 0 | 0 | 0 | 0 | 273024
102 |  | Grid enhancment and development | CP_RDF_00Q_0_00 RDF 220kV Yard Capex Inv |  | 0 | 0 | 0 | 0 | 1303875
103 |  | Grid enhancment and development | CP_RDF_00P_0_00 RDF Interim Resilience |  | 0 | 0 | 0 | 0 | 378942
104 |  | Grid enhancment and development | CP_HPI_00G_0_00 HPI Advancing Designation Alteration |  | 0 | 0 | 0 | 0 | 258006
105 |  | Grid enhancment and development | CP_VAR_1T6_0_00 ENC Southland Capex Investigation |  | 0 | 0 | 0 | 0 | 433320
106 |  | Grid enhancment and development | CP_HAY_SJ_00_00 HVDC cable replacement and capacity increase - capex investigation |  | 0 | 0 | 0 | 0 | 5436329
107 |  | Grid enhancment and development | Resilience program |  | 0 | 0 | 0 | 0 | 1514197
108 |  | Grid enhancment and development | Other |  | 114707 | 98464 | 0 | 2451 | 382016
109 |  | Grid enhancment and development | Operating leases (transmisson line) |  | 0 | 0 | 0 | 3469576.02 | 0 | Leases are included in Opex as a separate line item on F4(i) from 2025. Leases are captialised with Commissioned Assets.
110 |  | Grid enhancment and development | Unapproved MCP: HVDC Cable Replacement and new cable - CRA Cable deposit |  | 0 | 0 | 0 | 0 | 18575697
111 |  | Total grid enhancement and development |  |  | 15288759 | 7115716 | 21873281 | 47076178.02 | 47822321
112 |  | *Insert additional rows and update calculation of totals as needed
113
114 |  | IST | Transmission Systems | IT Transmission Systems | 6586360.16 | 13446005.82 | 6212577.44 | 9853103.08 | 17102446.26
115 |  | IST | Transmission Systems | IT Meter Data Management | -758 | 0 | 0 | 0 | 0
116 |  | IST | Asset Management Systems | IT Asset Management Systems | 4249364 | 371279 | 126246 | 1196150 | 2899047
117 |  | IST | Asset Management Systems | IT Outage Management | 0 | 7589 | 0 | 0 | 0
118 |  | IST | Telecommunications | IT Shared Comms Infrastructure | 556424 | -13987 | 0 | 0 | 0
119 |  | IST | Telecommunications | IT Subst Comms Infrastructure | 189744 | 0 | 0 | 0 | 0
120 |  | IST | Telecommunications | IT Telecommunications Networks | 544117 | 315 | 0 | 5490879.65 | 20329757.87
121 |  | IST | Corporate Systems | IT Stakeholder Management | 0 | 0 | 7419277.9 | 0 | 0
122 |  | IST | Corporate Systems | IT Corporate Systems | 5399452 | 2573515 | 0 | 1789889 | 4143034
123 |  | IST | IST Shared Services | IT Enabling Infrastructure | 33647 | 0 | 2595752 | 0 | 0
124 |  | IST | IST Shared Services | IT Shared Services | 6890141 | 2909836 | 0 | 2872678 | 3112734
125 |  | IST | Security Services | IT Security Infrastructure | 0 | 0 | 2624771 | 0 | 0
126 |  | IST | Security Services | IT Telecoms Network Security | 2668335 | 6328038 | 0 | 0 | 0
127 |  | IST | Security Services | Transmission Pricing Methodology | 0 | 2032566 | 1939856 | 1003838 | 0
128 |  | IST | Security Services | Operating leases | -1677593 | 598664 | 923250.4 | 186034.35 | 0 | Leases are included in Opex as a separate line item on F4(i) from 2025. Leases are captialised with Commissioned Assets.
129 |  | Total IST |  |  | 25439233.16 | 28253820.82 | 21841730.74 | 22392572.08 | 47587019.13
130
131 |  | Business support | Office buildings and facilities | BS Office buildings and facilities | 321685 | 21311 | 829670.76 | 686866 | 370784
132 |  | Business support | Minor Fixed Assets | BS Vehicles | 1196702 | 773459 | 651262 | 1197992 | 2164485
133 |  | Business support | Minor Fixed Assets | BS Office Equipment | 2011051 | 1689250 | 2084513 | 3061363 | 3839823
134 |  | Business support | Spares and inventory | BS Mobile Substation | 0 | 0 | 0 | 0 | 0
135 |  | Business support | Properties | BS Strategic Properties | 0 | 0 | 0 | 0 | 3207014
136 |  | Business support | Other | BS Other | 39752 | 72152 | 246826 | 0 | 0
137 |  | Business support | Operating leases | Operating leases | 311223 | 14768273 | 48035.077 | 4795372.5442 | 0 | Leases are included in Opex as a separate line item on F4(i) from 2025. Leases are captialised with Commissioned Assets.
138 |  | Total business support |  |  | 3880413 | 17324445 | 3860306.837 | 9741593.5442 | 9582106
139
453928020.81

## F4. Actuals vs Forecasts
[6 empty] | Transpower |  | Disclosure Date |  | 2025-10-24
SCHEDULE F4: COMPARISON OF FORECASTS FOR OPEX AND BASE CAPEX | [7 empty] | Disclosure Year (year ended) |  | 2025-06-30
Disclosure of line items required from disclosure year 2026 onward are specified in column O.
ref
5
6 | F4(i): Opex
7 |  |  | CY | CY | CY
8 |  |  | Actual | Forecast* | Variance
9 |  |  | ($M) | ($M) | %
10 |  | Grid maintenance | 140066409.58 | 134587295.6284 | 4.071%
11 |  | ICT | 50768700.1301 | 44219183.7984 | 14.81% | Note 1
12 |  | Asset Management & Operations | 87587487.2681 | 77367032.6368 | 13.21% | Note 2
13 |  | Business Support | 63787820.2521 | 57781288.8015 | 10.4%
14 |  | Insurance | 32216912.76 | 22324331.0621 | 44.31% | Note 3
15 |  | Total operating expenditure | 374427329.9902 | 336279131.9273 | 11.34%
16
17 |  | Leases expenditure | 11770942.6932 | 11365803.1885 | 3.565% |  | Note this has been added as a seperate category as we are now reporting capex on spend basis (not commissioned which included lease additions).
18
19 | F4(ii): Base Capex |  | SPEND BASIS | SPEND BASIS
20 |  |  | CY | CY | CY
21 |  |  | Actual | Forecast* | Variance
22 |  |  | ($M) | ($M) | %
23 |  | Grid - replacement and refurbishment | 348936574.68 | 280936158.9234 | 24.2% | Note 4
24 |  | Grid - enhancement and development - ACA capacity |  |  | 0% | [5 empty] | Required from disclosure year 2026
25 |  | Grid - enhancement and development - other | 47822321 | 14793921.8262 | 223.3% | Note 5 |  |  |  |  | Required from disclosure year 2026
26 |  | IST | 47587019.13 | 35733870.7312 | 33.17% | Note 6
27 |  | Business support | 9582106 | 4285977.668 | 123.6% | Note 7
28 |  | Total base capex expenditure | 453928020.81 | 335749929.1487 | 35.2%
29 |  |  | *Prior year disclosure of CY forecast nominal value
30
31
32
33 | F4(iii): Opex comparison by expenditure categories
34 |  |  | CY | CY | CY
35 |  |  | Actual | Forecast in RCP Proposal | Variance
36 |  |  | ($M) | ($M) | %
37 |  | Preventive Maintenance | 49747927.3945 | N/A | N/A | [5 empty] | Required from disclosure year 2026
38 |  | Predictive Maintenance | 82766497.0755 | N/A | N/A | [5 empty] | Required from disclosure year 2026
39 |  | Corrective Maintenance | 6505954.67 | N/A | N/A | [5 empty] | Required from disclosure year 2026
40 |  | Proactive Maintenance | 1046030.44 | N/A | N/A | [5 empty] | Required from disclosure year 2026
41 |  | Resilience | 0 | N/A | N/A | [5 empty] | Required from disclosure year 2026
42 |  | Total - Grid maintenance | 140066409.58 | N/A | N/A | [5 empty] | Required from disclosure year 2026
43
44 |  | ICT Opex | 50768700.1301 | N/A | N/A | [5 empty] | Required from disclosure year 2026
45 |  | ICT Software as a Service | 0 | N/A | N/A | [5 empty] | Required from disclosure year 2026
46 |  | Total - ICT | 50768700.1301 | N/A | N/A | [5 empty] | Required from disclosure year 2026
47
48 |  | Asset Management & Operations | 87587487.2681 | N/A | N/A | [5 empty] | Required from disclosure year 2026
49 |  | Sustainability | 0 | N/A | N/A | [5 empty] | Required from disclosure year 2026
50 |  | Total - Asset Management & Operations | 87587487.2681 | N/A | N/A | [5 empty] | Required from disclosure year 2026
51
52 |  | Business support | 63787820.2521 | N/A | N/A | [5 empty] | Required from disclosure year 2026
53
54 |  | Insurance | 32216912.76 | N/A | N/A | [5 empty] | Required from disclosure year 2026
55
56
57 | F4(iv): Base capex comparison by expenditure categories
58 |  |  | CY | CY | CY | CY | CY | CY | CY
59 |  |  | Actual | Forecast in RCP Proposal | Variance | Actual change in percentage of assets with AHI between 8 and 10. | Forecast change in percentage of assets with AHI between 8 and 10. | Variance | CY change in percentage of Asset health index = 0.5
60 |  |  | ($M) | ($M) | % |  |  | %
61
62 |  | ACS Power Transformers | 33191462 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
63 |  | ACS Outdoor to Indoor Conv | 1795688 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
64 |  | ACS Buildings & Grounds-Seismic | 0 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
65 |  | ACS Buildings & Grounds | 48463912.68 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
66 |  | ACS Outdoor Circuit Breakers | 1440364 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
67 |  | ACS Indoor Switchgear | 16513010 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
68 |  | ACS Capacitors and Reactors | 718668 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
69 |  | ACS Structures & Buswork | 4031968 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
70 |  | ACS Instrument Transformers | 2904788 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
71 |  | ACS Disconnectors & E/S | 2558001 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
72 |  | ACS Other Station Equipment | 6254533 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
73 |  | ACS Power Cables | 30671176 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
74 |  | ACS Dynamic Reactive | 5684479 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
75 |  | SA Metering | 1868163 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
76 |  | SA BZ Protection | 10697535 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
77 |  | SA Line Protection | 7089970 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
78 |  | SA Transformer Protection | 3700653 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
79 |  | SA Batteries & DC Systems | 3583167 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
80 |  | SA Feeder Protection | 2196741 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
81 |  | SA Special Protection Schemes | 700396 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
82 |  | SA Substation Mgmt Systems | 8673551 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
83 |  | HVDC | 24601589 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
84 |  | TL Paint | 55702469 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
85 |  | TL Tower | 16813227 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
86 |  | TL Foundation | 17639445 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
87 |  | TL Grillage | 9074071 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
88 |  | TL Conductor | 10475871 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
89 |  | TL Pole | 13564950 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
90 |  | TL Insulators | 6651104 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
91 |  | TL Access | 1675623 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
92 |  | Total grid refurbishment and replacement | 348936574.68 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
93
94 |  | IT SCADA/RTS | 0 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
95 |  | IT Time Series | 0 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
96 |  | IT Transmission Systems | 17102446.26 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
97 |  | IT Meter Data Management | 0 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
98 |  | IT Asset Management Systems | 2899047 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
99 |  | IT Spatial & Drawings | 0 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
100 |  | IT Outage Management | 0 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
101 |  | IT Communication Services | 0 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
102 |  | IT Shared Comms Infrastructure | 0 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
103 |  | IT Subst Comms Infrastructure | 0 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
104 |  | IT Telecommunications Networks | 20329757.87 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
105 |  | IT Stakeholder Management | 0 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
106 |  | IT Corp Info & Doc Mgmt | 0 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
107 |  | IT Safety | 0 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
108 |  | IT Risk/Audit Management | 0 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
109 |  | IT Finance | 0 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
110 |  | IT Human Resources | 0 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
111 |  | IT Corporate Systems | 4143034 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
112 |  | IT Enabling Infrastructure | 0 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
113 |  | IT Service Management | 0 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
114 |  | IT Workforce Mobility | 0 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
115 |  | IT Data Centre | 0 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
|  | IT Shared Services | 3112734 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2027
|  | IT Security Infrastructure | 0 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2028
|  | IT Telecoms Network Security | 0 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2029
|  | Transmission Pricing Methodology | 0 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2030
120 |  | Total IST (excl Lease expenses) | 47587019.13 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
121
122 |  | BS Office buildings and facilities | 370784 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
123 |  | BS Vehicles | 2164485 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
124 |  | BS Office Equipment | 3839823 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
125 |  | BS Mobile Substation | 0 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
126 |  | BS Strategic Properties | 3207014 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
127 |  | BS Other | 0 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
128 |  | Total business support | 9582106 | N/A | N/A | N/A | N/A | N/A | N/A |  | Required from disclosure year 2026
129
130
131
132 | Opex variance explanations (required for variances greater than 10% or $10 million between actual and forecast base capex expenditure)
133
134 | Note 1 | ICT is 15% higher as result of Software as a service (SaaS) cost not include in the allowance as these cost were previously capitalised
135
136 | Note 2 | Asset Management and Operations is 13% over due to the increase in workforce to build capacity for our future work programme as signalled in our RCP4 submission
137
138 | Note 3 | Increase in insurance costs across the industry
139
140
141 | Base capex variance explanations (required for variances greater than 10% or $10 million between actual and forecast base capex expenditure)
142
143 | Note 4 | The 24% higher expenditure in FY2025 compared to forecast is primarily driven by: - an increase in scope and cost of our warehouses’ redevelopment $30 million, - additional costs of cable joint repairs on the Brownhill - Pakuranga cable $24 million, - a number of transformer replacements, including the purchase of strategic transformer spares, being completed in FY2025, later than originally anticipated $20m, - the reclassification of attachment point expenditure to capital from operating expenditure $8 million, - increased scope and complexity of marine foundations on the Henderson - Otahuhu A line $8 million, - restoration work related to weather events $6m. This has been partially offset by savings related to our transmission line initiatives such as Tower Corrosion and Intelligent Conductor programs.
| Note 5 | E&D commissioning is $33m above forecast due primarily to the following: - HVDC cable replacement initial enabling work included under Base E&D capex until HVDC major capex project (due for submission to Commerce Commission in September 2025) is approved later in the FY2025 $5.4m, - HVDC MCP cable replacement Capacity Reservation Agreement deposit, $18m. This is included in Base capex as has not yet been approved by the Commerce Commission, - A number of other smaller works such as Timaru voltage stability $2.0m, due to high demand growth as a result of dairy plants and irrigation in the Timaru region, resulting in the need for improved voltage stability, - the development of a digital substation program including Protection, Automation and Control (PAC) solution to greenfield substation sites $1.1m, - the commencement of a resilience program due to the increasing impact of large weather events $1.1m.
| Note 6 | Higher expenditure of ICT work is primarily due to the commencement of the TransGo project earlier than anticipated to enable the network to meet future technological requirements, as signalled in the RCP4 submission.
146 | Note 7 | The purchase of property in Wellington adjacent to the Central Park substation to alleviate congestion at the substation site, an increase in our vehicle fleet to accommodate our growing delivery workforce, site digitisation work and increased cost of general office equipment such as laptops, monitors and smart phones have resulted in the increase against forecast.
147

## F5. Major Capex Projects
[15 empty] | Transpower |  | Disclosure Date |  | 2025-10-24
SCHEDULE F5: MAJOR CAPITAL EXPENDITURE (MAJOR CAPEX) | [16 empty] | Disclosure Year (year ended) |  | 2025-06-30
ref
5 | F5(i): Major Capex Projects (Summary): Approved But Not Yet Commissioned
6
7 |  |  |  | Initial Project Approvals | [8 empty] | Amendments to Approved Projects
8 |  |  |  | Approved MCP Outputs | Major Capex Allowance | Max. Recoverable costs | Recovery Scheme |  | Commissioning Date(s) | P50 | Approval Expiry Date | Completion date Assumption | Major Capex Allowance | Max. Recoverable costs | Recovery Scheme | P50 | Approval Expiry Date | Completion Date Assumption | Approved MCP Outputs
9 |  |  | Project Name |  | ($M) | ($M) |  |  |  | ($M) |  |  | ($M) | ($M) |  | ($M)
10 |  |  | Stage 1 - Waikato and Upper North Island Voltage Management | 1) one dynamic reactive device in the Upper North Island capable of delivering (within 10%) 150 Mvar capacitive to 150 Mvar inductive at nominal voltage 2) one dynamic reactive device in the Waikato capable of delivering (within 10%) 150 Mvar capacitive to 150 Mvar inductive at nominal voltage 3) a post-fault demand management scheme for the Waikato Upper North Island region 4) preparatory works for Stage 2, including additional investigation, consultation, obtaining property rights and environmental approvals, design work and non-binding tendering for future series capacitors and installation works on the BrownhillWhakamaru 1&2 transmission lines (BHL-WKM lines) | 143000000 | n/a | Capex |  | Dec 2022 (except for Stage 2 preparatory works) | 143000000 | 2029-12-01 | Dec 2022 (except for Stage 2 preparatory works)
11 |  |  | Net Zero Grid Pathways stage one | HVDC upgrade – increasing transfer capacity from 1071 MW to closer to 1200 MW by installing: 1) reactive plant; 2) filter banks; and 3) associated equipment to upgrade the HVDC. Central North Island upgrade - increasing transfer capacity north from Bunnythorpe by between 60% and 90% by: 1)installing variable line rating and tactical thermal upgrade of the Tokaanu-Whakamaru and the Bunnythorpe-Tokaanu circuits; 2) duplexing the Tokaanu-Whakamaru circuits with Goat conductor; 3) splitting the Bunnythorpe-Ongarue circuit; 4) upgrading protection on the Huntly-Stratford circuit; and 5) replacing special protection scheme at Tokaanu. Wairakei ring upgrade - increasing transmission capacity by 25% (300 MW) under typical operating conditions by: 1) tactical thermal upgrade of both circuits of the WairakeiWhakamaru C line; 2) a tactical thermal upgrade of the Edgecumbe-Kawerau 3 circuit on the Ohakuri-Edgecumbe A and Kawerau-Deviation lines; and 3) splitting the Edgecumbe-Kawerau circuit. NZGP1 stage two preparatory work to: - carry out a detailed design of duplex Bunnythorpe-Tokaanu A and B lines; - carry out a detailed design for tactical thermal upgrade of Bunnythorpe-Wairakei A line; - investigate options for reconductoring one of the two 200 kV Brunswick-Stratford lines; - develop quantifying resilience methodology; - carry out a study on diversification of Bunnythorpe substation; - carry out a study on lower North Island voltage stability; and - carry out a study on lower North Island system stability. | 392900000 | n/a | Capex |  | Various | 392900000 | 2035-12-31 | 2028-06-30 | 0 | 0
12 |  |  | Western Bay of Plenty | $83.2m for the enhancement of the WBOP transmission grid, namely: Western corridor - Kaitemako: - install a new 220kV/110kV interconnecting transformer at Kaitemako; Western corridor - Reconductoring: - reconductor the interconnection section of the Kaitemako-Tauranga 110kV line to a rating of 200MVA; Eastern corridor - reconductor the Okere-Te Matai, Okere-Tarukenga, and Kaitemako-Te Matai 110kV lines to a rating of 195 MVA; and Potential non-transmission solution (NTS) - $2.9m to fund NTS. Refer to Final Decision WBOP MCP 11 June 2025 "treat the capital cost contingency risk component of the MCA, and the development NTS recoverable cost component, as exempt major capex, equal to $12.5 million ($ nominal)" | 86100000 | n/a | Capex |  | Various | 86100000 | 2037-12-31 | 2032-12-31
13 |  |  | [insert project]
14 |  |  | [insert project]
15 |  |  | [insert project]
16 |  |  | [insert project]
17
18 | F5(ii): Major Capex Projects (Detail): Approved But Not Yet Commissioned*
19 |  | *Insert additional tables as required for projects
20 |  |  |  |  | CY-4 + previous | CY-3 | CY-2 | CY-1 | CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5 | CY+6 | CY+7 | CY+8 | Total
21 |  |  |  |  | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M)
22 |  | Project name | Stage 1 - Waikato and Upper North Island Voltage Management | Forecast Expenditure | 61912683.6561 | 58226755.8104 | 22892086.324 | 95919.4824 | [9 empty] | 143127445.2729
23 |  |  |  | Actual Expenditure | 7494449 | 21550100 | 16658094 | 25468587 | 25253307 | [8 empty] | 96424537
24 |  |  |  | Variance | 54418234.6561 | 36676655.8104 | 6233992.324 | -25372667.5176 | -25253307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46702908.2729
25
26 |  |  |  |  | CY-4 + previous | CY-3 | CY-2 | CY-1 | CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5 | CY+6 | CY+7 | CY+8 | Total
27 |  |  |  |  | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M)
28 |  | Project name | Net Zero Grid Pathways stage one | Forecast Expenditure | 0 | 11550 | 1663743 | 11558970 | 30586642 | 62336009 | 74376298 | 81114742 | 109771515 | 21480531 |  |  |  | 392900000
29 |  |  |  | Actual Expenditure |  |  |  | 11563060 | 28769904 | [8 empty] | 40332964
30 |  |  |  | Variance | 0 | 11550 | 1663743 | -4090 | 1816738 | 62336009 | 74376298 | 81114742 | 109771515 | 21480531 | 0 | 0 | 0 | 352567036
31
32 |  |  |  |  | CY-4 + previous | CY-3 | CY-2 | CY-1 | CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5 | CY+6 | CY+7 | CY+8 | Total
33 |  |  |  |  | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M)
34 |  | Project name | Western Bay of Plenty - (Excluding approved NTS recoverable cost of $2.9m) | Forecast Expenditure |  |  |  |  | 315000 | 3943000 | 10489000 | 12616000 | 22669000 | 21683000 | 9787000 | 1662000 |  | 83164000
35 |  |  |  | Actual Expenditure |  |  |  |  | 1538687 | [8 empty] | 1538687
36 |  |  |  | Variance | 0 | 0 | 0 | 0 | -1223687 | 3943000 | 10489000 | 12616000 | 22669000 | 21683000 | 9787000 | 1662000 | 0 | 81625313
37
38 |  |  |  |  | CY-4 + previous | CY-3 | CY-2 | CY-1 | CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5 | CY+6 | CY+7 | CY+8 | Total
39 |  |  |  |  | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M)
40 |  |  |  |  | CY-4 + previous | CY-3 | CY-2 | CY-1 | CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5 | CY+6 | CY+7 | CY+8 | Total
41 |  |  |  |  | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M)
42 |  | Project name | [insert project] | Forecast Expenditure | [13 empty] | 0
43 |  |  |  | Actual Expenditure | [13 empty] | 0
44 |  |  |  | Variance | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45
46 |  |  |  |  | CY-4 + previous | CY-3 | CY-2 | CY-1 | CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5 | CY+6 | CY+7 | CY+8 | Total
47 |  |  |  |  | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M)
48 |  | Project name | [insert project] | Forecast Expenditure | [13 empty] | 0
49 |  |  |  | Actual Expenditure | [13 empty] | 0
50 |  |  |  | Variance | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51
52 |  |  |  |  | CY-4 + previous | CY-3 | CY-2 | CY-1 | CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5 | CY+6 | CY+7 | CY+8 | Total
53 |  |  |  |  | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M)
54 |  | Project name | [insert project] | Forecast Expenditure | [13 empty] | 0
55 |  |  |  | Actual Expenditure | [13 empty] | 0
56 |  |  |  | Variance | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57
58 |  |  |  |  | CY-4 + previous | CY-3 | CY-2 | CY-1 | CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5 | CY+6 | CY+7 | CY+8 | Total
59 |  |  |  |  | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M)
60 |  | Project name | [insert project] | Forecast Expenditure | [13 empty] | 0
61 |  |  |  | Actual Expenditure | [13 empty] | 0
62 |  |  |  | Variance | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63
64 | F5(iii): Future Major Capex Projects Under Consideration: Not Yet Approved
65
66 |  |  | Project Name | Project Description |  |  | Estimated cost ($M) | Estimated Start Date | Estimated Commissioning Date | Purpose/Benefits of Project
67 |  |  | [insert project] | There were no MCPs that were submitted to the Commission (under consideration) for approval as at 30 June 2025
68 |  |  | [insert project]
69 |  |  | [insert project]
70
71
72 | F5(iv): Commissioned Major Capex Projects | [15 empty] | Required from disclosure year 2026
73 |  |  |  |  | Value of Commissioned Assets | [5 empty] | Commissiong Dates |  |  |  | Project Outputs |  | Major Capex Adjustments
74 |  |  | Project Name | Project Description | Expected (P50) ($M) | MCA ($M) | Adjusted MCA ($M) | Actual Cost ($M) | Variance v adjusted MCA ($M) | Material Change in Value? (y/n) | Approved Date | Actual Date | Variance (months) | Material Change in Date? (y/n) | Variance to approved outputs? (y/n) | Material Variance? (y/n) | Incentive rate % | Exempt major capex ($M) | Major capex expenditure adjustment
75 |  |  | Upper North Island Dynamic Reactive Support | (1) Install load monitoring equipment in the upper North Island region. (2) Install software enhancements to improve dynamic stability calculations. (3) Undertake a range of demand-side initiatives in the upper North Island region. (4) Install and commission a Reactive Power Controller (RPC) for the upper North Island region. (5) Install and commission a reactive support device in Auckland. (6) Install and commission a reactive support device in Northland. (7) Procure, construct and commission substation facilities to facilitate the above connections and equipment. (8) Obtain property rights and environmental approvals required for these works. (9) Carry out any additional minor works and activities required to facilitate the above. | 103.4 | 98.2 | 98.2 | 50.8 | -47.4 | Y
76 |  |  | Project Outputs
77 |  |  | See schedule TP4 | [7 empty] | See schedule TP4 | See schedule TP4 | See schedule TP4 | See schedule TP4 | See schedule TP4 | See schedule TP4
78
79 |  |  |  |  | Value of Commissioned Assets | [5 empty] | Commissiong Dates |  |  |  | Project Outputs |  | Major Capex Adjustments
80 |  |  | Project Name | Project Description | Expected (P50) ($M) | MCA ($M) | Adjusted MCA ($M) | Actual Cost ($M) | Variance v adjusted MCA ($M) | Material Change in Value? (y/n) | Approved Date | Actual Date | Variance (months) | Material Change in Date? (y/n) | Variance to approved outputs? (y/n) | Material Variance? (y/n) | Incentive rate % | Exempt major capex ($M) | Major capex expenditure adjustment
81 |  |  | Bombay Otahuhu Regional major capex project | 1) procuring, installing and commissioning two 150/175 MVA 220/110kV transformers at Transpower’s Bombay substation 2) procuring, installing and commissioning a connection for these transformers to the 220kV Huntly-Otahuhu A line 3) undertaking preparatory works, including additional investigation, consultation and design work, for reconductoring the OtahuhuWiri line Amendment to outputs approved September 2021: 4) removing the existing conductor, and procuring, installing and commissioning Goat ACSR conductor on the Otahuhu-Wiri section of the Bombay-Otahuhu A 110 kV transmission line; 5) works on the foundations and towers required for the spans on which the Goat ACSR conductor is installed. | 50.538 | 50.538 | 50.538 | 31.4561 | -19.0819 | Y
82 |  |  | Project Outputs
83 |  |  | See schedule TP4 | [7 empty] | See schedule TP4 | See schedule TP4 | See schedule TP4 | See schedule TP4 | See schedule TP4 | See schedule TP4
84

## F6. Revenues
[8 empty] | Transpower |  | Disclosure Date |  | 2025-10-24
SCHEDULE F6: REGULATED REVENUE | [9 empty] | Disclosure Year (year ended) |  | 2025-06-30
Regulated revenue is received in Pricing Years, ending on 31 March each year. For example, the pricing year corresponding to the 30 June 2025 disclosure year is the pricing year ended 31 March 2025. All revenue numbers here are stated in pricing years, except where indicated.
ref
5 | F6(i): Regulated Electricity Transmission Revenue
6 |  |  |  |  | CY-4 | CY-3 | CY-2 | CY-1 | CY
7 |  |  |  |  | ($M) | ($M) | ($M) | ($M) | ($M)
8 |  |  | HVAC - Interconnection (excl. EV) |  | 602570425.18 | 604814791.8 | 613546718.02 | [18 empty] | Not required from disclosure year 2029
9 |  |  | HVAC - NEA and PDA income |  | 2558695.9106 | 2555722.3106 | 2555722 | [18 empty] | Not required from disclosure year 2029
10 |  |  | HVAC - Connection (excl.EV) |  | 111448127.94 | 112834125.69 | 123570620.82 | [18 empty] | Not required from disclosure year 2029
11 |  |  | HVAC - EV adjustment |  | -23351896.08 | -21429212.64 | -24219180.24 | [18 empty] | Not required from disclosure year 2029
|  |  | HVDC - NEA and PDA income |  | 491017.68 | 491017.6894 | 491017.6894
13 |  |  | HVDC (excl. EV) |  | 92725713 | 93503907.12 | 92684583.76 | [18 empty] | Not required from disclosure year 2029
14 |  |  | HVDC - EV adjustment |  | -647836.68 | -1413568.8 | -632608.96 | [18 empty] | Not required from disclosure year 2029
15 |  |  | Connection charge |  |  |  |  | 117347730.42 | 125.5793
16 |  |  | Benefits-based charge |  |  |  |  | 256192595.84 | 266.7212
17 |  |  | Residual charge |  |  |  |  | 468224196.22 | 476.5666
18 |  |  | Transitional cap (charge) |  |  |  |  | 1420055.04 | -0.00062518
19 |  |  | EV Adjustment |  |  |  |  | -24668816.76 | -24.9325
20 |  |  | Other regulated transmission revenue* |  | 4187156.8911 | 9752516.03 | 22133254.72 | 8590990.0455 | 10.9513
21 |  |  | Total regulated electricity transmission revenue |  | 789981403.8417 | 801109299.2 | 830130127.8094 | 827106750.8055 | 854.8853
22 |  |  | * "Other regulated transmission revenue" includes insurance proceeds as well as the sale of scrap metal to a variety of scrap metal merchants. Comparative years have been restated for previously unreported self-insurance proceeds.
23
24 | F6(ii): Regulated Revenue
25
26
27 |  | Total Revenue (CY) - (PY = ending 31/03/2025)
28 |  |  |  |  | Connection charge ($M) | Benefits-based charge ($M) | Residual charge ($M) | Transitional cap (charge) ($M) | Other regulated transmission revenue ($M) | Total Revenue ($M) | EV adjustment ($M) | TOTAL ($M) | Offtake quantities (MWH) | Injection quantities (MWH)
29 |  |  |  | Distributor | 84.4799 | 146.4677 | 415.9506 | 0.4226 |  | 647.3208 | -21.7612 | 625.5595 | 31521735.4 | 1350074.7
30 |  |  |  | Direct Connect | 9.6607 | 18.3976 | 54.3025 | -0.49346 |  | 81.8674 | -2.8409 | 79.0264 | 5512683.9 | 336550.5
31 |  |  |  | Generator | 31.4387 | 101.8559 | 6.3135 | 0.070233 |  | 139.6783 | -0.3303 | 139.348 | 51134.1 | 36806547.6
32 |  |  |  | Other |  |  |  |  | 10.9513 | 10.9513 |  | 10.9513
33 |  |  |  | Grand Total | 125.5793 | 266.7212 | 476.5666 | -0.00062518 | 10.9513 | 879.8177 | -24.9325 | 854.8853 | 37085553.4 | 38493172.8
34
35
36
37
38 | F6(iii): Customer Charges
39 |  |  | The customer charges shown must include all charges irrespective of the form of the contract
40 | [7 empty] | Current Year Charges (CY) | [8 empty] | Current Year +1 (CY+1) Charges
[9 empty] | Required from disclosure year 2026 |  | Required from disclosure year 2026 |  |  |  | Required from disclosure year 2026 |  |  | Required from disclosure year 2026 |  | Required from disclosure year 2026 |  |  |  | Required from disclosure year 2026
42 |  |  |  | Customer Code | Customer Name | Location Code (New Field) | Location Name | Connection Charge ($M) | ACA portion of Connection charge ($M) | Benefits-based charge ($M) | ACA portion of Benefits-based charge ($M) | Residual charge ($M) | Transitional cap (charge) ($M) | Investment Contract Charge ($M) | ACA portion of Investment Contract Charge ($M) | Total Charges ($M) | Connection Charge ($M) | ACA portion of Connection charge ($M) | Benefits-based charge ($M) | ACA portion of Benefits-based charge ($M) | Residual charge ($M) | Transitional cap (charge) ($M) | Investment Contract Charges ($M) | ACA portion of Investment Contract Charges ($M) | Total Charges ($M)
43 |  |  |  | ALPE | Alpine Energy Ltd | ABY011S1 | Albury | 0.41308 |  | 0.0094637 |  | 0.24955 |  |  |  | 0.6721 | 0.52753 |  | 0.013824 |  | 0.29048 | 0 |  |  | 0.83183
44 |  |  |  | ALPE | Alpine Energy Ltd | BPD110S1 | Bells Pond | 0.011149 |  | 0.11208 |  | 0.48351 |  | 0.089173 |  | 0.69592 | 0.012331 |  | 0.12617 |  | 0.62179 | 0 | 0.089173 |  | 0.84947
45 |  |  |  | ALPE | Alpine Energy Ltd | STU011S1 | Studholme | 0.18344 |  | 0.16287 |  | 0.66548 |  |  |  | 1.0118 | 0.22759 |  | 0.18207 |  | 0.79888 | 0 |  |  | 1.2085
46 |  |  |  | ALPE | Alpine Energy Ltd | TKA033S1 | Tekapo A | 0.22442 |  | 0.05892 |  | 0.22009 |  |  |  | 0.50343 | 0.32399 |  | 0.066287 |  | 0.24957 | 0 |  |  | 0.63985
47 |  |  |  | ALPE | Alpine Energy Ltd | TMK033S1 | Temuka | 1.011 |  | 0.54897 |  | 3.0198 |  | 0.053848 |  | 4.6336 | 1.2654 |  | 0.64257 |  | 3.5486 | 0 | 0.053848 |  | 5.5104
48 |  |  |  | ALPE | Alpine Energy Ltd | TIM011S1 | Timaru | 0.48758 |  | 0.97625 |  | 3.8629 |  | 1.1009 |  | 6.4276 | 0.59071 |  | 1.1057 |  | 4.4668 | 0 | 1.1009 |  | 7.2641
49 |  |  |  | ALPE | Alpine Energy Ltd | TWZ033S1/TWZ033S3 | Twizel | 0.22666 |  | 0.038321 |  | 0.16377 |  |  |  | 0.42875 | 0.24355 |  | 0.040707 |  | 0.18943 | 0 |  |  | 0.47369
50 |  |  |  | ALPE | Alpine Energy Ltd | N/A | All Locations | [5 empty] | 0.0086014 |  |  | 0.0086014 | 0 |  | 0 |  | 0 | 0.0066559 |  |  | 0.0066559
51 |  |  |  | BUEL | Buller Electricity Ltd | ORO110S1 | Orowaiti Tee | 1.2791 |  | 0.1742 |  | 0.57687 |  |  |  | 2.0301 | 1.7226 |  | 0.22593 |  | 0.65975 | 0 |  |  | 2.6083
52 |  |  |  | BUEL | Buller Electricity Ltd | N/A | All Locations | 1.5054 |  |  |  | 0.043039 | 0.00058752 |  |  | 1.5491 | 0 |  | 0 |  | 0 | 0.00044379 |  |  | 0.00044379
53 |  |  |  | CHBP | Centralines Limited | WPW011S1/WPW033S1 | Waipawa | 0.45793 |  | 0.56505 |  | 1.1289 |  |  |  | 2.1519 | 0.56107 |  | 0.68945 |  | 1.3099 | 0 |  |  | 2.5604
54 |  |  |  | CHBP | Centralines Limited | N/A | All Locations | [5 empty] | 0.0011831 |  |  | 0.0011831 | 0 |  | 0 |  | 0 | 0.00090163 |  |  | 0.00090163
55 |  |  |  | CHHE | Oji Fibre Solutions (NZ) Ltd | KAW011S1/SA/S2 | Kawerau | 0.68587 |  | 0.21732 |  |  |  | 0.25593 |  | 1.1591 | 0.8346 |  | 0.2629 |  | 0 | 0 | 0.25593 |  | 1.3534
56 |  |  |  | CHHE | Oji Fibre Solutions (NZ) Ltd | N/A | All Locations | 0 |  |  |  |  | 0.00010932 |  |  | 0.00010932 | 0 |  | 0 |  | 0 | 7.517e-05 |  |  | 7.517e-05
57 |  |  |  | COUP | Counties Energy Ltd | BOB033S1/BOB110S1 | Bombay | 0.36929 |  | 3.4045 |  | 5.2002 |  | 0.20811 |  | 9.1821 | 0.18579 |  | 3.8109 |  | 6.2853 | 0 | 0.20811 |  | 10.4901
58 |  |  |  | COUP | Counties Energy Ltd | GLN033SA/GLN033S3 | Glenbrook | 0.75949 |  | 0.73121 |  | 1.8672 |  |  |  | 3.3579 | 0.82091 |  | 0.85682 |  | 2.1764 | 0 |  |  | 3.8541
59 |  |  |  | COUP | Counties Energy Ltd | N/A | All Locations | [5 empty] | 0.008728 |  |  | 0.008728 | 0 |  | 0 |  | 0 | 0.0067045 |  |  | 0.0067045
60 |  |  |  | CTCT | Contact Energy Limited | CYD033S1 | Clyde | 0.41524 |  | 9.2693 |  | 0.35218 |  |  |  | 10.0367 | 0.51205 |  | 9.9682 |  | 0.37765 | 0 |  |  | 10.8579
61 |  |  |  | CTCT | Contact Energy Limited | N/A | Ohaaki | 1.5364 |  | 0.65591 |  | 0.030651 |  |  |  | 2.2229 | 1.9112 |  | 0.76417 |  | 0.11212 | 0 |  |  | 2.7875
62 |  |  |  | CTCT | Contact Energy Limited | OTA022S1 | Otahuhu A |  |  |  |  | 0.023202 |  |  |  | 0.023202 | [8 empty] | 0
63 |  |  |  | CTCT | Contact Energy Limited | N/A | Poihipi | 0.26154 |  | 0.80953 |  | 0.012089 |  |  |  | 1.0832 | 0.30476 |  | 0.93841 |  | 0.016251 | 0 |  |  | 1.2594
64 |  |  |  | CTCT | Contact Energy Limited | N/A | Roxburgh | 0.23115 |  | 6.7188 | [5 empty] | 6.9499 | 0.28544 |  | 7.0723 |  | 5.38e-06 | 0 |  |  | 7.3577
65 |  |  |  | CTCT | Contact Energy Limited | SFD033S1 | Stratford | 0.15398 |  | 2.4513 |  | 0.49432 |  |  |  | 3.0996 | 0.17411 |  | 2.9192 |  | 0.56098 | 0 |  |  | 3.6543
66 |  |  |  | CTCT | Contact Energy Limited | TAB033S1 | Tauhara B | 0.17756 |  | -0.050203 |  |  |  | 2.1524 |  | 2.2798 | 0.18006 |  | 0 |  | 0 | 0 | 2.1524 |  | 2.3325
67 |  |  |  | CTCT | Contact Energy Limited | TWH033S1 | Te Kowhai |  |  | 0.026503 | [5 empty] | 0.026503 | 0 |  | 0.037091 |  | 0 | 0 |  |  | 0.037091
68 |  |  |  | CTCT | Contact Energy Limited | N/A | Te Mihi | 0.20471 |  | 2.7265 |  | 0.056906 |  | 1.731 |  | 4.7191 | 0.22028 |  | 3.1792 |  | 0.016139 | 0 | 1.731 |  | 5.1466
69 |  |  |  | CTCT | Contact Energy Limited | WRK033S1 | Wairakei | 0.061729 |  | 2.2147 |  | 0.0065942 |  |  |  | 2.283 | 0.075589 |  | 2.5784 |  | 0.0076066 | 0 |  |  | 2.6616
70 |  |  |  | CTCT | Contact Energy Limited | WHI011SA | Whirinaki | 0.058999 |  | 0.042239 |  | 0.24521 |  |  |  | 0.34645 | 0.072914 |  | 0.044726 |  | 0.26884 | 0 |  |  | 0.38648
71 |  |  |  | CTCT | Contact Energy Limited | N/A | All Locations | [5 empty] | 0.017974 | 0.085436 |  | 0.10341 | 0 |  | 0 |  | 0 | 0.012482 | 0.085436 |  | 0.097918
72 |  |  |  | DUNE | Aurora Energy Limited | CYD033S1 | Clyde | 0.79946 |  | 0.039018 |  | 1.1477 |  |  |  | 1.9862 | 0.99044 |  | 0.049636 |  | 1.352 | 0 |  |  | 2.3921
73 |  |  |  | DUNE | Aurora Energy Limited | CML033S1 | Cromwell | 0.3513 |  | 0.38635 |  | 2.4478 |  | 0.40847 |  | 3.5939 | 0.43559 |  | 0.41187 |  | 2.9254 | 0 | 0.40847 |  | 4.1814
74 |  |  |  | DUNE | Aurora Energy Limited | FKN033S1/S2 | Frankton | 1.6481 |  | 0.76631 |  | 3.2319 |  | 0.32116 |  | 5.9675 | 2.0059 |  | 0.81106 |  | 3.7094 | 0 | 0.32116 |  | 6.8475
75 |  |  |  | DUNE | Aurora Energy Limited | HWB033S1/S2 | Halfway Bush | 0.7786 |  | 0.77019 |  | 6.6006 |  |  |  | 8.1494 | 0.96855 |  | 0.84302 |  | 7.3978 | 0 |  |  | 9.2094
76 |  |  |  | DUNE | Aurora Energy Limited | SDN033S1 | South Dunedin | 1.8043 |  | 0.75191 |  | 3.8828 |  | 0.045279 |  | 6.4843 | 2.2329 |  | 0.81879 |  | 4.5543 | 0 | 0.045279 |  | 7.6513
77 |  |  |  | DUNE | Aurora Energy Limited | N/A | All Locations | [5 empty] | 0.016747 |  |  | 0.016747 | 0 |  | 0 |  | 0 | 0.012783 | 0.57376 |  | 0.58654
78 |  |  |  | EASH | EA Networks | ASB066SA | Ashburton | 0.32053 |  | 1.2316 |  | 8.8535 |  | 0.057445 |  | 10.4631 | 0.3586 |  | 1.3329 |  | 10.554 | 0 | 0.057445 |  | 12.303
79 |  |  |  | EASH | EA Networks | N/A | All Locations | [5 empty] | 0.0083036 | 0.0042969 |  | 0.012601 | 0 |  | 0 |  | 0 | 0.0065585 | 0.0042969 |  | 0.010855
80 |  |  |  | EAST | Firstlight Network Limited | TUI110S2 | Tuai | 0.3263 |  | 0.91333 |  | 3.2979 |  | 0.07475 |  | 4.6122 | 0.40252 |  | 1.0323 |  | 3.8182 | 0 | 0.07475 |  | 5.3278
81 |  |  |  | EAST | Firstlight Network Limited | N/A | All Locations | [5 empty] | 0.0031661 |  |  | 0.0031661 | 0 |  | 0 |  | 0 | 0.0024284 |  |  | 0.0024284
82 |  |  |  | GENE | Genesis Energy Ltd | HLY033SA | Huntly | 0.15401 |  | 3.7361 |  | 0.0035292 |  |  |  | 3.8937 | 0.18331 |  | 5.0817 |  | 0.0032631 | 0 |  |  | 5.2683
83 |  |  |  | GENE | Genesis Energy Ltd | RPO220I1 | Rangipo | 0.9918 |  | 1.3019 | [5 empty] | 2.2937 | 1.2266 |  | 1.502 |  | 0 | 0 |  |  | 2.7286
84 |  |  |  | GENE | Genesis Energy Ltd | TKA033S1 | Tekapo A | 0.87052 |  | 0.44312 |  | 0.014333 |  |  |  | 1.328 | 1.0461 |  | 0.46909 |  | 0.018525 | 0 |  |  | 1.5337
85 |  |  |  | GENE | Genesis Energy Ltd | TKA033S2 | Tekapo B | 0.61957 |  | 3.4245 | [5 empty] | 4.044 | 0.76895 |  | 3.7656 |  | 1.346e-05 | 0 |  |  | 4.5346
86 |  |  |  | GENE | Genesis Energy Ltd | TKU033S1 | Tokaanu | 1.3428 |  | 1.754 |  | 0.70174 |  |  |  | 3.7986 | 1.639 |  | 2.014 |  | 0.79884 | 0 |  |  | 4.4518
87 |  |  |  | GENE | Genesis Energy Ltd | TUI110S2 | Tuai | 0.13592 |  | 1.2229 |  | 0.00064824 |  |  |  | 1.3595 | 0.16796 |  | 1.246 |  | 0.00014281 | 0 |  |  | 1.4141
88 |  |  |  | GENE | Genesis Energy Ltd | N/A | All Locations | 0 |  |  |  |  | 0.0063647 | 0.026002 |  | 0.032367 | 0 |  | 0 |  | 0 | 0.0044438 | 0.026002 |  | 0.030446
89 |  |  |  | HORO | Electra Limited | MHO033S1 | Mangahao | 1.2953 |  | 0.27795 |  | 2.4937 |  | 0.09649 |  | 4.1634 | 1.6328 |  | 0.35664 |  | 2.9084 | 0 | 0.09649 |  | 4.9942
90 |  |  |  | HORO | Electra Limited | PRM033S1 | Paraparaumu | 0.40523 |  | 1.026 |  | 3.6318 |  | 0.57851 |  | 5.6416 | 0.47155 |  | 1.1803 |  | 4.1905 | 0 | 0.57851 |  | 6.4208
91 |  |  |  | HORO | Electra Limited | N/A | All Locations | [5 empty] | 0.0059321 |  |  | 0.0059321 | 0 |  | 0 |  | 0 | 0.0045528 |  |  | 0.0045528
92 |  |  |  | HRZE | Horizon Energy Distribution Ltd | EDG033S1 | Edgecumbe | 0.41942 |  | 0.58343 |  | 3.441 |  |  |  | 4.4439 | 0.51892 |  | 0.74615 |  | 3.9469 | 0 |  |  | 5.212
93 |  |  |  | HRZE | Horizon Energy Distribution Ltd | KAW011S1 | Kawerau | 0.46011 |  | 0.040283 |  | 1.14 |  |  |  | 1.6404 | 0.56925 |  | 0.064342 |  | 1.336 | 0 |  |  | 1.9696
94 |  |  |  | HRZE | Horizon Energy Distribution Ltd | WAI011S1 | Waiotahi | 0.19624 |  | 0.033888 |  | 0.14198 |  |  |  | 0.3721 | 0.98449 |  | 0.16048 |  | 0.66751 | 0 |  |  | 1.8125
95 |  |  |  | HRZE | Horizon Energy Distribution Ltd | N/A | All Locations | 0 |  |  |  |  | 0.0046451 | 0.018563 |  | 0.023208 | 0 |  | 0 |  | 0 | 0.0035985 | 0.018563 |  | 0.022162
96 |  |  |  | HRZE | Horizon Energy Distribution Ltd | WAI011S1/WAI005S1 | Waiotahe | 0.58871 |  | 0.10166 |  | 0.42594 |  |  |  | 1.1163 | [8 empty] | 0
97 |  |  |  | KIWI | Whareroa Cogeneration Limited | HWA033S1/HWA033S2 | Hawera | 0.13024 |  | 0.21451 |  | 1.4644 |  |  |  | 1.8091 | 0.16068 |  | 0.27064 |  | 1.6488 | 0 |  |  | 2.0801
98 |  |  |  | KIWI | Whareroa Cogeneration Limited | N/A | All Locations | 0 |  |  |  |  | 0.0012866 |  |  | 0.0012866 | 0 |  | 0 |  | 0 | 0.00096913 |  |  | 0.00096913
99 |  |  |  | KUPE | Beach Energy Resources NZ (Holdings) Ltd | HWA033S1/HWA033S2 | Hawera | 0.11974 |  | 0.26995 |  | 0.51409 |  |  |  | 0.90378 | 0.14147 |  | 0.33439 |  | 0.6209 | 0 |  |  | 1.0968
100 |  |  |  | KUPE | Beach Energy Resources NZ (Holdings) Ltd | N/A | All Locations | [5 empty] | 0.0005292 |  |  | 0.0005292 | 0 |  | 0 |  | 0 | 0.00041787 |  |  | 0.00041787
101 |  |  |  | KWGL | Kawerau Geothermal Limited | KAW011S1 | Kawerau | 0.023298 |  | 0.45331 | [5 empty] | 0.47661 | 0.026354 |  | 0.54321 |  | 0.077385 | 0 |  |  | 0.64694
102 |  |  |  | KWGL | Kawerau Geothermal Limited | N/A | All Locations | [5 empty] | 0.00018564 |  |  | 0.00018564 | 0 |  | 0 |  | 0 | 0.00017185 |  |  | 0.00017185
103 |  |  |  | MARL | Marlborough Lines Limited | BLN033S1 | Blenheim | 0.42267 |  | 1.3891 |  | 4.0489 |  | 0.41092 |  | 6.2716 | 0.50634 |  | 1.887 |  | 4.7117 | 0 | 0.41092 |  | 7.5159
104 |  |  |  | MARL | Marlborough Lines Limited | N/A | All Locations | [5 empty] | 0.0041201 |  |  | 0.0041201 | 0 |  | 0 |  | 0 | 0.0031589 |  |  | 0.0031589
105 |  |  |  | MELT | MEL (Te Apiti) Limited | WDV011S1 | Woodville | 0.031434 |  | 0.33119 |  | 0.052086 |  |  |  | 0.41471 | 0.036504 |  | 0.41521 |  | 0.065166 | 0 |  |  | 0.51688
106 |  |  |  | MELT | MEL (Te Apiti) Limited | N/A | All Locations | [5 empty] | 0.0001128 |  |  | 0.0001128 | 0 |  | 0 |  | 0 | 8.463e-05 |  |  | 8.463e-05
107 |  |  |  | MELW | MEL (West Wind) Limited | WWD110I1 | West Wind | 0.038099 |  | 0.57563 |  | 0.066212 |  | 0.71311 |  | 1.393 | 0.043173 |  | 0.65048 |  | 0.075819 | 0 | 0.71311 |  | 1.4826
108 |  |  |  | MELW | MEL (West Wind) Limited | N/A | All Locations | [5 empty] | 0.00024864 |  |  | 0.00024864 | 0 |  | 0 |  | 0 | 0.00017614 |  |  | 0.00017614
109 |  |  |  | MERI | Meridian Energy Limited | AVI220I1 | Aviemore | 0.087498 |  | 3.3208 |  | 0.042623 |  |  |  | 3.451 | 0.10822 |  | 3.6815 |  | 0.0295 | 0 |  |  | 3.8192
110 |  |  |  | MERI | Meridian Energy Limited | BEN220I1 | Benmore | 0.11477 |  | 11.6881 |  | 0.087606 |  |  |  | 11.8905 | 0.14036 |  | 12.694 |  | 0.11047 | 0 |  |  | 12.9448
111 |  |  |  | MERI | Meridian Energy Limited | BRB033S1 | Bream Bay | 0.65725 | [7 empty] | 0.65725 | [8 empty] | 0
112 |  |  |  | MERI | Meridian Energy Limited | MAN220I1 | Manapouri | 14.3992 |  | 18.465 | [5 empty] | 32.8642 | 17.9094 |  | 20.013 |  | 0 | 0 |  |  | 37.9225
113 |  |  |  | MERI | Meridian Energy Limited | OHA220I1 | Ohau A | 1.2382 |  | 3.8225 |  | 0.10165 |  |  |  | 5.1624 | 1.5331 |  | 4.255 |  | 0.1053 | 0 |  |  | 5.8934
114 |  |  |  | MERI | Meridian Energy Limited | OHB220I1 | Ohau B | 0.60181 |  | 3.3506 |  | 0.07518 |  |  |  | 4.0276 | 0.74525 |  | 3.7196 |  | 0.076672 | 0 |  |  | 4.5416
115 |  |  |  | MERI | Meridian Energy Limited | OHC220I1 | Ohau C | 0.63543 |  | 3.3268 |  | 0.071452 |  |  |  | 4.0337 | 0.78745 |  | 3.6935 |  | 0.074044 | 0 |  |  | 4.555
116 |  |  |  | MERI | Meridian Energy Limited | TWZ033S1/S3 | Twizel | 0.089572 |  | 0.015137 |  | 0.86413 |  |  |  | 0.96884 | 0.10043 |  | 0.016034 |  | 0.96261 | 0 |  |  | 1.0791
117 |  |  |  | MERI | Meridian Energy Limited | WTK011S2 | Waitaki | 0.54141 |  | 1.8 | [5 empty] | 2.3414 | 0.69564 |  | 1.9923 |  | 0 | 0 |  |  | 2.6879
118 |  |  |  | MERI | Meridian Energy Limited | N/A | All Locations | [5 empty] | 0.034011 | 0.055344 |  | 0.089355 | 0 |  | 0 |  | 0 | 0.023796 | 0.055344 |  | 0.07914
119 |  |  |  | MERI | Meridian Energy Limited | HRP220I1 | Harapaki | 0.41405 |  | 0.83513 |  |  |  | 1.4063 |  | 2.6555 | 0.24921 |  | 0.5211 |  | 0 | 0 | 1.4063 |  | 2.1766
120 |  |  |  | METH | Methanex New Zealand Ltd | MNI011SA | Motunui | 0.39273 |  | 0.21957 |  | 0.49244 |  |  |  | 1.1047 | 0.48664 |  | 0.27014 |  | 0.55485 | 0 |  |  | 1.3116
121 |  |  |  | METH | Methanex New Zealand Ltd | N/A | All Locations | [5 empty] | 0.00049884 |  |  | 0.00049884 | 0 |  | 0 |  | 0 | 0.0003719 |  |  | 0.0003719
122 |  |  |  | MPOW | Mainpower New Zealand Limited | ASY011S1 | Ashley | 0.65423 |  | 0.28084 |  | 0.99455 |  | 0.30353 |  | 2.2331 | 0.80139 |  | 0.32708 |  | 1.1821 | 0 | 0.30353 |  | 2.6141
123 |  |  |  | MPOW | Mainpower New Zealand Limited | CUL033S1 | Culverden | 0.91659 |  | 0.26815 |  | 1.1536 |  |  |  | 2.3384 | 1.1342 |  | 0.29838 |  | 1.3156 | 0 |  |  | 2.7481
124 |  |  |  | MPOW | Mainpower New Zealand Limited | KAI011S1 | Kaiapoi | 0.77141 |  | 0.46421 |  | 1.5922 |  | 0.4188 |  | 3.2466 | 0.94369 |  | 0.53819 |  | 1.8629 | 0 | 0.4188 |  | 3.7636
125 |  |  |  | MPOW | Mainpower New Zealand Limited | SBK066S1 | Southbrook | 0.25059 |  | 0.77323 |  | 2.7151 |  | 0.36303 |  | 4.102 | 0.30287 |  | 0.89876 |  | 3.1935 | 0 | 0.36303 |  | 4.7582
126 |  |  |  | MPOW | Mainpower New Zealand Limited | WPR033S1 | Waipara | 0.23309 |  | 0.17518 |  | 0.84132 |  | 0.054632 |  | 1.3042 | 0.28448 |  | 0.20508 |  | 0.97662 | 0 | 0.054632 |  | 1.5208
127 |  |  |  | MPOW | Mainpower New Zealand Limited | N/A | All Locations | [5 empty] | 0.0074156 | 0.0087472 |  | 0.016163 | 0 |  | 0 |  | 0 | 0.0057084 | 0.05298 |  | 0.058689
128 |  |  |  | MRPL | Mercury NZ Limited | ARI110S2 | Arapuni | 0.18265 |  | 1.1431 |  | 0.019516 |  |  |  | 1.3452 | 0.22578 |  | 1.3064 |  | 0.02921 | 0 |  |  | 1.5614
129 |  |  |  | MRPL | Mercury NZ Limited | ARA220I1 | Aratiatia | 0.63732 |  | 1.0266 | [5 empty] | 1.664 | 0.78793 |  | 1.1554 |  | 2.94e-06 | 0 |  |  | 1.9434
130 |  |  |  | MRPL | Mercury NZ Limited | ATI220S1 | Atiamuri | 0.077201 |  | 0.74334 |  | 0.22119 |  |  |  | 1.0417 | 0.095418 |  | 0.84787 |  | 0.27077 | 0 |  |  | 1.2141
131 |  |  |  | MRPL | Mercury NZ Limited | KPO110I1 | Karapiro | 0.057469 |  | 0.64117 | [5 empty] | 0.69864 | 0.071013 |  | 0.77054 |  | 0 | 0 |  |  | 0.84155
132 |  |  |  | MRPL | Mercury NZ Limited | MTI220I1 | Maraetai | 1.4104 |  | 2.0226 |  | 0.0037949 |  |  |  | 3.4368 | 1.7251 |  | 2.342 |  | 0.0063228 | 0 |  |  | 4.0735
133 |  |  |  | MRPL | Mercury NZ Limited | OHK220I1 | Ohakuri | 0.088238 |  | 1.3752 |  | 0.005602 |  |  |  | 1.4691 | 0.10908 |  | 1.5342 |  | 0.0063728 | 0 |  |  | 1.6497
134 |  |  |  | MRPL | Mercury NZ Limited | SWN025S1 | Southdown |  |  | 0.0023698 | [5 empty] | 0.0023698 | 0 |  | 0.0034669 |  | 0 | 0 |  |  | 0.0034669
135 |  |  |  | MRPL | Mercury NZ Limited | WPA220I1 | Waipapa | 0.78895 |  | 0.47943 |  | 0.0009036 |  |  |  | 1.2693 | 0.97924 |  | 0.56236 |  | 0.0014261 | 0 |  |  | 1.543
136 |  |  |  | MRPL | Mercury NZ Limited | WKM220I1 | Whakamaru | 0.1447 |  | 1.5608 |  | 1.5561 |  |  |  | 3.2616 | 0.17874 |  | 1.7537 |  | 1.7975 | 0 |  |  | 3.7299
137 |  |  |  | MRPL | Mercury NZ Limited | N/A | All Locations | 0 |  |  |  |  | 0.0067819 | 0.01536 |  | 0.022142 | 0 |  | 0 |  | 0 | 0.004822 | 0.01536 |  | 0.020182
138 |  |  |  | MSVP | Mercury SPV Limited | LTN033S1 | Linton | 0.05123 |  | 0.67047 | [5 empty] | 0.7217 | 0.057446 |  | 0.85704 |  | 0.04405 | 0 |  |  | 0.95854
139 |  |  |  | MSVP | Mercury SPV Limited | N/A | All Locations | 0 |  |  |  |  | 0.0001914 |  |  | 0.0001914 | 0 |  | 0 |  | 0 | 0.00015777 |  |  | 0.00015777
140 |  |  |  | NAPA | Nga Awa Purua Joint Venture | NAP220I1 | Nga Awa Purua | 0.46852 |  | 2.4399 |  | 0.26146 |  | 0.42182 |  | 3.5917 | 0.56113 |  | 2.8417 |  | 0.27082 | 0 | 0.42182 |  | 4.0955
141 |  |  |  | NAPA | Nga Awa Purua Joint Venture | N/A | All Locations | [5 empty] | 0.0015343 |  |  | 0.0015343 | 0 |  | 0 |  | 0 | 0.0010575 |  |  | 0.0010575
142 |  |  |  | NELS | Nelson Electricity Ltd | STK033S1 | Stoke | 0.067809 |  | 0.13892 |  | 0.76258 |  |  |  | 0.96931 | 0.087038 |  | 0.15444 |  | 0.87254 | 0 |  |  | 1.114
143 |  |  |  | NELS | Nelson Electricity Ltd | N/A | All Locations | [5 empty] | 0.00074148 |  |  | 0.00074148 | 0 |  | 0 |  | 0 | 0.00056239 |  |  | 0.00056239
144 |  |  |  | NPOW | Northpower Limited | BRB033S1 | Bream Bay | 1.8557 |  | 1.7792 |  | 0.90261 |  |  |  | 4.5375 | 3.1159 |  | 2.1795 |  | 3.0948 | 0 |  |  | 8.3901
145 |  |  |  | NPOW | Northpower Limited | MPE110S1 | Maungatapere | 0.32186 |  | 5.7068 |  | 5.9259 |  |  |  | 11.9546 | 0.39645 |  | 6.6588 |  | 4.9316 | 0 |  |  | 11.9868
146 |  |  |  | NPOW | Northpower Limited | MTO033S1 | Maungaturoto | 0.39676 |  | 0.79244 |  | 1.0339 |  |  |  | 2.2231 | 0.49077 |  | 0.92626 |  | 0.8457 | 0 |  |  | 2.2627
147 |  |  |  | NPOW | Northpower Limited | N/A | All Locations | [5 empty] | 0.01058 |  |  | 0.01058 | 0 |  | 0 |  | 0 | 0.0077495 |  |  | 0.0077495
148 |  |  |  | NTRG | Ngatamariki Geothermal Ltd | NAP220I2 | Nga Awa Purua | 0.26898 |  | 1.4887 |  | 0.085301 |  | 0.43224 |  | 2.2752 | 0.3346 |  | 1.7363 |  | 0.10715 | 0 | 0.43224 |  | 2.6103
149 |  |  |  | NTRG | Ngatamariki Geothermal Ltd | N/A | All Locations | 0 |  |  |  |  | 0.0008676 |  |  | 0.0008676 | 0 |  | 0 |  | 0 | 0.0006084 |  |  | 0.0006084
150 |  |  |  | NZAS | NZ Aluminium Smelters Limited | TWI220S1 | Tiwai | 1.3651 |  | 12.0945 |  | 32.3234 |  |  |  | 45.7829 | 1.6904 |  | 13.1448 |  | 36.9711 | 0 |  |  | 51.8063
151 |  |  |  | NZAS | NZ Aluminium Smelters Limited | N/A | All Locations | [5 empty] | 0.03674 |  |  | 0.03674 | 0 |  | 0 |  | 0 | 0.027527 |  |  | 0.027527
152 |  |  |  | NZST | New Zealand Steel Limited | GLN033SA | Glenbrook | 2.3466 |  | 3.0508 |  | 8.5391 |  | 0.083772 |  | 14.0202 | 3.0453 |  | 3.4405 |  | 9.9066 | 0 | 0.083772 |  | 16.4761
153 |  |  |  | NZST | New Zealand Steel Limited | N/A | All Locations | [5 empty] | 0.009402 |  |  | 0.009402 | 0 |  | 0 |  | 0 | 0.0071288 |  |  | 0.0071288
154 |  |  |  | OMVP | OMV New Zealand Limited | MNI011SA | Motunui | 0.30464 |  | 0.28141 |  | 0.14082 |  |  |  | 0.72687 | 0.37485 |  | 0.33634 |  | 0.32351 | 0 |  |  | 1.0347
155 |  |  |  | OMVP | OMV New Zealand Limited | N/A | All Locations | [5 empty] | 0.00024564 |  |  | 0.00024564 | 0 |  | 0 |  | 0 | 0.00027181 |  |  | 0.00027181
156 |  |  |  | ORON | Orion New Zealand Limited | APS011S1 | Arthurs Pass | 0.097608 |  | 0.0035586 |  | 0.01243 |  |  |  | 0.1136 | 0.12069 |  | 0.0041241 |  | 0.015252 | 0 |  |  | 0.14007
157 |  |  |  | ORON | Orion New Zealand Limited | BRY066SA | Bromley | 2.1269 |  | 1.6861 |  | 8.2455 |  | 0.58524 |  | 12.6438 | 2.6456 |  | 1.8818 |  | 9.6043 | 0 | 0.58524 |  | 14.7168
158 |  |  |  | ORON | Orion New Zealand Limited | CLH011S1 | Castle Hill | 0.12125 |  | 0.0061529 |  | 0.020717 |  |  |  | 0.14812 | 0.15006 |  | 0.0070348 |  | 0.023552 | 0 |  |  | 0.18064
159 |  |  |  | ORON | Orion New Zealand Limited | COL011S1 | Coleridge | 0.11214 |  | 0.0037896 |  | 0.016574 |  |  |  | 0.1325 | 0.13888 |  | 0.0044001 |  | 0.016747 | 0 |  |  | 0.16002
160 |  |  |  | ORON | Orion New Zealand Limited | HOR033S1 | Hororata | 0.3175 |  | 0.46493 |  | 2.0303 |  |  |  | 2.8127 | 0.39015 |  | 0.54446 |  | 2.2021 | 0 |  |  | 3.1367
161 |  |  |  | ORON | Orion New Zealand Limited | ISL033S1 | Islington | 1.7909 |  | 8.1022 |  | 30.2432 |  | 0.14497 |  | 40.2814 | 2.2111 |  | 9.3081 |  | 35.2024 | 0 | 0.14497 |  | 46.8665
162 |  |  |  | ORON | Orion New Zealand Limited | KBY066SA | Kimberley | 0.021664 |  | 0.15093 |  | 0.86599 |  |  |  | 1.0386 | 0.024459 |  | 0.18501 |  | 1.048 | 0 |  |  | 1.2574
163 |  |  |  | ORON | Orion New Zealand Limited | NWD066S1 | Norwood | 0.22492 | [5 empty] | 2.5468 |  | 2.7717 | [6 empty] | 2.5468 |  | 2.5468
164 |  |  |  | ORON | Orion New Zealand Limited | N/A | All Locations | [5 empty] | 0.041826 | 0.0082672 |  | 0.050093 | 0.24038 |  | 0 |  | 0 | 0.03203 | 0.0082672 |  | 0.28067
165 |  |  |  | PANP | Pan Pac Forest Product Limited | WHI011SA | Whirinaki | 1.1746 |  | 1.1452 |  | 3.9649 |  |  |  | 6.2848 | 1.4417 |  | 1.403 |  | 4.321 | 0 |  |  | 7.1656
166 |  |  |  | PANP | Pan Pac Forest Product Limited | N/A | All Locations | [5 empty] | 0.00389 |  |  | 0.00389 | 0 |  | 0 |  | 0 | 0.0028237 |  |  | 0.0028237
167 |  |  |  | POCO | Powerco Limited | ARI110S2 | Arapuni | 0.028932 | [5 empty] | 0.14242 |  | 0.17136 | 0.033269 |  | 0 |  | 0 | 0 | 0.14242 |  | 0.17569
168 |  |  |  | POCO | Powerco Limited | BRK033S1 | Brunswick | 0.19036 |  | 0.39005 |  | 1.3797 |  |  |  | 1.9601 | 0.23509 |  | 0.45698 |  | 1.5984 | 0 |  |  | 2.2905
169 |  |  |  | POCO | Powerco Limited | BPE033S1 | Bunnythorpe | 0.75679 |  | 1.2033 |  | 5.2984 |  | 0.040643 |  | 7.299 | 0.93648 |  | 1.3989 |  | 6.0618 | 0 | 0.040643 |  | 8.4378
170 |  |  |  | POCO | Powerco Limited | CST033S1 | Carrington St | 0.44178 |  | 1.4738 |  | 2.635 |  | 0.44485 |  | 4.9955 | 0.53333 |  | 1.7802 |  | 3.2795 | 0 | 0.44485 |  | 6.0379
171 |  |  |  | POCO | Powerco Limited | GYT033S1 | Greytown | 0.45994 |  | 0.23914 |  | 0.83123 |  |  |  | 1.5303 | 0.56829 |  | 0.27687 |  | 0.9798 | 0 |  |  | 1.825
172 |  |  |  | POCO | Powerco Limited | HWA033S1 | Hawera | 0.43923 |  | 0.42823 |  | 1.3288 |  |  |  | 2.1963 | 0.54033 |  | 0.58379 |  | 1.26 | 0 |  |  | 2.3841
173 |  |  |  | POCO | Powerco Limited | HIN033S1 | Hinuera | 0.68824 |  | 0.93051 |  | 2.324 |  | 0.17863 |  | 4.1214 | 0.85676 |  | 1.112 |  | 2.7079 | 0 | 0.17863 |  | 4.8553
174 |  |  |  | POCO | Powerco Limited | HUI033S1 | Huirangi | 0.40664 |  | 0.6741 |  | 2.1035 |  | 0.69358 |  | 3.8778 | 0.4862 |  | 0.83043 |  | 2.3556 | 0 | 0.69358 |  | 4.3658
175 |  |  |  | POCO | Powerco Limited | KMO033S1 | Kaitimako | 0.11825 |  | 0.16315 |  | 0.84819 |  | 0.40946 |  | 1.5391 | 0.13492 |  | 0.19482 |  | 0.99089 | 0 | 0.40946 |  | 1.7301
176 |  |  |  | POCO | Powerco Limited | KIN011SA | Kinleith | 1.2807 |  | 0.81164 |  | 7.2662 |  | 0.037269 |  | 9.3958 | 1.5687 |  | 0.98024 |  | 8.2415 | 0 | 0.037269 |  | 10.8277
177 |  |  |  | POCO | Powerco Limited | KPU066S1 | Kopu | 3.035 |  | 0.97311 |  | 2.4315 |  | 0.13112 |  | 6.5707 | 3.7552 |  | 1.1626 |  | 2.8245 | 0 | 0.13112 |  | 7.8735
178 |  |  |  | POCO | Powerco Limited | LTN033S1 | Linton | 0.85402 |  | 0.4902 |  | 2.8669 |  | 0.1722 |  | 4.3833 | 1.0565 |  | 0.56944 |  | 3.3533 | 0 | 0.1722 |  | 5.1514
179 |  |  |  | POCO | Powerco Limited | MGM033S1 | Mangamaire | 0.52975 |  | 0.37761 |  | 0.86515 |  |  |  | 1.7725 | 0.65401 |  | 0.4612 |  | 1.026 | 0 |  |  | 2.1412
180 |  |  |  | POCO | Powerco Limited | MTN033S1 | Marton | 0.31381 |  | 0.41746 |  | 0.99521 |  |  |  | 1.7265 | 0.38409 |  | 0.51102 |  | 1.1508 | 0 |  |  | 2.0459
181 |  |  |  | POCO | Powerco Limited | MST033S1 | Masterton | 0.35729 |  | 0.98631 |  | 2.4937 |  | 0.44491 |  | 4.2822 | 0.4291 |  | 1.1439 |  | 2.8824 | 0 | 0.44491 |  | 4.9004
182 |  |  |  | POCO | Powerco Limited | MTR033S1 | Mataroa | 0.26664 |  | 0.16267 |  | 0.36755 |  |  |  | 0.79686 | 0.32914 |  | 0.19782 |  | 0.42429 | 0 |  |  | 0.95125
183 |  |  |  | POCO | Powerco Limited | MTM033S1 | Mt Maunganui | 1.1407 |  | 0.64801 |  | 3.2627 |  | 0.90681 |  | 5.9582 | 0.85066 |  | 0.76758 |  | 3.5681 | 0 | 0.90681 |  | 6.0932
184 |  |  |  | POCO | Powerco Limited | No POS Code | New Plymouth |  |  |  |  | 0.77468 |  |  |  | 0.77468 | 0 |  | 0 |  | 0.62319 | 0 |  |  | 0.62319
185 |  |  |  | POCO | Powerco Limited | OKN011S2 | Ohakune | 0.081429 |  | 0.042685 |  | 0.11309 |  |  |  | 0.23721 | 0.10229 |  | 0.051421 |  | 0.12747 | 0 |  |  | 0.28118
186 |  |  |  | POCO | Powerco Limited | OPK033S1 | Opunake | 1.3262 |  | 0.22328 |  | 0.54284 |  |  |  | 2.0924 | 1.4546 |  | 0.27367 |  | 0.62044 | 0 |  |  | 2.3487
187 |  |  |  | POCO | Powerco Limited | PAO110S1 | Piako | 0.31056 |  | 0.76283 |  | 2.1205 |  | 1.069 |  | 4.2629 | 0.36198 |  | 0.92516 |  | 2.4724 | 0 | 1.069 |  | 4.8285
188 |  |  |  | POCO | Powerco Limited | SFD033S1 | Stratford | 0.40954 |  | 0.59629 |  | 1.719 |  |  |  | 2.7248 | 0.50692 |  | 0.72969 |  | 1.9009 | 0 |  |  | 3.1375
189 |  |  |  | POCO | Powerco Limited | TGA011S1 | Tauranga | 1.0267 |  | 0.80214 |  | 6.0674 |  | 1.1596 |  | 9.0559 | 1.249 |  | 0.96233 |  | 7.1598 | 0 | 1.1596 |  | 10.5308
190 |  |  |  | POCO | Powerco Limited | TMI033S1 | Te Matai | 0.26393 |  | 0.36244 |  | 2.1883 |  | 0.26329 |  | 3.078 | 0.31612 |  | 0.44424 |  | 2.8415 | 0 | 0.26329 |  | 3.8652
191 |  |  |  | POCO | Powerco Limited | WHU033S1 | Waihou | 1.1229 |  | 0.7479 |  | 1.8264 |  |  |  | 3.6972 | 1.4359 |  | 0.89063 |  | 2.1093 | 0 |  |  | 4.4358
192 |  |  |  | POCO | Powerco Limited | WKO033S1 | Waikino | 1.3138 |  | 0.76991 |  | 2.0017 |  |  |  | 4.0854 | 1.6273 |  | 0.92283 |  | 2.3319 | 0 |  |  | 4.882
193 |  |  |  | POCO | Powerco Limited | WGN033S1 | Wanganui | 0.38954 |  | 0.68744 |  | 1.6285 |  | 0.060836 |  | 2.7663 | 0.4819 |  | 0.84256 |  | 1.9074 | 0 | 0.060836 |  | 3.2927
194 |  |  |  | POCO | Powerco Limited | WVY011S1 | Waverley | 0.2523 |  | 0.11233 |  | 0.26577 |  |  |  | 0.6304 | 0.31175 |  | 0.137 |  | 0.29536 | 0 |  |  | 0.74411
195 |  |  |  | POCO | Powerco Limited | N/A | All Locations | [5 empty] | 0.055571 | 0.022252 |  | 0.077823 | 0 |  | 0 |  | 0 | 0.042312 | 0.022252 |  | 0.064564
196 |  |  |  | POWN | Powernet Ltd | BAL033S1 | Balclutha | 1.0127 |  | 0.49763 |  | 1.7353 |  |  |  | 3.2456 | 1.2534 |  | 0.56596 |  | 2.0126 | 0 |  |  | 3.8319
197 |  |  |  | POWN | Powernet Ltd | CML033S1 | Cromwell | [6 empty] | 0.046396 |  | 0.046396 | [6 empty] | 0.046396 |  | 0.046396
198 |  |  |  | POWN | Powernet Ltd | EDN033S1 | Edendale | 0.17479 |  | 0.55249 |  | 1.4788 |  | 0.037273 |  | 2.2434 | 0.21042 |  | 0.48649 |  | 1.7093 | 0 | 0.037273 |  | 2.4435
199 |  |  |  | POWN | Powernet Ltd | FKN033S1 | Frankton | 0.31854 |  | 0.060692 |  | 0.2766 |  | 0.060855 |  | 0.71669 | 0.40643 |  | 0.064803 |  | 0.35702 | 0 | 0.12461 |  | 0.95285
200 |  |  |  | POWN | Powernet Ltd | GOR033S1 | Gore | 0.52675 |  | 1.7435 |  | 1.6982 |  | 0.10394 |  | 4.0724 | 0.65391 |  | 1.5556 |  | 2.0154 | 0 | 0.10394 |  | 4.3288
201 |  |  |  | POWN | Powernet Ltd | HWB033S1 | Halfway Bush | 0.069712 |  | 0.076477 |  | 0.33068 |  |  |  | 0.47687 | 0.080255 |  | 0.083179 |  | 0.3835 | 0 |  |  | 0.54693
202 |  |  |  | POWN | Powernet Ltd | INV033S1 | Invercargill | 0.45226 |  | 1.038 |  | 4.6713 |  | 0.64046 |  | 6.802 | 0.54169 |  | 1.1295 |  | 5.5136 | 0 | 0.64046 |  | 7.8253
203 |  |  |  | POWN | Powernet Ltd | NSY033S1 | Naseby | 0.70813 |  | 0.40251 |  | 2.3426 |  |  |  | 3.4532 | 0.87851 |  | 0.42767 |  | 2.6788 | 0 |  |  | 3.985
204 |  |  |  | POWN | Powernet Ltd | NMA033S1 | North Makarewa | 0.60214 |  | 0.18875 |  | 2.919 |  |  |  | 3.7099 | 0.74559 |  | 0.21545 |  | 3.3324 | 0 |  |  | 4.2934
205 |  |  |  | POWN | Powernet Ltd | N/A | All Locations | [5 empty] | 0.015329 | 0.01088 |  | 0.026209 | 0 |  | 0 |  | 0 | 0.012173 | 0.01088 |  | 0.023052
206 |  |  |  | RAYN | Daiken Southland Limited | BDE011S1 | Brydone | 0.17286 |  | 0.2444 |  | 0.50286 |  |  |  | 0.92011 | 0.18886 |  | 0.27239 |  | 0.58474 | 0 |  |  | 1.046
207 |  |  |  | RAYN | Daiken Southland Limited | N/A | All Locations | [5 empty] | 0.00057384 |  |  | 0.00057384 | 0 |  | 0 |  | 0 | 0.00043492 |  |  | 0.00043492
208 |  |  |  | SCAN | Scanpower Limited | DVK011S1 | Dannevirke | 0.26447 |  | 0.34237 |  | 0.69412 |  | 0.17066 |  | 1.4716 | 0.32181 |  | 0.41599 |  | 0.80008 | 0 | 0.17066 |  | 1.7085
209 |  |  |  | SCAN | Scanpower Limited | WDV011S1 | Woodville | 0.2892 |  | 0.063371 |  | 0.12976 |  | 0.098177 |  | 0.58051 | 0.35323 |  | 0.077112 |  | 0.14904 | 0 | 0.098177 |  | 0.67756
210 |  |  |  | SCAN | Scanpower Limited | N/A | All Locations | [5 empty] | 0.00086556 |  |  | 0.00086556 | 0 |  | 0 |  | 0 | 0.00065552 |  |  | 0.00065552
211 |  |  |  | SCGL | Mercury NZ Limited | N/A | All Locations | [8 empty] | 0 | [8 empty] | 0
212 |  |  |  | SGGP | Southern Generation | MAT110I1/MAT110S1 | Southland | 0.22898 | [7 empty] | 0.22898 | 0.26848 |  | 0.037264 | [5 empty] | 0.30574
213 |  |  |  | SHPK | Southpark Utilities Limited | PEN022S1 | Penrose | 0.025432 |  | 0.00052992 |  | 0.0096536 |  | 0.022425 |  | 0.05804 | 0.031201 |  | 0.00083656 |  | 0.01084 | 0 | 0.022425 |  | 0.065302
214 |  |  |  | SHPK | Southpark Utilities Limited | N/A | All Locations | [5 empty] | 8.28e-06 |  |  | 8.28e-06 | 0 |  | 0 |  | 0 | 6.19e-06 |  |  | 6.19e-06
215 |  |  |  | SOLE | Resolution Development Ltd | BDE011S1 | Brydone | 0.0043871 |  | 0.0019646 |  | 0.011453 |  |  |  | 0.017805 | 0.0035971 |  | 0.0020948 |  | 0.009399 | 0 |  |  | 0.015091
216 |  |  |  | SOLE | Resolution Development Ltd | N/A | All Locations | [5 empty] | -0.0077686 |  |  | -0.0077686 | 0 |  | 0 |  | 0 | -0.0056048 |  |  | -0.0056048
217 |  |  |  | TARW | Tararua Wind Power | TWC220S1 | Tararua | 0.021135 |  | 0.46441 |  | 0.058249 |  | 0.3406 |  | 0.8844 | 0.026499 |  | 0.59903 |  | 0.066796 | 0 | 0.3406 |  | 1.0329
218 |  |  |  | TARW | Tararua Wind Power | N/A | All Locations | 0 |  |  |  |  | 0.0001698 |  |  | 0.0001698 | 0 |  | 0 |  | 0 | 0.00012146 |  |  | 0.00012146
219 |  |  |  | TASM | Network Tasman Limited | KIK011S1 | Kikiwa | 0.043901 |  | 0.034516 |  | 0.14365 |  |  |  | 0.22207 | 0.053088 |  | 0.038505 |  | 0.16953 | 0 |  |  | 0.26112
220 |  |  |  | TASM | Network Tasman Limited | MCH011S1 | Murchison | 0.23583 |  | 0.038793 |  | 0.1284 |  |  |  | 0.40302 | 0.29209 |  | 0.053716 |  | 0.14763 | 0 |  |  | 0.49344
221 |  |  |  | TASM | Network Tasman Limited | STK033S1 | Stoke | 1.2255 |  | 1.5596 |  | 7.7531 |  | 1.1132 |  | 11.6514 | 1.5018 |  | 1.8038 |  | 8.9718 | 0 | 1.1132 |  | 13.3906
222 |  |  |  | TASM | Network Tasman Limited | N/A | All Locations | [5 empty] | 0.007849 |  |  | 0.007849 | 0 |  | 0 |  | 0 | 0.0060116 | 0.024889 |  | 0.030901
223 |  |  |  | TBOP | Nova Energy Limited | JRD110I1 | Junction Road | 0.0096128 |  | 0.64973 |  | 0.0008262 |  | 0.25481 |  | 0.91497 | 0.010815 |  | 0.7733 |  | 0.0020531 | 0 | 0.25481 |  | 1.041
224 |  |  |  | TBOP | Nova Energy Limited | KPA110S1 | Kaponga | 0.35732 |  | 0.15959 |  | 0.42732 |  |  |  | 0.94423 | 0.46508 |  | 0.20335 |  | 0.53514 | 0 |  |  | 1.2036
225 |  |  |  | TBOP | Nova Energy Limited | MKE110I1 | McKee | 0.013085 |  | 0.64689 |  | 0.0066966 |  | 0.16724 |  | 0.83392 | 0.014346 |  | 0.77038 |  | 0.006566 | 0 | 0.16724 |  | 0.95853
226 |  |  |  | TBOP | Nova Energy Limited | N/A | All Locations | [5 empty] | 0.0008994 |  |  | 0.0008994 | 0 |  | 0 |  | 0 | 0.0006768 | 0.62604 |  | 0.62671
227 |  |  |  | TOD3 | Nova Energy Limited | N/A | All Locations | [6 empty] | 0.0079845 |  | 0.0079845 | [6 empty] | 0.0079845 |  | 0.0079845
228 |  |  |  | TOPE | Top Energy Ltd | KOE110S1 | Kaikohe | 1.583 |  | 1.7083 |  | 3.7982 |  |  |  | 7.0895 | 1.9607 |  | 1.9563 |  | 4.3938 | 0 |  |  | 8.3107
229 |  |  |  | TOPE | Top Energy Ltd | N/A | All Locations | [5 empty] | 0.0041764 | 0.014225 |  | 0.018401 | 0 |  | 0 |  | 0 | 0.0031632 | 0.014225 |  | 0.017388
230 |  |  |  | TRNZ | KiwiRail Holdings Limited | BPE033S1 | Bunnythorpe | 0.30551 |  | 0.012546 |  | 0.14134 |  |  |  | 0.4594 | 0.37593 |  | 0.014249 |  | 0.1321 | 0 |  |  | 0.52228
231 |  |  |  | TRNZ | KiwiRail Holdings Limited | HAM011S1 | Hamilton | 0.30058 |  | 0.01387 |  | 0.12536 |  |  |  | 0.43981 | 0.36959 |  | 0.015463 |  | 0.11607 | 0 |  |  | 0.50112
232 |  |  |  | TRNZ | KiwiRail Holdings Limited | PEN022S1 | Penrose | 0.13308 |  | 0.11748 |  | 0.83229 |  |  |  | 1.0828 | 0.14906 |  | 0.13181 |  | 0.95381 | 0 |  |  | 1.2347
233 |  |  |  | TRNZ | KiwiRail Holdings Limited | SWN025S1 | Southdown | 0.096842 |  | 0.11436 |  | 0.82801 |  | 0.4929 |  | 1.5321 | 0.11337 |  | 0.12855 |  | 0.94634 | 0 | 0.4929 |  | 1.6811
234 |  |  |  | TRNZ | KiwiRail Holdings Limited | TNG011S1 | Tangiwai | 0.41872 |  | 0.013387 |  | 0.16385 |  |  |  | 0.59596 | 0.48205 |  | 0.015353 |  | 0.15109 | 0 |  |  | 0.6485
235 |  |  |  | TRNZ | KiwiRail Holdings Limited | TMN055SA | Taumarunui | 0.35491 |  | 0.016617 |  | 0.1598 |  |  |  | 0.53133 | 0.43733 |  | 0.018679 |  | 0.15079 | 0 |  |  | 0.60681
236 |  |  |  | TRNZ | KiwiRail Holdings Limited | N/A | All Locations | 0 |  |  |  |  | -0.54023 |  |  | -0.54023 | 0 |  | 0 |  | 0 | -0.40582 |  |  | -0.40582
237 |  |  |  | TRUG | Manawa Energy Ltd | ARG110I1 | Argyle | 0.045922 |  | 0.20321 |  | 0.027777 |  |  |  | 0.27691 | 0.056904 |  | 0.24004 |  | 0.033734 | 0 |  |  | 0.33068
238 |  |  |  | TRUG | Manawa Energy Ltd | BWK110I1 | Berwick | 0.09784 |  | 0.040407 |  | 0.0020354 |  |  |  | 0.14028 | 0.12097 |  | 0.052509 |  | 0.0016933 | 0 |  |  | 0.17517
239 |  |  |  | TRUG | Manawa Energy Ltd | COL011S1 | Coleridge | 0.034914 |  | 0.62193 |  | 0.0025884 |  |  |  | 0.65943 | 0.043121 |  | 0.68735 |  | 0.0033807 | 0 |  |  | 0.73385
240 |  |  |  | TRUG | Manawa Energy Ltd | HWA033S1 | Hawera | 0.074037 |  | 0.11997 |  | 0.0015232 |  |  |  | 0.19554 | 0.091398 |  | 0.15887 |  | 0.0018581 | 0 |  |  | 0.25212
241 |  |  |  | TRUG | Manawa Energy Ltd | MAT110S1 | Matahina | 0.48331 |  | 0.22286 | [5 empty] | 0.70617 | 0.61769 |  | 0.25424 |  | 0 | 0 |  |  | 0.87193
242 |  |  |  | TRUG | Manawa Energy Ltd | N/A | All Locations | [5 empty] | 0.00077652 | 0.011979 |  | 0.012756 | 0 |  | 0 |  | 0 | 0.00054019 | 0.011979 |  | 0.012519
243 |  |  |  | UNET | Wellington Electricity Lines Limited | CPK011S1 | Central Park | 1.1907 |  | 3.6015 |  | 10.0477 |  |  |  | 14.8399 | 1.475 |  | 4.158 |  | 11.3223 | 0 |  |  | 16.9553
244 |  |  |  | UNET | Wellington Electricity Lines Limited | GFD033S1 | Gracefield | 1.8605 |  | 1.2575 |  | 3.4967 |  |  |  | 6.6147 | 2.3274 |  | 1.4547 |  | 4.0344 | 0 |  |  | 7.8165
245 |  |  |  | UNET | Wellington Electricity Lines Limited | HAY011S1 | Haywards | 0.56095 |  | 0.59389 |  | 1.8436 |  |  |  | 2.9984 | 0.76957 |  | 0.68824 |  | 2.135 | 0 |  |  | 3.5928
246 |  |  |  | UNET | Wellington Electricity Lines Limited | KWA011S1 | Kaiwharawhara | 0.48031 |  | 0.68755 |  | 1.8836 |  | 0.64399 |  | 3.6954 | 0.58162 |  | 0.79284 |  | 2.0977 | 0 | 0.64399 |  | 4.1162
247 |  |  |  | UNET | Wellington Electricity Lines Limited | MLG011S1 | Melling | 1.5263 |  | 1.1552 |  | 3.1802 |  |  |  | 5.8617 | 1.8926 |  | 1.3342 |  | 3.6371 | 0 |  |  | 6.864
248 |  |  |  | UNET | Wellington Electricity Lines Limited | PNI033S1 | Pauatahanui | 1.1913 |  | 0.31574 |  | 0.87571 |  |  |  | 2.3827 | 1.4738 |  | 0.36511 |  | 1.003 | 0 |  |  | 2.8419
249 |  |  |  | UNET | Wellington Electricity Lines Limited | TKR033S1 | Takapu Road | 0.71225 |  | 1.7725 |  | 5.0976 |  | 0.066403 |  | 7.6488 | 0.47969 |  | 2.0584 |  | 5.915 | 0 | 0.066403 |  | 8.5194
250 |  |  |  | UNET | Wellington Electricity Lines Limited | UHT033S1 | Upper Hutt | 0.2316 |  | 0.58122 |  | 1.6408 |  |  |  | 2.4536 | 0.27759 |  | 0.67366 |  | 1.9143 | 0 |  |  | 2.8656
251 |  |  |  | UNET | Wellington Electricity Lines Limited | WIL033S1 | Wilton | 1.303 |  | 0.17295 |  | 2.6609 |  | 0.089042 |  | 4.226 | 1.6185 |  | 0.23846 |  | 3.0314 | 0 | 0.089042 |  | 4.9774
252 |  |  |  | UNET | Wellington Electricity Lines Limited | N/A | All Locations | [5 empty] | 0.031217 |  |  | 0.031217 | 0.38729 |  | 0 |  | 0 | 0.023551 |  |  | 0.41084
253 |  |  |  | UNIS | Unison Networks Limited | FHL033S1 | Fernhill | 0.56922 |  | 0.86478 |  | 3.2888 |  | 0.33353 |  | 5.0563 | 0.70404 |  | 0.978 |  | 3.8336 | 0 | 0.33353 |  | 5.8492
254 |  |  |  | UNIS | Unison Networks Limited | OWH011S1 | Owhata | 1.0719 |  | 0.037164 |  | 0.65138 |  | 0.019534 |  | 1.7799 | 1.3318 |  | 0.057753 |  | 0.75742 | 0 | 0.019534 |  | 2.1665
255 |  |  |  | UNIS | Unison Networks Limited | RDF033S1 | Redclyffe | 0.34555 |  | 0.89628 |  | 3.5039 |  | 0.55565 |  | 5.3014 | 0.41122 |  | 1.0102 |  | 4.0754 | 0 | 0.55565 |  | 6.0525
256 |  |  |  | UNIS | Unison Networks Limited | ROT011S1 | Rotorua | 1.7085 |  | 0.25647 |  | 4.1055 |  | 0.031034 |  | 6.1015 | 2.1143 |  | 0.34267 |  | 4.6871 | 0 | 0.031034 |  | 7.1751
257 |  |  |  | UNIS | Unison Networks Limited | TRK011S1 | Tarukenga | 0.12252 |  | 0.077552 |  | 0.41632 |  |  |  | 0.61639 | 0.14527 |  | 0.092423 |  | 0.48437 | 0 |  |  | 0.72207
258 |  |  |  | UNIS | Unison Networks Limited | WRK033S1 | Wairakei | 0.34041 |  | 0.1769 |  | 2.8963 |  |  |  | 3.4137 | 0.42066 |  | 0.24436 |  | 3.3836 | 0 |  |  | 4.0486
259 |  |  |  | UNIS | Unison Networks Limited | WTU033S1 | Whakatu | 1.6239 |  | 1.1389 |  | 5.0576 |  | 0.031647 |  | 7.8521 | 2.0113 |  | 1.3915 |  | 5.8807 | 0 | 0.031647 |  | 9.3151
260 |  |  |  | UNIS | Unison Networks Limited | N/A | All Locations | [5 empty] | 0.018325 | 0.0091811 |  | 0.027507 | 0.037954 |  | 0 |  | 0 | 0.014137 | 0.025792 |  | 0.077883
261 |  |  |  | VEC8 | Vector Limited | N/A | All Locations | [6 empty] | 0.024673 |  | 0.024673 | [6 empty] | 0.024673 |  | 0.024673
262 |  |  |  | VECT | Vector Limited | ALB033S1 | Albany | 1.4912 |  | 7.062 |  | 11.5582 |  | 0.2813 |  | 20.3927 | 1.8425 |  | 7.9857 |  | 13.397 | 0 | 0.2813 |  | 23.5066
263 |  |  |  | VECT | Vector Limited | HEN033S1 | Henderson | 0.421 |  | 3.829 |  | 5.8929 |  | 0.31974 |  | 10.4626 | 0.5026 |  | 3.9577 |  | 6.8042 | 0 | 0.31974 |  | 11.5842
264 |  |  |  | VECT | Vector Limited | HEP033S1 | Hepburn Road | 0.76696 |  | 5.0683 |  | 7.8969 |  | 0.2854 |  | 14.0176 | 0.94985 |  | 5.8897 |  | 8.9825 | 0 | 0.2854 |  | 16.1074
265 |  |  |  | VECT | Vector Limited | HOB110S1 | Hobson St | 0.23426 |  | 1.8987 |  | 3.1306 |  | 2.9595 |  | 8.2231 | 0.24933 |  | 2.2267 |  | 3.7228 | 0 | 2.9595 |  | 9.1583
266 |  |  |  | VECT | Vector Limited | LFD110S1 | Lichfield | 0.030557 |  | 0.11609 |  | 0.8341 |  |  |  | 0.98075 | 0.037682 |  | 0.14249 |  | 0.95507 | 0 |  |  | 1.1352
267 |  |  |  | VECT | Vector Limited | MNG033S1 | Mangere | 0.52709 |  | 4.9157 |  | 7.7994 |  | 0.1208 |  | 13.363 | 0.6364 |  | 5.7323 |  | 9.0139 | 0 | 0.1208 |  | 15.5034
268 |  |  |  | VECT | Vector Limited | MTM033S1 | Mt Roskill | 0.8067 |  | 5.6699 |  | 8.5685 |  |  |  | 15.045 | 0.9831 |  | 6.5747 |  | 9.824 | 0 |  |  | 17.3818
269 |  |  |  | VECT | Vector Limited | OTA022S1 | Otahuhu A | 0.58146 |  | 2.0259 |  | 3.8672 |  |  |  | 6.4746 | 0.71931 |  | 2.2813 |  | 4.4291 | 0 |  |  | 7.4297
270 |  |  |  | VECT | Vector Limited | PAK033S1 | Pakuranga | 1.1797 |  | 4.9619 |  | 7.7127 |  | 0.35658 |  | 14.2109 | 1.3514 |  | 5.5082 |  | 8.9427 | 0 | 0.35658 |  | 16.1589
271 |  |  |  | VECT | Vector Limited | PEN022S1 | Penrose | 1.7381 |  | 16.3616 |  | 27.8069 |  | 0.11179 |  | 46.0183 | 2.3486 |  | 18.2625 |  | 31.3267 | 0 | 0.11179 |  | 52.0496
272 |  |  |  | VECT | Vector Limited | SVL033S1 | Silverdale | 0.90706 |  | 2.6885 |  | 5.1454 |  | 0.49293 |  | 9.2339 | 1.0774 |  | 2.8652 |  | 6.0714 | 0 | 0.49293 |  | 10.5069
273 |  |  |  | VECT | Vector Limited | TAK033S1 | Takanini | 1.2587 |  | 3.21 |  | 6.532 |  | 0.023352 |  | 11.024 | 1.5592 |  | 3.6497 |  | 7.6551 | 0 | 0.023352 |  | 12.8873
274 |  |  |  | VECT | Vector Limited | WRD033S1 | Wairau Road | 0.30433 |  | 2.0665 |  | 3.6289 |  | 2.2312 |  | 8.2309 | 0.32498 |  | 2.3129 |  | 4.1465 | 0 | 2.2312 |  | 9.0156
275 |  |  |  | VECT | Vector Limited | WEL033S1 | Wellsford | 0.28667 |  | 1.3403 |  | 2.0582 |  |  |  | 3.6851 | 0.35097 |  | 1.5572 |  | 2.3914 | 0 |  |  | 4.2996
276 |  |  |  | VECT | Vector Limited | WIR033S1 | Wiri | 1.3222 |  | 4.631 |  | 5.8929 |  | 0.052843 |  | 11.8989 | 1.6728 |  | 5.2762 |  | 6.7521 | 0 | 0.052843 |  | 13.754
277 |  |  |  | VECT | Vector Limited | N/A | All Locations |  |  | 0 |  |  | 0.13633 |  |  | 0.13633 | 0 |  | 0 |  | 0 | 0.10162 |  |  | 0.10162
278 |  |  |  | WAIP | Waipa Networks Limited | CBG011S1 | Cambridge | 0.61513 |  | 0.93264 |  | 2.2385 |  | 0.10861 |  | 3.8949 | 0.76052 |  | 1.1218 |  | 2.6261 | 0 | 0.10861 |  | 4.6171
279 |  |  |  | WAIP | Waipa Networks Limited | TMI033S1 | Te Awamutu | 0.62568 |  | 0.81166 |  | 1.9262 |  | 0.49268 |  | 3.8562 | 0.77233 |  | 0.97385 |  | 2.2435 | 0 | 0.49268 |  | 4.4824
280 |  |  |  | WAIP | Waipa Networks Limited | N/A | All Locations | [5 empty] | 0.0043943 |  |  | 0.0043943 | 0 |  | 0 |  | 0 | 0.0033673 | 1.2916 |  | 1.2949
281 |  |  |  | WATA | Network Waitaki Limited | BPT110S1 | Blackpoint | 0.013789 |  | 0.091997 |  | 0.26517 |  | 0.15892 |  | 0.52987 | 0.016976 |  | 0.10047 |  | 0.40778 | 0 | 0.15892 |  | 0.68414
282 |  |  |  | WATA | Network Waitaki Limited | OAM033S1 | Oamaru | 0.56241 |  | 0.58509 |  | 2.5939 |  | 0.051408 |  | 3.7928 | 0.68905 |  | 0.6484 |  | 3.0932 | 0 | 0.051408 |  | 4.482
283 |  |  |  | WATA | Network Waitaki Limited | TWZ033S1 | Twizel | 0.19696 |  | 0.032617 |  | 0.15201 |  |  |  | 0.38159 | 0.2916 |  | 0.03457 |  | 0.17745 | 0 |  |  | 0.50362
284 |  |  |  | WATA | Network Waitaki Limited | WTK011S2 | Waitaki | 0.18734 |  | 0.080401 |  | 0.42819 |  | 0.05093 |  | 0.74685 | 0.20837 |  | 0.085683 |  | 0.55565 | 0 | 0.05093 |  | 0.90063
285 |  |  |  | WATA | Network Waitaki Limited | N/A | All Locations | [5 empty] | 0.0034536 |  |  | 0.0034536 | 0 |  | 0 |  | 0 | 0.0027832 |  |  | 0.0027832
286 |  |  |  | WAV1 | Waverley Windfarm Limited | WVY011S1 | Waverley | 0.037874 |  | 0.40168 | [5 empty] | 0.43955 | 0.044374 |  | 0.51345 |  | 0.010214 | 0 |  |  | 0.56804
287 |  |  |  | WAV1 | Waverley Windfarm Limited | N/A | All Locations | [5 empty] | 0.0001146 |  |  | 0.0001146 | 0 |  | 0 |  | 0 | 8.528e-05 |  |  | 8.528e-05
288 |  |  |  | WELE | WEL Networks Limited | HAM011S1 | Hamilton | 0.95447 |  | 2.5097 |  | 8.6656 |  | 0.11124 |  | 12.241 | 1.1728 |  | 2.9445 |  | 10.0338 | 0 | 0.11124 |  | 14.2624
289 |  |  |  | WELE | WEL Networks Limited | HLY033SA | Huntly | 0.17746 |  | 0.75219 |  | 1.4464 |  | 0.70662 |  | 3.0827 | 0.20072 |  | 0.83093 |  | 1.6789 | 0 | 0.70662 |  | 3.4171
290 |  |  |  | WELE | WEL Networks Limited | TMI033S1 | Te Kowhai | 0.32577 |  | 0.14696 |  | 6.0491 |  | 1.421 |  | 7.9428 | 0.34698 |  | 0.21202 |  | 7.0357 | 0 | 1.421 |  | 9.0157
291 |  |  |  | WELE | WEL Networks Limited | N/A | All Locations | [5 empty] | 0.015732 |  |  | 0.015732 | 0 |  | 0 |  | 0.00010203 | 0.012069 |  |  | 0.012171
292 |  |  |  | WNST | Winstone Pulp International | TNG011S1 | Tangiwai | 1.1431 |  | 0.43024 |  | 1.3736 | 8.978e-05 |  |  | 2.947 | 2.0218 |  | 0.72268 |  | 2.1813 | 0 |  |  | 4.9257
293 |  |  |  | WNST | Winstone Pulp International | N/A | All Locations | [5 empty] | 0.0013097 |  |  | 0.0013097 | 0 |  | 0 |  | 0 | 0.0014692 |  |  | 0.0014692
294 |  |  |  | WPOW | Westpower Limited | NA | Atarau |  |  | 0.0089956 |  | 0.031577 |  |  |  | 0.040572 | 0 |  | 0.013332 |  | 0.05085 | 0 |  |  | 0.064182
295 |  |  |  | WPOW | Westpower Limited | DOB033S1 | Dobson | 0.26686 |  | 0.021168 |  | 0.50324 |  |  |  | 0.79126 | 0.3304 |  | 0.027241 |  | 0.57957 | 0 |  |  | 0.93721
296 |  |  |  | WPOW | Westpower Limited | GYM066S1 | Greymouth | 0.005098 |  | 0.10847 |  | 0.65657 |  |  |  | 0.77014 | 0.0063323 |  | 0.1352 |  | 0.74931 | 0 |  |  | 0.89085
297 |  |  |  | WPOW | Westpower Limited | HKK066S1 | Hokitika | 0.11431 |  | 0.078555 |  | 1.3023 |  |  |  | 1.4952 | 0.14664 |  | 0.095066 |  | 1.4882 | 0 |  |  | 1.7299
298 |  |  |  | WPOW | Westpower Limited | KUM066S1 | Kumara | 0.0025489 |  | 0.0096932 |  | 0.092454 |  |  |  | 0.1047 | 0.0031662 |  | 0.016527 |  | 0.1065 | 0 |  |  | 0.1262
299 |  |  |  | WPOW | Westpower Limited | OTI011S1 | Otira | 0.12332 |  | 0.0040841 |  | 0.0165 |  |  |  | 0.1439 | 0.15263 |  | 0.0047967 |  | 0.018826 | 0 |  |  | 0.17625
300 |  |  |  | WPOW | Westpower Limited | RFN110SA | Reefton | 0.0042712 |  | 0.075985 |  | 0.24209 |  |  |  | 0.32234 | 0.0045312 |  | 0.10195 |  | 0.26809 | 0 |  |  | 0.37457
301 |  |  |  | WPOW | Westpower Limited | N/A | All Locations | [5 empty] | 0.0025603 | 0.0043783 |  | 0.0069386 | 0 |  | 0 |  | 0 | 0.0019584 | 0.0043783 |  | 0.0063367
302 |  |  |  | WTOM | The Lines Company Ltd | HTI033S1 | Hangatiki | 0.3366 |  | 0.71971 |  | 2.6778 |  |  |  | 3.7342 | 0.41544 |  | 0.86447 |  | 3.025 | 0 |  |  | 4.3049
303 |  |  |  | WTOM | The Lines Company Ltd | NPK033S1 | National Park | 0.34224 |  | 0.082116 |  | 0.22839 |  |  |  | 0.65274 | 0.42762 |  | 0.10033 |  | 0.25887 | 0 |  |  | 0.78683
304 |  |  |  | WTOM | The Lines Company Ltd | OKN011S2 | Ohakune | 0.20042 |  | 0.090704 |  | 0.24608 |  |  |  | 0.53721 | 0.24698 |  | 0.1106 |  | 0.28278 | 0 |  |  | 0.64037
305 |  |  |  | WTOM | The Lines Company Ltd | ONG033S1 | Ongarue | 0.2421 |  | 0.064801 |  | 0.60805 |  |  |  | 0.91494 | 0.29783 |  | 0.081475 |  | 0.68643 | 0 |  |  | 1.0657
306 |  |  |  | WTOM | The Lines Company Ltd | TNG011S1 | Tangiwai |  |  |  |  | 0.00042144 |  |  |  | 0.00042144 | 0 |  | 0 |  | 0.00028903 | 0 |  |  | 0.00028903
307 |  |  |  | WTOM | The Lines Company Ltd | TKU033S1 | Tokaanu | 0.10739 |  | 0.094239 |  | 0.45298 |  |  |  | 0.65461 | 0.15436 |  | 0.11256 |  | 0.53318 | 0 |  |  | 0.80009
308 |  |  |  | WTOM | The Lines Company Ltd | N/A | All Locations | [5 empty] | 0.0040769 |  |  | 0.0040769 | 0 |  | 0 |  | 0 | 0.0030715 |  |  | 0.0030715
309 |  |  |  | NEW | Loadstone Energy | NA | Bay of Plenty | [8 empty] | 0 | [6 empty] | 0.98475 |  | 0.98475
310 |  |  |  | Total |  |  |  | 125.5793 | 0 | 266.7212 | 0 | 451.6341 | -0.00062518 | 37.1975 | 0 | 881.1315 | 152.5777 | 0 | 302.3373 | 0 | 521.8282 | 5.2042e-18 | 40.8231 | 0 | 1017.5663
311
312 | F6(iv): Other Regulated Income (excl Asset Disposals)
313 |  |  | Note: this section states the revenue received in the disclosure year (ended on 30 June 2025)
314 |  |  |  |  | Total Income | Distributors | Direct Connects | Generators | Other
315 |  |  |  | Type of Income | ($M) | ($M) | ($M) | ($M) | ($M)
316 |  |  |  | Insurance Proceeds | 18300000 |  |  |  | 18300000
|  |  |  | Scrap Metal proceeds (138 items avg $93k each | 1300000 |  |  |  | 1300000
|  |  |  | Meridian Transformer Lease | 300000 |  |  | 300000
|  |  |  | Micellaneous items (incl 5 fleet disposal) | 500000 |  |  |  | 500000
320 |  |  |  | Car park lease | 75000 |  |  |  | 75000
321 |  |  |  | TOTAL | 20475000 | 0 | 0 | 300000 | 20175000
322 |  |  |  | *Insert additional rows and update calculation of totals as needed
323
324 | F6(v): Asset Disposals
325 |  |  | There are too many assets to list individually. Minor assets disposals are therefore reported on one line
326 |  |  |  |  | Total Income/(Loss) | Disposal Value
327 |  |  |  | Asset | ($M) | ($M)
|  |  |  | Minor Asset Disposals | -2.285 | 3.4194
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
|  |  |  | TOTAL | -2.285 | 3.4194
360
361
362 | F6(vi): Asset Divestments
363 |  |  | Amounts stated are in the year to 30 June 2025
364 |  |  |  | Party Asset Divested to | Description of Assets Divested | Disposal Value
365 | [5 empty] | ($M)
366 |  |  |  | None | Kawerau Control Room | -0.19043
367
368
369 |  |  |  | TOTAL |  | -190430.26
370 |  |  |  | *Insert additional rows and update calculation of totals as needed
371

## TP1. ROI and profit
[5 empty] | Transpower | Disclosure Date | 2025-10-24
Return on Investment (ROI) and Profit calculations | [5 empty] | Disclosure Year (year ended) | 2025-06-30
under paragraphs 8.6 to 8.13 of the Transpower Information Disclosure Determination 2014
Reconciliation from the regulatory WACC to our ROI (clause 8.10.2)
67th percentile vanilla WACC (IPP version) | 4.57%
Effect of permanent voluntary revenue reductions | -0.2423%
Contribution from incentives | -0.9672%
Transpower's actual ROI | 3.36% |  |  | 106040286.5192
Adjust for exclusion of interest on EV account from ROI calculation | 0.08838%
Adjust for exclusion of IDC adjustment from ROI calculation | 0%
Adjust for exclusion of PT/recoverable wash-up from ROI calculation | 0%
Double-count TCSD in tax allowance | 0.01219%
Adjust to include IRIS as cashflow in regulatory profit calculation | -0.02638%
Apply incorrect cashflow timing factor adjustment to revenue | 0.1209%
Adjust to ID RAB rather than IPP RAB | 0%
Vanilla ROI calculated under clause 8.6 | 3.556%
Transpower's ROI (clauses 8.6 and 8.7) |  |  | =
ROI (vanilla) | 3.556% | Vanilla ROI calculated as required by Clause 8.6
Cost of debt (ID) | 6.23%
ROI (post-tax) | 2.823% | Post-tax ROI calculated as required by Clause 8.7
A comparison of our ROI to the WACC used to calculate our revenue (clause 8.8.4)
ROI (vanilla) | 3.556% | per clause 8.6
67th percentile vanilla WACC (IPP version) | 4.57% | this is the WACC used for the purposes of calculating revenue for the disclosure year
Difference | -1.014%
Comparison required by Clause 8.8.3
ROI (vanilla) | 3.556% | per clause 8.6
75th percentile vanilla WACC (ID version) | 7.67%
Difference | -4.114%
Comparison required by Clause 8.9.3
ROI (post-tax) | 2.823% | per clause 8.7
75th percentile post-tax WACC (ID version) | 6.94%
Difference | -4.117%
Clause 8.10.1 and clause 8.10.3
This difference has the same components as those described under Clause 8.10.2 above, but with the added difference that the ID vanilla WACC rate is different from the IPP vanilla WACC rate and
the 67th and 75th percentile WACCs are different.
67th percentile vanilla WACC (IPP version) | 4.57%
75th percentile vanilla WACC (ID version) | 7.67%
Difference | -3.1%
as above | -1.014%
as above (8.8.3) | -4.114%
Comparison required by Clause 8.8.2
ROI (vanilla) | 3.556% | per clause 8.6
Mid-point vanilla WACC (ID version) | 6.99%
Difference | -3.434% | this difference (also see below) is the same as those calculated above but updated for the difference between the mid-point and 75th percentile WACCs
Comparison required by Clause 8.9.2
ROI (post-tax) | 2.823% | per clause 8.7
Mid-point post-tax WACC (ID version) | 6.26%
Difference | -3.437% | see above
Regulatory profit/loss before tax
Revenue | 854912647.6396
Operating expenditure (incl. operating lease costs capitalised under GAAP) | -386193053.8603
Pass-through costs | -22991947.99
Recoverable costs | -4804218.5459
Depreciation (tax depreciation and write-offs) | -332717138.053
IDC Cap adjustment (included in RAB depreciation) | 0 | based on Clause 2.81.2 - the IDC adjustment between the depreciation and commissioned asset impairment
TCSD | -2166002.6713 | double counted in Notional Interest until the rules are corrected
Regulatory profit/loss before tax | 106040286.5192 | Disclosure required by Clause 8.11
Notional interest (IM clause 2.3.1(3)(a)) | -64101806.0426
41938480.4766
Tax | 11742774.5334
Regulatory profit/loss before tax including EV account movement | 120940494.772 | Disclosure required by Clause 8.12
Regulatory profit/loss after tax including EV account movement | 105025661.9278 | Disclosure required by Clause 8.13

## TP2. Major project costs
|  |  |  | Transpower |  | Disclosure Date |  | 2025-10-24
SCHEDULE TP2: PARTIALLY COMPLETED MAJOR PROJECTS: COSTS | [5 empty] | Disclosure Year (year ended) |  | 2025-06-30
ref
5 | Updated cost forecasts for partially completed major projects
6
7 |  |  | Major capex allowance | Current forecast expected cost | Original forecast expected costs | Variance in the expected cost | Variance in the expected cost | Material (1)
8 |  |  | ($M) | ($M) | ($M) | ($M) | (%) | (Y or N)
9 |  | Stage 1 - Waikato and Upper North Island Voltage Management | 143 | 102.5175 | 143 | -40.4825 | -28.31% | Y
10 |  | Net Zero Grid Pathways Stage 1 | 392.9 | 344.3932 | 392.9 | -48.5068 | -12.35% | Y
11 |  | Western Bay of Plenty | 86.1 | 86.1 | 86.1 | 0 | 0% | N
12
13 |  |  | 622 | 533.0107 | 622 | -88.9893
14
15 |  | (1) 'Material' has been specified in our Information Disclosure Determination as being greater than 10% or $10m.
16
18 |  | Stage 1 - Waikato and Upper North Island Voltage Management
19 |  | The reduction in cost is driven by three primary factors: a Special Protection Scheme that will no longer be constructed, a land purchase at Hangawera for a new site to host series capacitors that is not required, and thirdly a reduction in forecast due to cost savings realised through the construction phases of the Hamilton and Otahuhu STATCOMs.
Net Zero Grid Pathways Stage 1
21 |  | This project is still in its initial setup phase, and pricing for major works has not yet been received. The lower forecast is related to the risk allowance being excluded until more certainty regarding tender prices have been obtained and the project has progressed in delivery.
22
23

## TP3. Major project timing
|  |  | Transpower | Disclosure Date | 2025-10-24
SCHEDULE TP3: PARTIALLY COMPLETED MAJOR PROJECTS: TIMING |  |  |  | Disclosure Year (year ended) | 2025-06-30
ref
5 | Updated timing forecasts for partially completed major projects
6
7 |  |  | Forecast commissioning at approval | Current forecast commissioning | Material (1)
8 |  |  | (date or date range) | (date or date range) | (Y or N)
9 |  | Stage 1 - Waikato and Upper North Island Voltage Management | Dec 2022 (except for Stage 2 preparatory works) | 2023 to October 2025 (except for stage 2 preparatory works) | Y
|  | Net Zero Grid Pathways Stage 1 | Various with final commissioning June 2028 | Various with final commissioning June 2029 | Y
|  | Western Bay of Plenty | Various with final commissioning in Dec 2032 | Various with final commissioning in Dec 2032 | N
13
14 |  | (1) 'Material' has been specified in our Information Disclosure Determination as being greater than 3 months
15
16
17 |  | Stage 1 - Waikato and Upper North Island Voltage Management (WUNIVM):
18 |  | The WUNIVM investment challenge was complex when considering both prospective generation changes from the Huntly Power Station, and demand growth in the region. Given these uncertainties, the potential for a significant reduction in generation at short notice, and the lead times for investment, Transpower initially decided to proceed with the first phase of the WUNIVM stage 1 proposal in November 2020: one grid stability device at Hamilton with a target commissioning date of winter 2023. This plan reduced risk by addressing voltage stability needs should regional thermal generation reduce, and demand increase as forecast. Transpower needed 30 months to install the equipment. By undertaking construction of the first of two phases of stage one of the project, we could adequately manage risk to electricity supply by winter 2023 and the following one to two years. Prior to committing to the device at Hamilton, we investigated possible non-transmission alternatives to the transmission investment. Given the technical performance requirements of the voltage stability need at Hamilton we were unable to secure a lower-cost option. We then undertook an RFP process for the installation of a non-transmission investment that could potentially defer or replace the need for transmission investment of the second STATCOM at Otahuhu. This evaluation concluded that neither Battery Energy Storage Systems options were economic when compared with the second STATCOM. As a result, installation of the Otahuhu STATCOM was confirmed as the preferred option to provide additional voltage support for the WUNI region. This output is unchanged from that which was approved originally by the Commerce Commission and this stage has now been commissioned with final milestone payments due to Hitachi Energy in FY26.
19 |  | Net Zero Grid Pathways Stage 1
20 |  | Commissoning dates of a number for works have been extended due to long lead times from suppliers for Statcoms, as well as the requirement of lines work to be extended over an additional summer to accommodate outages and lines service provider resource.
21
22

## TP4. Project close-out reports
[5 empty] | Transpower | Disclosure Date | 2025-10-24
SCHEDULE TP4: FULLY-COMMISSIONED PROJECT CLOSE-OUT REPORTS | [5 empty] | Disclosure Year (year ended) | 2025-06-30
ref
5 | Report in relation to Upper North Island Dynamic Reactive Support
6
7 | Project description
8 | UNIDRS (Upper North Island Demand Side Response) was approved by the Electricity Commission in July 2010 for $110.2 million with a forecast completion date in 2015.
9 | The outputs approved were:
10
11 | • Auckland Statcom at Penrose $31.0m
12 | • Northland Statcom at Marsden $32.3m
13 | • Reactive power controller $32.8m
14 | • System operator software $1.3m
15 | • Load monitoring equipment $0.8m
16 | • Demand side management $12.0m
17
18 | The last output was to undertake a range of demand side initiatives in the Upper North Island region. An outputs amendment was approved in November 2013 to expand the geographical area of Transpower’s demand response programme to the whole of New Zealand. No additional cost increases were sought.
19
20 | In the 2018 disclosures we noted that the final component of the program (Auckland Reactive Power Controller) had been deferred in order to carry out an assessment into an alternative solution, which has been agreed with the Commerce Commission, providing a cost saving. That component was delivered in September 2018. Since then, during our investigation in voltage management for the Waikato and Upper North Island (WUNI) region, we discovered the risk that transient over-voltage can occur following a severe fault that trips voltage-sensitive load due to low voltages. We commissioned the Automatic Over-Voltage Capacitor Scheme (AOVCS) as a low cost method of helping to mitigate this risk and commissioned the scheme in June 2025.
21
22 |  |  | Forecast final end cost | Expected cost at approval | Variance | Material?
23 | Commissioned values |  | $'m | $'m | $'m
24 | Project costs |  | 50.8 | 103.4 | -52.6 | Yes
25
26
27 | Project outputs and related commissioning dates | Variance to approved outputs | Actual date | Forecast commission date at approval | Timing variance? | Material?
28 | Auckland Statcom at Penrose | No | 2013-07-01 | 2011-2015 | No | No
29 | Northland Statcom at Marsden | No | 2013-12-01 | 2011-2015 | No | No
30 | Reactive power controller | Yes | 2018-09-01 | 2011-2015 | Yes | Yes
31 | Automatic Over-Voltage Capacitor Scheme (AOVCS) - subsequent enhancement to Reactive power controller | Yes | 2024-11-01 | N/A | No | No
32 | System operator software | Yes | No longer required | 2011-2015 | Yes | Yes
33 | Load monitoring equipment | No | 2012-07-01 | 2011-2015 | No | No
34 | Demand side management | No | 2011-2015 | 2011-2015 | Yes | Yes
35
36 | Lessons learnt
37 | Engagement and communications:
38 | Engagement and clear communication with key stakeholders, e.g. manufacturer and service providers to ensure all aspects of design, implementation and site specific requirements known and understood.
39 | Environmental issues:
40 | Early identification and communication of environemntal issues on sites such as soil contaminaton to enable mitigation of risks.
41
42 |  |  | Estimated value | Assumptions
43 | Cost efficiencies |  | $'m
44 | Scope changes |  | -34.2 | Reactive Power Controller ($32.8M) and System Operator Software ($1.3M) not required
45 | Project uncertainties/risk not realised |  | -6.36 | Uncertainties of timing, cost and scope that did not arise
46
47 | Major capex over-spend adjustment |  | $'m
48 | Allowance at approval (Electricity Commission) |  | 110.2
49 | Adjustment in respect of CPI |  | -
50 | Adjustment in respect of FX |  | -
51 | Allowance adjusted for the disparity between forecast and actual CPI and FX rates |  | 110.2
52 | Allowance at approval (P90) |  | 110.2
53 | Adjustment for undelivered grid outputs (P90) |  | -
54 | Allowance adjusted for outputs which were not required and were therefore not delivered |  | 110.2
55 | Forecast final end cost |  | 50.8
56 | (Excess amount) |  | -59.36
57 | Over-spend adjustment |  | -
58
59 | Commissioning date variance explanations
60 | The final component of the program (Auckland Reactive Power Controller) had been deferred in order to carry out an assessment into an alternative solution, which has been agreed with the Commerce Commission, providing a cost saving. That component was delivered in September 2018. Since then, during our investigation in voltage management for the Waikato and Upper North Island (WUNI) region, we discovered the risk that transient over-voltage can occur following a severe fault that trips voltage-sensitive load due to low voltages.
61
62 | Commissioned value variance explanation
63 | The project was delivered well under the allowance delivering significant benefits for consumers through refining the scope and identifying and achieving efficiencies. The final project cost is $50.8M, materially below the maximum approved amount of $110.2m (P90) allowed by the Commission. This outcome is due primarily to:
64 | - delivering a centralised SCADA based solution instead of a site based Reactive power controller (RPC) at much lower cost
65 | - actual costs across the project were at the lower bounds of our estimates
66 | Project output variance explanation
67 | The RPC was delivered through a centralised SCADA based solution rather than a distributed model.
68 | With the RPC delivered as a centralised solution, there was no longer a need for a separate project to enhance the System Operator software tools. Any requirements in this space were integrated into the RPC solution.
69
70 | Report in relation to the Bombay Otahuhu Regional Major Capex Project
71
72 | Project description
73 | In 2021, Transpower applied to the Commission to investment in the first phase of upgrading the transmission network supplying the Bombay-Otahuhu region (region). The approved major capex outputs for the Project are: 1. procuring, installing and commissioning two 150/175 MVA 220/110kV transformers at Transpower’s Bombay substation; 2. procuring, installing and commissioning a connection for these transformers to the 220kV Huntly-Otahuhu A line; and 3. undertaking preparatory works, including additional investigation, consultation and design work, for reconductoring the OtahuhuWiri line Later in 2021, Trasnpower sought to amend the outputs to include: 5. removing the existing conductor, and procuring, installing and commissioning Goat ACSR conductor on the Otahuhu-Wiri section of the Bombay-Otahuhu A 110 kV transmission line; and 6. works on the foundations and towers required for the spans on which the Goat ACSR conductor is installed
74
75 |  |  | Forecast final end cost | Expected (P50) cost at approval | Variance | Material?
76 | Commissioned values |  | $'m | $'m | $'m
77 | Project costs |  | 31.4561 | 50.538 | -19.0819 | Yes
78
79
80 | Project outputs and related commissioning dates | Variance to approved outputs | Actual date | Forecast commission date at approval | Timing variance? (see footnote) | Material? (see footnote)
81 | 1) Procuring, installing and commissioning two 150/175 MVA 220/110kV transformers at Transpower’s Bombay substation | No | 2022/23 | 2023-04-01 | Yes | Yes
82 | 2) Procuring, installing and commissioning a connection for these transformers to the 220kV Huntly-Otahuhu A line | No | 2022/23 | 2023-04-01 | Yes | Yes
83 | 3) Undertaking preparatory works, including additional investigation, consultation and design work, for reconductoring the Otahuhu Wiri line. Amendment to outputs approved September 2021: | No | 2022/23 | 2023-04-01 | Yes | Yes
84 | 4) Removing the existing conductor, and procuring, installing and commissioning Goat ACSR conductor on the Otahuhu-Wiri section of the Bombay-Otahuhu A 110 kV transmission line; (amendment 2) | No | 2022/23 | 2023-04-01 | Yes | Yes
85 | 5) Works on the foundations and towers required for the spans on which the Goat ACSR conductor is installed. (amendment 2) | No | 2022/23 | 2023-04-01 | Yes | Yes
86
87 | Lessons learnt
88 |  |  | Estimated value | Assumptions
89 | Cost efficiencies |  | $'m
90 | Scope changes |  | 0
91 | Delivery efficiencies |  | 0
92 | Productivity efficiencies |  | 0
93 | Project uncertainties/risk not realised |  | -19.0819
94
95 | Major capex over-spend adjustment |  | $'m
96 | Allowance at approval (P50) |  | 45.93
97 | Adjustment in respect of CPI |  | 2
98 | Adjustment in respect of IDC |  | 2.608
99 | Allowance adjusted for the disparity between forecast and actual CPI and FX rates |  | 50.538
100 | Allowance at approval |  | 50.538
101 | Adjustment for undelivered grid outputs |  | -
102 | Allowance adjusted for outputs which were not required and were therefore not delivered |  | 50.538
103 | Forecast final end cost |  | 31.4561
104 | (Excess amount) |  | -19.0819
105 | Over-spend adjustment |  | -
106
107 | Commissioning date variance explanations
108 | We met the forecast commissioning date on time and before the project expiry date
109 | Commissioned value variance explanation
110 | There are a number of reasons this program is forecasting lower costs. They are primarily: - the transformer procurement for Bombay occurred after a supplier had another order cancelled and was able to offer a better price. - an alteration to the timing of Counties Power’s new zone substation at Bombay avoided a work planning clash and allowed for simpler implementation at the site. - through smart design we were able to significantly reduce the required enabling works, for example the use of new technology (smaller/lighter Catenary Support System Blocks) reduced the amount of temporary strengthening works and infrastructure protection required and no requirement for hurdles over motorways.
111 | The expected commissioning date of the project was April 2023 and the project expiry date approved by the commission is 31 December 2028 to allow for potential delays in procurement and consenting.
112 | The project close out date (when all costs have been accounted for) is usually later than the date of the equipment going into service.
113
114 | Project output variance explanation
115 | There were no variances to the approved outputs of this project
116 | Expected (P50) cost at approval includes the initial approval of $35.9M and amendment of $14.6M.

## TP5. Related party transactions
|  |  | Transpower | Disclosure Date | 2025-10-24
SCHEDULE TP5: RELATED PARTY TRANSACTIONS |  |  |  | Disclosure Year (year ended) | 2025-06-30
ref
5
6 | Transactions with key management personnel
7 | The Group did not conduct any business with key management personnel aside from the compensation payments below.
8
9 | Key management personnel compensation
10 | Key management personnel received the following compensation for their services to the Group.
11
12 |  | $m
13 | Directors' fees | 0.5
14 | Other key management personnel | 6.21
15 | Defined contribution schemes | 0.24
16
17 | There were no termination payments to key management personnel in 2025.
18 | There was no long-term compensation paid to key management personnel in 2025.
19
20 | Transactions with other parts of Transpower | $m
21 | Risk Reinsurance Limited - claims received | 9.9
22 | Risk Reinsurance Limited - intercompany facility fee received | 0.5
23 | Risk Reinsurance Limited - premiums paid | -30.8
24 | Risk Reinsurance Limited - insurance expenses paid | -1
25
26 | Transpower procures insurance services from a captive insurance company, Risk Reinsurance Limited.
27 | Note that transactions with Risk Reinsurance Limited (RRL) are valued consistent with IFRS17, following RRL’s adoption of the standard from disclosure year 2024.
28
29 | Some directors of the company may be directors or officers of other companies or organisations with
30 | which Transpower may transact.
31
32 | All transactions are carried out at on an "arm's length" basis.
33

## TP6. Investment contracts
Investment Contracts (new contracts in the disclosure year) |  | Transpower |  | Disclosure Date |  |  | 2025-10-24
under paragraph 10 of the Transpower Information Disclosure Determination 2014 |  |  |  | Disclosure Year (year ended) |  |  | 2025-06-30
[5 empty] | Required from 2026 |  | Required from 2026
Customer Name | Contract Title | Brief Description | Contract Signed Date | New Investment Contract - Total Capacity (kV) | Anticipatory Connection Asset - ACA Capacity | New Investment Contract Costs (Budget / estimated build costs) | New Investment Contract Costs allocated to ACA
Powerco Limited | Waverley ODID TWA | Replacing outdoor switchgear with connection to Powerco's indoor 11kV switchroom. | 2024-07-11 | 11kV | 11kV | 1622134.66
Vector Limited | Wairau Road Development TWA | Procurement, installation and commissioning of a new 120MVA 220/33kV transformer. | 2024-07-12 | 220kV | 220kV | 17579495
Centralines Limited | Waipawa 33kV ODID Conversion TWA | Replacing outdoor switchgear with connection to Centralines' indoor 33kV switchroom. Design and construction of the associated dual differential protection system and installation of new local service transformers. | 2024-07-31 | 33kV | 33kV | 3919577
The Power Company Limited | Open Country Dairy Invercargill GXP Upgrade TWA (The Power Company) | Invercargill GXP upgrade, including 1x 220/66kV transformer and 66kV bay. | 2024-08-07 | 220kV | 220kV | 17243000
Unison Networks Limited | Additional 33kV Feeders at Whakatu GXP TWA | 2x 33kV feeders at Whakatu for Unison. | 2024-08-21 | 33kV | 33kV | 1060000
Aurora Energy Limited | CML-FKN TTU TWA | Thermal uprating of the CML-FKN-A line (Aurora covers 90% of costs, based on AMD). | 2024-09-17 | 110kV | 110kV | 8854200
Lakeland Network Limited | CML-FKN TTU TWA (Lakeland Network Limited) | Thermal uprating of the CML-FKN-A line (Lakeland covers 10% of costs, based on AMD). | 2024-09-18 | 110kV | 110kV | 983800
Wellington Electricity Lines Limited | KHD-TKR Uprating TWA | Pole replacement on KHD-TKR line. | 2024-09-19 | 33kV | 33kV | 1925310
Powerco Limited | Greytown ODID TWA | Replacing outdoor switchgear with connection to Powerco's indoor 33kV switchroom. | 2024-10-21 | 33kV | 33kV | 2096621.03
Powerco Limited | MTN ODID TWA | Replacing outdoor switchgear with connection to Powerco's indoor 33kV switchroom. Design and construction of the associated TOPS, and replacement of 1x local service transformer. | 2024-10-22 | 33kV | 33kV | 3988120.79
Wellington Electricity Lines Limited | KHD-TKR Uprating Pole 20x TWA | New intermediate Poles A0020A and A0020B to enable a connection to WE*'s Grenada zone sub. | 2024-11-07 | 33kV | 33kV | 1500000
Powerco Limited | Te Matai T1 Transformer Replacement TWA | Procurement, installation and commissioning of a new 80MVA 110/33kV transformer. | 2025-03-17 | 110kV | 110kV | 637400
The Power Company Limited | Edendale 220kV GXP TWA | Design, construction of a new 220kV GXP near Edendale (now named Puna Awa) | 2025-05-23 | 220kV | 220kV | 50379061
Contact Energy Limited | Glenbrook BESS TWA | Contact Energy will construct a 100 MVA Battery Energy Storage System (BESS), near Glenbrook Substation (GLN). Transpower will install a new 2,500 amp 33 kV feeder panel and associated protection on Bus R, Building B, GLN to facilitate the connection. | 2024-08-07 | 33kV | 33kV | 1683189
Far North Solar Farm Ltd | Ohau C Solar Farm (The Point) TWA | Design, install and commission of a substation platform and all associated 220kV assets required to facilitate the connection of the customer solar farm. | 2024-08-27 | 220kV | 220kV | 21552000
Drury South Limited | Drury Line Relocation TWA | Relocation of the HLY-OTA-A transmission line between towers A0143 and A0146. Installation of new towers HLY-OTA-A A0144A and HLY-OTA-A A0145A and associated hardware and conductor. Removal of existing towers HLY-OTA-A A0144 and HLY-OTA-A A0145 and associated hardware and conductors. Modifications to towers HLY-OTA-A A143 and HLY-OTA-A A146 | 2024-12-12 | 220kV | 220kV | 3221694
New Zealand Steel Limited | Glenbrook Arc Furnace TWA | Installation of 1 off 2,500 amp 33 kV feeder panels. New Feeder protections. | 2025-02-28 | 33kV | 33kV | 1270640
Masterton Solar and Energy Storage Limited (NZCE) | Masterton Solar and BESS Project TWA | Design, procure, installation and commissioning of two switchgear panels Design, procure, installation and commissioning of revenue and protection panels Modification of existing arcflash protection system Construction of building egress | 2025-03-26 | 33kV | 33kV | 2800000
Meridian Energy Limited | Ruakaka Stage 2 TOPS TWA | The Customer’s project is currently underway to develop a Solar Farm at Ruakākā. Installation of a TOPS at the Bream Bay site | 2025-05-28 | 33kV | 33kV | 696600
Far North Solar Farm Ltd | Greytown Solar Farm TWA | Design, install and commission connections from the FNSF solar farm switchyard to the UHTMST 1&2 circuits. Also, construct the tie spans between the UHT-MST 1&2 line bays to FNSF’s switchyard on behalf of FNSF, with ownership divested to FNSF on Commissioning Date. | 2025-06-12 | 110kV | 110kV | 9847831
NOTE: PPA's are not included in investment contracts as these agreements are for materials and not the provision of electricity transmission services |  |  |  | 0 | 0 | 152860673.48 | 0

## G1. System Statistics
|  |  | Transpower |  | Disclosure Date | 2025-10-24
SCHEDULE G1: TRANSMISSION SYSTEM STATISTICS |  |  |  |  | Disclosure Year (year ended) | 2025-06-30
ref
5 | G1(i): Circuit Information | Transmission System Statistics
6
7 |  | System length by operating voltage (kV) | CY-1 (km) | CY (km)
8 |  | Total | 16525.2061 | 16525.93
9 |  | 350kV (HVDC) | 1263 | 1262.97
10 |  | 0 kV (HVDC earth electrode) | 12 | 12.05
11 |  | 220kV (HVAC) | 9114.0887 | 9114.65
12 |  | 110kV (HVAC) | 5490.3094 | 5490.35
13 |  | 66/50kV (HVAC) (Includes leased assets) | 645.808 | 645.91
14
15 |  | Circuit length of overhead electric lines by operating voltage (kV)
16 |  | Total | 16315 | 16316.09
17 |  | 350kV (HVDC) | 1142 | 1142.34
18 |  | 0 kV (HVDC earth electrode) | 12 | 12.05
19 |  | 220kV (HVAC) | 9049 | 9049.56
20 |  | 110kV (HVAC) | 5469 | 5469.04
21 |  | 66/50kV (HVAC) (includes leased assets) | 643 | 643.1
23 |  | Route length of overhead electric lines by operating voltage (kV)
24 |  | Total | 10905 | 10906.17
25 |  | 350kV (HVDC) | 571 | 571.17
26 |  | 0 kV (HVDC earth electrode) | 12 | 12.05
27 |  | 220kV (HVAC) | 5918 | 5919.25
28 |  | 110kV (HVAC) | 4075 | 4075.07
29 |  | 66/50kV (HVAC) (includes leased assets) | 329 | 328.63
31 |  | Circuit length of HVAC underground transmission cable by operating voltage (kV)
32 |  | Total | 89.2061 | 89.21
33 |  | 350kV (HVDC) | 0 | 0
34 |  | 220kV (HVAC) | 65.0887 | 65.09
35 |  | 110kV (HVAC) | 21.3094 | 21.31
36 |  | 66kV (HVAC) | 2.808 | 2.81
38 |  | Total length of HVDC submarine cable by operating voltage (kV)
39 |  | Total | 121 | 120.63
40 |  | 350kV (HVDC) | 121 | 120.63
41
42 |  |  | CY-1 (Quantity) | CY (Quantity)
43 |  | HVAC Substation/Switching Station | 172 | 173
44 |  | HVDC Convertor stations | 2 | 2
45 |  | HVDC Electrode stations | 2 | 2
46 |  | HVDC Cable transition stations | 2 | 2
47 |  | HVAC Cable transition stations | 15 | 15
48 |  | Interconnecting Transformer Banks ( 66 kV and above) | 56 | 56
49 |  | Supply Transformer Banks ( 66 kV and above) | 246 | 246
50 |  | Dynamic Reactive power Static (SVCs and STATCOMs) | 11 | 11
51 |  | Dynamic Reactive power Synchronous Condensers | 8 | 8
52 |  | Capacitor Banks (HVAC System) | 61 | 61
53 |  | AC filter Banks (HVDC) | 14 | 14
54 |  | Series and Shunt reactors | 134 | 134
55 |  | Outdoor Circuit Breakers ( 66 kV and above) | 1192 | 1198
56 |  | Outdoor Circuit Breakers (33,22,11kV) | 158 | 158
57 |  | Indoor Circuit Breakers ( 66 kV and above) | 73 | 73
58 |  | Indoor Circuit Breakers (33,22,11kV) | 1087 | 1083
59

## G2. Grid Demand and Injection
[6 empty] | Transpower |  | Disclosure Date | 2025-10-24
SCHEDULE G2: GRID DEMAND AND INJECTION | [7 empty] | Disclosure Year (year ended) | 2025-06-30
ref
5 | G2(i): Demand and Injection
6 |  |  |  | CY-4 | CY-3 | CY-2 | CY-1 | CY
7 |  | Energy Volume (GWh) |  | (GWh) | (GWh) | (GWh) | (GWh) | (GWh)
8 |  |  | Generators (Injection) | 37924.3719 | 37621.2635 | 37945.8546 | 38372.6401 | 37143.1
9 |  |  | GXP-EDBs (offtake) | 31000.7696 | 30875.8585 | 31115.5327 | 32002.8752 | 31521.74
10 |  |  | GXP-direct connects (Offtake) | 6974.5022 | 6698.3162 | 6541.4076 | 6342.2661 | 5563.82
11 |  |  | HVDC flows north | 2043.0672 | 3206.1183 | 3445.7202 | 2324.3044 | 2017.41
12 |  |  | HVDC flows south | 315.1949 | 171.2783 | 208.4649 | 380.4834 | 745.26
13 |  |  | HVDC Losses | 73.298 | 122.2175 | 136.8536 | 90.3007 | 95.94
14 |  |  | AC System Losses | 1217.6865 | 1314.0607 | 1361.8535 | 1240.9011 | 1311.68
15
|  |  |  | CY-4 | CY-3 | CY-2 | CY-1 | CY
17 |  | Maximum peak demand (MW) |  | (MW) | (MW) | (MW) | (MW) | (MW)
18 |  |  | Generators (Injection) | 6594.9657 | 6741.6326 | 6674.0215 | 6864.13 | 6632.69
19 |  |  | GXP-EDBs (offtake) | 5781.5361 | 5924.438 | 5764.7683 | 5965.03 | 5834.4
20 |  |  | GXP-direct connects (Offtake) | 889.5149 | 833.344 | 821.0555 | 788.65 | 742.99
21 |  |  | HVDC flows north | 829.0841 | 1025.16 | 1108.9106 | 932.38 | 999.78
22 |  |  | HVDC flows south | 478.0921 | 542.0445 | 687.3949 | 578.5 | 765.93
23 |  |  | HVDC Losses | 37.6409 | 57.4255 | 66.096 | 46.84 | 55.16
24 |  |  | AC System Losses | 241.4058 | 286.0115 | 281.1247 | 264.12 | 268
25
26

## G3. GXP Capacity and Demand
[11 empty] | Transpower |  | Disclosure Date |  | 2025-10-24
SCHEDULE G3: GRID EXIT POINT (GXP) CONNECTION CAPACITY AND DEMAND (ACTUAL AND FORECAST) | [12 empty] | Disclosure Year (year ended) |  | 2025-06-30
Disclosure of line items required and not required from disclosure year 2026 onward are specified in column U.
ref
5 | G3(i): Current Connection Capacity vs Actual and Forecast Demand
6
7 |  |  | Firm Capacity | Actual Demand (MW) | Forecast Net Demand (MW)
8 |  | GXP Name / Region Name | CY | CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5 | CY+6 | CY+7 | CY+8 | CY+9 | CY+10 | Comments on Capacity
9 |  | Bream Bay | Yes | 36 | 25 | 25 | 31 | 31 | 75 | 77 | 77 | 78 | 79 | 80 | No issues. Northpower has advised a 38 MW step load in 2030 due to Channel Infrastructure’s plan for an ‘Energy Precinct’ at Marsden Point.
10 |  | Kaikohe | Yes | 71.96 | 78 | 80 | 81 | 83 | 84 | 85 | 87 | 88 | 89 | 90 | No issues. Kaikohe load is a gross demand value. It excludes generation from Ngawha.
11 |  | Maungatapere | N/A | 110.81 | 126 | 127 | 128 | 129 | 130 | 131 | 131 | 132 | 132 | 132 | Northpower owns the supply transformers at Maungatapere.
12 |  | Maungaturoto | Yes | 22.2 | 24 | 25 | 25 | 26 | 26 | 27 | 27 | 28 | 28 | 29 | No issues.
13 |  | Wellsford | No | 39.63 | 45 | 47 | 48 | 49 | 51 | 53 | 55 | 58 | 59 | 61 | Peak load at Wellsford already exceeds the n-1 capacity of the supply transformers.
14 |  | Albany 33 kV | Yes | 141.63 | 171 | 175 | 186 | 192 | 200 | 209 | 215 | 222 | 228 | 234 | Peak load at Albany is forecast to exceed the n-1 capacity of the supply transformers from winter 2033. There are significant new load increases forecast from data centres across the Auckland grid exit points of Henderson, Silverdale, Albany 33 kV, Hobson Street and Takanini.
15 |  | Bombay 33 kV | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | . | Counties Energy has constructed a new zone substation supplied from Bombay 110 kV bus and has relinquished Bombay 33 kV Grid Exit Point.
16 |  | Bombay 110 kV | Yes | 99.07 | 119 | 124 | 130 | 135 | 140 | 146 | 150 | 155 | 160 | 165 | No issues.
17 |  | Glenbrook 33 kV (clean bus) | No | 81.02 | 74 | 70 | 71 | 73 | 74 | 75 | 76 | 77 | 79 | 80 | No issues. The Glenbrook clean bus is supplied by a single 220/33 kV, 140 MVA transformer. This is the Glenbrook 33 kV load on the clean bus with no contribution from the generation connected directly onto the 33 kV bus at Glenbrook.
18 |  | Glenbrook - NZ Steel (dirty bus) | Yes | 122.52 | 112 | 129 | 86 | 85.9727 | 85.9727 | 85.9727 | 85.9727 | 85.9727 | 85.9727 | 85.9727 | No issues. The large load reduction from 2027 is due to the announced commissioning of the electric furnace and subsequent decommissioning of some existing plants.
19 |  | Henderson | Yes | 129.15 | 138 | 150 | 171 | 195 | 209 | 223 | 236 | 249 | 264 | 275 | Peak load at Henderson is forecast to exceed the n-1 capacity of the supply transformers from winter 2025 and the n capacity from winter 2033. There are significant new load increases forecast from data centres across the Auckland grid exit points of Henderson, Silverdale, Albany 33 kV, Hobson Street and Takanini.
20 |  | Hepburn Rd | Yes | 137.05 | 171 | 175 | 177 | 179 | 185 | 189 | 192 | 196 | 199 | 202 | No issues.
21 |  | Hobson Street | Yes | 124.93 | 111 | 120 | 131 | 143 | 156 | 165 | 169 | 174 | 180 | 190 | The load split between Hobson Street and Liverpool Street–Penrose is an estimate only. The Vector and Transpower networks between these grid exit points are operated in parallel. There are significant new load increases forecast from data centres across the Auckland grid exit points of Henderson, Silverdale, Albany 33 kV, Hobson Street and Takanini.
22 |  | Mangere 33 kV | Yes | 110.52 | 136 | 141 | 146 | 151 | 156 | 161 | 166 | 169 | 172 | 176 | Peak load at Mangere 33 kV is forecast to exceed the n-1 capacity of the supply transformers from winter 2026. Capacity is limited by equipment other than the supply transformer(s)
23 |  | Mangere 110 kV | N/A | 18.38 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | Vector owns the 110 kV feeders at Mangere.
24 |  | Mt Roskill 22 kV | Yes | 112.04 | 123 | 127 | 128 | 131 | 135 | 140 | 144 | 148 | 152 | 155 | Peak load at Mount Roskill is forecast to exceed the n-1 capacity of the supply transformers from winter 2038.
25 |  | Mt Roskill 110 kV - Kingsland feeder | N/A | 61.95 | 124 | 127 | 129 | 132 | 137 | 141 | 145 | 150 | 154 | 158 | Vector owns the 110 kV feeders at Mount Roskill. This includes the Kingsland feeders only.
26 |  | Otahuhu | Yes | 60.72 | 72 | 75 | 76 | 78 | 80 | 82 | 84 | 85 | 87 | 89 | Peak load at Otahuhu is forecast to exceed the n-1 capacity of the supply transformers from winter 2035. Capacity is limited by equipment other than the supply transformer(s)
27 |  | Pakuranga | Yes | 139.28 | 167 | 169 | 171 | 181 | 185 | 189 | 192 | 195 | 198 | 201 | No issues.
28 |  | Penrose 22 kV | Yes | 34.65 | 48 | 50 | 51 | 52 | 54 | 56 | 57 | 58 | 60 | 61 | Peak load at Penrose 22 kV exceeds the n-1 capacity of the supply transformers from 2028. Capacity is limited by equipment other than the supply transformer(s) The Penrose 22 kV load is split between three 33/22 kV transformers that are in not directly connected on the 22 kV side. Only the aggregate 22 kV load is forecast, not separate load forecasts for the three 33/22 kV transformers.
29 |  | Penrose 25 kV | Yes | 18.66 | 15 | 15 | 15 | 15 | 15 | 15 | 17 | 19 | 20 | 22 | No issues. A single 220/25 kV traction transformer at Penrose supplies the Auckland passenger rail system. This transformer, along with the single traction transformer at Southdown, provides switched n 1 security. The average transformer loading is low, with high levels of peak load occurring for only a few minutes at a time. Therefore, we do not assess the capacity of traction transformers in the TPR.
30 |  | Penrose 33 kV | Yes | 261.83 | 297 | 318 | 327 | 335 | 347 | 359 | 368 | 378 | 388 | 396 | Peak load at Penrose 33 kV is forecast to exceed the n-1 capacity of the supply transformers from winter 2031.
31 |  | Penrose 110 kV - Liverpool Street | Yes | 147.9 | 111 | 120 | 131 | 143 | 156 | 165 | 169 | 174 | 180 | 190 | The load split between Hobson Street and Liverpool Street–Penrose is an estimate only. The Vector and Transpower networks between these grid exit points are operated in parallel.
32 |  | Silverdale | Yes | 100.6 | 111 | 118 | 123 | 136 | 144 | 152 | 160 | 167 | 174 | 183 | Peak load at Silverdale is forecast to exceed the n-1 capacity of the transformers from winter 2029. There are significant new load increases forecast from data centres across the Auckland grid exit points of Henderson, Silverdale, Albany 33 kV, Hobson Street and Takanini.
33 |  | Southdown 25 kV | Yes | 22.5 | 15 | 15 | 15 | 15 | 15 | 15 | 17 | 18 | 20 | 22 | No issues. A single 220/25 kV traction transformer at Southdown supplies the Auckland passenger rail system. This transformer, along with the single traction transformer at Penrose, provides switched n 1 security. The average transformer loading is low, with high levels of peak load occurring for only a few minutes at a time. Therefore, we do not assess the capacity of traction transformers in the TPR.
34 |  | Takanini | Yes | 127.35 | 158 | 182 | 223 | 265 | 268 | 272 | 274 | 277 | 279 | 281 | Peak load at Takanini is forecast to exceed the n-1 capacity of the supply transformers from winter 2027. There are significant new load increases forecast from data centres across the Auckland grid exit points of Henderson, Silverdale, Albany 33 kV, Hobson Street and Takanini.
35 |  | Wairau Road | Yes | 103.75 | 156 | 161 | 164 | 169 | 179 | 184 | 188 | 192 | 196 | 200 | Peak load at Wairau Road is forecast to exceed the n-1 capacity of the transformers from winter 2026. Capacity is limited by equipment other than the supply transformer(s)
36 |  | Wiri | Yes | 89.76 | 115 | 119 | 122 | 126 | 130 | 132 | 133 | 135 | 137 | 140 | Peak load at Wiri is forecast to exceed the n-1 capacity of the supply transformers from winter 2025.
37 |  | Arapuni North | N/A | 24.3958 | 21 | 22 | 22 | 22 | 22 | 23 | 23 | 23 | 23 | 23 | Powerco owns the 110 kV feeders at Arapuni North.
38 |  | Cambridge | Yes | 47.13 | 44 | 66 | 66 | 68 | 70 | 71 | 60 | 62 | 44 | 46 | Peak load at Cambridge is forecast to exceed the n-1 capacity of the supply transformers from 2027. Capacity is limited by equipment other than the supply transformer(s). High growth at Cambridge from new industrial load and residential development. Some of the Cambridge load will be transferred to the new Hautapu grid exit point over the forecast period.
39 |  | Hamilton 11 kV | Yes | 30.22 | 37 | 38 | 39 | 34 | 35 | 36 | 37 | 37 | 38 | 38 | No issues. Load shifting of 5 MW from Hamilton 11 kV to Hamilton 33 kV in 2029.
40 |  | Hamilton 33 kV | No | 142.05 | 175 | 180 | 184 | 185 | 189 | 148 | 152 | 156 | 160 | 165 | Peak load at Hamilton 33 kV already exceeds the n-1 capacity of the 220/33 kV transformers and is expected to exceed the n capacity from 2026 until forecast load transfer to Te Kowhai in 2031. Load shifting of 5 MW from Hamilton 11 kV to Hamilton 33 kV in 2029. Load shifting of 9 MW and 42 MW from Hamilton 33 kV to Te Kowhai in 2029 and 2031, respectively.
41 |  | Hamilton NZR | Yes | 6.9 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | No issues. Two 220/55 kV traction transformers at Hamilton supply the KiwiRail North Island Main Trunk railway line. The two transformers are operated normally split, each providing n security to a portion of the railway line. The average transformer loading is low, with high levels of peak load occurring for only a few minutes at a time. Therefore, we do not assess the capacity of traction transformers in the TPR.
42 |  | Hangatiki 33 kV | No | 27 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | Peak load at Hangatiki 33 kV grid exit point already exceeds the n-1 capacity of the supply transformers.
43 |  | Hangatiki 110 kV | N/A | 15.8 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | The 110 kV grid exit point is on n security and its capacity is not reported in the TPR as the supply transformer is owned by The Lines Company.
44 |  | Hinuera | Yes | 34.65 | 33 | 33 | 34 | 34 | 35 | 35 | 35 | 36 | 36 | 36 | Peak load at Hinuera is forecast to exceed the n-1 capacity of the supply transformers from 2033
45 |  | Huntly | Yes | 32.92 | 48 | 49 | 50 | 52 | 53 | 79 | 80 | 82 | 83 | 85 | Peak load at Huntly is forecast to exceed the summer n-1 capacity of the supply transformers from 2033. Capacity is limited by equipment other than the supply transformer(s). Load shifting of 26 MW from Te Kowhai to Huntly in 2031.
46 |  | Hautapu | Yes | 11.36 | 11 | 24 | 25 | 25 | 25 | 26 | 41 | 41 | 60 | 61 | No issues. High growth at Cambridge from new industrial load and residential development. Some of the Cambridge load will be transferred to the new Hautapu grid exit point over the forecast period.
47 |  | Kinleith 11 kV | Yes | 75.55 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | No issues. Oji Fibre Solutions announced closure of paper production at Kinleith.
48 |  | Kinleith 33 kV | No | 23 | 26 | 27 | 27 | 28 | 28 | 29 | 30 | 31 | 32 | 33 | The winter peak 33 kV load at Kinleith already exceeds the continuous capacity of T5 but is within the continuous capacity of T9
49 |  | Kopu | Yes | 46.65 | 55 | 57 | 59 | 60 | 62 | 63 | 64 | 65 | 65 | 66 | Peak load at Kopu is forecast to exceed the n-1 capacity of the supply transformers from winter 2027. Capacity is limited by equipment other than the supply transformer(s).
50 |  | Lichfield | N/A | 16.42 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | The supply transformers at Lichfield are owned by Vector and are not reported in the TPR.
51 |  | Piako | N/A | 40 | 49 | 50 | 51 | 52 | 53 | 53 | 54 | 54 | 55 | 55 | Powerco owns the supply transformers at Piako. Peak load at Piako is forecast to remain within the n-1 capacity of the two Piako–Morrinsville Tee line sections. Load shifting of 3.5 MW from Piako to Waihou in 2025.
52 |  | Te Awamutu | Yes | 43.29 | 53 | 57 | 60 | 62 | 64 | 65 | 66 | 73 | 74 | 75 | Peak load at Te Awamutu is forecast to exceed the n-1 capacity of the transformers from 2026
53 |  | Te Kowhai | Yes | 111.5 | 127 | 145 | 149 | 170 | 175 | 207 | 213 | 220 | 228 | 237 | Peak load at Te Kowhai (excluding contribution from Te Uku) is forecast to exceed the n-1 capacity of the 220/33 kV transformers from 2027. Capacity is limited by equipment other than the supply transformer(s). Load shifting of 9 MW and 42 MW from Hamilton 33 kV to Te Kowhai in 2029 and 2031, respectively. Load shifting of 26 MW from Te Kowhai to Huntly in 2031.
54 |  | Waihou | Yes | 40.09 | 48 | 49 | 50 | 50 | 51 | 52 | 52 | 52 | 53 | 53 | No issues. Load shifting of 3.5 MW from Piako to Waihou in 2025.
55 |  | Waikino | Yes | 40.14 | 45 | 46 | 47 | 51 | 55 | 58 | 62 | 63 | 63 | 63 | Peak load at Waikino is forecast to exceed the n-1 capacity of the T1 transformer from 2025
56 |  | Whakamaru | Yes | 11.85 | 12 | 12 | 12 | 13 | 13 | 13 | 13 | 14 | 14 | 14 | No issues. This load is gross, no embedded generation is included.
57 |  | Edgecumbe | Yes | 59.1 | 103 | 105 | 106 | 108 | 109 | 111 | 112 | 114 | 115 | 116 | The peak load is forecast to exceed the n-1 capacity of T4 and T7 in 2026 following the planned electrification of Fonterra’s dairy plant at Edgecumbe. Horizon advised a 34 MW step load increase at Edgecumbe in 2026, caused by the electrification of the Fonterra dairy plant.
58 |  | Kaitimako | No | 41.32 | 45 | 47 | 49 | 52 | 39 | 40 | 41 | 42 | 43 | 44 | No issues. A single 110/33 kV, 75 MVA transformer supplies load at Kaitemako, resulting in n security. Powerco advised a 13 MW load shift from Kaitemako to Tauranga 33 kV in 2030. Several major commercial, industrial and residential load increases are expected in the Tauriko area, which will be supplied from Tauranga 33 kV.
59 |  | Kawerau Horizon | Yes | 20.441 | 20 | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | No issues. This load is a gross demand value. It excludes embedded generation.
60 |  | Kawerau T6 - T9 | Yes | 26.3 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | No issues. This load is a gross demand value. It excludes embedded generation.
61 |  | Matahina | Yes | 14.1088 | 7 | 7 | 7 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | No issues. This load is supplied by transformers owned by Pioneer Energy and located at Aniwhenua. This load is a gross demand value. It excludes embedded generation.
62 |  | Mt Maunganui 33 kV | Yes | 63.1 | 72 | 75 | 76 | 77 | 79 | 60 | 61 | 62 | 63 | 64 | No issues. Powerco advised the following load shifts from Mount Maunganui 33 kV to Te Matai: 18MW in 2031 and 13.5 MW in 2038.
63 |  | Owhata | Yes | 12.91 | 18 | 20 | 21 | 21 | 22 | 22 | 22 | 23 | 23 | 23 | No issues.
64 |  | Rotorua 11 kV | Yes | 29.75 | 30 | 30 | 31 | 32 | 32 | 32 | 33 | 33 | 33 | 33 | No issues.
65 |  | Rotorua 33 kV | Yes | 48.24 | 54 | 56 | 57 | 58 | 59 | 59 | 59 | 59 | 63 | 69 | Peak load at Rotorua 33 kV is forecast to exceed the n-1 capacity of the supply transformers from 2035
66 |  | Tarukenga 11 kV | No | 8.42 | 11 | 12 | 12 | 13 | 13 | 13 | 14 | 14 | 14 | 14 | No issues. A single 110/11 kV, 20 MVA supply transformer supplies the Tarukenga grid exit point resulting in n security
67 |  | Tauranga 11 kV | Yes | 23 | 26 | 27 | 28 | 29 | 31 | 32 | 33 | 33 | 33 | 34 | No issues.
68 |  | Tauranga 33 kV | Yes | 93.04 | 93 | 97 | 101 | 105 | 108 | 135 | 139 | 141 | 144 | 146 | Peak load at Tauranga 33 kV is forecast to exceed the n-1 capacity of the supply transformers from winter 2030 if Kaimai generation is low (14 MW) and from 2032 if Kaimai generation is medium (33 MW). Powerco advised a 13 MW load shift from Kaitemako to Tauranga 33 kV in 2030. Several major commercial, industrial and residential load increases are expected in the Tauriko area, which will be supplied from Tauranga 33 kV.
69 |  | Te Matai | Yes | 49.5 | 64 | 73 | 77 | 85 | 89 | 121 | 126 | 131 | 135 | 139 | The Te Matai load is forecast to exceed the n-1 capacity of T2 from winter 2025 and the n capacity of T1 from winter 2026. Powerco advised the following load shifts from Mount Maunganui 33 kV to Te Matai: 18MW in 2031 and 13.5 MW in 2038.
70 |  | Waiotahe 11 kV | Yes | 13.6 | 14 | 14 | 14 | 15 | 15 | 15 | 16 | 16 | 16 | 17 | The combined 11 kV and 50 kV peak load is forecast to exceed the n-1 rating of the 11 kV windings of the transformers from winter 2025
71 |  | Waiotahe 50 kV | No | 1.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | A single 11/50 kV, 3 MVA transformer supplies the 50 kV load, resulting in n security. The peak load at Waiotahe 50 kV shows minimal load growth over the forecast period and no capacity issues are expected.
72 |  | Bunnythorpe 33 kV | Yes | 89.99 | 100 | 87 | 90 | 92 | 93 | 95 | 96 | 97 | 98 | 99 | Peak load at Bunnythorpe is forecast to reach the n-1 capacity of the supply transformers in winter 2025 before decreasing due to permanent load transfers to Linton and Marton. Capacity is limited by equipment other than the supply transformer(s). Powerco has advised a 3 MW load shift from Bunnythorpe to Linton in 2026. Powerco has advised a 15 MW load shift from Bunnythorpe to Marton in 2027.
73 |  | Bunnythorpe - NZR | Yes | 6.57 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | No issues. Two 220/55 kV traction transformers at Bunnythorpe supply the KiwiRail North Island Main Trunk railway line. The two transformers are operated normally split, each providing n security to a portion of the railway line. The average transformer loading is low, with high levels of peak load occurring for only a few minutes at a time. Therefore, we do not assess the capacity of traction transformers in the TPR.
74 |  | Dannevirke | Yes | 13.08 | 16 | 20 | 20 | 21 | 21 | 21 | 22 | 22 | 22 | 23 | Peak load at Dannevirke is forecast to exceed the n-1 capacity of the supply transformers from winter 2036. Capacity is limited by equipment other than the supply transformer(s).
75 |  | Linton | Yes | 71.97 | 79 | 83 | 87 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | No issues. Powerco has advised a 3 MW load shift from Bunnythorpe to Linton in 2026. Powerco has advised 6 MW of industrial load increases at Linton across 2026-2028
76 |  | Mangahao | No | 51.07 | 44 | 45 | 45 | 46 | 48 | 49 | 49 | 50 | 50 | 52 | Peak load at Mangahao already exceeds the n-1 capacity of the supply transformers when Mangahao power station is not generating.
77 |  | Mangamaire | Yes | 14.5 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 18 | No issues.
78 |  | Marton | Yes | 23.36 | 20 | 38 | 39 | 41 | 43 | 45 | 46 | 48 | 50 | 50 | Peak load at Marton is forecast to exceed the n-1 capacity of the supply transformers from winter 2027. The n capacity of the smaller transformer (T2) is forecast to be exceeded at peak time from winter 2032. Powerco has advised a 15 MW load shift from Bunnythorpe to Marton in 2027. Powerco has advised 7 MW of industrial load increases at Marton across 2030-2034.
79 |  | Mataroa | No | 6.5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 9 | 9 | No capacity issues. The load at Mataroa is supplied by a single 110/33 kV, 26 MVA supply transformer comprising three single-phase units, resulting in n security.
80 |  | National Park | No | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | No capacity issues. The load at National Park is supplied through a single Ohakune–National Park–Ongarue 110 kV circuit and a single 110/33 kV, 15 MVA supply transformer, resulting in n security.
81 |  | Ohakune | No | 8.32 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | No capacity issues. The load at Ohakune is supplied by a single 110/11 kV, 20 MVA supply transformer, resulting in n security.
82 |  | Ongarue | No | 8.64 | 9 | 9 | 10 | 10 | 12 | 12 | 12 | 12 | 13 | 13 | No capacity issues. The load at Ongarue is supplied by a single 110/33 kV, 20 MVA supply transformer comprising three single-phase units, resulting in n security.
83 |  | Tangiwai 11 kV | N/A | 34.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Following Winstone Pulp International’s decision to indefinitely close its Tangiwai Sawmill and Karioi Pulpmill in 2024, no load is supplied by the Tangiwai 220/11 kV transformers
84 |  | Tangiwai NZR | Yes | 8.12 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | No issues. Two 220/55 kV traction transformers at Tangiwai supply the KiwiRail North Island Main Trunk railway line. The two transformers are operated normally split, each providing n security to a portion of the railway line. The average transformer loading is low, with high levels of peak load occurring for only a few minutes at a time. Therefore, we do not assess the capacity of traction transformers in the TPR.
85 |  | Tokaanu | No | 8.3 | 9 | 9 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | No capacity issues. The load at Tokaanu is supplied by a single 220/33 kV, 20 MVA supply transformer, with a second transformer that can be manually switched into service when required.
86 |  | Waipawa | Yes | 22.35 | 31 | 32 | 31 | 33 | 33 | 34 | 34 | 35 | 35 | 35 | Peak load at Waipawa 33 kV (combined 33 kV and 11 kV load) is forecast to exceed the n-1 capacity of the supply transformers from winter 2025. Capacity is limited by equipment other than the supply transformer(s). The 11 kV load is supplied from the 33 kV via a single 33/11 kV transformer. Centralines has advised 10 MW of load increase from heavy industry and residential development at Waipawa across 2025-2028.
87 |  | Wairakei | Yes | 55.89 | 51 | 49 | 49 | 47 | 46 | 45 | 44 | 43 | 42 | 43 | No issues, assuming the new transformers are comissioned by the end of 2025. Wairakei load is a gross demand value. It excludes embedded generation. Unison has advised a 37 MW load shift in total across 2025-2034 from Wairakei to Tauhara (Hawke’s Bay region).
88 |  | Woodville | Yes | 2.6 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | No issues.
89 |  | Brunswick | No | 35.42 | 35 | 36 | 37 | 38 | 38 | 38 | 39 | 39 | 39 | 39 | No capacity issues. The Brunswick load is supplied by a single 220/33 kV, 50 MVA transformer, resulting in n security.
90 |  | Carrington Street | Yes | 62.4 | 73 | 75 | 76 | 77 | 78 | 80 | 80 | 81 | 84 | 85 | No issues.
91 |  | Huirangi | Yes | 29 | 32 | 33 | 34 | 35 | 36 | 37 | 37 | 37 | 38 | 38 | No issues.
92 |  | Hawera | Yes | 31.3 | 30 | 31 | 31 | 32 | 32 | 32 | 32 | 33 | 35 | 35 | No issues.
93 |  | Hawera 110 kV (Whareroa) | Yes | 28.55 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | Fonterra has feeders connected directly to the Hawera 110 kV bus; their capacity is not reported in the TPR. This is a gross load. Embedded generation has been excluded.
94 |  | Hawera (Kupe) | No | 14.2 | 10 | 8 | 8 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | No issues. A single 110/33 kV, 30 MVA supply transformer (T3) supplies the Beach Energy Kupe load, resulting in n security. Load reduction from industrial sectors from 2026,
95 |  | Kapuni | N/A | 8.71 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | Kapuni load and generation is connected to the grid through a single 110 kV circuit (owned by Nova Energy) which is Tee-connected to the 110 kV Opunake–Stratford–2 circuit, resulting in n security. The capacity of the assets owned by Nova Energy is not reported in the TPR.
96 |  | Motunui | Yes | 11.8 | 19 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | No issues.
97 |  | Opunake | Yes | 11.2 | 13 | 13 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 15 | No issues.
98 |  | Stratford 33 kV | Yes | 33.7 | 31 | 31 | 32 | 32 | 33 | 33 | 34 | 34 | 40 | 40 | No issues. Step increase of 4.67 MW in 2034 from industrial sector as part of RETA.
99 |  | Taumarunui | Yes | 7.7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | No issues. Two 220/55 kV traction transformers at Taumarunui supply the KiwiRail North Island Main Trunk railway line. The two transformers are normally operated split, each providing n security to a portion of the railway line. The average transformer loading is low, with high levels of peak load occurring for only a few minutes at a time. Therefore, we do not assess the capacity of traction transformers in the TPR.
100 |  | Waverley | No | 4.7 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | No capacity issues. A single 110/11 kV, 10 MVA transformer supplies load at Waverley resulting in n security.
101 |  | Whanganui | No | 33.3 | 35 | 37 | 38 | 42 | 43 | 44 | 44 | 44 | 44 | 44 | Peak load at Whanganui already exceeds the n-1 capacity of the supply transformers. Capacity is limited by equipment other than the supply transformer(s).
102 |  | Fernhill | No | 77.62 | 79 | 81 | 84 | 86 | 88 | 89 | 90 | 91 | 92 | 92 | Peak load at Fernhill has exceeded the n-1 capacity of the smaller transformer (T2) since 2023. Capacity is limited by equipment other than the supply transformer(s).
103 |  | Redclyffe | Yes | 76.9 | 106 | 111 | 116 | 120 | 123 | 127 | 129 | 132 | 135 | 137 | Peak load at Redclyffe is forecast to exceed the n-1 capacity of the supply transformers from 2035. Capacity is limited by equipment other than the supply transformer(s). Unison advised a 16 MW load shift from Whakatu to Redclyffe in 2025.
104 |  | Tuai | N/A | 61.3 | 77 | 79 | 80 | 82 | 84 | 86 | 87 | 89 | 90 | 91 | Eastland Networks owns the 110 kV feeders at Tuai
105 |  | Tauhara | No | 8.8 | 26 | 32 | 36 | 38 | 41 | 43 | 46 | 46 | 47 | 49 | No capacity issues. Tauhara is a new GXP commissioned in 2024. A single 220/33 kV, 70 MVA transformer supplies the Unison load at Tauhara, resulting in n security. Tauhara load is a gross demand value. It excludes embedded generation.
106 |  | Whakatu | Yes | 87.87 | 106 | 108 | 109 | 110 | 111 | 111 | 111 | 112 | 112 | 112 | No issues. Unison advised a 16 MW load shift from Whakatu to Redclyffe in 2025.
107 |  | Whirinaki | Yes | 53.8 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | No issues.
108 |  | Central Park 11 kV | Yes | 20.325 | 24 | 24 | 24 | 25 | 26 | 26 | 27 | 27 | 27 | 27 | No issues.
109 |  | Central Park 33 kV | Yes | 135.93 | 149 | 158 | 160 | 161 | 163 | 164 | 165 | 166 | 167 | 168 | No issues. Central Park 33 kV has multiple step loads from expected public transport electrification upgrades and several new buildings planned.
110 |  | Gracefield | Yes | 60.6 | 73 | 70 | 71 | 72 | 76 | 77 | 78 | 79 | 81 | 81 | Peak load at Gracefield is forecast to exceed the n 1 capacity of the supply transformers from winter 2030 . Gracefield has multiple step loads due to public transport electrification and industrial development. In 2027, there is a 9 MW load shift from Gracefield to Melling.
111 |  | Greytown | Yes | 16.13 | 18 | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 19 | No issues.
112 |  | Haywards 11 kV | Yes | 20.8 | 22 | 22 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 24 | No issues with 11 kV load. The combined peak load at Haywards 33 kV and 11 kV is forecast to exceed the n-1 capacity of the supply transformers from winter 2028. Haywards, Melling – public transport electrification, industrial developments and residential developments in Manor Park, Naenae, Waterloo and Wainuiomata.
113 |  | Haywards 33 kV | Yes | 19.4688 | 32 | 33 | 37 | 37 | 38 | 38 | 38 | 38 | 38 | 38 | Peak load at Haywards 33 kV is forecast to exceed the n-1 capacity of the supply transformers from winter 2026. The combined peak load at Haywards 33 kV and 11 kV is forecast to exceed the n-1 capacity of the supply transformers from winter 2028. Capacity is limited by equipment other than the supply transformer(s). Haywards, Melling – public transport electrification, industrial developments and residential developments in Manor Park, Naenae, Waterloo and Wainuiomata.
114 |  | Kaiwharawhara | Yes | 28 | 34 | 34 | 57 | 57 | 58 | 58 | 59 | 59 | 59 | 60 | Kaiwharawhara peak load is forecast to exceed the n 1 capacity of the supply transformers from winter 2028. Capacity is limited by equipment other than the supply transformer(s). Kaiwharawhara growth from expected industrial development, public transport electrification and port upgrades.
115 |  | Masterton | Yes | 53.2 | 59 | 61 | 63 | 64 | 65 | 66 | 66 | 67 | 68 | 68 | No issues.
116 |  | Melling 11 kV | Yes | 25.04 | 32 | 32 | 33 | 33 | 33 | 33 | 33 | 34 | 34 | 34 | The 11 kV peak load is forecast to exceed the n-1 capacity of the supply transformers from winter 2029
117 |  | Melling 33 kV | Yes | 34.36 | 38 | 51 | 51 | 52 | 52 | 53 | 53 | 53 | 53 | 54 | No issues. In 2027, there is a 9 MW load shift from Gracefield to Melling. Haywards, Melling – public transport electrification, industrial developments and residential developments in Manor Park, Naenae, Waterloo and Wainuiomata.
118 |  | Paraparaumu | Yes | 63.6 | 73 | 74 | 76 | 77 | 78 | 80 | 81 | 82 | 83 | 84 | No issues.
119 |  | Pauatahanui | Yes | 20.4 | 25 | 26 | 34 | 34 | 34 | 35 | 35 | 36 | 36 | 36 | Peak load at Pāuatahanui is forecast to exceed the n-1 capacity of the supply transformers from winter 2026. Takapu Road and Pāuatahanui growth from public transport electrification and significant industrial and residential developments.
120 |  | Takapu Rd | Yes | 94.47 | 113 | 119 | 120 | 122 | 124 | 126 | 127 | 128 | 130 | 131 | Peak load at Takapu Road is forecast to exceed the n-1 capacity of the supply transformers from winter 2027. Takapu Road and Pāuatahanui growth from public transport electrification and significant industrial and residential developments.
121 |  | Upper Hutt | Yes | 31.48 | 32 | 33 | 34 | 34 | 34 | 35 | 35 | 35 | 35 | 35 | No issues.
122 |  | Wilton | Yes | 46.09 | 53 | 53 | 54 | 54 | 55 | 55 | 56 | 56 | 56 | 57 | No issues.
123 |  | Blenheim | Yes | 72.9 | 81 | 87 | 89 | 91 | 93 | 95 | 96 | 96 | 97 | 98 | No issues. Marlborough Lines advised of about 10 MW of industrial load increase between 2025 and 2029.
124 |  | Kikiwa | No | 2.95 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | No issues. The Kikiwa load is normally supplied from the 11 kV tertiary winding of the Kikiwa–T1 interconnecting transformer resulting in n security. There is a backup supply from the T2 interconnecting transformer. Transferring the load between T1 and T2 requires a short interruption to the load.
125 |  | Stoke 33 kV | Yes | 137.2 | 145 | 148 | 150 | 152 | 155 | 157 | 160 | 162 | 167 | 168 | Peak load at Stoke 33 kV is forecast to exceed the n-1 capacity of the supply transformers from winter 2025. Capacity is limited by equipment other than the supply transformer(s). Stoke 33 kV load includes supply to the Network Tasman and Nelson Electricity networks.
126 |  | Stoke 66 kV | Yes | 26.9 | 29 | 29 | 30 | 34 | 35 | 35 | 36 | 36 | 36 | 37 | No issues. Stoke 66 kV load is a gross value. It includes demand that will be supplied from embedded generation at Cobb (distribution network connected).
127 |  | Arthur's Pass | No | 0.6684 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | No capacity issues. A single 66/11 kV, 3 MVA transformer supplies load at Arthur’s Pass, resulting in n security.
128 |  | Atarau | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Atarau grid exit point was decommissioned on June 2023. The substation was dismantled in 2025.
129 |  | Castle Hill | No | 0.7 | 0.7 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | No capacity issues. A single 66/11 kV, 3.8 MVA transformer supplies load at Castle Hill, resulting in n security.
130 |  | Dobson | Yes | 8.6 | 10 | 14 | 15 | 15 | 15 | 15 | 15 | 15 | 16 | 16 | No issues.
131 |  | Greymouth | N/A | 14.46 | 16 | 16 | 17 | 17 | 17 | 18 | 18 | 18 | 19 | 19 | Westpower owns the supply transformers at Greymouth.
132 |  | Hokitika | N/A | 19.02 | 22 | 23 | 24 | 24 | 25 | 25 | 26 | 26 | 27 | 27 | Westpower owns the supply transformers at Hokitika. Peak load at Hokitika is forecast to exceed the n-1 transmission capacity from 2028. This is the gross load assuming no embedded generation contribution at Hokitika.
133 |  | Kumara | N/A | 3.25 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | Kumara load is supplied via a single 66/11 kV supply transformer, resulting in n security. The supply transformer is owned by Westpower and is not reported in the TPR.
134 |  | Murchison | No | 2.67 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | No capacity issues. Murchison is supplied by a single 110/11 kV, 10 MVA transformer resulting in n security.
135 |  | Otira | No | 0.8 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | No capacity issues. Otira is supplied by a single 66/11 kV, 2.5 MVA transformer, resulting in n security.
136 |  | Reefton | N/A | 6 | 15 | 15 | 15 | 15 | 15 | 16 | 16 | 16 | 16 | 16 | The supply transformers at Reefton are owned by Westpower and are not reported in the TPR. Westpower advised 8 MW load increase from heavy industry at Reefton in 2026.
137 |  | Robertson Street | N/A | 10.4 | 12 | 13 | 13 | 14 | 14 | 14 | 14 | 14 | 15 | 15 | The supply transformers at Robertson Street are owned by Buller Electricity and are not reported in the TPR. Robertson Street (owned by Westpower) is connected to the grid at Orowaiti.
138 |  | Ashburton 66 kV | Yes | 183.02 | 213 | 216 | 219 | 222 | 225 | 229 | 232 | 235 | 243 | 246 | Peak load at Ashburton is forecast to exceed the n-1 capacity of the supply transformers from summer 2035.
139 |  | Ashley - MainPower 11 kV | Yes | 13.55 | 13 | 13 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | No issues. Took the peak historical load when both Mainpower and Daiken load supply transformers and in service rather than during a maintenance of either transformer resulting in the load being delivered through a single transformer. Planned load shifts as advised by MainPower from Ashley 11 kV (MainPower): 3 MW to Ashley 66 kV in 2028. Planned load shifts as advised by MainPower from Kaiapoi 11 kV: 2 MW to Ashley 11 kV (MainPower) in 2025 and 4 MW to Ashley 66 kV in 2028. Planned load shifts as advised by MainPower from Southbrook 66 kV: 1 MW to Ashley 11 kV (MainPower) in 2025; 7 MW, 3 MW and 3 MW to Ashley 66 kV in 2027, 2030 and 2032, respectively.
140 |  | Ashley - MainPower 66 kV | N/A | 0 | 0 | 0.2 | 16 | 18 | 22 | 23 | 27 | 28 | 30 | 31 | Mainpower will have feeders directly connected to the Ashley 66 kV bus from 2027. The combined 11 kV and 66 kV peak load at Ashley is forecast to exceed the n-1 capacity of the Ashley–Waipara and Ashley–Southbrook transmission circuits from winter 2032. Planned load shifts as advised by MainPower from Ashley 11 kV (MainPower): 3 MW to Ashley 66 kV in 2028. Planned load shifts as advised by MainPower from Kaiapoi 11 kV: 2 MW to Ashley 11 kV (MainPower) in 2025 and 4 MW to Ashley 66 kV in 2028. Planned load shifts as advised by MainPower from Southbrook 66 kV: 1 MW to Ashley 11 kV (MainPower) in 2025; 7 MW, 3 MW and 3 MW to Ashley 66 kV in 2027, 2030 and 2032, respectively.
141 |  | Ashley - Daiken | Yes | 11.94 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | No issues. Took the peak historical load when both Mainpower and Daiken load supply transformers and in service rather than during a maintenance of either transformer resulting in the load being delivered through a single transformer.
142 |  | Bromley 66 kV | Yes | 166.4 | 169 | 173 | 235 | 240 | 248 | 207 | 210 | 276 | 280 | 282 | Peak load at Bromley is forecast to exceed the n-1 capacity of the supply transformers from winter 2028. Planned load shifts as advised by Orion from Bromley 66 kV: 50 MW to Islington 66 kV in 2031. Planned load shifts as advised by Orion from Islington 66 kV: 48 MW and 36 MW to Bromley 66 kV in 2028 and 2033 respectively; 23 MW to Norwood in 2030.
143 |  | Coleridge | No | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | No capacity issues. A single 66/11 kV, 2.5 MVA transformer supplies the load at Coleridge, resulting in n security.
144 |  | Culverden 33 kV | Yes | 19.07 | 22 | 23 | 23 | 24 | 24 | 25 | 25 | 25 | 26 | 26 | The combined 33 kV and 66 kV peak load at Culverden is forecast to exceed the n-1 capacity of the supply transformers from summer 2029
145 |  | Culverden 66 kV | No | 9.8 | 7 | 8 | 8 | 9 | 9 | 10 | 10 | 10 | 11 | 11 | No capacity issues. A single 33/66 kV, 20 MVA transformer supplies the 66 kV load, resulting in n security.
146 |  | Hororata 33 kV | Yes | 21.94 | 21 | 22 | 23 | 23 | 24 | 25 | 26 | 19 | 22 | 22 | Peak load on the Hororata 33 kV bus is forecast to exceed the n-1 capacity of the supply transformers from summer 2026. Capacity is limited by equipment other than the supply transformer(s). Planned load shifts as advised by Orion from Hororata 33 kV: 7 MW to Norwood in 2033.
147 |  | Hororata 66 kV | N/A | 15.85 | 18 | 18 | 19 | 20 | 21 | 22 | 23 | 1 | 1 | 2 | Orion owns the 66 kV feeders at Hororata. Planned load shifts as advised by Orion from Hororata 66 kV: 20 MW to Norwood in 2033.
148 |  | Islington 33 kV | Yes | 80.6 | 76 | 79 | 82 | 84 | 92 | 94 | 97 | 99 | 106 | 108 | Peak load at Islington 33 kV is forecast to exceed the n-1 capacity of the supply transformers from winter 2034. Capacity is limited by equipment other than the supply transformer(s).
149 |  | Islington 66 kV | N/A | 434.42 | 489 | 505 | 470 | 488 | 484 | 550 | 565 | 541 | 554 | 562 | Orion owns the 66 KV feeders at Islington. Planned load shifts as advised by Orion from Bromley 66 kV: 50 MW to Islington 66 kV in 2031. Planned load shifts as advised by Orion from Islington 66 kV: 48 MW and 36 MW to Bromley 66 kV in 2028 and 2033 respectively; 23 MW to Norwood in 2030.
150 |  | Kaiapoi | Yes | 29.95 | 33 | 34 | 32 | 33 | 34 | 35 | 36 | 38 | 39 | 40 | Peak load at Kaiapoi is forecast to exceed the n-1 capacity of the supply transformers from winter 2033. Capacity is limited by equipment other than the supply transformer(s). Planned load shifts as advised by MainPower from Kaiapoi 11 kV: 2 MW to Ashley 11 kV (MainPower) in 2025 and 4 MW to Ashley 66 kV in 2028.
151 |  | Kimberley | N/A | 15.6 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 23 | 24 | 24 | Orion owns the supply transformers at Kimberley.
152 |  | Norwood | Yes | 37.87 | 43 | 44 | 47 | 49 | 73 | 76 | 78 | 108 | 108 | 109 | No issues. Planned load shifts as advised by Orion from Hororata 33 kV: 7 MW to Norwood in 2033. Planned load shifts as advised by Orion from Hororata 66 kV: 20 MW to Norwood in 2033. Planned load shifts as advised by Orion from Islington 66 kV: 48 MW and 36 MW to Bromley 66 kV in 2028 and 2033 respectively; 23 MW to Norwood in 2030.
153 |  | Southbrook 66 kV | N/A | 54.16 | 63 | 58 | 60 | 62 | 61 | 62 | 61 | 62 | 68 | 69 | Mainpower owns the 66 kV feeders at Southbrook. Planned load shifts as advised by MainPower from Southbrook 66 kV: 1 MW to Ashley 11 kV (MainPower) in 2025; 7 MW, 3 MW and 3 MW to Ashley 66 kV in 2027, 2030 and 2032, respectively.
154 |  | Waipara 33 kV | No | 8 | 9 | 9 | 10 | 10 | 10 | 11 | 11 | 12 | 12 | 13 | No capacity issues. A single 66/33 kV, 16 MVA transformer supplies 33 kV load at Waipara resulting in n security.
155 |  | Waipara 66 kV | N/A | 9.2 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | Mainpower owns the 66 kV feeders at Waipara
156 |  | Albury | No | 4.5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | No capacity issues. A single 110/11 kV, 20 MVA transformer supplies the load at Albury resulting in n security.
157 |  | Bells Pond | N/A | 15.1 | 18 | 19 | 20 | 21 | 22 | 22 | 23 | 24 | 24 | 25 | Alpine Energy owns the supply transformers at Bells Pond. Bells Pond is connected via a single 110 kV Tee connection to the Oamaru–Studholme–Bells Pond–Waitaki–2 circuit providing 34/34 MVA (summer/winter) capacity, resulting in n security. No transmission capacity issues.
158 |  | Black Point | N/A | 16.4 | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | No issues. Network Waitaki owns the supply transformers at Black Point. Black Point is connected via a single 110 kV Tee connection to the Oamaru–Black Point–Waitaki–1 circuit providing 44/44 MVA (summer/winter) capacity, resulting in n security.
159 |  | North Otago Grid Exit Point | N/A | 0 | 0.1 | 9 | 20 | 20 | 20 | 27 | 27 | 27 | 27 | 27 | This is a planned new GXP by Network Waitaki which is in the investigation phase. Advised by Network Waitaki: 8 MW, 5 MW, 5 MW load shift from Oamaru to North Otago GXP in 2027, 2028 and 2031, respectively. The North Otago GXP is currently uncommitted. Advised by Network Waitaki: 5 MW load shift from Waitaki to North Otago GXP in 2028.
160 |  | Oamaru | Yes | 39.2 | 50 | 61 | 42 | 44 | 45 | 41 | 42 | 43 | 43 | 43 | The peak load at Omaru is forecast to exceed the n-1 circuit capacity from 2025, and the voltage stability limit from summer 2026 until summer 2028. Capacity is limited by equipment other than the supply transformer(s). Advised by Network Waitaki: 8 MW, 5 MW, 5 MW load shift from Oamaru to North Otago GXP in 2027, 2028 and 2031, respectively. The North Otago GXP is currently uncommitted.
161 |  | Studholme | No | 14.8 | 17 | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 19 | The peak load at Studholme already exceeds the n-1 capacity of the supply transformers and is forecast to exceed n capacity from summer 2027.
162 |  | Tekapo A | No | 5.84 | 6 | 6 | 7 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | Peak load at Tekapo A is forecast to exceed the continuous rating of T1 in 2032, assuming Tekapo A is not generating during peak load periods. A single 110/11 kV, 35 MVA transformer (T6) in series with a single 33/11 kV, 10 MVA transformer (T1) supplies load at Tekapo, resulting in n security. Includes several commercial developments around Tekapo (from customer information).
163 |  | Temuka | No | 59.7 | 65 | 68 | 70 | 75 | 76 | 113 | 114 | 115 | 116 | 116 | The peak load at Temuka already exceeds the n-1 capacity of the supply transformers in summer, and is forecast to exceed the n capacity from summer 2031.
164 |  | Timaru | Yes | 69.54 | 94 | 106 | 108 | 112 | 114 | 115 | 116 | 118 | 119 | 121 | The peak load at Timaru is forecast to exceed the continuous capacity of two supply transformers in service from 2026. Capacity is limited by equipment other than the supply transformer(s).
165 |  | Twizel | Yes | 7.975 | 7 | 8 | 8 | 8 | 9 | 9 | 10 | 10 | 10 | 10 | No issues.
166 |  | Waitaki | N/A | 14.1 | 14 | 14 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | No issues. Network Waitaki is normally supplied through an 11/33 kV, 20 MVA step up transformer owned by Network Waitaki. There is also a lower capacity alternate supply through an 11/33 kV, 5.5 MVA step up transformer (T28) owned by Transpower that is too small to supply the peak load and normally has no load connected to it. Advised by Network Waitaki: 5 MW load shift from Waitaki to North Otago GXP in 2028.
167 |  | Balclutha | Yes | 32.9 | 32 | 33 | 34 | 34 | 34 | 35 | 35 | 35 | 35 | 36 | Peak load at Balclutha is forecast to exceed the n-1 capacity of the supply transformers from Shoulder 2027.
168 |  | Brydone | Yes | 11.3 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | No issues.
169 |  | Clyde | Yes | 16.21 | 21 | 21 | 23 | 23 | 24 | 25 | 26 | 26 | 27 | 28 | No issues.
170 |  | Cromwell | Yes | 49.7 | 73 | 79 | 81 | 86 | 87 | 99 | 100 | 102 | 103 | 104 | Peak load at Cromwell 33 kV is forecast to exceed the 33 kV cable rating and the n-1 capacity of the transformers’ 33 kV winding from winter 2026. Capacity is limited by equipment other than the supply transformer(s). Load increase at Cromwell from 2026 contributed mainly by heavy industry.
171 |  | Edendale 33 kV | No | 48.75 | 54 | 54 | 33 | 37 | 38 | 38 | 38 | 38 | 39 | 39 | Peak load at Edendale already exceeds the n-1 capacity of the supply transformers in summer. 20 MW of the existing Edendale 33 kV load may be transferred to the new 220 kV GXP from 2027.
|  | Edendale 220 kV | N/A | 0 | 0 | 0 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | PowerNet requested a new Edendale GXP to enable electrification and resolve n-1 supply capacity issues. The new Edendale GXP is expected to be commissioned by 2027. 20 MW of the existing Edendale load may be transferred to the new 220 kV GXP from 2027.
173 |  | Frankton | Yes | 81.27 | 94 | 99 | 104 | 108 | 117 | 123 | 128 | 133 | 138 | 141 | Peak load at Frankton is forecast to exceed the n-1 thermal capacity of the 110 kV Cromwell–Frankton circuits from winter 2025 and the n-1 capacity of the supply transformers from winter 2032.
174 |  | Gore | Yes | 46.35 | 45 | 46 | 47 | 49 | 50 | 51 | 53 | 54 | 56 | 57 | No issues.
175 |  | Halfway Bush | Yes | 118.76 | 123 | 125 | 132 | 134 | 137 | 139 | 140 | 141 | 142 | 143 | Assuming no contribution from the embedded generators, the peak load at Halfway Bush is forecast to exceed the n-1 capacity of the supply transformers from winter 2027.
176 |  | Invercargill | Yes | 105.7 | 144 | 147 | 156 | 162 | 165 | 190 | 192 | 195 | 197 | 200 | Peak load at Invercargill is forecast to exceed the n-1 capacity of the supply transformers from winter 2028
177 |  | Naseby | Yes | 32.3432 | 30 | 31 | 32 | 36 | 37 | 38 | 38 | 38 | 38 | 39 | No issues.
178 |  | North Makarewa | Yes | 51.65 | 63 | 66 | 69 | 86 | 90 | 93 | 104 | 106 | 108 | 110 | Assuming no local generation at White Hill wind farm, peak load at North Makarewa is forecast to exceed the n-1 capacity of the supply transformers from summer 2025. PowerNet advised of a 5 MW step load at North Makarewa in 2032 from commercial sector.
179 |  | South Dunedin | Yes | 72.82 | 80 | 81 | 82 | 83 | 83 | 84 | 85 | 85 | 86 | 86 | No issues.
180 |  | Tiwai | N/A | 566 | 585 | 585 | 585 | 585 | 585 | 585 | 585 | 585 | 585 | 585 | New Zealand Aluminium Smelter owns the 220 kV feeders connected directly to the Tiwai 220 kV bus and their capacity is not reported in the TPR.
181 |  | GXPs Total |  | 8529.4759 | 9596.2 | 10007.4 | 10310.2 | 10673.1727 | 10989.3727 | 11348.4727 | 11565.5727 | 11798.5727 | 12030.5727 | 12230.5727
182 |  | *Insert additional rows and update calculation of totals as needed
183
184 | G3(ii): Current Connection Capacity vs Actual and Forecast Injection
185
186 |  | Grid Injection point (generator location if embedded) |  | Forecast Injection (MVA)
187 |  |  | CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5 | CY+6 | CY+7 | CY+8 | CY+9 | CY+10 | Comments on Capacity
188 |  | Bream Bay (Marsden Diesel) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  |  |  | Not required from disclosure year 2026
189 |  | Bream Bay – Ruakākā Solar Farm | 0 | 0 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | New solar farm added
190 |  | Kaikohe – Ngawha B | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
191 |  | Kaikohe (Ngawha A) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
192 |  | Kaikohe (Kohira Solar Farm) | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23
193 |  | Kaikohe (Pukenui Solar Farm) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
194 |  | Kaikohe (Twin Rivers Solar Farm) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | Twin Rivers Solar Farm is expected to be commissioned in November 2025.
195 |  | Maungatapere (Wairua Falls) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
196 |  | Maungatapere (Kaiwaikawe Wind Farm) | 0 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | New wind farm embedded in Northpower's network in Maungatapere: Being developed by Mercury.
197 |  | Maungaturoto (Papareireiā Solar Farm) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | Papareireiā Solar Farm is expected to be commissioned by late 2025.
198 |  | Maungaturoto (Te Puna Mauri ō Omaru) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
199 |  | Bombay (Hampton Downs Landfill) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
200 |  | Bombay (Papakura) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
201 |  | Glenbrook | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | This value includes an embedded generating unit with a nominal rating of 38 MW, but continuous output of approximately 25 MW. With the installation of the electric arc furnace and shutdown of two kilns and a melter, the generation output is expected to decrease; the magnitude of this reduction is currently unknown.
202 |  | Mangare (Watercare Mangere) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
203 |  | Otahuhu (Greenmount) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
204 |  | Penrose (Auckland Hospital) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
205 |  | Silverdale (Redvale Landfill) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | Installed capacity is 14x 1 MW machines but only 12 can be in service at any time.
206 |  | Takanini (Whitford Landfill) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
207 |  | Arapuni | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198
208 |  | Atiamuri | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84
209 |  | Cambridge (Swayne Rd) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
210
211 |  | Hangatiki (Mangapehi) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
212 |  | Hangatiki (Mokauiti) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
213 |  | Hangatiki (Speedies Road) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
214 |  | Hangatiki (Wairere) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
215 |  | Huntly | 1204 | 1204 | 1204 | 1204 | 1204 | 1204 | 454 | 454 | 454 | 454 | 454 | The timing of the three Rankine units’ retirement is uncertain. Our assumption of closure date at the end of 2030 is prudent to ensure we can plan for the worst case.
216 |  | Huntly (Taiohi Solar) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33
217 |  | Karapiro | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | Karapiro hydro station is being refurbished which, when completed in 2025, will increase the installed capacity by 17% to 112 MW.
218 |  | Kinleith (Kinleith Pulp & Paper) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | Oji Fibre Solutions has indicated the cogeneration output will be about 15 MW following cessation of paper production at Kinleith.
219 |  | Kopu (Pamu Ra ki Whitianga Solar) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32
220 |  | Maraetai | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360
221 |  | Ohakuri | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112
222 |  | Te Awamutu (Anchor Products) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
223 |  | Te Kowhai (Horotiu Landfill) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
224 |  | Te Kowhai (Te Uku) | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67
225 |  | Waihou – Tauhei Solar | 0 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
226 |  | Waikino (Tirohia Landfill) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
227 |  | Waikino (Whangamata Diesel) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
228 |  | Waipapa | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51
229 |  | Whakamaru | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126
230 |  | Whakamaru (Mokai) | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 136
231 |  | Edgecumbe (Bay Milk) | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Edgecumbe Bay milk cogeneration decommissioning in 2026 for Fonterra electrification
232 |  | Edgecumbe (Rangitaiki solar farm) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
233 |  | Edgecumbe (Omeheu solar farm) | 0 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
234 |  | Kawerau – KAG | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107
235 |  | Kawerau (Onepu) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | Onepu is the market designation for the aggregation of the following four generators: GDL/KA24 (9 MW), TA2 (16 MW), TA3 (8 MW) and TOPP1 (27 MW).
236 |  | Kawerau (Te Ahi O Maui) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
237 |  | Kawerau (TOPP 2) | 0 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49
238 |  | Matahina | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
239 |  | Matahina (Aniwhenua) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
240 |  | Mount Maunganui (Ballance Agri) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
241 |  | Rotorua (Fletcher Forests) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
242 |  | Rotorua (Wheao Flaxy Scheme) | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
243 |  | Tauranga (Kaimai) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | Kaimai is a run-of-river hydro scheme that injects at the Tauranga 33 kV bus. Output from the scheme varies between 14 MW and 40 MW – typically, 14 MW is the minimum generation available from the scheme at peak load, though this relies on sufficient water being available.
244 |  | Waiotahe (Te Herenga O Te Ra solar farm) | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23
245 |  | Aratiatia | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
246 |  | Bunnythorpe (Tararua Wind – North) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34
247 |  | Linton (Tararua Wind – South) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34
248 |  | Linton – Turitea Wind | 221 | 221 | 221 | 221 | 221 | 221 | 221 | 221 | 221 | 221 | 221
249 |  | Mangahao | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
250 |  | Ngā Awa Pūrua | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140
251 |  | Ngā Awa Pūrua – Ngā Tamariki | 82 | 128 | 128 | 128 | 128 | 128 | 128 | 128 | 128 | 128 | 128 | Mercury is building a 46 MW expansion to its Ngā Tamariki geothermal plant. First power is expected late 2025.
252 |  | Ohaaki | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
253 |  | Ongarue (Mokauiti, Kuratau and Wairere Falls) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
254 |  | Poihipi | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51
255 |  | Rangipo | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
256 |  | Tararua Wind Central – Tararua Wind Stage 3 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93
257 |  | Tararua Wind Central – Te Rere Hau | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49
258 |  | Te Mihi | 175 | 175 | 276 | 276 | 276 | 276 | 276 | 276 | 276 | 276 | 276 | Contact Energy confirmed, in November 2024, its redevelopment plan for the Wairakei steam field. A new 101 MW geothermal plant will be built in late 2027 at Te Mihi (Te Mihi Stage 2). Contact will retain 67 MW of capacity at the Wairakei station from mid-2027 until mid-2031.
259 |  | Tokaanu | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240
260 |  | Wairakei | 132 | 132 | 67 | 67 | 67 | 67 | 67 | 0 | 0 | 0 | 0 | Contact Energy confirmed, in November 2024, its redevelopment plan for the Wairakei steam field. A new 101 MW geothermal plant will be built in late 2027 at Te Mihi (Te Mihi Stage 2). Contact will retain 67 MW of capacity at the Wairakei station from mid-2027 until mid-2031.
261 |  | Wairakei (Hinemaiaia) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
262 |  | Wairakei (Rotokawa) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
263 |  | Wairakei (Te Huka) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
264 |  | Woodville – Te Apiti | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
265 |  | Carrington St (Mangorei) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
266 |  | Hawera (Patea) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32
267 |  | Hawera (Whareroa) | 64 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
268 |  | Hawera (Kapuni Solar) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
269 |  | Hawera (Origin Hawera) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
270 |  | Huirangi (Mangahewa) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
271 |  | Huirangi (Motukawa) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
272 |  | Junction Road | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
273 |  | Kapuni | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
274 |  | McKee | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94
275 |  | Taranaki Combined Cycle | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | The generator is assumed to remain in service until the end of winter 2025.
276 |  | Stratford Peaker | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
277 |  | Stratford (Stratford Austral Pacific) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
278 |  | Waverley – Waipipi | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130
279 |  | Harapaki | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176
280 |  | Kaitawa | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | Kaitawa, Piripaua and Tuai are collectively known as the Waikaremoana scheme and connect to the Tuai 110 kV bus.
281 |  | Piripaua | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | Kaitawa, Piripaua and Tuai are collectively known as the Waikaremoana scheme and connect to the Tuai 110 kV bus.
282 |  | Redclyffe (Esk River) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
283 |  | Tauhara | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174
284 |  | Tauhara (Te Huka 3) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51
285 |  | Tuai | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | Kaitawa, Piripaua and Tuai are collectively known as the Waikaremoana scheme and connect to the Tuai 110 kV bus.
286 |  | Tuai (Gisborne) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
287 |  | Tuai (Matawai) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
288 |  | Tuai (Waihi) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
289 |  | Whirinaki | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156
290 |  | Whirinaki (Pan Pac) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
291 |  | Te Rahui | 0 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
292 |  | Central Park (Southern Landfill) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
293 |  | Central Park (Wellington Hospital) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | The Wellington Hospital generation is standby only.
294 |  | Greytown (Hau Nui) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
295 |  | Haywards (Silverstream) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
296 |  | Masterton (Kourarau A and B) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
297 |  | West Wind | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143
298 |  | Wilton (Mill Creek) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
299 |  | Argyle – Branch River Scheme | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
300 |  | Blenheim (Ra Nui Solar) | 0 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | Ra Nui Solar Farm is expected to begin commissioning late 2025.
301 |  | Blenheim (Lulworth Wind) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
302 |  | Blenheim (Waihopai hydro) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
303 |  | Blenheim (Wairau Valley Solar) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
304 |  | Stoke (Cobb) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32
305 |  | Stoke (Onekaka hydro) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
306 |  | Dobson (Arnold) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
307 |  | Dobson (Inchbonnie) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
308 |  | Hokitika (Amethyst) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
309 |  | Hokitika (McKays Creek and Kaniere Forks) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
310 |  | Hokitika (Wahapo) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
311 |  | Kumara (Kumara and Dillmans) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | The Dillmans hydro power scheme does not have significant water storage but is expected to supply an average of 5 MW during summer peaks.
312 |  | Murchison (Matiri) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
313 |  | Robertson Street (Rochfort) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
314 |  | Ashburton (Highbank) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
315 |  | Ashburton (Lauriston) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
316 |  | Ashburton (Montalto) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
317 |  | Coleridge | 41 | 42 | 42 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
318 |  | Islington (Kowhai Park) | 0 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
319 |  | Albury (Opuha) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
320 |  | Aviemore | 232 | 232 | 232 | 232 | 232 | 232 | 232 | 232 | 232 | 232 | 232
321 |  | Benmore | 540 | 540 | 540 | 540 | 540 | 540 | 540 | 540 | 540 | 540 | 540
322 |  | Clandeboye Solar Farm | 0 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28
323 |  | Ohau A | 264 | 264 | 264 | 264 | 264 | 264 | 264 | 264 | 264 | 264 | 264
324 |  | Ohau B | 212 | 212 | 212 | 212 | 212 | 212 | 212 | 212 | 212 | 212 | 212
325 |  | Ohau C | 212 | 212 | 212 | 212 | 212 | 212 | 212 | 212 | 212 | 212 | 212
326 |  | Tekapo A | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
327 |  | Tekapo B | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154
328 |  | Waitaki | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
329 |  | Balclutha (Mount Stuart) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
330 |  | Berwick (Waipori 2) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
331 |  | Clyde | 464 | 464 | 464 | 464 | 464 | 464 | 464 | 464 | 464 | 464 | 464
332 |  | Clyde (Horseshoe Bend hydro) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
333 |  | Clyde (Horseshoe Bend wind) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
334 |  | Clyde (Lower Fraser) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
335 |  | Clyde (Upper Fraser) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
336 |  | Clyde (Kowhai) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
337 |  | Clyde (Talla Burn) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
338 |  | Clyde (Teviot) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
339 |  | Cromwell (Roaring Meg) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
340 |  | Frankton (Wye Creek and Glenorchy) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
341 |  | Gore (Blue Mountain Lumber) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
342 |  | Gore (Kaiwera Downs 1) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
343 |  | Halfway Bush (Deep Stream) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
344 |  | Halfway Bush (Waipori 1) | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
345 |  | Halfway Bush (Mahinerangi) | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
346 |  | Invercargill (Flat Hill) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
347 |  | Kaiwera Downs 2 | 0 | 0 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155
348 |  | Manapouri | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820
349 |  | Naseby (Falls Dam) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
350 |  | Naseby (Paerau) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
351 |  | Naseby (Patearoa) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
352 |  | North Makarewa (Monowai) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
353 |  | North Makarewa (White Hill) | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58
354 |  | Roxburgh | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320
355 |  | GIPs Total | 10884 | 10851 | 11522 | 11481 | 11524 | 11524 | 10774 | 10707 | 10707 | 10707 | 10707 |  |  |  | Not required from disclosure year 2026
356 |  | *Insert additional rows and update calculation of totals as needed
357
358 | G3(iii): Anticipatory Connection Asset capacity
|  |  | CY |  |  | Forecast Anticipatory capacity (MVA)
360 |  | Grid Injection point (generator location if embedded) | Total Capacity (MVA) | Opening Anticipatory capacity (MVA) | Closing Anticipatory capacity (MVA) | CY+1 | CY+2 | CY+3 | CY+4 | CY+5 | CY+6 | CY+7 | CY+8 | CY+9 | CY+10 | Comments on Capacity
361 |  | Albany (Rosedale1) (example) | 5 | 3 | 1 | [11 empty] | Required from disclosure year 2026
362 |  | Northland (example) | [14 empty] | Required from disclosure year 2026
363 |  | [insert GIP] | [14 empty] | Required from disclosure year 2026
364 |  | [insert GIP] | [14 empty] | Required from disclosure year 2026
365 |  | [insert GIP] | [14 empty] | Required from disclosure year 2026
366 |  | GIPs Total | 5 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Required from disclosure year 2026
367 |  | *Insert additional rows and update calculation of totals as needed
368
369

## G4. Quality Grid Outputs
[11 empty] | Transpower |  | Disclosure Date |  | 2025-10-24
SCHEDULE G4: QUALITY OF SUPPLY: GRID OUTPUTS AND PERFORMANCE MEASURES | [12 empty] | Disclosure Year (year ended) |  | 2025-06-30
ref
5 | G4(i): Grid Output Historical and Forecast Measures and Targets
6
7 |  | Grid Output Measure - Quality | Actual performance |  |  |  |  | CY Target | CY Target Achieved | Forecast Performance
8 |  |  | CY-4 | CY-3 | CY-2 | CY-1 | CY |  | (Yes/No) | CY+1 | CY+2 | CY+3 | CY+4 | CY+5
9 |  | Number of loss of supply events greater than 0.05 system minutes | 12 | 9 | 13 | 9 | 9 | None | None | None | None | None | None | None
10 |  | Number of loss of supply events greater than 1 system minute | 0 | 0 | 1 | 1 | 2 | None | None | None | None | None | None | None
11 |  | Unplanned HVAC circuit unavailability (%) | 0.134% | 0.337% | 0.494% | 0.06% | 0.034% | None | None | None | None | None | None | None
12 |  | Unplanned HVDC bi-pole unavailability (%)* | 0.099% | 1.264% | 0.05% | 0.066% | 0.646% | None | None | None | None | None | None | None
13 |  | Total impact of interruptions (measured in system minutes) | 5.89 | 6.04 | 334.46 | 2.53 | 5.77 | None | None | None | None | None | None | None
14 |  | *No target currently specified
15 |  | The number of loss of supply for the above quality measures relate to unplanned loss of supply events.
16
17 | G4(ii): Grid Connection Point Performance Measures
18
19
20 |  | Point of Service Performance - Demand | No target currently specified. The Point of Service code and description have been used to identify the locations.
21 | [5 empty] | Number of Interruptions |  |  |  |  | Unserved energy % X100
22 |  |  | Point of Service |  |  | CY-2 Actual | CY-1 Actual | CY Actual | CY Target | 5 year average | CY-2 Actual | CY-1 Actual | CY Actual | CY Target | 5 year average
23 |  |  | ABY011S1 | Albury 11 kV POS S 1 |  | 1 | 3 | 1 | None | 1 | 7.9904 | 10.6106 | 95.7394 | None | 22.8681
24 |  |  | ALB033S1 | Albany 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
25 |  |  | ALB110S1 | Albany 110 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
26 |  |  | APS011S1 | Arthurs Pass 11 kV POS S 1 |  | 1 | 3 | 3 | None | 1.8 | 3.0664 | 6.1035 | 4.6091 | None | 3.5383
27 |  |  | ARI110S2 | Arapuni 110 kV POS S 2 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
28 |  |  | ASB066SA | Ashburton 66 kV POS S |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
29 |  |  | ASY011S1 | Ashley 11 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
30 |  |  | ATI220S1 | Atiamuri 220 kV POS S 1 |  | - | 0 | 0 | None | 0 | - | 0 | 0 | None | 0
31 |  |  | BAL033S1 | Balclutha 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
32 |  |  | BDE011S1 | Brydone 11 kV POS S 1 |  | 0 | 1 | 0 | None | 0.2 | 0 | 1.4543 | 0 | None | 0.29085
33 |  |  | BDE011S2 | Brydone 11 kV POS S 2 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
34 |  |  | BLN033S1 | Blenheim 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
35 |  |  | BOB110S1 | Bombay 110 kV POS S 1 |  | 1 | 0 | 0 | None | 0.2 | 0.43154 | 0 | 0 | None | 0.086309
36 |  |  | BPD110S1 | Bells Pond 110 kV POS S 1 |  | 0 | 1 | 2 | None | 0.8 | 0 | 1.528 | 1.7385 | None | 0.82776
37 |  |  | BPE033S1 | Bunnythorpe 33 kV POS S 1 |  | 1 | 0 | 0 | None | 0.2 | 0.39101 | 0 | 0 | None | 0.078203
38 |  |  | BPE055SA | Bunnythorpe 55 kV POS S |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
39 |  |  | BPT110S1 | Black Point 110 kV POS S 1 |  | 0 | 2 | 3 | None | 1 | 0 | 1.9648 | 0.70982 | None | 0.53491
40 |  |  | BRB033S1 | Bream Bay 33 kV POS S 1 |  | 0 | 1 | 0 | None | 0.2 | 0 | 2.3133 | 0 | None | 0.46266
41 |  |  | BRK033S1 | Brunswick 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
42 |  |  | BRY066SA | Bromley 66 kV POS S |  | 0 | 1 | 0 | None | 0.2 | 0 | 0.11256 | 0 | None | 0.022511
43 |  |  | CBG011S1 | Cambridge 11 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
44 |  |  | CLH011S1 | Castle Hill 11 kV POS S 1 |  | 2 | 3 | 3 | None | 1.8 | 2.5815 | 9.2648 | 4.8334 | None | 3.579
45 |  |  | CML033S1 | Cromwell 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
46 |  |  | COL011S1 | Coleridge 11 kV POS S 1 |  | 0 | 0 | 0 | None | 0.2 | 0 | 0 | 0 | None | 1.0923
47 |  |  | CPK011S1 | Central Park 11 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
48 |  |  | CPK033S1 | Central Park 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
49 |  |  | CST033S1 | Carrington Street 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
50 |  |  | CUL033S1 | Culverden 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
51 |  |  | CUL066S1 | Culverden 66 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
52 |  |  | CYD033S1 | Clyde 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
53 |  |  | DOB033S1 | Dobson 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0.2 | 0 | 0 | 0 | None | 0.31806
54 |  |  | DVK011S1 | Dannevirke 11 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
55 |  |  | EDG033S1 | Edgecumbe 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
56 |  |  | EDN033S1 | Edendale 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0.2 | 0 | 0 | 0 | None | 0.38782
57 |  |  | FHL033S1 | Fernhill 33 kV POS S 1 |  | 1 | 0 | 1 | None | 0.6 | 2.5952 | 0 | 2.0997 | None | 0.96645
58 |  |  | FKN033S1 | Frankton 33 kV (A) POS S 1 |  | 0 | 1 | 0 | None | 0.2 | 0 | 0.057267 | 0 | None | 0.011453
59 |  |  | FKN033S2 | Frankton 33 kV (B) POS S 2 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
60 |  |  | GFD033S1 | Gracefield 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
61 |  |  | GLN033SA | Glenbrook 33 kV (B) POS S |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
62 |  |  | GLN033S3 | Glenbrook 33 kV (A) POS S 3 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
63 |  |  | GOR033S1 | Gore 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
64 |  |  | GYM066S1 | Greymouth 66 kV POS S 1 |  | 0 | 0 | 0 | None | 0.4 | 0 | 0 | 0 | None | 0.42543
65 |  |  | GYT033S1 | Greytown 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0.2 | 0 | 0 | 0 | None | 0.49637
66 |  |  | HAM011S1 | Hamilton 11 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
67 |  |  | HAM033S1 | Hamilton 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
68 |  |  | HAM055SA | Hamilton 55 kV POS S |  | 0 | 1 | 0 | None | 0.2 | 0 | 0.018206 | 0 | None | 0.0036411
69 |  |  | HAY011S1 | Haywards 11 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
70 |  |  | HAY033S1 | Haywards 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
71 |  |  | HEN033S1 | Henderson 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
72 |  |  | HEP033S1 | Hepburn Road 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
73 |  |  | HIN033S1 | Hinuera 33 kV POS S 1 |  | 0 | 0 | 2 | None | 0.6 | 0 | 0 | 0.53041 | None | 0.60441
74 |  |  | HKK066S1 | Hokitika 66 kV POS S 1 |  | 1 | 0 | 1 | None | 0.8 | 0.5555 | 0 | 1.0543 | None | 3.194
75 |  |  | HLY033SA | Huntly 33 kV POS S |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
76 |  |  | HOB110S1 | Hobson Street 110 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
77 |  |  | HOR033S1 | Hororata 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
78 |  |  | HOR066S1 | Hororata 66 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
79 |  |  | HTI033S1 | Hangatiki 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0.2 | 0 | 0 | 0 | None | 0.77829
80 |  |  | HTI110S1 | Hangatiki 110 kV POS S 1 |  | 0 | 0 | 0 | None | 0.2 | 0 | 0 | 0 | None | 0.64118
81 |  |  | HTU033S1 | Hautapu 33kV POS S 1 |  | - | - | 0 | None | 0 | - | - | 0 | None | 0
82 |  |  | HUI033S1 | Huirangi 33 kV POS S 1 |  | 1 | 0 | 0 | None | 0.2 | 1.8744 | 0 | 0 | None | 0.37488
83 |  |  | HWA033S1 | Hawera 33 kV (A) POS S 1 |  | 0 | 0 | 1 | None | 0.2 | 0 | 0 | 0.4879 | None | 0.09758
84 |  |  | HWA033S2 | Hawera 33 kV (B) POS S 2 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
85 |  |  | HWB033S1 | Halfway Bush 33 kV (A) POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
86 |  |  | HWB033S2 | Halfway Bush 33 (B) kV POS S 2 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
87 |  |  | INV033S1 | Invercargill 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
88 |  |  | ISL033S1 | Islington 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
89 |  |  | ISL066S1 | Islington 66 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
90 |  |  | KAI011S1 | Kaiapoi 11 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
91 |  |  | KAW011S1 | Kawerau 11 kV (A) POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
92 |  |  | KAW011S2 | Kawerau 11 kV POS S 2 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
93 |  |  | KAW011SA | Kawerau 11 kV (B) POS S |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
94 |  |  | KBY066SA | Kimberley 66 kV POS S |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
95 |  |  | KIK011S1 | Kikiwa 11 kV POS S 1 |  | 0 | 0 | 0 | None | 0.4 | 0 | 0 | 0 | None | 4.3229
96 |  |  | KIN011SA | Kinleith 11 kV POS S |  | 0 | 0 | 1 | None | 0.2 | 0 | 0 | 0.2363 | None | 0.047261
97 |  |  | KIN033S1 | Kinleith 33 kV POS S 1 |  | 1 | 0 | 0 | None | 0.2 | 0.32221 | 0 | 0 | None | 0.064442
98 |  |  | KMO033S1 | Kaitemako 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
99 |  |  | KOE110S1 | Kaikohe 110 kV POS S 1 |  | 0 | 1 | 0 | None | 0.2 | 0 | 144.2917 | 0 | None | 28.8583
100 |  |  | KPA110S1 | Kaponga Tee 110 kV POS S1 |  | - | 1 | 1 | None | 1 | - | 0 | 0 | None | 0
101 |  |  | KPU066S1 | Kopu 66 kV POS S 1 |  | 0 | 1 | 0 | None | 0.4 | 0 | 1.0971 | 0 | None | 1.0744
102 |  |  | KUM066S1 | Kumara 66 kV POS S 1 |  | 1 | 0 | 0 | None | 0.6 | 0.24778 | 0 | 0 | None | 1.2636
103 |  |  | KWA011S1 | Kaiwharawhara 11 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
104 |  |  | LFD110S1 | Lichfield 110 kV POS S 1 |  | 0 | 1 | 0 | None | 0.2 | 0 | 0.099267 | 0 | None | 0.019853
105 |  |  | LTN033S1 | Linton 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
106 |  |  | MAT110S1 | Matahina 110 kV (A) POS S 1 |  | - | 0 | 0 | None | 0 | - | 0 | 0 | None | 0
107 |  |  | MCH011S1 | Murchison 11 kV POS S 1 |  | 0 | 0 | 1 | None | 0.6 | 0 | 0 | 3.3091 | None | 2.9248
108 |  |  | MGM033S1 | Mangamaire 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
109 |  |  | MHO033S1 | Mangahao 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
110 |  |  | MLG011S1 | Melling 11 kV POS S 1 |  | 0 | 0 | 0 | None | 0.2 | 0 | 0 | 0 | None | 0.27741
111 |  |  | MLG033S1 | Melling 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
112 |  |  | MNG033S1 | Mangere 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
113 |  |  | MNG110S1 | Mangere 110 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
114 |  |  | MNI011SA | Motunui 11 kV POS S |  | 0 | 0 | 0 | None | 0.2 | 0 | 0 | 0 | None | 0.0080778
115 |  |  | MNI011S3 | Motunui 11 kV POS S 3 |  | 0 | 0 | 0 | None | 0.2 | 0 | 0 | 0 | None | 0.32505
116 |  |  | MPE110S1 | Maungatapere 110 kV POS S 1 |  | 0 | 1 | 0 | None | 0.2 | 0 | 1.1638 | 0 | None | 0.23276
117 |  |  | MST033S1 | Masterton 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
118 |  |  | MTM033S1 | Mt Maunganui 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
119 |  |  | MTN033S1 | Marton 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0.4 | 0 | 0 | 0 | None | 0.56413
120 |  |  | MTO033S1 | Maungaturoto 33 kV POS S 1 |  | 0 | 0 | 2 | None | 1 | 0 | 0 | 4.0827 | None | 2.0606
121 |  |  | MTR033S1 | Mataroa 33 kV POS S 1 |  | 1 | 0 | 0 | None | 0.6 | 0.57038 | 0 | 0 | None | 0.828
122 |  |  | NMA033S1 | North Makarewa 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
123 |  |  | NPK033S1 | National Park 33 kV POS S 1 |  | 1 | 0 | 0 | None | 1.2 | 0.39831 | 0 | 0 | None | 0.76932
124 |  |  | NSY033S1 | Naseby 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
125 |  |  | NWD066S1 | Norwood 66 kV POS S 1 |  | - | 0 | 0 | None | 0 | - | 0 | 0 | None | 0
126 |  |  | OAM033S1 | Oamaru 33 kV POS S 1 |  | 0 | 0 | 1 | None | 0.2 | 0 | 0 | 1.4339 | None | 0.28679
127 |  |  | OKN011S2 | Ohakune 11 kV (A) POS S 2 |  | 1 | 0 | 0 | None | 0.8 | 0.49247 | 0 | 0 | None | 0.88756
128 |  |  | OKN011S1 | Ohakune 11 kV (B) POS S 1 |  | 1 | 0 | 0 | None | 0.8 | 0.93416 | 0 | 0 | None | 0.96169
129 |  |  | ONG033S1 | Ongarue 33 kV POS S 1 |  | 1 | 0 | 0 | None | 1 | 0.33843 | 0 | 0 | None | 1.0264
130 |  |  | OPK033S1 | Opunake 33 kV POS S 1 |  | 1 | 0 | 0 | None | 0.6 | 1.7543 | 0 | 0 | None | 1.2981
131 |  |  | ORO110S1 | Orowaiti Tee 110 kV POS S 1 |  | 0 | 2 | 0 | None | 0.8 | 0 | 0.57376 | 0 | None | 0.34943
132 |  |  | OTA022S1 | Otahuhu 22 kV (A) POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
133 |  |  | OTI011S1 | Otira 11 kV POS S 1 |  | 0 | 0 | 0 | None | 0.4 | 0 | 0 | 0 | None | 0.60348
134 |  |  | OWH011S1 | Owhata 11 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
135 |  |  | PAK033S1 | Pakuranga 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
136 |  |  | PAO110S1 | Piako 110 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
137 |  |  | PEN022S1 | Penrose 22 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
138 |  |  | PEN025S1 | Penrose 25 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
139 |  |  | PEN033S1 | Penrose 33 kV (A) POS S 1 |  | 0 | 1 | 0 | None | 0.2 | 0 | 0.12268 | 0 | None | 0.024536
140 |  |  | PEN033S2 | Penrose 33 kV (B) POS S 2 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
141 |  |  | PEN110S1 | Penrose 110 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
142 |  |  | PNI033S1 | Pauatahanui 33 kV POS S 1 |  | 2 | 1 | 0 | None | 0.6 | 0.94434 | 0.93832 | 0 | None | 0.37653
143 |  |  | PRM033S1 | Paraparaumu 33 kV POS S 1 |  | 0 | 0 | 1 | None | 0.2 | 0 | 0 | 0.10122 | None | 0.020245
144 |  |  | RDF033S1 | Redclyffe 33 kV POS S 1 |  | 2 | 0 | 1 | None | 0.6 | 195.5621 | 0 | 1.9783 | None | 39.5081
145 |  |  | RFN110SA | Reefton 110 kV POS S |  | 0 | 1 | 0 | None | 0.4 | 0 | 0.41096 | 0 | None | 0.32269
146 |  |  | ROS022S1 | Mount Roskill 22 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
147 |  |  | ROS110S1 | Mount Roskill 110 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
148 |  |  | ROT011S1 | Rotorua 11 kV POS S 1 |  | 0 | 0 | 1 | None | 0.2 | 0 | 0 | 1.0656 | None | 0.21311
149 |  |  | ROT033S1 | Rotorua 33 kV POS S 1 |  | 0 | 0 | 1 | None | 0.2 | 0 | 0 | 1.4581 | None | 0.29162
150 |  |  | SBK066S1 | Southbrook 66 kV POS S1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
151 |  |  | SDN033S1 | South Dunedin 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
152 |  |  | SFD033S1 | Stratford 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
153 |  |  | STK033S1 | Stoke 33 kV (A) POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
154 |  |  | STK033S2 | Stoke 33 kV (B) CB 2162 POS S 2 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
155 |  |  | STK066S1 | Stoke 66 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
156 |  |  | STU011S1 | Studholme 11 kV POS S 1 |  | 0 | 0 | 1 | None | 0.2 | 0 | 0 | 2.5285 | None | 0.50571
157 |  |  | SVL033S1 | Silverdale 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
158 |  |  | SWN025S1 | Southdown 25 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
159 |  |  | TAB033S1 | Tauhara 33 kV POS S 1 |  | - | 0 | 1 | None | 0.5 | - | 0 | 26.3405 | None | 13.1702
160 |  |  | TAK033S1 | Takanini 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
161 |  |  | TGA011S1 | Tauranga 11 kV POS S 1 |  | 1 | 0 | 0 | None | 0.2 | 2.5642 | 0 | 0 | None | 0.51283
162 |  |  | TGA033S1 | Tauranga 33 kV POS S 1 |  | 1 | 0 | 0 | None | 0.2 | 1.5256 | 0 | 0 | None | 0.30512
163 |  |  | TIM011S1 | Timaru 11 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
164 |  |  | TKA033S1 | Tekapo A 33 kV POS S 1 |  | 6 | 0 | 2 | None | 2 | 4.539 | 0 | 35.487 | None | 8.7665
165 |  |  | TKR033S1 | Takapu Road 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
166 |  |  | TKU033S1 | Tokaanu 33 kV (A) POS S 1 |  | 0 | 1 | 0 | None | 0.2 | 0 | 0.49224 | 0 | None | 0.098448
167 |  |  | TMI033S1 | Te Matai 33 kV POS S 1 |  | 1 | 0 | 0 | None | 0.2 | 1.0787 | 0 | 0 | None | 0.21575
168 |  |  | TMK033S1 | Temuka 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
169 |  |  | TMN055SA | Taumarunui 55 kV POS S |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
170 |  |  | TMU011SA | Te Awamutu 11 kV POS S |  | 0 | 2 | 0 | None | 0.4 | 0 | 0.16787 | 0 | None | 0.033574
171 |  |  | TNG055SA | Tangiwai 55 kV POS S |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
172 |  |  | TRK011S1 | Tarukenga 11 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
173 |  |  | TUI110S2 | Tuai 110 kV POS S2 |  | 2 | 0 | 1 | None | 0.8 | 9.1666 | 0 | 1.6876 | None | 2.3015
174 |  |  | TWC220S1 | Tararua Wind Central 220 kV POS S 1 |  | - | 0 | 0 | None | 0 | - | 0 | 0 | None | 0
175 |  |  | TWH033S1 | Te Kowhai 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
176 |  |  | TWI220S1 | Tiwai 220 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
177 |  |  | TWZ033S1 | Twizel 33 kV (A) POS S 1 |  | 0 | 0 | 0 | None | 0.2 | 0 | 0 | 0 | None | 0.085584
178 |  |  | TWZ033S3 | Twizel 33 kV (B) POS S 3 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
179 |  |  | UHT033S1 | Upper Hutt 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
180 |  |  | WAI011S1 | Waiotahe 11 kV POS S 1 |  | 0 | 0 | 1 | None | 0.2 | 0 | 0 | 0.29491 | None | 0.058981
181 |  |  | WAI050S1 | Waiotahe 50 kV POS S 1 |  | 0 | 1 | 1 | None | 0.4 | 0 | 0.35904 | 0.23777 | None | 0.11936
182 |  |  | WDV011S1 | Woodville 11 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
183 |  |  | WEL033S1 | Wellsford 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0.2 | 0 | 0 | 0 | None | 0.38894
184 |  |  | WGN033S1 | Whanganui 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0.2 | 0 | 0 | 0 | None | 0.11519
185 |  |  | WHI011SA | Whirinaki 11 kV POS S |  | 1 | 0 | 1 | None | 0.4 | 1035.1195 | 0 | 1.7596 | None | 207.3758
186 |  |  | WHU033S1 | Waihou 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
187 |  |  | WIL033S1 | Wilton 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
188 |  |  | WIR033S1 | Wiri 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
189 |  |  | WKO033S1 | Waikino 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
190 |  |  | WPR033S1 | Waipara 33 kV POS S 1 |  | 0 | 0 | 1 | None | 0.2 | 0 | 0 | 0.33665 | None | 0.067329
191 |  |  | WPR066S1 | Waipara 66 kV POS S 1 |  | 0 | 0 | 1 | None | 0.2 | 0 | 0 | 0.34678 | None | 0.069356
192 |  |  | WPW011S1 | Waipawa 11 kV POS S 1 |  | 2 | 0 | 0 | None | 0.4 | 6.3432 | 0 | 0 | None | 1.2686
193 |  |  | WPW033S1 | Waipawa 33 kV POS S 1 |  | 2 | 0 | 0 | None | 0.4 | 2.9112 | 0 | 0 | None | 0.58223
194 |  |  | WRD033S1 | Wairau Road 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
195 |  |  | WRK033S1 | Wairakei 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
196 |  |  | WTK011S2 | Waitaki 11kV POS S 2 |  | 0 | 0 | 0 | None | 0.2 | 0 | 0 | 0 | None | 0.15886
197 |  |  | WTK033S1 | Waitaki 33 kV POS S 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
198 |  |  | WTU033S1 | Whakatu 33 kV POS S 1 |  | 1 | 0 | 1 | None | 0.4 | 95.7939 | 0 | 1.2501 | None | 19.4088
199 |  |  | WVY011S1 | Waverley 11 kV POS S 1 |  | 0 | 0 | 0 | None | 0.4 | 0 | 0 | 0 | None | 0.71155
200
201 |  |  | An update on the data has been done since last year's report. This has affected some numbers for two points of service, KPA110S1 and TWC220S1.
202 |  |  | *Insert additional rows as needed
203
204 |  | Point of Service Performance - Injection | [6 empty] | Not required from disclosure year 2026 |  |  |  |  | Not required from disclosure year 2026
205 | [5 empty] | Number of Interruptions |  |  |  |  | Duration in minutes
206 |  |  | Point of Service |  |  | CY-2 Actual | CY-1 Actual | CY Actual | CY Target | 5 year average | CY-2 Actual | CY-1 Actual | CY Actual | CY Target | 5 year average
207 |  |  | ARA220I1 | Aratiatia 220 kV POS I 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
208 |  |  | ARG110I1 | Argyle 110 kV POS I 1 |  | 3 | 0 | 3 | None | 1.8 | 12 | 0 | 20 | None | 71.6
209 |  |  | ARI110I1 | Arapuni 110 kV POS I 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
210 |  |  | AVI220I1 | Aviemore 220 kV POS I 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
211 |  |  | BEN220I1 | Benmore 220 kV POS I 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
212 |  |  | BRB033I1 | Bream Bay 33 kV POS I 1 |  | 0 | 1 | 0 | None | 0.2 | 0 | 89 | 0 | None | 17.8
213 |  |  | BWK110I1 | Berwick 110 kV POS I 1 |  | 3 | 1 | 1 | None | 1.4 | 157 | 96 | 3 | None | 53.6
214 |  |  | COL066I1 | Coleridge 66 kV POS I 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
215 |  |  | CYD220I1 | Clyde 220 kV POS I 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
216 |  |  | GLN033I1 | Glenbrook 33 kV POS I 1 |  | 0 | 0 | 0 | None | 0.2 | 0 | 0 | 0 | None | 10.6
217 |  |  | HLY220I1 | Huntly 220 kV POS I 1 |  | 0 | 0 | 0 | None | 0.2 | 0 | 0 | 0 | None | 32.8
218 |  |  | HRP220I1 | Harapaki 220 kV POS I 1 |  | 0 | 0 | 1 | None | 0.2 | 0 | 0 | 133 | None | 26.6
219 |  |  | HWA110I1 | Hawera 110 kV (A) POS I 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
220 |  |  | HWA110I2 | Hawera 110 kV (B) POS I 2 |  | 0 | 0 | 0 | None | 0.2 | 0 | 0 | 0 | None | 25.2
221 |  |  | JRD110I1 | Junction Road 110 kV POS I 1 |  | 1 | 0 | 0 | None | 0.6 | 3 | 0 | 0 | None | 4.4
222 |  |  | KAW110I1 | Kawerau 110 kV POS I 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
223 |  |  | KPO110I1 | Karapiro 110 kV POS I 1 |  | 0 | 0 | 1 | None | 0.2 | 0 | 0 | 35 | None | 7
224 |  |  | LTN220I1 | Linton 220 kV POS I 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
225 |  |  | MAN220I1 | Manapouri 220 kV POS I 1 |  | 2 | 0 | 0 | None | 0.4 | 24291 | 0 | 0 | None | 4858.2
226 |  |  | MAT110I2 | Matahina 110 kV (B) POS I 2 |  | 0 | 0 | 1 | None | 0.2 | 0 | 0 | 131 | None | 26.2
227 |  |  | MHO033I2 | Mangahao 33 kV POS I 2 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
228 |  |  | MKE110I1 | McKee 110 kV POS I 1 |  | 0 | 0 | 0 | None | 0.2 | 0 | 0 | 0 | None | 3
229 |  |  | MTI220I1 | Maraetai 220 kV POS I 1 |  | 0 | 2 | 1 | None | 1 | 0 | 412 | 158 | None | 175.6
230 |  |  | NAP220I1 | Nga Awa Purua 220 kV POS I 1 |  | 0 | 0 | 1 | None | 0.2 | 0 | 0 | 549 | None | 109.8
231 |  |  | NAP220I2 | Nga Awa Purua 220 kV POS I 2 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
232 |  |  | OHA220I1 | Ohau A 220 kV POS I 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
233 |  |  | OHB220I1 | Ohau B 220 kV POS I 1 |  | 4 | 0 | 0 | None | 0.8 | 118 | 0 | 0 | None | 23.6
234 |  |  | OHC220I1 | Ohau C 220 kV POS I 1 |  | 0 | 0 | 0 | None | 0.2 | 0 | 0 | 0 | None | 5.6
235 |  |  | OHK220I1 | Ohakuri 220 kV POS I 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
236 |  |  | OKI220I1 | Ohaaki 220 kV POS I 1 |  | 0 | 0 | 0 | None | 0.2 | 0 | 0 | 0 | None | 7.4
237 |  |  | PPI220I1 | Poihipi 220 kV POS I 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
238 |  |  | ROT110I1 | Rotorua 110 kV POS I 1 |  | 0 | 0 | 2 | None | 0.4 | 0 | 0 | 650 | None | 130
239 |  |  | ROX110I1 | Roxburgh 110 kV POS I 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
240 |  |  | ROX220I1 | Roxburgh 220 kV POS I 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
241 |  |  | RPO220I1 | Rangipo 220 kV POS I 1 |  | 4 | 1 | 1 | None | 1.4 | 548 | 14 | 205 | None | 475.8
242 |  |  | SFD220I1 | Stratford 220 kV POS I 1 |  | 0 | 0 | 0 | None | 0.2 | 0 | 0 | 0 | None | 29.2
243 |  |  | SWN220I1 | Southdown 220 kV POS I 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
244 |  |  | TAB220I1 | Tauhara 220 kV POS I 1 |  | 0 | 0 | 1 | None | 0.2 | 0 | 0 | 102 | None | 20.4
245 |  |  | THI220I1 | Te Mihi 220 kV POS I 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
246 |  |  | TKA011I1 | Tekapo A 11 kV POS I 1 |  | 6 | 2 | 2 | None | 2.4 | 278 | 8 | 1795 | None | 454
247 |  |  | TKB220I1 | Tekapo B 220 kV POS I 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
248 |  |  | TKU220I1 | Tokaanu 220 kV POS I 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
249 |  |  | TUI110I1 | Tuai 110 kV POS I 1 |  | 2 | 0 | 1 | None | 0.8 | 282 | 0 | 97 | None | 82.6
250 |  |  | WAI033I1 | Waiotahe 33 kV POS I 1 |  | 0 | 0 | 1 | None | 0.2 | 0 | 0 | 25 | None | 5
251 |  |  | WDV110I1 | Woodville - Te Apiti Wind Farm 110 kV POS I 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
252 |  |  | WHI220I1 | Whirinaki 220 kV POS I 1 |  | 1 | 0 | 1 | None | 0.4 | 31641 | 0 | 80 | None | 6344.2
253 |  |  | WKM220I1 | Whakamaru 220 kV POS I 1 |  | 0 | 0 | 0 | None | 0.2 | 0 | 0 | 0 | None | 59.4
254 |  |  | WPA220I1 | Waipapa 220 kV POS I 1 |  | 0 | 2 | 0 | None | 0.4 | 0 | 1449 | 0 | None | 289.8
255 |  |  | WRK220I1 | Wairakei 220 kV POS I 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
256 |  |  | WTK011I1 | Waitaki 11 kV POS I 1 |  | 0 | 0 | 0 | None | 0.2 | 0 | 0 | 0 | None | 44
257 |  |  | WVY110I1 | Waverley 110 kV POS I 1 |  | 0 | 0 | 0 | None | 0 | 0 | 0 | 0 | None | 0
258 |  |  | WWD110I1 | West Wind 110 kV POS I 1 |  | 3 | 0 | 0 | None | 0.8 | 682 | 0 | 0 | None | 140.2
259
260 |  |  | *Insert additional rows as needed
261
262 | G4(iii): Unplanned Interruption Causes
263
264 |  | Cause of interruption | Annual Performance (System Minutes) |  |  |  |  | Significant Events (System Minutes) |  |  |  |  | Underlying Events (System Minutes)
265 |  |  | CY-4 | CY-3 | CY-2 | CY-1 | CY | CY-4 | CY-3 | CY-2 | CY-1 | CY | CY-4 | CY-3 | CY-2 | CY-1 | CY
266 |  | Transpower Unplanned
267 |  | Environment | 0.8 | 2.03 | 333.47 | 0.11 | 2.74 | 0 | 0 | 331.99 | 0 | 2.47 | 0.80247 | 2.03 | 1.48 | 0.11 | 0.27
268 |  | Equipment | 0.92 | 0.9 | 0.62 | 0.23 | 0.49 | 0 | 0 | 0 | 0 | 0 | 0.92286 | 0.9 | 0.62 | 0.23 | 0.49
269 |  | Human error | 0.28 | 0.31 | 0.2 | 2.02 | 0.42 | 0 | 0 | 0 | 1.55 | 0 | 0.27742 | 0.31 | 0.2 | 0.47 | 0.42
270 |  | Miscellaneous | 0.05 | 0 | 0 | 0.07 | 1.75 | 0 | 0 | 0 | 0 | 1.72 | 0.046429 | 0 | 0 | 0.07 | 0.03
271 |  | Not Known | 0.18 | 0.04 | 0.16 | 0.09 | 0.38 | 0 | 0 | 0 | 0 | 0 | 0.17796 | 0.04 | 0.16 | 0.09 | 0.38
272 |  | Total Unplanned | 2.23 | 3.28 | 334.45 | 2.52 | 5.78 | 0 | 0 | 331.99 | 1.55 | 4.19 | 2.2271 | 3.28 | 2.46 | 0.97 | 1.59
273
274 |  | Transpower Planned | 3.66 | 2.76 | 1.24 | 1.82 | 1.75 | 0 | 0 | 0 | 0 | 0 | 3.6644 | 2.76 | 1.24 | 1.82 | 1.75
275
276 |  | Total Transpower Planned and Unplanned | 5.89 | 6.04 | 335.69 | 4.34 | 7.53 | 0 | 0 | 331.99 | 1.55 | 4.19 | 5.8915 | 6.04 | 3.7 | 2.79 | 3.34
277
278

## G5. Quality interconnection
[9 empty] | Transpower |  | Disclosure Date |  | 2025-10-24
SCHEDULE G5: QUALITY OF SUPPLY: INTERCONNECTION ASSETS | [10 empty] | Disclosure Year (year ended) |  | 2025-06-30
ref
5 | G5(i): Interconnection Asset Report
6
7 | Asset | Type* | Asset Category | Sub Cat | Planned Unavailability % | Unplanned Unavailability % | Number Planned Interruptions | Planned Unserved Energy MWh | Number Unplanned Interruptions | Unplanned Unserved Energy MWh | Number of Outages <1 Min | Number of Interruptions <1 min | Measures Exceeded (plan/Unplan) ? | Incidents Affecting Performance | Steps Being Taken To Improve Performance | IDENT
8 | Index Measures for Asset Category |  | CCT | 110 | 1.67 | 0.07 | 0.08 | 0.50 | 0.28 | 10.45 | None Apply | None Apply
9 | ARI-BOB-1 | I | CCT | 110 | 14.28 | 0.11 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/Y | Planned Outage /
10 | [13 empty] | 27-Jul-2024: ARI-BOB-1 trip,no auto-reclose. Yph-E fault, cause unknown. Line patrol HAM-MER-A0152 to 400 & public places patrol. | No fault found. No further action. | SN24111
11 | [13 empty] | 20-Sep-2024: ARI-BOB-1 trip, no A/R, Rph-E fault, probably caused by lightning, no line patrol, no LOS, SDTF recorded a lightning strike close to structure BOB-MER-A0019 and in span BOB-MER-A0018-0019. | No further action. | SN24136
12 | [13 empty] | 26-May-2025: ARI-BOB-1 tripped, no A/R, Yph-E fault, caused by human error by third party. A digger contacted yellow phase conductor at a construction site located in span ARI-HAM-A0127-A0128-10. | Developer has moved trenching away from poles to avoid this in the future. Northpower and Transpower visited site regularly to ensure compliance for ground reinstatement. | SN25071
13 | [13 empty] | 02-Jun-2025: ARI-BOB-1 trip, no A/R, BPh-E fault, cause unknown, line patrol found no cause. | No fault found. No further action. | SN25075
14 | [13 empty] | 03-Jun-2025: ARI-BOB-1 RFS, a short notice outage request (SNOR) to properly close ARI-DS-176's red phase contacts. ARI-DS-176 was opened & closed several times so that contacts on all phases were properly closed. | Outage put in place on 03Jun2025 to fully close disconnectors. | SN25080
15 | ARI-HAM-1 | I | CCT | 110 | 5.50 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
16 | ARI-HAM-2 | I | CCT | 110 | 9.87 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | Y/N | Planned Outage /
17 | ARI-HTI-1 | I | CCT | 110 | 1.31 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 5.00 | 0.00 | N/N | Planned Outage /
18 | ARI-HTI-ONG-1 | I | CCT | 110 | 3.12 | 0.05 | 0.00 | 0.00 | 0.00 | 0.00 | 2.00 | 0.00 | Y/N | Planned Outage /
19 | ARI-KIN-1 | I | CCT | 110 | 0.43 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | N/N | Planned Outage /
20 | ARI-KIN-2 | I | CCT | 110 | 0.20 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 2.00 | 0.00 | N/N | Planned Outage /
21 | ATU-DOB-1 | I | CCT | 110 | 5.96 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
22 | ATU-RFN-IGH-1 | I | CCT | 110 | 5.96 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 1.00 | Y/N | Planned Outage /
23 | BAL-GOR-1 | B | CCT | 110 | 4.44 | 0.19 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/Y | Planned Outage /
24 | [13 empty] | 07-Aug-2024: BAL-GOR-1 trip & A/R at GOR only, YPh-E, patrol of structures 209 to 312 found no cause. | No fault found. No further action. | SS24068
25 | BAL-HWB-1 | B | CCT | 110 | 3.33 | 0.02 | 0.00 | 0.00 | 0.00 | 0.00 | 2.00 | 0.00 | Y/N | Planned Outage /
26 | BDE-EDN-1 | B | CCT | 110 | 1.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
27 | BDE-GOR-1 | B | CCT | 110 | 0.18 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
28 | BLN-KIK-1 | I | CCT | 110 | 5.68 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 7.00 | 0.00 | Y/N | Planned Outage /
29 | BLN-STK-1 | I | CCT | 110 | 1.17 | 0.02 | 0.00 | 0.00 | 0.00 | 0.00 | 3.00 | 0.00 | N/N | Planned Outage /
30 | BLN-STK-2 | I | CCT | 110 | 0.00 | 0.01 | 0.00 | 0.00 | 0.00 | 0.00 | 2.00 | 0.00 | N/N
31 | BOB-HAM-1 | I | CCT | 110 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N
32 | BOB-HAM-2 | I | CCT | 110 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N
33 | BPE-MTN-WGN-1 | B | CCT | 110 | 4.03 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
34 | BPE-MTN-WGN-2 | B | CCT | 110 | 0.98 | 0.09 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/Y | 14-Oct-2024: BPE-MTN-WGN-2 tripped, for a blue phase to earth fault, only BPE CB212 A/R, probably caused by a lightning strike. MTN T2 remained in service, it did not trip. The circuit was not patrolled. | No further action. | SN24157
35 | [13 empty] | 07-Jan-2025: BPE-MTN-WGN-2 tripped, red phase to earth fault, no A/R, patrol found no cause. | No fault found. No further action. | SN25003
36 | BPE-MTR-1 | I | CCT | 110 | 0.45 | 0.01 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
37 | BPE-WDV-1 | I | CCT | 110 | 0.18 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | N/N | Planned Outage /
38 | BPE-WDV-2 | I | CCT | 110 | 0.58 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | N/N | Planned Outage /
39 | CPK-WIL-1 | B | CCT | 110 | 1.23 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
40 | CPK-WWD-WIL-2 | B | CCT | 110 | 2.63 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
41 | CPK-WWD-WIL-3 | B | CCT | 110 | 0.18 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
42 | CST-HUI-1 | I | CCT | 110 | 1.17 | 0.09 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/Y | 19-Oct-2024: CST-HUI-1 tripped at CST CB142 via bus zone differential protection when CST-DS-154's insulator skirt exploded caused by a bird strike. | Red phase insulator was replaced and the contacts were ductored. No further action | SN24160
43 | CST-HUI-2 | I | CCT | 110 | 1.23 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
44 | CST-JRD-SFD-1 | B | CCT | 110 | 3.09 | 0.09 | 0.00 | 0.00 | 0.00 | 0.00 | 2.00 | 0.00 | Y/Y | Planned Outage /
45 | [13 empty] | 19-Oct-2024: CST-JRD-SFD-1 tripped only at CST via bus zone differential protection when CST-DS-154's insulator skirt exploded caused by a bird strike. | Red phase insulator was replaced and the contacts were ductored. No further action | SN24160
46 | CST-MNI-1 | I | CCT | 110 | 0.23 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
47 | CST-NPL-1 | I | CCT | 110 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N
48 | CST-NPL-2 | I | CCT | 110 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N
49 | CST-SFD-1 | I | CCT | 110 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N
50 | CST-SFD-2 | I | CCT | 110 | 4.56 | 0.09 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/Y | Planned Outage /
51 | [13 empty] | 19-Oct-2024: CST-SFD-2 tripped & A/R at CST & SFD. Note SFD CB222 tripped due to protection zone 1 over-reach. | Red phase insulator was replaced and the contacts were ductored. No further action | SN24160
52 | CST-SFD-3 | I | CCT | 110 | 4.45 | 0.07 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/Y | Planned Outage /
53 | [13 empty] | 31-Aug-2024: CST-CB-62 low SF6 in YPh pole, CST-SFD-3 RFS to top up SF6. | Top-up SF6 on CST-CB-62. Pole replacement complete. | SN24123
54 | [13 empty] | 13-Oct-2024: CST-CB-62 low SF6 in YPh, CST-SFD-3 RFS to top up SF6. | Top-up SF6 on CST-CB-62. Pole replacement complete. | SN24155
55 | DOB-RFN-IGH-2 | I | CCT | 110 | 5.87 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
56 | EDG-KAW-1 | I | CCT | 110 | 7.66 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
57 | EDG-KAW-2 | I | CCT | 110 | 2.19 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | Y/N | Planned Outage /
58 | EDG-OWH-2 | B | CCT | 110 | 7.48 | 0.06 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
59 | EDN-INV-1 | I | CCT | 110 | 2.81 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | Y/N | Planned Outage /
60 | FHL-RDF-1 | I | CCT | 110 | 2.13 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | Y/N | Planned Outage /
61 | FHL-RDF-2 | I | CCT | 110 | 1.32 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | N/N | Planned Outage /
62 | FHL-TUI-1 | I | CCT | 110 | 3.50 | 0.01 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
63 | FHL-WPW-1 | I | CCT | 110 | 1.49 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
64 | FHL-WPW-2 | I | CCT | 110 | 1.14 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | N/N | Planned Outage /
65 | GOR-ROX-1 | I | CCT | 110 | 8.76 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | Y/N | Planned Outage /
66 | HAM-KPO-1 | I | CCT | 110 | 1.20 | 0.03 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
67 | HAM-KPO-2 | I | CCT | 110 | 2.70 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
68 | HAY-TKR-1 | I | CCT | 110 | 0.42 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
69 | HAY-TKR-2 | I | CCT | 110 | 1.59 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
70 | HAY-UHT-1 | I | CCT | 110 | 0.35 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
71 | HAY-UHT-2 | I | CCT | 110 | 1.14 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
72 | HEN-HEP-1 | I | CCT | 110 | 1.32 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
73 | HEN-HEP-2 | I | CCT | 110 | 1.32 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
74 | HEN-HEP-3 | I | CCT | 110 | 4.20 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
75 | HEN-HEP-4 | I | CCT | 110 | 5.91 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
76 | HEN-MPE-1 | I | CCT | 110 | 21.82 | 0.00 | 0.00 | 0.00 | 1.00 | 2.43 | 4.00 | 1.00 | Y/Y | Planned Outage /
77 | [13 empty] | 18-Apr-2025: HEN-MPE-1 & 2 trip & A/R. LOS at MTO to Northpower. | No further action. | SN25056
78 | HEN-MPE-2 | I | CCT | 110 | 22.85 | 0.00 | 0.00 | 0.00 | 1.00 | 2.43 | 4.00 | 1.00 | Y/Y | Planned Outage /
79 | [13 empty] | 18-Apr-2025: HEN-MPE-1 & 2 trip & A/R. LOS at MTO to Northpower. | No further action. | SN25056
80 | HEP-ROS-1 | I | CCT | 110 | 0.39 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
81 | HEP-ROS-2 | I | CCT | 110 | 1.24 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
82 | HOR-KBY-ISL-1 | B | CCT | 110 | 9.23 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
83 | HOR-KBY-ISL-2 | B | CCT | 110 | 1.48 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
84 | HUI-MNI-1 | I | CCT | 110 | 1.80 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
85 | HWA-SFD-1 | I | CCT | 110 | 0.61 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | N/N | Planned Outage /
86 | HWA-WVY-1 | I | CCT | 110 | 0.10 | 0.03 | 0.00 | 0.00 | 0.00 | 0.00 | 2.00 | 0.00 | N/N | Planned Outage /
87 | HWB-ROX-1 | I | CCT | 110 | 4.01 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 2.00 | 0.00 | Y/N | Planned Outage /
88 | HWB-ROX-2 | I | CCT | 110 | 4.01 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
89 | IGH-KIK-1 | I | CCT | 110 | 6.34 | 0.24 | 0.00 | 0.00 | 1.00 | 1.96 | 5.00 | 5.00 | Y/Y | Planned Outage /
90 | [13 empty] | 30-May-2025: KIK-MCH-1 circuit section of IGH-MCH-KIK-1 tripped & A/R, followed by trip, A/R, trip as it had a permanent fault, conductor drop caused by fallen trees in strong winds & rain. LOS to NWT at MCH. Bph conductor repaired & KIK-MCH-1 circuit section RTS on 31/5/2025 at 1401. | Bridge replacement planned in September 2025, tree felling planned for end of financial year. | SS25047
91 | IGH-KIK-2 | B | CCT | 110 | 1.15 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | N/N | Planned Outage /
92 | IGH-ROB-1 | B | CCT | 110 | 3.11 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
93 | IGH-ROB-2 | B | CCT | 110 | 2.72 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
94 | KIK-STK-3 | I | CCT | 110 | 2.46 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
95 | KIN-TRK-1 | I | CCT | 110 | 1.57 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 4.00 | 0.00 | N/N | Planned Outage /
96 | KIN-TRK-2 | I | CCT | 110 | 1.45 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 3.00 | 0.00 | N/N | Planned Outage /
97 | KMO-MTM-1 | I | CCT | 110 | 0.09 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
98 | KMO-MTM-TGA-2 | B | CCT | 110 | 2.04 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
99 | KMO-TGA-1 | B | CCT | 110 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N
100 | KMO-TMI-1 | I | CCT | 110 | 3.22 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
101 | KPO-TMU-1 | I | CCT | 110 | 4.82 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
102 | MDN-MPE-1 | I | CCT | 110 | 3.37 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | Y/N | Planned Outage /
103 | MDN-MPE-2 | I | CCT | 110 | 3.86 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | Y/N | Planned Outage /
104 | MGM-MST-1 | I | CCT | 110 | 4.36 | 0.24 | 0.00 | 0.00 | 0.00 | 0.00 | 2.00 | 0.00 | Y/Y | Planned Outage /
105 | [13 empty] | 15-May-2025: MGM-MST1 RFS after car hit and broke wood pole 396. Human error incident caused by a member of the public. Broken pole replaced with concrete pole. Car vs pole incident. | Broken pole replaced with concrete pole. | SN25068
106 | MGM-WDV-1 | I | CCT | 110 | 0.03 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 2.00 | 0.00 | N/N | Planned Outage /
107 | MNG-OTA-1 | I | CCT | 110 | 0.39 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
108 | MNG-OTA-2 | I | CCT | 110 | 0.65 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
109 | MNG-ROS-1 | I | CCT | 110 | 1.12 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
110 | MNG-ROS-2 | I | CCT | 110 | 1.72 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
111 | MNI-MKE-SFD-1 | B | CCT | 110 | 3.28 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | Y/N | Planned Outage /
112 | MST-UHT-1 | I | CCT | 110 | 2.39 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
113 | MST-UHT-2 | I | CCT | 110 | 1.77 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
114 | MTR-OKN-1 | I | CCT | 110 | 1.33 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
115 | OAM-BPT-WTK-1 | B | CCT | 110 | 2.42 | 0.05 | 4.00 | 21.34 | 4.00 | 30.41 | 1.00 | 1.00 | Y/Y | Planned Outage /
116 | [13 empty] | 15-Aug-2024: OAM-BPT-WTK-1 trip, BPh-E fault, circuit patrol found magpie possible cause, LOS at BPT. | Bird's nests were removed and bird deterrent installed to stop Herons nesting on towers, but Magpies nesting appear to have caused these faults. Our service provider have run a line patrol in September. An ornithologist was engaged to monitor birds and see if they can make recommendations for better mitigations. | SS24069
117 | [13 empty] | 23-Aug-2024: OAM-BPT-WTK-1 trip, Bph-E fault, possible cause birds, LOS at BPT. | Bird's nests were removed and bird deterrent installed to stop Herons nesting on towers, but Magpies nesting appear to have caused these faults. Our service provider have run a line patrol in September. An ornithologist was engaged to monitor birds and see if they can make recommendations for better mitigations. | SS24076
118 | [13 empty] | 26-Apr-2025: OAM-BPT-WTK-1 trip, Rph-E fault, cause unknown, LOS at BPT and OAM. | No fault found. No further action. | SS25035
119 | OAM-STU-BPD-WTK-2 | B | CCT | 110 | 1.22 | 0.04 | 1.00 | 7.12 | 2.00 | 8.83 | 0.00 | 1.00 | Y/Y | Planned Outage /
120 | [13 empty] | 28-Aug-2024: OAM-STU-BPD-WTK2 tripped, RPh-E fault, Cause bird's nests at str 80. LOS at BPD to Alpine Energy. TP advised ALP at 1030 that circuit was ready to be RTS. | Bird's nests were removed and bird deterrent installed to stop Herons nesting on towers, but Magpies nesting appear to have caused these faults. Our service provider have run a line patrol in September. An ornithologist was engaged to monitor birds and see if they can make recommendations for better mitigations. | SS24079
121 | [13 empty] | 26-Apr-2025: OAM-STU-BPD-WTK2 tripped. Cause unknown. LOS at BPD to Alpine Energy. | No fault found. No further action. | SS25034
122 | OKN-NPK-ONG-1 | B | CCT | 110 | 2.39 | 0.01 | 0.00 | 0.00 | 0.00 | 0.00 | 3.00 | 3.00 | Y/N | Planned Outage /
123 | OPK-SFD-1 | B | CCT | 110 | 5.25 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
124 | OTA-PEN-2 | I | CCT | 110 | 46.40 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
125 | OTA-ROS-1 | I | CCT | 110 | 21.62 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
126 | OTA-ROS-2 | I | CCT | 110 | 11.36 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
127 | OTA-WIR-1 | B | CCT | 110 | 1.57 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
128 | OTA-WIR-2 | B | CCT | 110 | 3.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
129 | RDF-TUI-1 | I | CCT | 110 | 2.86 | 0.35 | 0.00 | 0.00 | 0.00 | 0.00 | 2.00 | 0.00 | Y/Y | Planned Outage /
130 | [13 empty] | 13-Nov-2024: TUI-DS-166's red phase moving contact was not properly seated in the red phase fixed contact. RDF-TUI-1 RFS for repairs. Red phase moving arm and red phase fixed contact were replaced. | Repair carried out. No further action. | SN24179
131 | [13 empty] | 21-Dec-2024: RDF-TUI-1 RFS for the restoration of Hawkes Bay circuits. Note TUI-CB-162 was not opened. | No futher action. | SN24199
132 | RDF-TUI-2 | I | CCT | 110 | 2.30 | 0.01 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | Y/N | Planned Outage /
133 | STU-TIM-1 | I | CCT | 110 | 1.65 | 0.02 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 1.00 | N/N | Planned Outage /
134 | TKR-WIL-1 | I | CCT | 110 | 2.20 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
135 | TKR-WIL-2 | I | CCT | 110 | 1.74 | 0.01 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
136 | TMI-OWH-TRK-1 | B | CCT | 110 | 7.60 | 0.61 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | Y/Y | Planned Outage /
137 | [13 empty] | 24-Mar-2025: TRK-CB-142 RFS for a system split as TRK-TF-T2 RFS to repair an arcing fault on TRK-TF-ET2. | Neutral to earth link was installed between ET2 and grid earth. All primary supply cable were connected to ET2 earth bar. | SN25045
138 | WDV-DVK-WPW-1 | I | CCT | 110 | 3.31 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
139 | WDV-DVK-WPW-2 | I | CCT | 110 | 3.55 | 0.02 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
140 | WGN-WVY-1 | I | CCT | 110 | 1.21 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
141
142 | Asset | Type* | Asset Category | Sub Cat | Planned Unavailability % | Unplanned Unavailability % | Number Planned Interruptions | Planned Unserved Energy MWh | Number Unplanned Interruptions | Unplanned Unserved Energy MWh | Number of Outages <1 Min | Number of Interruptions <1 min | Measures Exceeded (plan/Unplan) ? | Incidents Affecting Performance | Steps Being Taken To Improve Performance | IDENT
143 | Index Measures for Asset Category |  | CCT | 220 | 0.88 | 0.05 | 0.00 | 0.00 | 0.13 | 9.87 | None Apply | None Apply
144 | ALB-HEN-3 | I | CCT | 220 | 5.03 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
145 | ALB-HPI-1 | B | CCT | 220 | 2.40 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
146 | ALB-SVL-2 | B | CCT | 220 | 3.34 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
147 | ALB-WRD-4 | I | CCT | 220 | 2.37 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
148 | ASB-BRY-1 | B | CCT | 220 | 3.08 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
149 | ASB-ISL-1 | B | CCT | 220 | 2.94 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
150 | ASB-TIM-TWZ-1 | I | CCT | 220 | 2.93 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | Y/N | Planned Outage /
151 | ASB-TIM-TWZ-2 | I | CCT | 220 | 1.36 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 2.00 | 0.00 | Y/N | Planned Outage /
152 | ATI-OHK-1 | I | CCT | 220 | 0.10 | 0.55 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | N/Y | 17-Feb-2025: ATI-OHK-1 delayed RTS because ATI CB112 VT selection switch left in wrong position and ATI-CB-112 failed to close. | VT selection switch position corrected circuit breaker returns to service. Nitrogen accumulator replaced. Investigation commenced to identify root cause. | SN25027
153 | ATI-TRK-1 | I | CCT | 220 | 1.83 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
154 | ATI-TRK-2 | I | CCT | 220 | 0.89 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
155 | ATI-WKM-1 | I | CCT | 220 | 0.17 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
156 | AVI-BEN-1 | I | CCT | 220 | 0.67 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
157 | AVI-BEN-2 | I | CCT | 220 | 0.62 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
158 | AVI-WTK-1 | I | CCT | 220 | 0.63 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
159 | BEN-OHB-1 | B | CCT | 220 | 0.09 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
160 | BEN-OHC-2 | B | CCT | 220 | 1.50 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
161 | BEN-TWZ-1 | I | CCT | 220 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N
162 | BPE-BRK-1 | I | CCT | 220 | 3.54 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | Y/N | Planned Outage /
163 | BPE-BRK-2 | I | CCT | 220 | 3.97 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
164 | BPE-LTN-2 | I | CCT | 220 | 0.48 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
165 | BPE-LTN-WIL-1 | I | CCT | 220 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N
166 | BPE-PRM-HAY-1 | B | CCT | 220 | 4.09 | 0.07 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | Y/Y | Planned Outage /
167 | [13 empty] | 16-Nov-2024: BPE-PRM-1 circuit section of BPE-PRM-HAY-1 RFS for the repair of BPE-DS-743. | As part of the repair, an M12 bolt installed to act as a pin to prevent future slipping of the mechanism which was the cause of the fault. | SN24182
168 | BPE-PRM-HAY-2 | B | CCT | 220 | 4.47 | 0.00 | 0.00 | 0.00 | 1.00 | 2.65 | 1.00 | 0.00 | Y/Y | Planned Outage /
169 | [13 empty] | 20-May-2025: BPE-PRM-HAY-2 trip & A/R for a Bph-E fault, cause unknown. PRM-TF-T2 trip & failed to A/R due to software bug. PRM-TF-T1 already out of service for planned maintenance. Total LOS at PRM to Electra Ltd. | Relay settings reviewed. They have identified an update is required. This change has now been implemented. | SN25069
170 | BPE-TKU-1 | B | CCT | 220 | 1.21 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
171 | BPE-TKU-2 | B | CCT | 220 | 2.54 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 2.00 | 0.00 | Y/N | Planned Outage /
172 | BPE-TNG-1 | B | CCT | 220 | 2.68 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | Y/N | Planned Outage /
173 | BPE-TWC-LTN-1 | B | CCT | 220 | 1.15 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
174 | BPE-WIL-1 | I | CCT | 220 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N
175 | BRB-HPI-1 | B | CCT | 220 | 7.41 | 0.26 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/Y | Planned Outage /
176 | [13 empty] | 22-Nov-2024: BRB-HPI-1 RTS delayed due to HPI-DS-324 fail to close during planned switching so unplanned outage. | DS324 has been selected to manual. This has a work order to fix the issue. | SN24185
177 | BRB-MDN-1 | B | CCT | 220 | 1.06 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
178 | BRK-SFD-1 | I | CCT | 220 | 4.86 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
179 | BRK-SFD-2 | I | CCT | 220 | 4.91 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
180 | BRK-SFD-3 | I | CCT | 220 | 1.26 | 0.01 | 0.00 | 0.00 | 0.00 | 0.00 | 2.00 | 0.00 | Y/N | Planned Outage /
181 | BRY-ISL-1 | B | CCT | 220 | 2.72 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
182 | CYD-CML-TWZ-1 | I | CCT | 220 | 0.87 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
183 | CYD-CML-TWZ-2 | I | CCT | 220 | 0.63 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | N/N | Planned Outage /
184 | CYD-ROX-1 | I | CCT | 220 | 0.62 | 0.01 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
185 | CYD-ROX-2 | I | CCT | 220 | 1.16 | 0.10 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/Y | Planned Outage /
186 | [13 empty] | 02-Nov-2024: CYD-ROX-2 trip & A/R, Y-B, then R-Y fault, trip, possible clashing conductors due to strong winds. A patrol between structures 4 and 27 found no faults. | No fault found. Review of clearances identified significant galloping risks. Investigation project established for delivery in FY27. | SS24096
187 | [13 empty] | 10-May-2025: CYD-ROX-2 delayed RTS when CYD-CB-462 failed to open, after Black Start test completed, caused by the failure of CB control system contactor. Faulty contactor was replaced. | The contactor was replaced with spare available on-site. Ongoing monitoring for this failure mode. | SS25040
188 | DRY-BOB-HLY-1 | B | CCT | 220 | 2.65 | 0.08 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/Y | Planned Outage /
189 | [13 empty] | 05-Jul-2024: HLY-CB-662 & HLY-CB-642 tripped via relay 642LDif1. This relay connected to CT's from CB642 and CB662. In ODJB662 the CT isolation switch was in direct contact with 250V motor supply cables. DC system arced and grounded to prot 1 CT secondary circuit as insulation had failed. | New fuse holders installed and isolation switch boot repaired. Wiring insulation resistance carried out with good results. CB tested to ensure spring charging. | SN24097
190 | [13 empty] | 25-Feb-2025: DRY-BOB-HLY-1 RFS for hot spot repair on HLY-DS-646 & 665, BOB-TF-T4 RFS for HLY DS repair. DRY-BOB-HLY-2 recalled. | Hot spot was fixed, switch contacts were checked and cleaned, and pin through arm was checked. | SN25034
191 | DRY-BOB-HLY-2 | B | CCT | 220 | 2.45 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | Y/N | Planned Outage /
192 | DRY-OTA-1 | B | CCT | 220 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N
193 | DRY-TAK-OTA-1 | B | CCT | 220 | 1.32 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
194 | DRY-TAK-OTA-2 | B | CCT | 220 | 1.59 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
195 | EDG-KAW-3 | I | CCT | 220 | 9.29 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
196 | EDG-TRK-1 | I | CCT | 220 | 9.31 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
197 | EDG-TRK-2 | I | CCT | 220 | 5.67 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
198 | HAM-OHW-1 | I | CCT | 220 | 1.92 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
199 | HAM-WKM-1 | I | CCT | 220 | 2.11 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
200 | HAY-WIL-LTN-1 | I | CCT | 220 | 5.13 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
201 | HAY-WIL-LTN-2 | I | CCT | 220 | 5.30 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
202 | HEN-HPI-1 | I | CCT | 220 | 1.20 | 0.08 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/Y | Planned Outage /
203 | [13 empty] | 23-Nov-2024: HEN-HPI-1 RFS, unplanned outage, for repair to HPI-DS-324 which failed to close during scheduled switching. | DS324 has been selected to manual. This has a work order to fix the issue. | SN24185
204 | HEN-OTA-1 | I | CCT | 220 | 3.52 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
205 | HEN-SWN-1 | I | CCT | 220 | 1.17 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
206 | HLY-OHW-1 | I | CCT | 220 | 0.85 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
207 | HLY-OHW-2 | I | CCT | 220 | 1.41 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
208 | HLY-OTA-2 | B | CCT | 220 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N
209 | HLY-SFD-1 | I | CCT | 220 | 0.92 | 0.01 | 0.00 | 0.00 | 0.00 | 0.00 | 5.00 | 0.00 | Y/N | Planned Outage /
210 | HLY-TWH-1 | B | CCT | 220 | 0.39 | 0.03 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
211 | HOB-PEN-1 | I | CCT | 220 | 0.72 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
212 | HOB-WRD-1 | I | CCT | 220 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N
213 | HPI-MDN-1 | I | CCT | 220 | 10.30 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
214 | HRP-RDF-1 | I | CCT | 220 | 2.65 | 0.02 | 0.00 | 0.00 | 6.00 | 277.69 | 0.00 | 0.00 | Y/Y | Planned Outage /
215 | [13 empty] | 21-Dec-2024: WHI-WRK-1 single ph trip, Bph-E, HRP-TAB-1 3ph trip, TAB-WRK-1, Bph-E, caused by lightning, LOS to Unison Networks Ltd at WTU. | No further action. | SN24199
216 | HRP-TAB-1 | I | CCT | 220 | 1.29 | 0.01 | 0.00 | 0.00 | 6.00 | 277.69 | 2.00 | 0.00 | Y/Y | Planned Outage /
217 | [13 empty] | 21-Dec-2024: WHI-WRK-1 single ph trip, Bph-E, HRP-TAB-1 3ph trip, TAB-WRK-1, Bph-E, caused by lightning, LOS to Unison Networks Ltd at WTU. | No further action. | SN24199
218 | HWB-SDN-1 | B | CCT | 220 | 4.72 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
219 | HWB-TMH-1 | B | CCT | 220 | 1.19 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
220 | INV-MAN-2 | B | CCT | 220 | 2.77 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
221 | INV-NMA-1 | B | CCT | 220 | 4.27 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
222 | INV-ROX-1 | I | CCT | 220 | 1.27 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
223 | INV-ROX-2 | I | CCT | 220 | 0.90 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
224 | INV-TWI-1 | I | CCT | 220 | 2.18 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
225 | INV-TWI-2 | I | CCT | 220 | 3.91 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
226 | ISL-KIK-1 | I | CCT | 220 | 5.23 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 5.00 | 0.00 | Y/N | Planned Outage /
227 | ISL-LIV-1 | I | CCT | 220 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N
228 | ISL-NWD-1 | I | CCT | 220 | 1.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
229 | ISL-TKB-1 | B | CCT | 220 | 0.62 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 4.00 | 0.00 | N/N | Planned Outage /
230 | ISL-WPR-CUL-KIK-2 | B | CCT | 220 | 1.55 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
231 | ISL-WPR-CUL-KIK-3 | B | CCT | 220 | 1.34 | 0.05 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
232 | KAW-OHK-1 | I | CCT | 220 | 3.37 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | Y/N | Planned Outage /
233 | KIK-STK-1 | I | CCT | 220 | 0.66 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
234 | KIK-STK-2 | I | CCT | 220 | 1.84 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
235 | KMO-TRK-1 | I | CCT | 220 | 1.46 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
236 | KMO-TRK-2 | I | CCT | 220 | 1.63 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
237 | LIV-NSY-1 | I | CCT | 220 | 1.26 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
238 | LIV-WTK-1 | I | CCT | 220 | 0.88 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | Y/N | Planned Outage /
239 | MAN-NMA-1 | B | CCT | 220 | 7.73 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
240 | MAN-NMA-2 | B | CCT | 220 | 6.63 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
241 | MAN-NMA-3 | B | CCT | 220 | 5.46 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
242 | NMA-GOR-TMH-1 | I | CCT | 220 | 5.51 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
243 | NMA-GOR-TMH-2 | I | CCT | 220 | 6.67 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
244 | NMA-TWI-1 | B | CCT | 220 | 8.33 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
245 | NMA-TWI-2 | B | CCT | 220 | 8.11 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
246 | NPL-SFD-1 | I | CCT | 220 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N
247 | NPL-SFD-2 | I | CCT | 220 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N
248 | NSY-ROX-1 | I | CCT | 220 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | N/N
249 | OHB-TWZ-3 | B | CCT | 220 | 0.05 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
250 | OHC-TWZ-4 | B | CCT | 220 | 1.17 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
251 | OHK-WRK-1 | I | CCT | 220 | 1.20 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
252 | OHW-OTA-1 | I | CCT | 220 | 9.68 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
253 | OHW-OTA-2 | I | CCT | 220 | 6.27 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
254 | OHW-WKM-1 | I | CCT | 220 | 2.87 | 0.03 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
255 | OTA-HTU-WKM-1 | I | CCT | 220 | 597.71 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | Y/N | Planned Outage /
256 | OTA-HTU-WKM-2 | I | CCT | 220 | 485.35 | 14.93 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/Y | Planned Outage /
257 | [13 empty] | 21-May-2025: OTA-HTU-WKM-2 tripped & A/R for a yellow phase to earth fault, cause unknown. HTU DCB 282 was already open as T2 not yet commissioned. The circuit and cable section were patrolled. | Bird guarding being installed this financial year. | SN25070
258 | OTA-PAK-3 | I | CCT | 220 | 2.63 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
259 | OTA-PAK-4 | I | CCT | 220 | 1.76 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
260 | OTA-PEN-5 | I | CCT | 220 | 5.94 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
261 | OTA-PEN-6 | I | CCT | 220 | 1.97 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
262 | OTA-SWN-1 | I | CCT | 220 | 2.39 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
263 | OTA-WKM-1 | I | CCT | 220 | 8.33 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 3.00 | 0.00 | Y/N | Planned Outage /
264 | OTA-WKM-2 | I | CCT | 220 | 9.22 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | Y/N | Planned Outage /
265 | PAK-PEN-3 | I | CCT | 220 | 6.92 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
266 | PAK-WKM-1 | I | CCT | 220 | 1.50 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
267 | PAK-WKM-2 | I | CCT | 220 | 97.01 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
268 | RDF-WHI-1 | I | CCT | 220 | 0.33 | 0.01 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
269 | RDF-WRK-1 | I | CCT | 220 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N
270 | ROX-TMH-1 | I | CCT | 220 | 3.28 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
271 | ROX-TMH-2 | I | CCT | 220 | 0.64 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | N/N | Planned Outage /
272 | RPO-TNG-1 | B | CCT | 220 | 3.31 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
273 | RPO-WRK-1 | B | CCT | 220 | 0.96 | 0.29 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | Y/Y | Planned Outage /
274 | [13 empty] | 18-Oct-2024: RPO-WRK-1 RFS on a SNOR as RPO-DS-526 was not closed properly. Repairs and adjustments required especially on blue phase. | RPO-DS-526 was removed from service and a maintenance service undertaken to correct alignment issues. No further action. | SN24162
275 | [13 empty] | 20-Dec-2024: RPO-WRK-1 tripped & A/R, yellow phase to earth fault, patrol on 23/12/2024 found large bird's nest on structure BPE-WRK-A0452, above the yellow phase insulator string. Service provider removed nest and cleaned insulator string during planned outage on 24/12/2024 from 0905 to 1309. | Service provider removed bird's nest on the structure. Birds nest is not a systemic issue on this line. | SN24195
276 | SDN-TMH-1 | B | CCT | 220 | 2.16 | 0.11 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/Y | Planned Outage /
277 | [13 empty] | 08-Feb-2025: SDN-DS-477 failed to close as its contacts were out of alignment. SDN-TMH-1, & SDN-BS-220-447-477-497 RFS to repair SDN-DS-477. | SDN-DS-477 was repaired to get the contacts aligned. Ground settlement is causing misalignment issues at SDN. Investigation underway to address the geotech issues at this site. | SS25014
278 | SFD-TMN-1 | I | CCT | 220 | 1.21 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 3.00 | 0.00 | Y/N | Planned Outage /
279 | TAB-WRK-1 | I | CCT | 220 | 0.11 | 0.01 | 0.00 | 0.00 | 6.00 | 277.69 | 0.00 | 0.00 | N/Y | 21-Dec-2024: WHI-WRK-1 single ph trip, Bph-E, HRP-TAB-1 3ph trip, TAB-WRK-1, Bph-E, caused by lightning, LOS to Unison Networks Ltd at WTU. | No further action. | SN24199
280 | THI-WKM-1 | B | CCT | 220 | 0.65 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
281 | THI-WRK-1 | B | CCT | 220 | 0.94 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
282 | TKB-TWZ-1 | B | CCT | 220 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N
283 | TKU-WKM-1 | B | CCT | 220 | 7.55 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
284 | TKU-WKM-2 | B | CCT | 220 | 6.88 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | Y/N | Planned Outage /
285 | TMN-TWH-1 | B | CCT | 220 | 1.20 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | Y/N | Planned Outage /
286 | WHI-WRK-1 | I | CCT | 220 | 3.98 | 0.01 | 0.00 | 0.00 | 6.00 | 277.69 | 2.00 | 0.00 | Y/Y | Planned Outage /
287 | [13 empty] | 21-Dec-2024: WHI-WRK-1 single phase trip, transient red phase to earth fault, A/R on red phase only. Vaisala FALLS recorded a lightning strike close to structure WRK-WHI-A0043. No patrol of the circuit. No LOS. | No further action. | SN24199
288 | WKM-WRK-1 | I | CCT | 220 | 0.68 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
289
290 | Asset | Type* | Asset Category | Sub Cat | Planned Unavailability % | Unplanned Unavailability % | Number Planned Interruptions | Planned Unserved Energy MWh | Number Unplanned Interruptions | Unplanned Unserved Energy MWh | Number of Outages <1 Min | Number of Interruptions <1 min | Measures Exceeded (plan/Unplan) ? | Incidents Affecting Performance | Steps Being Taken To Improve Performance | IDENT
291 | Index Measures for Asset Category |  | CCT | 66 | 1.25 | 0.08 | 0.14 | 0.46 | 1.31 | 1.88 | None Apply | None Apply
292 | ASY-SBK-1 | B | CCT | 66 | 0.13 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
293 | ASY-WPR-1 | B | CCT | 66 | 2.69 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
294 | COL-HOR-2 | I | CCT | 66 | 1.48 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
295 | COL-HOR-3 | I | CCT | 66 | 3.54 | 0.04 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
296 | COL-OTI-1 | I | CCT | 66 | 7.18 | 0.36 | 0.00 | 0.00 | 6.00 | 1.77 | 6.00 | 12.00 | Y/Y | Planned Outage /
297 | [13 empty] | 26-Oct-2024: COL-OTI-1 trip, A/R, trip, for a RPh - YPh fault, cause ice or snow, LOS to ORN at APS and CLH. The circuit was patrolled on 27/10/24 and found broken blue phase conductors between structures 231 to 232 and 232 and 233 in the Arthurs Pass to Castle Hill section of COL-OTI-A. | Hardware was repaired. Conductor clearance risks for snow to be mitigated when the pole replacements are due. | SS24091
298 | [13 empty] | 26-Oct-2024: COL-OTI-1 trip, A/R at OTI & COL, only COL272 tripped again with A/R lockout, Rph-E fault. Caused by snow & ice loading, momentary LOS at APS & CLH as load was fed from OTI. | Hardware was repaired. Conductor clearance risks for snow to be mitigated when the pole replacements are due. | SS24090
299 | [13 empty] | 26-Oct-2024: COL-OTI-1 trip & A/R for a Rph - Yph fault then trip for Yph-BPh fault &no A/R. LOS to ORN at APS & CLH. Cause ice or snow build up on conductors caused them to clash. Note CLH-COL-1 cct section already RFS. The circuit was patrolled on 27/10/24 and found broken blue phase. conductors 231-233. | Hardware was repaired. Conductor clearance risks for snow to be mitigated when the pole replacements are due. | SS24092
300 | [13 empty] | 26-Oct-2024: COL-OTI-1 trip, A/R, trip for a Yph-E fault then for Yph-BPh-E fault. LOS to ORN at APS & CLH. Cause ice or snow build up on conductors caused them to clash. Note CLH-COL-1 cct section already RFS. The circuit was patrolled on 27/10/24 and found broken blue phase conductors 231-233. | Hardware was repaired. Conductor clearance risks for snow to be mitigated when the pole replacements are due. | SS24093
301 | [13 empty] | 05-Dec-2024: APS-CLH-1 & COL-OTI-2 RFS, on a SNOR, due to a large scrub fire between double circuit poles between CLH & APS, no damage. | No further action. | SS24104
302 | COL-OTI-2 | I | CCT | 66 | 6.67 | 1.23 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/Y | Planned Outage /
303 | [13 empty] | 26-Oct-2024: COL-OTI-2 tripped, A/R, tripped. RPh-YPh-E fault caused by snow and ice loading. | Hardware was repaired. Conductor clearance risks for snow to be mitigated when the pole replacements are due. | SS24090
304 | [13 empty] | 05-Dec-2024: APS-CLH-1 & COL-OTI-2 RFS, on a SNOR, due to a large scrub fire between double circuit poles between CLH & APS, no damage. | No further action. | SS24104
305 | DOB-GYM-1 | I | CCT | 66 | 0.39 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
306 | GYM-KUM-1 | I | CCT | 66 | 3.79 | 0.08 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
307 | HKK-KUM-1 | B | CCT | 66 | 0.53 | 0.01 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
308 | HKK-OTI-2 | B | CCT | 66 | 5.29 | 0.02 | 0.00 | 0.00 | 1.00 | 4.27 | 0.00 | 0.00 | Y/Y | Planned Outage /
309 | [13 empty] | 16-Dec-2024: HKK-OTI-2 tripped, 3Ph fault, probably caused by lightning. SDTF recorded a lightning strike at 04:07:34 close to span 294 to 295 on AHA-OTI-A line. LOS at HKK. | No further action. | SS24107
310 | [13 empty] | 07-Apr-2025: HKK-OTI-2 tripped, Rph-E fault, patrolled no fault found, cause unknown. | No fault found. No further action. | SS25030
311 | ISL-SBK-1 | I | CCT | 66 | 1.03 | 0.22 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/Y | 17-Feb-2025: ISL-SBK-1 trip & A/R, trip, patrol found broken insulator at tower 29, repairs required. The root cause was a broken insulator stud due to incorrect installation. | Line to be reconductored in September 2025. | SS25016
312 | ISL-SBK-2 | I | CCT | 66 | 0.50 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
313 | KUM-OTI-1 | B | CCT | 66 | 4.94 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
314 | SBK-WPR-1 | I | CCT | 66 | 4.23 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
315
316 | Asset | Type* | Asset Category | Sub Cat | Planned Unavailability % | Unplanned Unavailability % | Number Planned Interruptions | Planned Unserved Energy MWh | Number Unplanned Interruptions | Unplanned Unserved Energy MWh | Number of Outages <1 Min | Number of Interruptions <1 min | Measures Exceeded (plan/Unplan) ? | Incidents Affecting Performance | Steps Being Taken To Improve Performance | IDENT
317 | Index Measures for Asset Category |  | Shunt | CAP_HV | 0.81 | 1.33 | 0.00 | 0.00 | 0.02 | 0.03 | None Apply | None Apply
318 | ALB-CAPS-C1 | I | Shunt | CAP_HV | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N
319 | ALB-CAPS-C2 | I | Shunt | CAP_HV | 0.41 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
320 | HAM-CAPS-C1 | I | Shunt | CAP_HV | 1.83 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
321 | HAM-CAPS-C2 | I | Shunt | CAP_HV | 5.78 | 1.11 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
322 | HEN-CAPS-C1 | I | Shunt | CAP_HV | 1.42 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
323 | HEP-CAPS-C11 | I | Shunt | CAP_HV | 12.60 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
324 | HEP-CAPS-C12 | I | Shunt | CAP_HV | 12.53 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
325 | HEP-CAPS-C13 | I | Shunt | CAP_HV | 0.36 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
326 | ISL-CAPS-C14 | I | Shunt | CAP_HV | 38.14 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
327 | ISL-CAPS-C15 | I | Shunt | CAP_HV | 100.00 | 100.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/Y | Planned Outage /
328 | [13 empty] | 01-Jul-2024: ISL-CAPS-C15 tripped due cap unbalance when insulator bushing exploded. | No fault found. Operations Engineering decided with advice from NZ Insulators that 33kV insulators be replaced with 66kV solid core insultarors. Extra weight from the upgrade means structure needs strengthening with extra support. Design still being carried out on design for support structure. | SS23117
329 | ISL-CAPS-C16 | I | Shunt | CAP_HV | 0.15 | 10.86 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/Y | 22-May-2025: ISL-CAPS-C16 unavailable for service, blown fuses, broken insulators, cause unknown, still investigated, accidentally found. C16 was already out of service prior to incident. Expected RTS 30 August 2025. | Materials ordered for repair. Repair planned for early 2026. | SS25042
330 | ISL-CAPS-C21 | I | Shunt | CAP_HV | 2.93 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
331 | ISL-CAPS-C22 | I | Shunt | CAP_HV | 0.81 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
332 | ISL-CAPS-C25 | I | Shunt | CAP_HV | 3.21 | 1.35 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/Y | Planned Outage /
333 | [13 empty] | 19-May-2025: ISL-CAPS-C25 unavailable for service due noises from R492 red phase. | Bolted joints of the coils (horizontal and vertical) inspected and found loose. Retightened as necessary. All fasteners were re-torqued. Internal spiderwebs using fibreglass struts also retightened. | SS25041
334 | ISL-CAPS-C26 | I | Shunt | CAP_HV | 2.14 | 1.66 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/Y | Planned Outage /
335 | [13 empty] | 22-Aug-2024: ISL-CB-5012 spring charge motor pin sheared off, C26 unavailable. The spring charge motor was replaced. | Spring charge motor was replaced. Service instruction issued to detune these spring tensions and improve component service life. | SS24075
336 | ISL-CAPS-C27 | I | Shunt | CAP_HV | 0.42 | 0.25 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
337 | MTM-CAPS-C1 | I | Shunt | CAP_HV | 0.40 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
338 | NMA-CAPS-C1 | I | Shunt | CAP_HV | 1.80 | 1.37 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/Y | Planned Outage /
339 | [13 empty] | 18-Oct-2024: NMA-CAPS-C1 tripped, via inverse time overcurrent protection probably caused by an overload due to the failure of capacitor cans. Two blue phase capacitor cans were replaced. | Two blue phase capacitor cans were replaced. | SS24088
340 | NMA-CAPS-C3 | I | Shunt | CAP_HV | 0.39 | 0.25 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
341 | OHW-CAPS-C1 | I | Shunt | CAP_HV | 0.04 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
342 | OHW-CAPS-C2 | I | Shunt | CAP_HV | 0.05 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
343 | OTA-CAPS-C11 | I | Shunt | CAP_HV | 0.08 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
344 | OTA-CAPS-C12 | I | Shunt | CAP_HV | 0.88 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
345 | OTA-CAPS-C29 | I | Shunt | CAP_HV | 0.08 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
346 | OTA-CAPS-C30 | I | Shunt | CAP_HV | 2.59 | 46.95 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/Y | Planned Outage /
347 | [13 empty] | 01-Jul-2024: OTA-CAPS-C30 tripped when OTA-CB-1422 tripped on close. CB1422 failed to latch closed and this was caused by worn anvils in its closing mechanism. | Replaced phase discrepancy relays on mechanism box for CB1422. Three closing arm anvils/ dogs, all 3 dashpots, all 3 close coil catch gears, opening coils and all 3 gearboxes on CB1422 were replaced. Tests were carried out. Then OTA-CAPS-C30 was made available for service. | SN24087
348 | OTA-CAPS-C31 | I | Shunt | CAP_HV | 3.87 | 3.08 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/Y | Planned Outage /
349 | [13 empty] | 23-Sep-2024: OTA-CAPS-C31 trip on close, C31 unavailable for service or RPC. CB1412 faulty, many parts replaced. | Repairs were carried out on CB1412 with several parts replaced. | SN24146
350 | PEN-CAPS-C1 | I | Shunt | CAP_HV | 3.41 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
351 | PEN-CAPS-C11 | I | Shunt | CAP_HV | 1.98 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
352 | PEN-CAPS-C12 | I | Shunt | CAP_HV | 1.39 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
353 | PEN-CAPS-C13 | I | Shunt | CAP_HV | 1.93 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
354 | PEN-CAPS-C14 | I | Shunt | CAP_HV | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N
355 | SBK-CAPS-C11 | I | Shunt | CAP_HV | 5.12 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
356 | TGA-CAPS-C11 | I | Shunt | CAP_HV | 1.22 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
357 | TMU-CAPS-C1 | I | Shunt | CAP_HV | 2.14 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
358 | TMU-CAPS-C2 | I | Shunt | CAP_HV | 2.16 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
359
360 | Asset | Type* | Asset Category | Sub Cat | Planned Unavailability % | Unplanned Unavailability % | Number Planned Interruptions | Planned Unserved Energy MWh | Number Unplanned Interruptions | Unplanned Unserved Energy MWh | Number of Outages <1 Min | Number of Interruptions <1 min | Measures Exceeded (plan/Unplan) ? | Incidents Affecting Performance | Steps Being Taken To Improve Performance | IDENT
361 | Index Measures for Asset Category |  | Shunt | CAP_LV | 0.81 | 1.33 | 0.00 | 0.00 | 0.02 | 0.03 | None Apply | None Apply
362 | BAL-CAPS-C1 | I | Shunt | CAP_LV | 0.67 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
363 | BAL-CAPS-C2 | I | Shunt | CAP_LV | 0.91 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
364 | BLN-CAPS-C1 | I | Shunt | CAP_LV | 0.01 | 4.48 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/Y | 26-Apr-2025: BLN-CB2082 spring change motor failed, BLN-CAPS-C1 RFS, motor was replaced | Spring charge motor replaced with a refurbished one, future work programme is going to remove these spring charge motors, refurbish and install to avoid any tripping of breaker due to burn out coils. | SS25037
365 | BLN-CAPS-C2 | I | Shunt | CAP_LV | 0.01 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
366 | BLN-CAPS-C3 | I | Shunt | CAP_LV | 0.00 | 1.09 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N
367 | BLN-CAPS-C4 | I | Shunt | CAP_LV | 0.01 | 0.27 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
368 | BRY-CAPS-C5A | I | Shunt | CAP_LV | 3.48 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 2.00 | 0.00 | Y/N | Planned Outage /
369 | BRY-CAPS-C7A | I | Shunt | CAP_LV | 1.01 | 1.59 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/Y | Planned Outage /
370 | [13 empty] | 02-Aug-2024: BRY-DS-2004 hot spots on red and blue phases as identified by Thermovision checks so forced outage to BRY-CAPS-C7A. Contacts were serviced. | Contacts serviced and returned to normal operating condition. | SS24067
371 | GYM-CAPS-C1 | I | Shunt | CAP_LV | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
372 | GYM-CAPS-C2 | I | Shunt | CAP_LV | 0.01 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
373 | GYM-CAPS-C3 | I | Shunt | CAP_LV | 0.01 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
374 | HKK-CAPS-C7 | I | Shunt | CAP_LV | 0.01 | 0.02 | 0.00 | 0.00 | 0.00 | 0.00 | 2.00 | 0.00 | N/N | Planned Outage /
375 | HKK-CAPS-C8 | I | Shunt | CAP_LV | 0.14 | 0.09 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
376 | HKK-CAPS-C9 | I | Shunt | CAP_LV | 0.00 | 1.55 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/Y | 30-Jul-2024: HKK-CAPS-C9 RFS for final repairs to HKK-CAPS-C7. | No further action. | SS22109
377 | [13 empty] | 29-Aug-2024: HKK-CAPS-C7, C8 and C9 tripped, no cause found. | No fault found. No further action. | SS24081
378 | [13 empty] | 16-Dec-2024: HKK-CAPS-C7, HKK-CAPS-C8, HKK-CAPS-C7 RFS to investigate CB fault alarms following the circuit trippings. The 400V to 110V power supply transformer had tripped. Reset the MCBs and cleared the RPC alarms. | No further action. | SS24107
379 | KTA-CAPS-C1 | I | Shunt | CAP_LV | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N
380 | KTA-CAPS-C11 | I | Shunt | CAP_LV | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N
381 | KTA-CAPS-C21 | I | Shunt | CAP_LV | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N
382 | KTA-CAPS-C31 | I | Shunt | CAP_LV | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N
383 | ONG-CAPS-C1 | I | Shunt | CAP_LV | 1.20 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
384 | STK-CAPS-C31 | I | Shunt | CAP_LV | 0.02 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
385 | STK-CAPS-C32 | I | Shunt | CAP_LV | 0.02 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
386 | STK-CAPS-C33 | I | Shunt | CAP_LV | 0.14 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
387 | STK-CAPS-C34 | I | Shunt | CAP_LV | 0.03 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
388
389 | Asset | Type* | Asset Category | Sub Cat | Planned Unavailability % | Unplanned Unavailability % | Number Planned Interruptions | Planned Unserved Energy MWh | Number Unplanned Interruptions | Unplanned Unserved Energy MWh | Number of Outages <1 Min | Number of Interruptions <1 min | Measures Exceeded (plan/Unplan) ? | Incidents Affecting Performance | Steps Being Taken To Improve Performance | IDENT
390 | Index Measures for Asset Category |  | Shunt | Filter | 1.03 | 1.71 | 0.00 | 0.00 | 0.00 | 0.00 | None Apply | None Apply
391 | S1.20DB72-FB5 | I | Shunt | Filter | 4.84 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
392 | S1.20DB74-FB6 | I | Shunt | Filter | 4.61 | 1.62 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
393 | S1.20DB80-FB7 | I | Shunt | Filter | 4.56 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
394 | S1.WA-Z1.FB4 | I | Shunt | Filter | 0.63 | 0.49 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
395 | S1.WA-Z2.FB3 | I | Shunt | Filter | 0.64 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
396 | S4.10DC96-FB6 | I | Shunt | Filter | 5.06 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
397 | S4.10DC98-FB5 | I | Shunt | Filter | 1.85 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
398 | S4.10DC98.A-FB5A | I | Shunt | Filter | 1.71 | 38.19 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/Y | Planned Outage /
399 | [13 empty] | 31-Jan-2025: HAY-F5A tripped when CB982A's yellow phase pole exploded. Yellow phase pole was replaced. | CB was replaced with spare. Other CBs of same design at HAY/BEN to be internally inspected to confirm they are not affected by defect which caused the CB982A failure. Point on wave relay settings to be changed to tighten alarm settings | SN25014
400 | S4.10DC98.A-FB5B | I | Shunt | Filter | 4.18 | 2.07 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/Y | Planned Outage /
401 | [13 empty] | 31-Jan-2025: HAY-F5B tripped when CB982A's yellow phase pole exploded. Yellow phase pole was replaced. | CB was replaced with spare. Other CBs of same design at HAY/BEN to be internally inspected to confirm they are not affected by defect which caused the CB982A failure. Point on wave relay settings to be changed to tighten alarm settings | SN25014
402 | [13 empty] | 07-Feb-2025: HAY-F5B RTS delayed due to HAY-DS-981 open on 1 phase, only 2 phases closed, caused by a worn selector switch that is part of its lockout sequence controls. There is play in the movement of this switch which must be pushed all the way home. | HAY-DS-981 was opened and closed again to restore the disconnector. | SN25023
403 | S4.10E04-FB7 | I | Shunt | Filter | 8.54 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
404 | S4.10E22-FB8 | I | Shunt | Filter | 1.15 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
405 | S4.WA-Z1.FB4 | I | Shunt | Filter | 1.18 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
406 | S4.WA-Z1.Z1.FB4A | I | Shunt | Filter | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N
407 | S4.WA-Z1.Z2.FB4B | I | Shunt | Filter | 0.00 | 0.03 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N
408 | S4.WA-Z2.FB3 | I | Shunt | Filter | 1.77 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
409 | S4.WA-Z2.Z1.FB3A | I | Shunt | Filter | 0.00 | 0.36 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N
410 | S4.WA-Z2.Z2.FB3B | I | Shunt | Filter | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N
411
412 | Asset | Type* | Asset Category | Sub Cat | Planned Unavailability % | Unplanned Unavailability % | Number Planned Interruptions | Planned Unserved Energy MWh | Number Unplanned Interruptions | Unplanned Unserved Energy MWh | Number of Outages <1 Min | Number of Interruptions <1 min | Measures Exceeded (plan/Unplan) ? | Incidents Affecting Performance | Steps Being Taken To Improve Performance | IDENT
413 | Index Measures for Asset Category |  | Shunt | REA | 1.33 | 0.31 | 0.00 | 0.00 | 0.00 | 0.00 | None Apply | None Apply
414 | HAY-REA-R1 | I | Shunt | REA | 2.68 | 0.99 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/Y | Planned Outage /
415 | [13 empty] | 22-Aug-2024: HAY-REA-R1 RFS for repairs to HAY-DS-75. | HAY-DS-75 fully overhauled and repaired. | SN24118
416 | [13 empty] | 21-Jan-2025: HAY-REA-R1 delayed RTS when HAY-TF-T1 's CB442 tripped on closing due to transformer inrush current caused by system operating conditions. Reactor R1 available for RPC at 1221. | Procedures revised to ensure livening done via BPE to reduce inrush current. | SN25007
417 | [13 empty] | 24-Jan-2025: HAY-TF-T1 RFS to restore links between SC1 and T1. | The faulty motor was replaced in March 2025 during a planned outage. | SN25009
418 | ISL-REA-R492 | I | Shunt | REA | 3.46 | 2.05 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/Y | Planned Outage /
419 | [13 empty] | 19-May-2025: ISL-REA-R492 RFS for noises coming from R492 red phase, loose bolts on the inner circle of the webs. Bolts were retightened | Bolted joints of the coils (horizontal and vertical) inspected and found loose. Retightened as necessary. All fasteners were re-torqued. Internal spiderwebs using fibreglass struts also retightened. | SS25041
420 | KIK-REA-R182 | I | Shunt | REA | 0.23 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
421 | OTA-REA-R472 | I | Shunt | REA | 0.12 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
422 | PAK-REA-R562 | I | Shunt | REA | 847.36 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
423 | PAK-REA-R582 | I | Shunt | REA | 1360.90 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
424 | PEN-REA-862 | I | Shunt | REA | 0.72 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
425 | WRD-REA-R182 | I | Shunt | REA | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N
426
427 | Asset | Type* | Asset Category | Sub Cat | Planned Unavailability % | Unplanned Unavailability % | Number Planned Interruptions | Planned Unserved Energy MWh | Number Unplanned Interruptions | Unplanned Unserved Energy MWh | Number of Outages <1 Min | Number of Interruptions <1 min | Measures Exceeded (plan/Unplan) ? | Incidents Affecting Performance | Steps Being Taken To Improve Performance | IDENT
428 | Index Measures for Asset Category |  | Shunt | SCM | 2.00 | 1.00 | 0.00 | 0.00 | 0.00 | 0.00 | None Apply | None Apply
429 | HAY-SC1 | I | Shunt | SCM | 13.44 | 0.85 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
430 | HAY-SC10 | I | Shunt | SCM | 40.34 | 0.05 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
431 | HAY-SC2 | I | Shunt | SCM | 2.29 | 0.01 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
432 | HAY-SC3 | I | Shunt | SCM | 2.07 | 4.18 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/Y | Planned Outage /
433 | [13 empty] | 05-Nov-2024: HAY-SC3 RFS for high winding temperature, cooling tower motor replaced. Motor overload relay was faulty and caused the issue. Follow on fault from that of 1/11/24. | HAY SC3/4 controls and excitation will be replaced in 2026. | SN24169
434 | [13 empty] | 08-Dec-2024: HAY-SC3 RFS to repair sparking brushes. | Monitor brushes after repairs. | SN24189
435 | [13 empty] | 05-Feb-2025: HAY-SC3 RFS for high winding temperature alarms. | HAY SC3/4 controls and excitation will be replaced in 2026. | SN25021
436 | HAY-SC4 | I | Shunt | SCM | 4.88 | 5.56 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/Y | Planned Outage /
437 | [13 empty] | 05-Feb-2025: HAY-S-4 tripped on start up after a planned outage. | HAY SC3/4 controls and excitation will be replaced in 2026. | SN25020
438 | [13 empty] | 20-Apr-2025: HAY-SC4 tripped, suspect measuring fault. | Measuring transducer was replaced. HAY SC3/4 controls and excitation will be replaced in 2026. | SN25057
439 | [13 empty] | 08-May-2025: HAY-SC4 tripped for a faulty LEM current module, a CT like device for measuring field current. | HAY SC3/4 controls and excitation will be replaced in 2026. | SN25073
440 | HAY-SC7 | I | Shunt | SCM | 3.34 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
441 | HAY-SC8 | I | Shunt | SCM | 6.96 | 1.03 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/Y | Planned Outage /
442 | [13 empty] | 01-Oct-2024: HAY-SC8 & T8 tripped while technician investigating SC7 & SC8 SEL-700G protection alarms. Trip occurred when relay was power cycled. It appears that SEL-700G relay tripped but it is unsure why. | Switch was tested as suspect this to be cause of trip. Switch to be replaced. | SN24147
443 | [13 empty] | 28-Jan-2025: HAY-SC8 tripped on start, control system fault. | Interface between T3000 and ABB excitation will be reviewed after SC3-4 upgrade completed. | SN25010
444 | [13 empty] | 04-Apr-2025: HAY-SC1, SC2, SC7&SC8 tripped due to error while removing logic associated with (UPS) systems which were physically decommissioned by a project in 2024. The engineer who made the change believed that the software being removed was only related to SCADA alarms and not control of SC1,2,7 and 8 | Internal procedures for work on control systems reinforced with HVDC & Power Electronics engineering team. | SN25047
445 | HAY-SC9 | I | Shunt | SCM | 1.58 | 7.96 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/Y | 22-Aug-2024: HAY-SC9 & T9 trip, faulty speed transducer was replaced. | Speed transducer replaced. Investigating code change to use key phasor as back-up if main transducer is lost. | SN24119
446 | [13 empty] | 11-Nov-2024: HAY-SC9 & T9 trip, relay 59D element setting in Beckwith relay not suitable minor change needed to setting to block out 3rd harmonic element when value is low. Also, the 59D element was to be replaced by a 27TN element in the relay. | Settings updated and fix also rolled out to SC7, 8, and 10. | SN24178
447 | [13 empty] | 09-Dec-2024: HAY-SC9 failed to start after planned outage, T9 RFS, 11kV CB2612 did not close. HAY-SC9 available for RPC at 1932. | Tested CB2612 but no fault found. Continue to monitor CB. | SN24190
448 | [13 empty] | 03-Jun-2025: HAY-SC9 & T9 RFS as SC9 was making an abnormal noise. | Initial inspection noted abnormal noise and wear pattern on commutator. Recommend a more indepth testing and evaluation of commutator. | SN25077
449
450 | Asset | Type* | Asset Category | Sub Cat | Planned Unavailability % | Unplanned Unavailability % | Number Planned Interruptions | Planned Unserved Energy MWh | Number Unplanned Interruptions | Unplanned Unserved Energy MWh | Number of Outages <1 Min | Number of Interruptions <1 min | Measures Exceeded (plan/Unplan) ? | Incidents Affecting Performance | Steps Being Taken To Improve Performance | IDENT
451 | Index Measures for Asset Category |  | Shunt | SVC | 0.82 | 0.04 | 0.00 | 0.00 | 0.00 | 0.00 | None Apply | None Apply
452 | ALB-SVC-7 | I | Shunt | SVC | 4.89 | 0.06 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/Y | Planned Outage /
453 | [13 empty] | 22-Aug-2024: ALB-CB-822 SF6 alarm, SVC7 and T7 RFS to top up CB822, gauges replaced later also. | No further action. | SN24120
454 | [13 empty] | 08-Nov-2024: ALB-SVC-7 and T7 tripping was due to control system 2 unexpectedly sending a trip signal when it was powered up. Control system 2 was powered down again and any further testing would likely need outages. Issue with control system 1 & 2 not working together. | UPS battery has been replaced. UPS is ageing and due for replacement during ALB-SVC7 controls upgrade. Controls due for refurbishment in 2027/28. | SN24176
455 | HAM-STC-3 | I | Shunt | SVC | 0.31 | 0.15 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/Y | 02-Jan-2025: HAM-STC-3 RFS for a cooling system leak repair. De-ionising chamber replaced. | Hitachi replaced defective ion exchange resin tank. | SN25001
456 | ISL-SVC-3 | I | Shunt | SVC | 24.28 | 0.77 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/Y | Planned Outage /
457 | [13 empty] | 12-Feb-2025: ISL-SVC-3 RFS for high neutral current due to a MEN link applied between neutral and earth at 400V switch board as per Transpower specifications & improve safety. MEN link to resolve induced voltage in the neutral cable that became hot. MEN link removed. | MEN link was removed. Engineering solution in development for completion this financial year. | SS25015
458 | [13 empty] | 23-Jun-2025: ISL-SVC-3 RFS due to water leak in thyristor valve. Pipe connection O-ring was pinched and was replaced | Hitachi replaced o-rings as SVC3 is still under warranty. | SS25053
459 | ISL-SVC-9 | I | Shunt | SVC | 1.27 | 0.08 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/Y | Planned Outage /
460 | [13 empty] | 18-Feb-2025: ISL-SVC-9 RFS to replace faulty UPS module. | Fault was traced to a faulty stabiliser. Job has been raised to replace/ upgrade it by December 2025. | SS25017
461 | [13 empty] | 26-Mar-2025: ISL-SVC-9 tripped when LIV-NWD-1 tripped for a Bph-E fault. The UPS for SVC9 was faulty & external cct trip caused UPS to stop working which led to SVC9 tripping. | Fault was traced to a faulty stabiliser. Job has been raised to replace/ upgrade it by December 2025. | SS25028
462 | [13 empty] | 07-Jun-2025: ISL-SVC-9 tripped, no cause found. | Fault not found. Monitor for future faults. | SS25050
463 | KIK-STC-2 | I | Shunt | SVC | 1.48 | 0.16 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/Y | Planned Outage /
464 | [13 empty] | 28-Aug-2024: KIK-STC-2B tripped due to a TDC hardware fault. TDC was power cycled to clear the fault. | No fault found. TDC was rebooted to clear the fault. | SS24080
465 | MDN-STC-5 | I | Shunt | SVC | 3.09 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
466 | MDN-STC-6 | I | Shunt | SVC | 4.57 | 1.26 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/Y | Planned Outage /
467 | [13 empty] | 01-May-2025: MDN-STC-6 tripped for a faulty PLC flash card which contains the running control code. This faulty flash card was replaced. | The faulty flash card was replaced. | SN25061
468 | PEN-STC-1 | I | Shunt | SVC | 0.34 | 56.46 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/Y | 01-Jul-2024: PEN-STC-1A trip on close when an attempt was made to RTS STC1 after a planned outage. Caused by a loose CT secondary wire in the control panel in the STC1A control room. STC-1B was already out of service, it was RFS on 20 May 2024 at 0732. | CT secondary wires re-terminated on test switch. CT was tested to ensure no damage to the CT from open circuit in secondary circuit. | SN24073
469 | [13 empty] | 29-Jan-2025: PEN-STC-1A tripped via its SVC Plus Controller caused by a faulty K31 relay in the water-cooling pump motor control circuit. K31 relay was replaced like for like (identical model and manufacturer). | Pump/Motor contactors replaced at PEN-STC1. Spares left on site. | SN25012
470 | [13 empty] | 27-Jan-2025: PEN-STC-1A tripped relay reset, control system went offline. | No actions planned. Rare communications fault on PLC card. | SN25016
471 | [13 empty] | 15-Jun-2025: PEN-STC-1A tripped, SVC Plus Controller - TDC rack hardware fault. Siemens controller was power cycled to reset. Control system went offline, it was a communication fault. | SVCPlus Controller was reset to fix the issue. | SN25086
472 | S4.10DB66-STC31 | I | Shunt | SVC | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N
473 | S4.10J01-STC31 | I | Shunt | SVC | 2.84 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
474
475 | Asset | Type* | Asset Category | Sub Cat | Planned Unavailability % | Unplanned Unavailability % | Number Planned Interruptions | Planned Unserved Energy MWh | Number Unplanned Interruptions | Unplanned Unserved Energy MWh | Number of Outages <1 Min | Number of Interruptions <1 min | Measures Exceeded (plan/Unplan) ? | Incidents Affecting Performance | Steps Being Taken To Improve Performance | IDENT
476 | Index Measures for Asset Category |  | TF | 110/066 | 2.25 | 0.02 | 0.00 | 0.00 | 0.00 | 0.00 | None Apply | None Apply
477 | DOB-TF-T11 | I | TF | 110/066 | 5.87 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
478 | DOB-TF-T12 | I | TF | 110/066 | 5.95 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | Y/N | Planned Outage /
479
480 | Asset | Type* | Asset Category | Sub Cat | Planned Unavailability % | Unplanned Unavailability % | Number Planned Interruptions | Planned Unserved Energy MWh | Number Unplanned Interruptions | Unplanned Unserved Energy MWh | Number of Outages <1 Min | Number of Interruptions <1 min | Measures Exceeded (plan/Unplan) ? | Incidents Affecting Performance | Steps Being Taken To Improve Performance | IDENT
481 | Index Measures for Asset Category |  | TF | 220/066 | 0.66 | 0.02 | 0.00 | 0.00 | 0.00 | 0.00 | None Apply | None Apply
482 | ISL-TF-T3 | I | TF | 220/066 | 3.51 | 0.01 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
483 | ISL-TF-T6 | I | TF | 220/066 | 0.93 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
484 | ISL-TF-T7 | I | TF | 220/066 | 0.17 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
485 | WPR-TF-T12 | I | TF | 220/066 | 5.51 | 0.00 | 0.00 | 0.00 | 2.00 | 1.58 | 0.00 | 0.00 | Y/Y | Planned Outage /
486 | [13 empty] | 16-Oct-2024: WPR-TF-T12, WPR-TF-T13, WPR-TF-T3, WPR-BS-66, WPR-BS-33, ASY-WPR-1 tripped via CBFail caused by human error by service provider on contract to Transpower working on CB102's protection. LOS to MainPower Ltd at WPR 66kV and 33kV. | Service provider has taken action to improve their process relating to CB fail. | SS24087
487 | WPR-TF-T13 | I | TF | 220/066 | 5.38 | 0.05 | 0.00 | 0.00 | 2.00 | 1.58 | 0.00 | 0.00 | Y/Y | Planned Outage /
488 | [13 empty] | 16-Oct-2024: WPR-TF-T13 tripped via CBFail protection caused by human error. | Service provider has taken action to improve their process relating to CB fail. | SS24087
489 | [13 empty] | 05-Jul-2024: ISL-WPR-CUL-KIK-3, CUL-TF-T23, WPR-TF-T13, ISL-CB-542 RFS to repair a hot spot (over heating) on KIK-CT-CT322. | Maintenance carried out on terminal palms and adapter plates to address the issue. | SS24060
490
491 | Asset | Type* | Asset Category | Sub Cat | Planned Unavailability % | Unplanned Unavailability % | Number Planned Interruptions | Planned Unserved Energy MWh | Number Unplanned Interruptions | Unplanned Unserved Energy MWh | Number of Outages <1 Min | Number of Interruptions <1 min | Measures Exceeded (plan/Unplan) ? | Incidents Affecting Performance | Steps Being Taken To Improve Performance | IDENT
492 | Index Measures for Asset Category |  | TF | 220/110 | 1.56 | 0.06 | 0.03 | 0.10 | 0.02 | 0.72 | None Apply | None Apply
493 | BOB-TF-T4 | I | TF | 220/110 | 2.65 | 0.07 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/Y | Planned Outage /
494 | [13 empty] | 25-Feb-2025: DRY-BOB-HLY-1 RFS for hot spot repair on HLY-DS-646 & HLY-DS-665, BOB-TF-T4 RFS for HLY DS repair. DRY-BOB-HLY-2 recalled. | Hot spot was fixed, switch contacts were checked and cleaned, and pin through arm was checked. | SN25034
495 | BOB-TF-T5 | I | TF | 220/110 | 2.45 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
496 | BPE-TF-T2 | I | TF | 220/110 | 0.19 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
497 | BPE-TF-T3 | I | TF | 220/110 | 0.06 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
498 | EDG-TF-T5 | I | TF | 220/110 | 0.91 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
499 | GOR-TF-T11 | I | TF | 220/110 | 6.69 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
500 | GOR-TF-T12 | I | TF | 220/110 | 6.67 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
501 | HAM-TF-T6 | I | TF | 220/110 | 0.54 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
502 | HAM-TF-T9 | I | TF | 220/110 | 0.10 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
503 | HAY-TF-T1 | I | TF | 220/110 | 2.68 | 0.98 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/Y | Planned Outage /
504 | [13 empty] | 22-Aug-2024: HAY-DS-73 arced when closed as DS-75 not fully closed on 2 phases and T1 tripped. | HAY-DS-75 fully overhauled and repaired. | SN24118
505 | [13 empty] | 21-Jan-2025: HAY-TF-T1's CB442 tripped on closing via EF(DefT)HV of relay 442Dif2 due to transformer inrush current caused by system operating conditions. There is now a NRT SCADA note for the livening of T1, T2 & T5. | Procedures revised to ensure livening done via BPE to reduce inrush current. | SN25007
506 | [13 empty] | 24-Jan-2025: HAY-TF-T1 RFS to restore links between SC1 and T1. | The faulty motor was replaced in March 2025 during a planned outage. | SN25009
507 | HAY-TF-T2 | I | TF | 220/110 | 2.27 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
508 | HAY-TF-T5 | I | TF | 220/110 | 1.99 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
509 | HEN-TF-T1 | I | TF | 220/110 | 2.69 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
510 | HEN-TF-T5 | I | TF | 220/110 | 1.90 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
511 | HWB-TF-T6 | I | TF | 220/110 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N
512 | INV-TF-T1 | I | TF | 220/110 | 2.81 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | Y/N | Planned Outage /
513 | KAW-TF-T12 | I | TF | 220/110 | 0.49 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
514 | KAW-TF-T13 | I | TF | 220/110 | 27.11 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
515 | KIK-TF-T1 | B | TF | 220/110 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N
516 | KIK-TF-T2 | B | TF | 220/110 | 1.45 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
517 | KMO-TF-T2 | I | TF | 220/110 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N
518 | KMO-TF-T4 | I | TF | 220/110 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N
519 | MDN-TF-T5 | I | TF | 220/110 | 3.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
520 | MDN-TF-T6 | I | TF | 220/110 | 4.57 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
521 | OTA-TF-T3 | I | TF | 220/110 | 2.38 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
522 | OTA-TF-T4 | I | TF | 220/110 | 1.19 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
523 | OTA-TF-T5 | I | TF | 220/110 | 2.55 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
524 | PEN-TF-T10 | I | TF | 220/110 | 16.53 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
525 | PEN-TF-T6 | I | TF | 220/110 | 5.97 | 0.26 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/Y | Planned Outage /
526 | [13 empty] | 03-Dec-2024: PEN-TF-T6 tripped, silica gel breather had bungs left in bottom, caused pressure build up and PRD to operate, oil expelled. | Safety Alert generated to inform everyone to be mindful of the seal that needs to be removed before installation. | SN24188
527 | RDF-TF-T3 | I | TF | 220/110 | 0.61 | 0.01 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
528 | RDF-TF-T4 | I | TF | 220/110 | 0.15 | 0.02 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
529 | ROX-TF-T10 | I | TF | 220/110 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N
530 | SFD-TF-T10 | I | TF | 220/110 | 2.32 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
531 | SFD-TF-T9 | I | TF | 220/110 | 0.45 | 0.37 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/Y | 07-Oct-2024: SFD-TF-T9 tripped via tap changer Buchholz trip (actually surge relay trip as alarms are common) due to water ingress into the surge relay cover. | Resealed the relay termination box to prevent moisture ingress. | SN24151
532 | [13 empty] | 07-Nov-2024: SFD-TF-T9 tripped via tap changer Buchholz trip (actually surge relay trip as alarms are common) due to water ingress into the surge relay cover. | Modified the Buchholz trip wiring to a SCADA alarm, and resealed the relay termination box to prevent moisture ingress. | SN24175
533 | STK-TF-T7 | I | TF | 220/110 | 1.84 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | Y/N | Planned Outage /
534 | TIM-TF-T5 | I | TF | 220/110 | 3.96 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.00 | 0.00 | Y/N | Planned Outage /
535 | TIM-TF-T8 | I | TF | 220/110 | 1.35 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 2.00 | 0.00 | N/N | Planned Outage /
536 | TRK-TF-T2 | I | TF | 220/110 | 4.22 | 0.61 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/Y | Planned Outage /
537 | [13 empty] | 24-Mar-2025: TRK-TF-ET2 arcing. The arcing occurred on the cable to drain leads. The neutral and drain wires had not been connected from ET2 to earth so TRK-TF-T2 RFS to remedy the issue | Neutral to earth link was installed between ET2 and grid earth. All primary supply cable were connected to ET2 earth bar. | SN25045
538 | TRK-TF-T3 | I | TF | 220/110 | 0.90 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | N/N | Planned Outage /
539 | WIL-TF-T8 | I | TF | 220/110 | 4.59 | 0.04 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | Y/N | Planned Outage /
540 | WTK-TF-T23 | I | TF | 220/110 | 1.21 | 0.04 | 0.00 | 0.00 | 2.00 | 8.83 | 0.00 | 0.00 | N/Y | 28-Aug-2024: WTK T23 tripped for OAM-STU-BPD-WTK2 fault, LOS. | Bird's nests were removed and bird deterrent installed to stop Herons nesting on towers, but Magpies nesting appear to have caused these faults. Our service provider have run a line patrol in September. An ornithologist was engaged to monitor birds and see if they can make recommendations for better mitigations. | SS24079
541 | [13 empty] | 26-Apr-2025: WTK-TF-T23 tripped for OAM-STU-BPD-WTK2 fault, LOS. | No fault found. No further action. | SS25034
542 | WTK-TF-T24 | I | TF | 220/110 | 1.36 | 0.05 | 1.00 | 0.69 | 2.00 | 29.49 | 1.00 | 0.00 | Y/Y | Planned Outage /
543 | [13 empty] | 26-Apr-2025: OAM-BPT-WTK-1 trip, Rph-E fault, cause unknown, LOS at BPT and OAM. | No fault found. No further action. | SS25035
544 | [13 empty] | 15-Aug-2024: OAM-BPT-WTK-1 trip, BPh-E fault, circuit patrol found magpie possible cause, LOS at BPT. | Bird's nests were removed and bird deterrent installed to stop Herons nesting on towers, but Magpies nesting appear to have caused these faults. Our service provider have run a line patrol in September. An ornithologist was engaged to monitor birds and see if they can make recommendations for better mitigations. | SS24069
545 | [13 empty] | 23-Aug-2024: OAM-BPT-WTK-1 trip, BPh-E fault, no circuit patrol possible cause birds nesting, LOS at BPT. The bird’s nests were removed at structures 91, 122, 123 and 124 on cct1. | Bird's nests were removed and bird deterrent installed to stop Herons nesting on towers, but Magpies nesting appear to have caused these faults. Our service provider have run a line patrol in September. An ornithologist was engaged to monitor birds and see if they can make recommendations for better mitigations. | SS24076
546
547 | Asset | Type* | Asset Category | Sub Cat | Planned Unavailability % | Unplanned Unavailability % | Number Planned Interruptions | Planned Unserved Energy MWh | Number Unplanned Interruptions | Unplanned Unserved Energy MWh | Number of Outages <1 Min | Number of Interruptions <1 min | Measures Exceeded (plan/Unplan) ? | Incidents Affecting Performance | Steps Being Taken To Improve Performance | IDENT
548 | Index Measures for Asset Category |  | HVDC | HVDC | 1.56 | 0.06 | 0.03 | 0.10 | 0.02 | 0.72 | None Apply | None Apply
549 | HVDC-BIPOLE |  | HVDC | HVDC | 2.56 | 0.65 | 0 | 0 | 0 | 0 | - | - | Y/N | Planned Outage /
550 | HVDC-POLE2 |  | HVDC | HVDC | 4.05 | 0.33 | 0 | 0 | 0 | 0 | - | - | Y/N | Planned Outage /
551 | HVDC-POLE3 |  | HVDC | HVDC | 1.49 | 0.87 | 0 | 0 | 0 | 0 | - | - | Y/N | Planned Outage /
552
553 | (1) Transpower’s asset management systems include plans and processes to maintain performance of all our assets, and to minimise the impact of events on customers and end-consumers. Events mentioned in this report will have been dealt with according to these plans and processes whether or not a specific response is given here.
554 | (2) Actions provided in the report are based on current available information.

## SO1. System Operator
|  |  |  | Transpower |  | Disclosure Date |  | 2025-10-24
SCHEDULE SO1: SYSTEM OPERATOR | [5 empty] | Disclosure Year (year ended) |  | 2025-06-30
ref
5 | SO1(i): Return on Investment
6 | [6 empty] | CY | CY
7 | [6 empty] | ($000) | ($000)
8 |  | Operating surplus/(deficit) |  |  |  |  | 18731191.3502
9 | less | Assets purchased or commissioned |  |  |  |  | 5986476.425
10 | less | Tax payable |  |  |  |  | 2517854.5388
11 |  | Notional cash flows for the year | [5 empty] | 10226860.3864
12
13 |  | Opening fixed assets | [5 empty] | -43913372.1856
14
15 |  | Closing fixed assets |  |  |  |  | 36972908.0921
16 | plus | Lost assets |  |  |  |  | 0
17 | less | Found assets |  |  |  |  | 0
18 |  | Adjusted closing fixed assets | [5 empty] | 36972908.0921
19
20
21 |  |  |  | CY-4 | CY-3 | CY-2 | CY-1 | CY
22 |  | Vanilla ROI |  | 23.52% | 10.96% | 10.3% | 10.09% | 8.448%
23
24 |  | Leverage (%) | ` | 42% | 42% | 42% | 42% | 42%
25 |  | Cost of debt (%) |  | 2.23% | 2.79% | 5.31% | 5.94% | 6.23%
26 |  | Corporate tax rate (%) |  | 28% | 28% | 28% | 28% | 28%
27
28 |  | Post-tax ROI |  | 23.26% | 10.63% | 9.673% | 9.394% | 7.715%
29
30 | SO1(ii): Regulatory Profit
31 |  |  |  | CY-4 | CY-3 | CY-2 | CY-1 | CY
32 |  |  |  | ($000) | ($000) | ($000) | ($000) | ($000)
33 |  | Total revenue |  | 42528920.28 | 41590965.45 | 46454101.75 | 49355603.28 | 50300674.07
34
35 | less | Operating expenditure |  | 20710450.5698 | 23122371.3924 | 25690107.234 | 27975450.0197 | 31569482.7198
36
37 |  | Operating surplus/(deficit) |  | 21818469.7102 | 18468594.0576 | 20763994.516 | 21380153.2603 | 18731191.3502
38
39 | less | Total depreciation |  | 10590779.7864 | 12253928.4572 | 14060800.3666 | 14564829.1823 | 12926940.5185
40
41 |  | Regulatory profit/(loss) before tax |  | 11227689.9238 | 6214665.6004 | 6703194.1495 | 6815324.078 | 5804250.8318
42
43 | less | Tax payable |  | 2812033.5997 | 1182820.7676 | 1671588.5127 | 2165300 | 2517854.5388
44
45 |  | Regulatory profit/(loss) after tax |  | 8415656.3241 | 5031844.8328 | 5031605.6368 | 4650024.078 | 3286396.293
46
47 | SO1(iii): Revenue
48 |  |  |  | CY-4 | CY-3 | CY-2 | CY-1 | CY
49 |  | Revenue |  | ($000) | ($000) | ($000) | ($000) | ($000)
50 |  | System operator service provider agreement revenue - operating |  | 26641688.04 | 27162644.04 | 28884630.68 | 30691110.5 | 31305160
|  | System operator service provider agreement revenue - capital |  | 15561106.7 | 13735212 | 16797069.51 | 17857031 | 18121508
52 |  | Technical services advisory revenue |  | 326125.54 | 693109.41 | 772401.56 | 807461.78 | 874006.07
53 |  | Other gains /(losses) (provide details)
54 |  | Total revenue |  | 42528920.28 | 41590965.45 | 46454101.75 | 49355603.28 | 50300674.07
55
56 |  |  |  | CY+1 | CY+2 | CY+3 | CY+4 | CY+5
57 |  | Revenue forecast |  | ($000) | ($000) | ($000) | ($000) | ($000)
58 |  | System operator service provider agreement revenue - operating |  | 35316234.7505 | 35847073.7988 | 36372993.3703 | 37829954.7742 | 38423707.3107
59 |  | System operator service provider agreement revenue - capital |  | 19665523 | 19600136 | 16671988 | 20899696 | 20899696
60 |  | Technical services advisory revenue |  | 602753 | 614808 | 627104 | 639646 | 652439
61 |  | Other gains /(losses) (provide details)
62 |  | Total forecast revenue |  | 55584510.7505 | 56062017.7988 | 53672085.3703 | 59369296.7742 | 59975842.3107
63
64 |  |  |  | CY-4 | CY-3 | CY-2 | CY-1 | CY
65 |  | Actual vs. forecast |  | ($000) | ($000) | ($000) | ($000) | ($000)
66 |  | Historical forecast revenue |  | 41966450.2208 | 41605327.1785 | 45725705.1703 | 49007369.4837 | 49900000
67 |  | Actual revenue |  | 42528920.28 | 41590965.45 | 46454101.75 | 49355603.28 | 50300674.07
68 |  | Variance ($) |  | -562470.0592 | 14361.7285 | -728396.5797 | -348233.7963 | -400674.07
69 |  | Variance (%) |  | -1.34% | 0.03452% | -1.593% | -0.7106% | -0.803%
70
71 | SO1(iv): Operating Expenditure
72 |  |  |  | CY-4 | CY-3 | CY-2 | CY-1 | CY
73 |  | Operating expenditure |  | ($000) | ($000) | ($000) | ($000) | ($000)
74 |  | Operating Costs |  | 15387327.7437 | 17571503.4853 | 19632397.7569 | 19868533.0981 | 21922013.3498
75 |  | IT Operations |  | 4420190.3537 | 5004667.6871 | 5223221.7371 | 6784151.6016 | 7918589.6899
76 |  | Investigation Expenses |  | 902932.4724 | 546200.22 | 834487.74 | 1322765.32 | 1728879.68
77 |  | [spare line]
78 |  | [spare line]
79 |  | Other opex
80 |  | Total operating expenditure |  | 20710450.5698 | 23122371.3924 | 25690107.234 | 27975450.0197 | 31569482.7198
81 |  | *Insert additional rows and update calculation of totals as needed
82 |  |  |  | CY+1 | CY+2 | CY+3 | CY+4 | CY+5
83 |  | Operating expenditure forecast |  | ($000) | ($000) | ($000) | ($000) | ($000)
84 |  | Operating Costs |  | 23899503.5816 | 24838717.0858 | 25569928.8441 | 26081327.421 | 26602953.9694
85 |  | IT Operations |  | 6647370.81 | 6791553.6325 | 7331567.4225 | 7478198.7709 | 7627762.7463
86 |  | Investigation Expenses |  | 1894918 | 1934772.09 | 2300292.0506 | 2346297.8916 | 2393223.8494
87 |  | [spare line]
88 |  | [spare line]
89 |  | Other opex
90 |  | Total forecast operating expenditure |  | 32441792.3916 | 33565042.8083 | 35201788.3171 | 35905824.0834 | 36623940.5651
91 |  | *Insert additional rows and update calculation of totals as needed
92 |  |  |  | CY-4 | CY-3 | CY-2 | CY-1 | CY
93 |  | Actual vs. forecast operating expenditure |  | ($000) | ($000) | ($000) | ($000) | ($000)
94 |  | Historical forecast operating expenditure |  | 20497484.5411 | 22671947.9047 | 25491613.7738 | 29044368.2283 | 32201612.9489
95 |  | Actual operating expenditure |  | 20710450.5698 | 23122371.3924 | 25690107.234 | 27975450.0197 | 31569482.7198
96 |  | Variance ($) |  | -212966.0287 | -450423.4877 | -198493.4601 | 1068918.2086 | 632130.2291
97 |  | Variance (%) |  | -1.039% | -1.987% | -0.7787% | 3.68% | 1.963%
98
99
100 | SO1(v): Capital Expenditure: Commissioned capex
101 |  |  |  | CY-4 | CY-3 | CY-2 | CY-1 | CY
102 |  | Capital expenditure |  | ($000) | ($000) | ($000) | ($000) | ($000)
103 |  | Buildings and grounds |  | 70514.6 | 6639.36 | 391027.3536 | 0 | 1.4552e-11
104 |  | IT market systems |  | 17516806.22 | 6089981.5 | 6995709.0063 | 5552200.14 | 5984932.6282
105 |  | IT market changes |  | 6106299.96 | 7208918.18 | 8087265 | 364421 | 0
106 |  | Other |  | 18210 | 2404137 | 1019183.823 | 0 | 1543.7968
107
108 |  | Capital Expenditure |  | 23711830.78 | 15709676.04 | 16493185.1829 | 5916621.14 | 5986476.425
109 |  | *Insert additional rows and update calculation of totals as needed
110 |  |  |  | CY+1 | CY+2 | CY+3 | CY+4 | CY+5
111 |  | Capital expenditure forecast |  | ($000) | ($000) | ($000) | ($000) | ($000)
112 |  | Buildings and grounds |  | 0 | 0 | 6218781.92 | 0 | 0
113 |  | IT market systems |  | 20028664.61 | 11283066.16 | 12130399.4 | 24228802.22 | 15531724.78
114 |  | IT market changes |  | 0 | 0 | 0 | 0 | 0
115 |  | Other |  | 314658.72 | 1099146.76 | 241347.84 | 253560.06 | 263803.86
116
117 |  | Total forecast capital expenditure |  | 20343323.33 | 12382212.92 | 18590529.16 | 24482362.28 | 15795528.64
118 |  | *Insert additional rows and update calculation of totals as needed
119 |  |  |  | CY-4 | CY-3 | CY-2 | CY-1 | CY
120 |  | Actual vs. forecast capital expenditure |  | ($000) | ($000) | ($000) | ($000) | ($000)
121 |  | Historical forecast capital expenditure |  | 20300246.74 | 18216151.9 | 19564292.44 | 10164024.16 | 11124953.87
122 |  | Actual capital expenditure |  | 23711830.78 | 15709676.04 | 16493185.1829 | 5916621.14 | 5986476.425
123 |  | Variance ($) |  | -3411584.04 | 2506475.86 | 3071107.2571 | 4247403.02 | 5138477.445
124 |  | Variance (%) |  | -16.81% | 13.76% | 15.7% | 41.79% | 46.19%
125
126 | SO1(vi): Fixed Assets: RAB equivalent values
127 |  |  |  | CY-4 | CY-3 | CY-2 | CY-1 | CY
128 |  |  |  | ($000) | ($000) | ($000) | ($000) | ($000)
129 |  | Opening fixed assets |  | 33552396.8351 | 46673447.8287 | 50129195.4115 | 52561580.2279 | 43913372.1856 | 43913.4
130 | plus | Found assets
131 | less | Disposed assets
132 | less | Lost assets
133 | plus | Assets purchased or commissioned |  | 23711830.78 | 15709676.04 | 16493185.1829 | 5916621.14 | 5986476.425 | 5986.5
134 | less | Total depreciation |  | 10590779.7864 | 12253928.4572 | 14060800.3666 | 14564829.1823 | 12926940.5185 | -12926.9
135 | plus | Adjustment resulting from asset allocation
136 |  | Closing fixed assets |  | 13121050.9936 | 50129195.4115 | 52561580.2279 | 43913372.1856 | 36972908.0921
137
138

## Drop down boxes (hidden)
Drop down boxes and Categories
dd_YesNo
Yes
No
[Select one]
dd_opexsalescapex
Transmission revenues
Insurance and other
Opex
Base capex
Major capex
Other assets (IP, etc)
Assets acquired
Assets disposed
Investments
Debt issue
Loan
[Select one]
Grid R&R
Grid E&D
IST
Business Support
AC Stations
Protection and Metering
HVDC Stations
Transmission Lines
Grid E&D
Transmission Systems
Asset Management Systems
Grid Operations
Telecommunications & Network
Corporate Systems
IST Shared Services
Security Services
Other
Office buildings and facilities
Spares and inventory
Properties