## Circuit Branches
Branch | Overall continuous capacity rating | [5 empty] | Resistive and Reactive Level of Positive Sequence Impedance |  | Resistive and Reactive Level of Zero Sequence Impedance |  | High voltage range that branch can operate over |  | Nominal HV Operating Voltage |  | Fault |  | Fault
| Summer |  | Shoulder |  | Winter |  | Resistance | Reactance | Resistance | Reactance | Maximum | Minimum |  | From | Current | To | Current
| Amps | MVA | Amps | MVA | Amps | MVA | PU (100MVA) | PU (100MVA) | PU (100MVA) | PU (100MVA) | kV | kV | kV | Site | Amp/sec | Site | Amp/sec
ALB.HEN.3 | 1473 | 561.34 | 1549 | 590.21 | 1620 | 617.47 | 0.0017913 | 0.015646 | 0.0098335 | 0.046145 | 242 | 198 | 220 | ALB | 54600 | HEN | 45000
ALB.HPI.1 | 1473 | 561.34 | 1549 | 590.21 | 1620 | 617.47 | 0.00096054 | 0.0085955 | 0.0053531 | 0.026856 | 242 | 198 | 220 | ALB | 54600 | HPI
ALB.WRD.4 | 1841 | 701.52 | 1841 | 701.52 | 2070 | 788.78 | 0.00017128 | 0.0029283 | 0.00073719 | 0.0010568 | 242 | 198 | 220 | ALB | 69300 | WRD | 86600
APS.CLH.1 | 232 | 26.51 | 259 | 29.61 | 283 | 32.39 | 0.25683 | 0.40214 | 0.39751 | 1.3336 | 72.6 | 59.4 | 66 | APS | 69300 | CLH | 69300
APS.OTI.1 | 232 | 26.51 | 259 | 29.61 | 283 | 32.39 | 0.080579 | 0.12812 | 0.12741 | 0.44423 | 72.6 | 59.4 | 66 | APS | 69300 | OTI | 43300
ARG.BLN.1 | 292 | 55.68 | 326 | 62.16 | 357 | 67.99 | 0.12151 | 0.23198 | 0.2037 | 0.72837 | 121 | 99 | 110 | ARG | 45600 | BLN | 43300
ARG.KIK.1 | 292 | 55.68 | 326 | 62.16 | 357 | 67.99 | 0.07265 | 0.13856 | 0.12179 | 0.43294 | 121 | 99 | 110 | ARG | 45600 | KIK | 45000
ARI.BOB.1 | 266 | 50.68 | 297 | 56.59 | 325 | 61.92 | 0.21412 | 0.41915 | 0.36499 | 1.3824 | 121 | 99 | 110 | ARI | 45600 | BOB | 69300
ARI.HAM.1 | 266 | 50.68 | 297 | 56.59 | 325 | 61.92 | 0.085755 | 0.16469 | 0.14314 | 0.48574 | 121 | 99 | 110 | ARI | 45600 | HAM | 43300
ARI.HAM.2 | 266 | 50.68 | 297 | 56.59 | 325 | 61.92 | 0.085923 | 0.16501 | 0.14342 | 0.48678 | 121 | 99 | 110 | ARI | 45600 | HAM | 43300
ARI.HTI.1 | 300 | 57.14 | 335 | 63.8 | 366 | 69.8 | 0.082126 | 0.19093 | 0.14833 | 0.59454 | 121 | 99 | 110 | ARI | 45600 | HTI | 43300
ARI.KIN.1 | 300 | 57.14 | 335 | 63.8 | 366 | 69.8 | 0.054717 | 0.12435 | 0.098949 | 0.39627 | 121 | 99 | 110 | ARI | 32900 | KIN | 54600
ARI.KIN.2 | 333 | 63.36 | 371 | 70.73 | 406 | 77.36 | 0.055465 | 0.12292 | 0.10044 | 0.39769 | 121 | 99 | 110 | ARI | 32900 | KIN | 54600
ARI.RTO.1 | 300 | 57.14 | 335 | 63.8 | 366 | 69.8 | 0.061769 | 0.14495 | 0.11147 | 0.44912 | 121 | 99 | 110 | ARI | 45600 | RTO
ASB.BRY.1 | 1822 | 694.33 | 1917 | 730.31 | 2006 | 764.34 | 0.0064523 | 0.055115 | 0.034769 | 0.2135 | 242 | 198 | 220 | ASB | 69300 | BRY | 54600
ASB.ISL.1 | 1822 | 694.33 | 1917 | 730.31 | 2006 | 764.34 | 0.0055603 | 0.047552 | 0.029964 | 0.18387 | 242 | 198 | 220 | ASB | 69300 | ISL | 45600
ASB.OPI.1 | 1822 | 694.33 | 1917 | 730.31 | 2006 | 764.34 | 0.0048275 | 0.041279 | 0.026012 | 0.16037 | 242 | 198 | 220 | ASB | 69300 | OPI
ASB.OPI.2 | 1822 | 694.33 | 1917 | 730.31 | 2000 | 762.1 | 0.0048275 | 0.041279 | 0.026012 | 0.16037 | 242 | 198 | 220 | ASB | 39800 | OPI
ASY.SBK.1 | 333 | 38.02 | 371 | 42.44 | 406 | 46.41 | 0.049685 | 0.10624 | 0.089979 | 0.35845 | 72.6 | 59.4 | 66 | ASY | 43300 | SBK | 43300
ASY.WPR.1 | 333 | 38.02 | 371 | 42.44 | 406 | 46.41 | 0.12059 | 0.25784 | 0.21838 | 0.8817 | 72.6 | 59.4 | 66 | ASY | 43300 | WPR | 43300
ATI.OHK.1 | 874 | 333.13 | 908 | 346 | 940 | 358.32 | 0.0010835 | 0.0052207 | 0.0029002 | 0.012286 | 242 | 198 | 220 | ATI | 45600 | OHK | 54600
ATI.REA.112 | 9999 | 3810.13 | 9999 | 3810.13 | 9999 | 3810.13 | 0.00011136 | 0.035124 |  |  | 242 | 198 | 220 | ATI | 45400
ATI.TRK.1 | 874 | 332.94 | 924 | 351.9 | 970 | 369.76 | 0.0062021 | 0.036954 | 0.019808 | 0.11345 | 242 | 198 | 220 | ATI | 45600 | TRK | 20800
ATI.TRK.2 | 874 | 332.94 | 924 | 351.9 | 970 | 369.76 | 0.0062014 | 0.03695 | 0.019806 | 0.11343 | 242 | 198 | 220 | ATI | 45600 | TRK | 20800
ATI.WKM.1 | 874 | 333.13 | 908 | 346 | 940 | 358.32 | 0.0043771 | 0.021014 | 0.011657 | 0.04803 | 242 | 198 | 220 | ATI | 45600 | WKM | 54600
AVI.BEN.1 | 530 | 201.99 | 591 | 225.39 | 647 | 246.43 | 0.0032033 | 0.015039 | 0.0085326 | 0.037921 | 242 | 198 | 220 | AVI | 45600 | BEN | 69300
AVI.BEN.2 | 530 | 201.99 | 591 | 225.39 | 647 | 246.43 | 0.0032008 | 0.015067 | 0.008526 | 0.037822 | 242 | 198 | 220 | AVI | 45600 | BEN | 69300
AVI.WTK.1 | 1495 | 569.84 | 1572 | 599.15 | 1645 | 626.83 | 0.00073926 | 0.0055362 | 0.0033952 | 0.018999 | 242 | 198 | 220 | AVI | 54600 | WTK | 39800
BAL.BWK.1 | 266 | 50.68 | 297 | 56.59 | 325 | 61.92 | 0.094011 | 0.18275 | 0.15772 | 0.56956 | 121 | 99 | 110 | BAL | 43300 | BWK | 45600
BAL.GOR.1 | 266 | 50.68 | 297 | 56.59 | 325 | 61.92 | 0.14569 | 0.28739 | 0.24387 | 0.87723 | 121 | 99 | 110 | BAL | 45600 | GOR | 43300
BDE.EDN.1 | 266 | 50.68 | 297 | 56.59 | 325 | 61.92 | 0.024918 | 0.049188 | 0.041757 | 0.15195 | 121 | 99 | 110 | BDE | 43300 | EDN | 43300
BDE.GOR.1 | 266 | 50.68 | 276 | 52.59 | 276 | 52.59 | 0.0304 | 0.06006 | 0.050894 | 0.18175 | 121 | 99 | 110 | BDE | 43300 | GOR | 43300
BDT.GNY.2 | 345 | 65.81 | 386 | 73.46 | 422 | 80.34 | 0.017751 | 0.041855 | 0.033272 | 0.13948 | 121 | 99 | 110 | BDT |  | GNY
BDT.WTK.2 | 333 | 63.36 | 371 | 70.73 | 406 | 77.36 | 0.071005 | 0.15945 | 0.13015 | 0.52168 | 121 | 99 | 110 | BDT |  | WTK | 45600
BEN.OHB.1 | 1464 | 558.03 | 1540 | 586.73 | 1611 | 613.84 | 0.0022959 | 0.025434 | 0.012657 | 0.060755 | 242 | 198 | 220 | BEN | 69300 | OHB | 69300
BEN.OHC.2 | 1464 | 558.03 | 1540 | 586.73 | 1611 | 613.84 | 0.0017955 | 0.021143 | 0.0099622 | 0.048187 | 242 | 198 | 220 | BEN | 69300 | OHC | 54600
BEN.TWZ.1 | 1060 | 403.98 | 1183 | 450.78 | 1293 | 492.85 | 0.0042483 | 0.029521 | 0.018403 | 0.086665 | 242 | 198 | 220 | BEN | 69300 | TWZ | 45600
BHL.PAK.1 | 2016 | 768.2 | 2016 | 768.2 | 2121 | 808.21 | 0.00021798 | 0.0039754 | 0.00079525 | 0.0013924 | 242 | 198 | 220 | BHL | 69300 | PAK
BHL.WKM.1 | 3181 | 1212.12 | 3181 | 1212.12 | 3181 | 1212.12 | 0.0056721 | 0.10805 | 0.062352 | 0.25081 | 242 | 198 | 220 | BHL |  | WKM
BLN.STK.1 | 530 | 100.99 | 591 | 112.69 | 647 | 123.21 | 0.05617 | 0.2401 | 0.14963 | 0.64993 | 121 | 99 | 110 | BLN | 43300 | STK | 43300
BLN.STK.2 | 551 | 104.89 | 614 | 117.04 | 672 | 127.97 | 0.052074 | 0.24011 | 0.14554 | 0.66037 | 121 | 99 | 110 | BLN | 43300 | STK | 43300
BOB.HAM.1 | 266 | 50.68 | 297 | 56.59 | 325 | 61.92 | 0.13016 | 0.25758 | 0.22094 | 0.82439 | 121 | 99 | 110 | BOB | 69300 | HAM | 43300
BOT.DRY.1 | 1822 | 694.33 | 1917 | 730.31 | 2006 | 764.34 | 0.0005593 | 0.0049116 | 0.0030167 | 0.014593 | 242 | 198 | 220 | BOT |  | DRY
BOT.DRY.2 | 1822 | 694.33 | 1917 | 730.31 | 2006 | 764.34 | 0.0005593 | 0.0049116 | 0.0030167 | 0.014593 | 242 | 198 | 220 | BOT |  | DRY
BOT.HLY.1 | 1822 | 694.33 | 1917 | 730.31 | 2006 | 764.34 | 0.0031267 | 0.027438 | 0.016851 | 0.081315 | 242 | 198 | 220 | BOT |  | HLY | 69300
BOT.HLY.2 | 1822 | 694.33 | 1917 | 730.31 | 2000 | 762.1 | 0.0031252 | 0.02742 | 0.016843 | 0.081248 | 242 | 198 | 220 | BOT |  | HLY | 69300
BPC.WTK.1 | 333 | 63.36 | 371 | 70.73 | 406 | 77.36 | 0.052871 | 0.11669 | 0.096155 | 0.37918 | 121 | 99 | 110 | BPC |  | WTK | 45600
BPE.BRK.1 | 1822 | 694.33 | 1917 | 730.31 | 2006 | 764.34 | 0.0049583 | 0.042601 | 0.026712 | 0.16387 | 242 | 198 | 220 | BPE | 45600 | BRK | 45600
BPE.BRK.2 | 1822 | 694.33 | 1870 | 712.57 | 1870 | 712.57 | 0.0049705 | 0.042708 | 0.026778 | 0.16424 | 242 | 198 | 220 | BPE | 45600 | BRK | 45600
BPE.LTN.2 | 1822 | 694.33 | 1917 | 730.31 | 2006 | 764.34 | 0.0014262 | 0.012506 | 0.0076833 | 0.03709 | 242 | 198 | 220 | BPE | 45600 | LTN
BPE.MTN.1 | 345 | 65.81 | 386 | 73.46 | 422 | 80.34 | 0.044383 | 0.10503 | 0.083205 | 0.34393 | 121 | 99 | 110 | BPE | 45600 | MTN
BPE.MTR.1 | 300 | 57.14 | 335 | 63.8 | 366 | 69.8 | 0.10746 | 0.25291 | 0.19391 | 0.77924 | 121 | 99 | 110 | BPE | 34600 | MTR | 54600
BPE.MTT.2 | 345 | 65.81 | 386 | 73.46 | 422 | 80.34 | 0.044568 | 0.10548 | 0.083548 | 0.34772 | 121 | 99 | 110 | BPE | 45600 | MTT
BPE.PRT.1 | 931 | 354.71 | 979 | 373.09 | 1025 | 390.47 | 0.012053 | 0.082114 | 0.04038 | 0.22608 | 242 | 198 | 220 | BPE | 69300 | PRT
BPE.PRT.2 | 931 | 354.71 | 979 | 373.09 | 1025 | 390.47 | 0.012119 | 0.082481 | 0.040566 | 0.22695 | 242 | 198 | 220 | BPE | 69300 | PRT
BPE.TKU.1 | 807 | 307.52 | 845 | 321.85 | 880 | 335.48 | 0.029951 | 0.14454 | 0.079784 | 0.40314 | 242 | 198 | 220 | BPE | 69300 | TKU | 45600
BPE.TKU.2 | 807 | 307.52 | 845 | 321.85 | 880 | 335.48 | 0.029896 | 0.14356 | 0.079639 | 0.40352 | 242 | 198 | 220 | BPE | 69300 | TKU | 45600
BPE.TNG.1 | 627 | 238.85 | 699 | 266.49 | 765 | 291.34 | 0.015957 | 0.098263 | 0.050961 | 0.28211 | 242 | 198 | 220 | BPE | 69300 | TNG | 45600
BPE.TWT.1 | 1822 | 694.33 | 1917 | 730.31 | 2006 | 764.34 | 0.00079587 | 0.0069822 | 0.004289 | 0.020711 | 242 | 198 | 220 | BPE | 45600 | TWT
BPE.WDV.1 | 300 | 57.14 | 335 | 63.8 | 366 | 69.8 | 0.033186 | 0.075768 | 0.060362 | 0.24572 | 121 | 99 | 110 | BPE | 34600 | WDV | 54600
BPE.WDV.2 | 300 | 57.14 | 335 | 63.8 | 366 | 69.8 | 0.033183 | 0.075762 | 0.060357 | 0.2457 | 121 | 99 | 110 | BPE | 34600 | WDV | 54600
BRB.HPI.1 | 875 | 333.31 | 924 | 352.24 | 971 | 370.08 | 0.014016 | 0.087232 | 0.047624 | 0.20565 | 242 | 198 | 220 | BRB | 54600 | HPI | 54600
BRB.MDN.1 | 1250 | 476.31 | 1250 | 476.31 | 1250 | 476.31 | 0.00023926 | 0.0022017 | 0.001337 | 0.0070147 | 242 | 198 | 220 | BRB | 54600 | MDN | 54600
BRK.SFD.1 | 610 | 232.53 | 685 | 260.95 | 752 | 286.38 | 0.013358 | 0.080227 | 0.04266 | 0.24362 | 242 | 198 | 220 | BRK | 45600 | SFD | 45600
BRK.SFD.2 | 610 | 232.53 | 685 | 260.95 | 752 | 286.38 | 0.013357 | 0.080221 | 0.042658 | 0.24363 | 242 | 198 | 220 | BRK | 45600 | SFD | 45600
BRK.SFD.3 | 610 | 232.53 | 685 | 260.95 | 752 | 286.38 | 0.013464 | 0.081732 | 0.043009 | 0.23733 | 242 | 198 | 220 | BRK | 45600 | SFD | 69300
BRY.ISL.1 | 1822 | 694.33 | 1917 | 730.31 | 2004 | 763.65 | 0.0019605 | 0.016645 | 0.010559 | 0.063757 | 242 | 198 | 220 | BRY | 54600 | ISL | 45600
BWK.HWB.1 | 266 | 50.68 | 297 | 56.59 | 325 | 61.92 | 0.06492 | 0.12814 | 0.10829 | 0.38545 | 121 | 99 | 110 | BWK | 45600 | HWB | 43300
CBG.HAM.1 | 300 | 57.14 | 335 | 63.8 | 366 | 69.8 | 0.028918 | 0.06585 | 0.052183 | 0.21289 | 121 | 99 | 110 | CBG | 45600 | HAM | 43300
CBG.HAM.2 | 300 | 57.14 | 335 | 63.8 | 366 | 69.8 | 0.028923 | 0.065872 | 0.052193 | 0.21286 | 121 | 99 | 110 | CBG | 45600 | HAM | 43300
CBG.KPO.1 | 300 | 57.14 | 335 | 63.8 | 366 | 69.8 | 0.010774 | 0.024626 | 0.019339 | 0.073705 | 121 | 99 | 110 | CBG | 45600 | KPO | 54600
CBG.KPO.2 | 300 | 57.14 | 335 | 63.8 | 366 | 69.8 | 0.010775 | 0.024649 | 0.019345 | 0.073656 | 121 | 99 | 110 | CBG | 45600 | KPO | 69300
CLH.COL.1 | 232 | 26.51 | 259 | 29.61 | 283 | 32.39 | 0.17605 | 0.26828 | 0.2717 | 0.9481 | 72.6 | 59.4 | 66 | CLH | 69300 | COL | 45600
CML.CYD.1 | 1464 | 558.03 | 1540 | 586.73 | 1611 | 613.84 | 0.0013948 | 0.016383 | 0.0077434 | 0.051452 | 242 | 198 | 220 | CML | 69300 | CYD | 69300
CML.CYD.2 | 1464 | 558.03 | 1540 | 586.73 | 1611 | 613.84 | 0.0013946 | 0.016379 | 0.0077419 | 0.051463 | 242 | 198 | 220 | CML |  | CYD | 69300
CML.TWZ.1 | 1473 | 561.34 | 1549 | 590.21 | 1620 | 617.47 | 0.0078934 | 0.09383 | 0.044236 | 0.29814 | 242 | 198 | 220 | CML | 69300 | TWZ | 69300
CML.TWZ.2 | 1473 | 561.34 | 1549 | 590.21 | 1620 | 617.47 | 0.0078938 | 0.093833 | 0.044237 | 0.29817 | 242 | 198 | 220 | CML | 69300 | TWZ | 69300
COL.HOR.2 | 266 | 30.41 | 297 | 33.95 | 325 | 37.15 | 0.22871 | 0.4251 | 0.38822 | 1.4937 | 72.6 | 59.4 | 66 | COL | 45600 | HOR | 45600
COL.HOR.3 | 266 | 30.41 | 297 | 33.95 | 325 | 37.15 | 0.22859 | 0.42496 | 0.38804 | 1.4932 | 72.6 | 59.4 | 66 | COL | 45600 | HOR | 45600
COL.OTI.2 | 232 | 26.51 | 259 | 29.61 | 283 | 32.39 | 0.51358 | 0.7985 | 0.79683 | 2.7273 | 72.6 | 59.4 | 66 | COL | 45600 | OTI | 31600
CST.HUI.1 | 333 | 63.36 | 371 | 70.73 | 406 | 77.36 | 0.023038 | 0.050432 | 0.041719 | 0.1391 | 121 | 99 | 110 | CST | 43300 | HUI | 43300
CST.HUI.2 | 333 | 63.36 | 371 | 70.73 | 406 | 77.36 | 0.02302 | 0.050392 | 0.041686 | 0.13897 | 121 | 99 | 110 | CST | 43300 | HUI | 43300
CST.JRT.1 | 482 | 91.89 | 507 | 96.69 | 531 | 101.24 | 0.0064174 | 0.013888 | 0.011621 | 0.042445 | 121 | 99 | 110 | CST | 43300 | JRT
CST.MNI.1 | 324 | 61.69 | 364 | 69.26 | 399 | 76.05 | 0.047844 | 0.11147 | 0.08884 | 0.30284 | 121 | 99 | 110 | CST | 43300 | MNI | 54600
CST.SFD.3 | 1220 | 232.53 | 1250 | 238.16 | 1250 | 238.16 | 0.013198 | 0.11122 | 0.071494 | 0.41914 | 121 | 99 | 110 | CST | 43300 | SFD | 54600
CUT.KIK.2 | 816 | 310.94 | 816 | 310.94 | 816 | 310.94 | 0.018534 | 0.11406 | 0.060214 | 0.27464 | 242 | 198 | 220 | CUT |  | KIK | 45600
CUT.KIK.3 | 816 | 310.94 | 816 | 310.94 | 816 | 310.94 | 0.018998 | 0.11406 | 0.06068 | 0.27464 | 242 | 198 | 220 | CUT |  | KIK | 54600
CUT.WTT.2 | 911 | 347.16 | 958 | 365.15 | 1003 | 382.17 | 0.0054186 | 0.03244 | 0.017308 | 0.088649 | 242 | 198 | 220 | CUT |  | WTT
CUT.WTT.3 | 911 | 347.16 | 958 | 365.15 | 1003 | 382.17 | 0.0054186 | 0.03244 | 0.017308 | 0.088649 | 242 | 198 | 220 | CUT |  | WTT
CYD.ROX.1 | 1862 | 709.42 | 1958 | 746.18 | 2049 | 780.95 | 0.0022864 | 0.020401 | 0.012763 | 0.078747 | 242 | 198 | 220 | CYD | 69300 | ROX | 69300
CYD.ROX.2 | 1862 | 709.42 | 1958 | 746.18 | 2049 | 780.95 | 0.0022866 | 0.020403 | 0.012765 | 0.078788 | 242 | 198 | 220 | CYD | 69300 | ROX | 69300
DOB.GYM.1 | 259 | 29.56 | 289 | 33 | 316 | 36.1 | 0.052381 | 0.081804 | 0.086398 | 0.27002 | 72.6 | 57.8 | 66 | DOB | 43300 | GYM | 27700
DOB.RFC.1 | 292 | 55.68 | 326 | 62.16 | 357 | 67.99 | 0.12256 | 0.23558 | 0.20815 | 0.77312 | 121 | 99 | 110 | DOB | 54600 | RFC
DOB.RFC.2 | 554 | 105.54 | 583 | 111.05 | 610 | 116.27 | 0.088074 | 0.24089 | 0.17988 | 0.84236 | 121 | 99 | 110 | DOB | 55400 | RFC
DRY.CB.412 | 4000 | 1524.2 | 4000 | 1524.2 | 4000 | 1524.2 | 0 | 0 |  |  | 242 | 198 | 220 | DRY | 69300
DRY.CB.422 | 4000 | 1524.2 | 4000 | 1524.2 | 4000 | 1524.2 | 0 | 0 |  |  | 242 | 198 | 220 | DRY | 69300
DRY.CB.432 | 4000 | 1524.2 | 4000 | 1524.2 | 4000 | 1524.2 | 0 | 0 |  |  | 242 | 198 | 220 | DRY | 69300
DRY.CB.442 | 4000 | 1524.2 | 4000 | 1524.2 | 4000 | 1524.2 | 0 | 0 |  |  | 242 | 198 | 220 | DRY | 69300
DRY.CB.452 | 4000 | 1524.2 | 4000 | 1524.2 | 4000 | 1524.2 | 0 | 0 |  |  | 242 | 198 | 220 | DRY | 69300
DRY.CB.462 | 4000 | 1524.2 | 4000 | 1524.2 | 4000 | 1524.2 | 0 | 0 |  |  | 242 | 198 | 220 | DRY | 69300
DRY.CB.482 | 4000 | 1524.2 | 4000 | 1524.2 | 4000 | 1524.2 | 0 | 0 |  |  | 242 | 198 | 220 | DRY | 69300
DRY.TAT.1 | 2991 | 1139.68 | 3145 | 1198.29 | 3290 | 1253.65 | 0.00034917 | 0.0062341 | 0.0036657 | 0.017193 | 242 | 198 | 220 | DRY |  | TAT
DRY.TAT.2 | 2991 | 1139.68 | 3145 | 1198.29 | 3290 | 1253.65 | 0.00035785 | 0.0063878 | 0.0037562 | 0.017615 | 242 | 198 | 220 | DRY |  | TAT
DVK.WDV.1 | 265 | 50.4 | 295 | 56.27 | 323 | 61.55 | 0.043535 | 0.068349 | 0.068911 | 0.23318 | 121 | 99 | 110 | DVK | 34600 | WDV | 54600
DVK.WDV.2 | 265 | 50.4 | 295 | 56.27 | 323 | 61.55 | 0.045169 | 0.07123 | 0.071494 | 0.24319 | 121 | 99 | 110 | DVK | 45600 | WDV | 54600
DVK.WPW.1 | 266 | 50.68 | 297 | 56.59 | 325 | 61.92 | 0.086687 | 0.16501 | 0.14453 | 0.53921 | 121 | 99 | 110 | DVK | 66000 | WPW | 55400
DVK.WPW.2 | 266 | 50.68 | 297 | 56.59 | 325 | 61.92 | 0.087788 | 0.16713 | 0.14643 | 0.54765 | 121 | 99 | 110 | DVK | 45600 | WPW | 55400
EDG.KAW.1 | 253 | 48.24 | 283 | 53.86 | 309 | 58.91 | 0.031386 | 0.049325 | 0.048419 | 0.14629 | 121 | 99 | 110 | EDG | 43300 | KAW | 45000
EDG.KAW.2 | 253 | 48.23 | 283 | 53.84 | 309 | 58.9 | 0.03176 | 0.049826 | 0.048999 | 0.14647 | 121 | 99 | 110 | EDG | 69300 | KAW | 54600
EDG.KAW.3 | 1035 | 394.26 | 1075 | 409.44 | 1113 | 423.98 | 0.0031661 | 0.019245 | 0.010115 | 0.047004 | 242 | 198 | 220 | EDG | 45600 | KAW | 54600
EDG.OWH.2 | 298 | 56.74 | 332 | 63.33 | 364 | 69.28 | 0.076173 | 0.19148 | 0.14341 | 0.57164 | 121 | 99 | 110 | EDG | 45600 | OWH | 43300
EDG.TRK.1 | 627 | 238.85 | 699 | 266.49 | 765 | 291.34 | 0.0092607 | 0.055386 | 0.0296 | 0.16905 | 242 | 198 | 220 | EDG | 22700 | TRK | 22700
EDG.TRK.2 | 627 | 238.85 | 699 | 266.49 | 765 | 291.34 | 0.009263 | 0.055395 | 0.029605 | 0.16908 | 242 | 198 | 220 | EDG | 22700 | TRK | 22700
EDN.INV.1 | 266 | 50.68 | 276 | 52.59 | 276 | 52.59 | 0.058977 | 0.11706 | 0.098573 | 0.35475 | 121 | 99 | 110 | EDN | 43300 | INV
FHL.RDF.1 | 266 | 50.68 | 297 | 56.59 | 325 | 61.92 | 0.013158 | 0.026353 | 0.022542 | 0.087414 | 121 | 99 | 110 | FHL | 34600 | RDF | 45400
FHL.RDF.2 | 266 | 50.68 | 297 | 56.59 | 325 | 61.92 | 0.013249 | 0.026681 | 0.0227 | 0.087737 | 121 | 99 | 110 | FHL | 34600 | RDF
FHL.TUI.1 | 530 | 100.99 | 591 | 112.69 | 647 | 123.21 | 0.077709 | 0.17918 | 0.21429 | 1.0508 | 121 | 99 | 110 | FHL | 34600 | TUI | 45600
FHL.WPW.1 | 266 | 50.68 | 297 | 56.59 | 325 | 61.92 | 0.082793 | 0.15673 | 0.13802 | 0.51746 | 121 | 99 | 110 | FHL | 45600 | WPW | 55400
FHL.WPW.2 | 266 | 50.68 | 297 | 56.59 | 325 | 61.92 | 0.08275 | 0.15778 | 0.13797 | 0.51534 | 121 | 99 | 110 | FHL | 45600 | WPW | 55400
GNY.STU.2 | 383 | 73.02 | 403 | 76.85 | 422 | 80.48 | 0.046177 | 0.073636 | 0.07309 | 0.24773 | 121 | 99 | 110 | GNY |  | STU | 45600
GOR.GOT.1 | 774 | 294.97 | 800 | 304.84 | 800 | 304.84 | 0.00026736 | 0.0016634 | 0.00087872 | 0.0036719 | 242 | 198 | 220 | GOR | 69300 | GOT
GOR.GOT.2 | 774 | 294.97 | 800 | 304.84 | 800 | 304.84 | 0.00027231 | 0.0016835 | 0.00089463 | 0.0037911 | 242 | 198 | 220 | GOR | 69300 | GOT
GOR.ROX.1 | 333 | 63.36 | 371 | 70.73 | 406 | 77.36 | 0.12593 | 0.28021 | 0.22804 | 0.89431 | 121 | 99 | 110 | GOR | 54600 | ROX | 45600
GOT.NMA.1 | 911 | 347.16 | 958 | 365.15 | 1003 | 382.17 | 0.0072343 | 0.043881 | 0.023104 | 0.10449 | 242 | 198 | 220 | GOT |  | NMA | 69300
GOT.NMA.2 | 911 | 347.16 | 958 | 365.15 | 1003 | 382.17 | 0.0072349 | 0.043882 | 0.023106 | 0.10448 | 242 | 198 | 220 | GOT |  | NMA | 69300
GOT.TMH.1 | 911 | 347.16 | 958 | 365.15 | 1003 | 382.17 | 0.02027 | 0.12379 | 0.065071 | 0.29486 | 242 | 198 | 220 | GOT |  | TMH | 69300
GOT.TMH.2 | 911 | 347.16 | 958 | 365.15 | 1003 | 382.17 | 0.02027 | 0.12379 | 0.065071 | 0.29486 | 242 | 198 | 220 | GOT |  | TMH | 69300
GYM.KUM.1 | 253 | 28.94 | 283 | 32.31 | 300 | 34.29 | 0.14624 | 0.20168 | 0.22561 | 0.7627 | 72.6 | 59.4 | 66 | GYM | 27700 | KUM | 43300
GYT.MST.1 | 463 | 88.15 | 489 | 93.22 | 514 | 97.99 | 0.034364 | 0.074564 | 0.062231 | 0.20871 | 121 | 99 | 110 | GYT | 45600 | MST | 43300
GYT.MST.2 | 463 | 88.15 | 489 | 93.22 | 514 | 97.99 | 0.034362 | 0.074561 | 0.062228 | 0.2087 | 121 | 99 | 110 | GYT | 45600 | MST | 43300
GYT.UHT.1 | 333 | 63.36 | 371 | 70.73 | 406 | 77.36 | 0.046398 | 0.099535 | 0.084019 | 0.33627 | 121 | 99 | 110 | GYT | 45600 | UHT | 43300
GYT.UHT.2 | 333 | 63.36 | 371 | 70.73 | 406 | 77.36 | 0.046382 | 0.099499 | 0.08399 | 0.33615 | 121 | 99 | 110 | GYT | 45600 | UHT | 45600
HAM.OHW.1 | 1614 | 615.03 | 1689 | 643.71 | 1761 | 670.96 | 0.0034835 | 0.022755 | 0.015135 | 0.074929 | 242 | 198 | 220 | HAM | 45600 | OHW
HAM.WKM.1 | 1614 | 615.03 | 1689 | 643.71 | 1761 | 670.96 | 0.0083494 | 0.054275 | 0.036184 | 0.17816 | 242 | 198 | 220 | HAM | 45600 | WKM | 54600
HAY.JFD.1 | 1822 | 694.33 | 1917 | 730.31 | 2000 | 762.1 | 0.00039132 | 0.0033519 | 0.0021066 | 0.011137 | 242 | 198 | 220 | HAY | 43300 | JFD
HAY.JFD.2 | 1822 | 694.33 | 1917 | 730.31 | 2000 | 762.1 | 0.00037913 | 0.0032554 | 0.002045 | 0.010812 | 242 | 198 | 220 | HAY | 43300 | JFD
HAY.PRT.1 | 931 | 354.71 | 979 | 373.09 | 1025 | 390.47 | 0.0035041 | 0.023271 | 0.011528 | 0.06363 | 242 | 198 | 220 | HAY | 43300 | PRT
HAY.PRT.2 | 931 | 354.71 | 979 | 373.09 | 1025 | 390.47 | 0.0035048 | 0.023276 | 0.011532 | 0.063641 | 242 | 198 | 220 | HAY | 43300 | PRT
HAY.TKR.1 | 2160 | 411.46 | 2214 | 421.79 | 2266 | 431.8 | 0.0032107 | 0.020602 | 0.014728 | 0.083534 | 121 | 99 | 110 | HAY | 54600 | TKR | 54600
HAY.TKR.2 | 2160 | 411.46 | 2214 | 421.79 | 2266 | 431.8 | 0.0032124 | 0.020612 | 0.014738 | 0.083611 | 121 | 99 | 110 | HAY | 54600 | TKR | 54600
HAY.UHT.1 | 548 | 104.41 | 552 | 105.17 | 570 | 108.6 | 0.0042322 | 0.024717 | 0.018494 | 0.074086 | 121 | 99 | 110 | HAY | 43300 | UHT | 45600
HAY.UHT.2 | 548 | 104.41 | 552 | 105.17 | 570 | 108.6 | 0.0042488 | 0.024777 | 0.018603 | 0.074199 | 121 | 99 | 110 | HAY | 34600 | UHT | 45600
HEN.HEP.1 | 501 | 95.43 | 527 | 100.42 | 552 | 105.15 | 0.0093347 | 0.021612 | 0.017501 | 0.068031 | 121 | 99 | 110 | HEN | 45600 | HEP | 54600
HEN.HEP.2 | 501 | 95.43 | 527 | 100.42 | 552 | 105.15 | 0.0093339 | 0.02161 | 0.017499 | 0.06801 | 121 | 99 | 110 | HEN | 43300 | HEP | 43300
HEN.HEP.3 | 501 | 95.43 | 527 | 100.42 | 552 | 105.15 | 0.0092645 | 0.021688 | 0.017368 | 0.067189 | 121 | 99 | 110 | HEN | 45600 | HEP | 43300
HEN.HEP.4 | 501 | 95.43 | 527 | 100.42 | 552 | 105.15 | 0.0092537 | 0.021661 | 0.017346 | 0.067101 | 121 | 99 | 110 | HEN | 45600 | HEP | 43300
HEN.HPI.1 | 1747 | 665.88 | 1847 | 703.81 | 1941 | 739.52 | 0.0008314 | 0.0070508 | 0.0044777 | 0.019236 | 242 | 198 | 220 | HEN | 69300 | HPI
HEN.OTA.1 | 2400 | 914.52 | 2400 | 914.52 | 2400 | 914.52 | 0.002181 | 0.019087 | 0.011775 | 0.058719 | 242 | 198 | 220 | HEN | 45600 | OTA | 69300
HEN.SWN.1 | 2400 | 914.52 | 2400 | 914.52 | 2400 | 914.52 | 0.0017764 | 0.015548 | 0.0095711 | 0.047683 | 242 | 198 | 220 | HEN | 45600 | SWN | 43300
HEN.WEL.1 | 292 | 55.68 | 326 | 62.16 | 357 | 67.99 | 0.12531 | 0.22138 | 0.21015 | 0.78191 | 121 | 99 | 110 | HEN | 45600 | WEL | 45600
HEN.WEL.2 | 292 | 55.68 | 326 | 62.16 | 357 | 67.99 | 0.12538 | 0.22154 | 0.21027 | 0.78237 | 121 | 99 | 110 | HEN | 45600 | WEL | 45600
HEP.ROS.1 | 800 | 152.42 | 800 | 152.42 | 800 | 152.42 | 0.0051496 | 0.011886 | 0.014169 | 0.057064 | 121 | 99 | 110 | HEP | 45600 | ROS | 45600
HEP.ROS.2 | 800 | 152.42 | 800 | 152.42 | 800 | 152.42 | 0.0049603 | 0.011352 | 0.013682 | 0.063556 | 121 | 99 | 110 | HEP | 45600 | ROS | 45600
HKK.OTI.2 | 232 | 26.51 | 259 | 29.61 | 283 | 32.39 | 0.437 | 0.65551 | 0.67742 | 2.3442 | 72.6 | 59.4 | 66 | HKK | 21700 | OTI | 43300
HLY.OHW.1 | 1822 | 694.33 | 1917 | 730.31 | 2006 | 764.34 | 0.001161 | 0.0102 | 0.0062638 | 0.032854 | 242 | 198 | 220 | HLY | 69300 | OHW
HLY.OHW.2 | 1822 | 694.33 | 1917 | 730.31 | 2006 | 764.34 | 0.001161 | 0.010184 | 0.0062556 | 0.032502 | 242 | 198 | 220 | HLY | 69300 | OHW
HLY.SFD.1 | 930 | 354.38 | 930 | 354.38 | 930 | 354.38 | 0.039089 | 0.23494 | 0.12487 | 0.71227 | 242 | 198 | 220 | HLY | 69300 | SFD | 69300
HLY.TWH.1 | 1231 | 469.17 | 1262 | 480.9 | 1292 | 492.27 | 0.0041762 | 0.02506 | 0.013367 | 0.074532 | 242 | 198 | 220 | HLY | 69300 | TWH | 54600
HOB.PEN.1 | 2360 | 899.28 | 2360 | 899.28 | 2400 | 914.52 | 0.00019979 | 0.0020014 | 0.0014107 | 0.00094112 | 242 | 198 | 220 | HOB | 86600 | PEN | 69300
HOB.WRD.1 | 1930 | 735.43 | 1930 | 735.43 | 2070 | 788.78 | 0.00021095 | 0.0031455 | 0.00098512 | 0.0011944 | 242 | 198 | 220 | HOB | 86600 | WRD | 86600
HOR.KBT.1 | 547 | 62.53 | 570 | 65.2 | 593 | 67.74 | 0.05964 | 0.14008 | 0.1118 | 0.46986 | 69.3 | 59.4 | 66 | HOR | 45600 | KBT
HOR.KBT.2 | 547 | 62.53 | 570 | 65.2 | 593 | 67.74 | 0.059626 | 0.14005 | 0.11178 | 0.46974 | 69.3 | 59.4 | 66 | HOR | 45600 | KBT
HPI.MDN.1 | 1600 | 609.68 | 1600 | 609.68 | 1600 | 609.68 | 0.0074244 | 0.063237 | 0.040037 | 0.17728 | 242 | 198 | 220 | HPI | 54600 | MDN | 45600
HRP.RDF.1 | 1254 | 477.69 | 1399 | 532.98 | 1529 | 582.67 | 0.0034963 | 0.029931 | 0.018845 | 0.11355 | 242 | 198 | 220 | HRP | 69300 | RDF | 45600
HRP.TAB.1 | 1254 | 477.69 | 1399 | 532.98 | 1529 | 582.67 | 0.0054998 | 0.04704 | 0.029637 | 0.18249 | 242 | 198 | 220 | HRP | 69300 | TAB | 69300
HTI.RTO.1 | 333 | 63.36 | 371 | 70.73 | 406 | 77.36 | 0.021005 | 0.045212 | 0.038086 | 0.15373 | 121 | 99 | 110 | HTI | 45600 | RTO
HTI.TMU.1.WAIPA | 554 | 105.54 | 583 | 111.05 | 610 | 116.27 | 0.038921 | 0.10901 | 0.079529 | 0.26427 | 121 | 99 | 110 | HTI | 69300 | TMU | 54600
HTT.OTA.1 | 770 | 293.44 | 810 | 308.67 | 848 | 323.09 | 0.021193 | 0.1046 | 0.057446 | 0.29065 | 242 | 198 | 220 | HTT |  | OTA | 69300
HTT.OTA.2 | 770 | 293.44 | 810 | 308.67 | 848 | 323.09 | 0.021191 | 0.10446 | 0.05737 | 0.29081 | 242 | 198 | 220 | HTT |  | OTA | 69300
HTT.WKM.1 | 770 | 293.44 | 810 | 308.67 | 848 | 323.09 | 0.013149 | 0.063211 | 0.035032 | 0.17633 | 242 | 198 | 220 | HTT |  | WKM | 54600
HTT.WKM.2 | 770 | 293.44 | 810 | 308.67 | 848 | 323.09 | 0.013173 | 0.063407 | 0.035099 | 0.17642 | 242 | 198 | 220 | HTT |  | WKM | 54600
HUI.MNI.1 | 501 | 95.43 | 527 | 100.42 | 552 | 105.15 | 0.011832 | 0.029132 | 0.022183 | 0.068955 | 121 | 99 | 110 | HUI | 43300 | MNI | 54600
HWA.SFD.1 | 805 | 153.41 | 836 | 159.36 | 866 | 165.05 | 0.021318 | 0.089079 | 0.053753 | 0.2814 | 121 | 99 | 110 | HWA | 43300 | SFD | 54600
HWA.WVY.1 | 805 | 153.41 | 836 | 159.36 | 866 | 165.05 | 0.028431 | 0.1196 | 0.071664 | 0.35607 | 121 | 99 | 110 | HWA | 55400 | WVY | 45600
HWB.ROX.1 | 333 | 63.36 | 371 | 70.73 | 406 | 77.36 | 0.19046 | 0.4387 | 0.34489 | 1.3387 | 121 | 99 | 110 | HWB | 45600 | ROX | 43300
HWB.ROX.2 | 333 | 63.36 | 371 | 70.73 | 406 | 77.36 | 0.19046 | 0.43868 | 0.3449 | 1.3387 | 121 | 99 | 110 | HWB | 45600 | ROX | 45600
HWB.SDN.1 | 875 | 333.31 | 924 | 352.24 | 971 | 370.08 | 0.0017176 | 0.010281 | 0.0054986 | 0.029099 | 242 | 198 | 220 | HWB | 45600 | SDN | 45600
HWB.TMH.1 | 875 | 333.31 | 924 | 352.24 | 971 | 370.08 | 0.00052128 | 0.0031196 | 0.0016636 | 0.0087948 | 242 | 198 | 220 | HWB | 45600 | TMH | 69300
IGH.KIK.2 | 482 | 91.89 | 507 | 96.69 | 531 | 101.24 | 0.058002 | 0.35126 | 0.18776 | 0.7993 | 121 | 99 | 110 | IGH | 45600 | KIK | 43300
IGH.MCH.1 | 292 | 55.68 | 326 | 62.16 | 357 | 67.99 | 0.067084 | 0.13115 | 0.1125 | 0.39144 | 121 | 99 | 110 | IGH | 43300 | MCH | 69300
IGH.RFC.1 | 292 | 55.68 | 326 | 62.16 | 357 | 67.99 | 0.051902 | 0.10032 | 0.087017 | 0.30575 | 121 | 99 | 110 | IGH | 45600 | RFC
IGH.RFC.2 | 554 | 105.54 | 583 | 111.05 | 610 | 116.27 | 0.031851 | 0.084078 | 0.065067 | 0.3038 | 121 | 99 | 110 | IGH | 43300 | RFC
INV.MAN.2 | 818 | 311.61 | 912 | 347.6 | 997 | 379.93 | 0.013278 | 0.091745 | 0.057414 | 0.30082 | 242 | 198 | 220 | INV | 45600 | MAN | 54600
INV.NMA.1 | 1060 | 403.98 | 1183 | 450.78 | 1200 | 457.26 | 0.0009686 | 0.0063475 | 0.0041942 | 0.019701 | 242 | 198 | 220 | INV | 45600 | NMA | 69300
INV.ROX.1 | 911 | 347.16 | 958 | 365.15 | 1003 | 382.17 | 0.018428 | 0.11252 | 0.058852 | 0.27189 | 242 | 198 | 220 | INV | 45600 | ROX | 45600
INV.ROX.2 | 911 | 347.16 | 958 | 365.15 | 1003 | 382.17 | 0.018098 | 0.11217 | 0.057804 | 0.32313 | 242 | 198 | 220 | INV | 45600 | ROX | 45600
INV.TWI.1 | 1011 | 385.42 | 1128 | 429.87 | 1200 | 457.26 | 0.0021087 | 0.015329 | 0.0097742 | 0.053341 | 242 | 198 | 220 | INV | 45600 | TWI | 54600
INV.TWI.2 | 1011 | 385.42 | 1128 | 429.87 | 1200 | 457.26 | 0.0021116 | 0.015349 | 0.009787 | 0.0532 | 242 | 198 | 220 | INV | 45600 | TWI | 54600
ISL.KBT.1 | 519 | 59.33 | 523 | 59.79 | 545 | 62.3 | 0.13448 | 0.33828 | 0.26172 | 1.1199 | 69.3 | 59.4 | 66 | ISL | 43300 | KBT
ISL.KBT.2 | 519 | 59.33 | 523 | 59.79 | 545 | 62.3 | 0.13448 | 0.33826 | 0.26171 | 1.1198 | 69.3 | 59.4 | 66 | ISL | 43300 | KBT
ISL.KIK.1 | 627 | 238.85 | 699 | 266.49 | 765 | 291.34 | 0.031998 | 0.20029 | 0.10219 | 0.56182 | 242 | 198 | 220 | ISL | 54600 | KIK | 45600
ISL.NWD.1 | 1060 | 403.98 | 1183 | 450.78 | 1293 | 492.85 | 0.0024271 | 0.016914 | 0.010515 | 0.057283 | 242 | 198 | 220 | ISL | 54600 | NWD | 69300
ISL.SBK.1 | 527 | 60.21 | 549 | 62.78 | 571 | 65.23 | 0.10664 | 0.22469 | 0.19309 | 0.78528 | 69.3 | 59.4 | 66 | ISL | 54600 | SBK | 43300
ISL.SBK.2 | 527 | 60.21 | 549 | 62.78 | 571 | 65.23 | 0.10662 | 0.22466 | 0.19306 | 0.78517 | 69.3 | 59.4 | 66 | ISL | 45600 | SBK | 43300
ISL.TKB.1 | 1461 | 556.65 | 1546 | 589.22 | 1600 | 609.68 | 0.019618 | 0.13389 | 0.084895 | 0.38559 | 242 | 198 | 220 | ISL | 54600 | TKB | 45600
ISL.WTT.2 | 911 | 347.16 | 958 | 365.15 | 1003 | 382.17 | 0.0073033 | 0.048005 | 0.025945 | 0.13519 | 242 | 198 | 220 | ISL | 45600 | WTT
ISL.WTT.3 | 911 | 347.16 | 958 | 365.15 | 1003 | 382.17 | 0.0075192 | 0.048004 | 0.02616 | 0.13519 | 242 | 198 | 220 | ISL | 54600 | WTT
JFD.LTN.1 | 1822 | 694.33 | 1917 | 730.31 | 2006 | 764.34 | 0.0071273 | 0.062513 | 0.038402 | 0.18504 | 242 | 198 | 220 | JFD |  | LTN | 86600
JFD.LTN.2 | 1822 | 694.33 | 1917 | 730.31 | 2006 | 764.34 | 0.0071267 | 0.062514 | 0.038403 | 0.18504 | 242 | 198 | 220 | JFD |  | LTN | 69300
JFD.WIL.1 | 1382 | 526.45 | 1435 | 546.62 | 1485 | 565.9 | 0.0020946 | 0.020026 | 0.010636 | 0.055363 | 242 | 198 | 220 | JFD |  | WIL | 54600
JFD.WIL.2 | 1382 | 526.45 | 1435 | 546.62 | 1485 | 565.9 | 0.00208 | 0.019985 | 0.010606 | 0.055249 | 242 | 198 | 220 | JFD |  | WIL | 54600
JRT.SFD.1 | 482 | 91.89 | 507 | 96.69 | 531 | 101.24 | 0.04794 | 0.104 | 0.086811 | 0.31759 | 121 | 99 | 110 | JRT |  | SFD | 43300
KAW.OHK.1 | 627 | 238.85 | 699 | 266.49 | 765 | 291.34 | 0.012501 | 0.076513 | 0.03993 | 0.18401 | 242 | 198 | 220 | KAW | 33300 | OHK
KIK.MCH.1 | 292 | 55.68 | 326 | 62.16 | 357 | 67.99 | 0.097048 | 0.19008 | 0.1627 | 0.57063 | 121 | 99 | 110 | KIK | 43300 | MCH | 69300
KIK.STK.1 | 627 | 238.85 | 699 | 266.49 | 765 | 291.34 | 0.007305 | 0.043529 | 0.023331 | 0.11436 | 242 | 198 | 220 | KIK | 45600 | STK | 45600
KIK.STK.2 | 627 | 238.85 | 699 | 266.49 | 765 | 291.34 | 0.0073074 | 0.043543 | 0.023339 | 0.11444 | 242 | 198 | 220 | KIK | 45600 | STK | 45600
KIK.STK.3 | 292 | 55.68 | 326 | 62.16 | 357 | 67.99 | 0.095617 | 0.18362 | 0.16029 | 0.5691 | 121 | 99 | 110 | KIK | 43300 | STK | 43300
KIN.LFT.1 | 266 | 50.68 | 297 | 56.59 | 325 | 61.92 | 0.029428 | 0.061039 | 0.050029 | 0.18342 | 121 | 99 | 110 | KIN | 54600 | LFT
KIN.LFT.2 | 333 | 63.36 | 371 | 70.73 | 406 | 77.36 | 0.026836 | 0.059763 | 0.048596 | 0.19101 | 121 | 99 | 110 | KIN | 54600 | LFT
KMO.MTM.1 | 333 | 63.36 | 371 | 70.73 | 406 | 77.36 | 0.014308 | 0.028752 | 0.026574 | 0.093583 | 121 | 99 | 110 | KMO | 54600 | MTM | 45600
KMO.TMI.1 | 333 | 63.36 | 371 | 70.73 | 406 | 77.36 | 0.026805 | 0.059892 | 0.048554 | 0.18986 | 121 | 99 | 110 | KMO | 43300 | TMI | 43300
KMO.TRK.1 | 955 | 363.85 | 999 | 380.78 | 1042 | 396.87 | 0.0054822 | 0.032675 | 0.017512 | 0.10013 | 121 | 99 | 220 | KMO | 54600 | TRK | 54600
KMO.TRK.2 | 955 | 363.85 | 999 | 380.78 | 1042 | 396.87 | 0.0054837 | 0.032684 | 0.017517 | 0.10016 | 121 | 99 | 220 | KMO | 54600 | TRK | 54600
KPO.TMU.1 | 333 | 63.36 | 371 | 70.73 | 406 | 77.36 | 0.033328 | 0.074329 | 0.06035 | 0.23448 | 121 | 99 | 110 | KPO | 69300 | TMU | 45600
KUM.OTI.1 | 232 | 26.51 | 259 | 29.61 | 283 | 32.39 | 0.37639 | 0.57244 | 0.58537 | 2.0324 | 72.6 | 59.4 | 66 | KUM | 43300 | OTI | 43300
LFT.TRK.1 | 300 | 57.14 | 335 | 63.8 | 366 | 69.8 | 0.053584 | 0.1298 | 0.098158 | 0.39947 | 121 | 99 | 110 | LFT |  | TRK | 45600
LFT.TRK.2 | 333 | 63.36 | 371 | 70.73 | 406 | 77.36 | 0.06666 | 0.14897 | 0.1207 | 0.47615 | 121 | 99 | 110 | LFT |  | TRK | 43300
LIV.NSY.1 | 1600 | 609.53 | 1683 | 641.18 | 1761 | 671.11 | 0.0040946 | 0.03069 | 0.018792 | 0.10766 | 242 | 198 | 220 | LIV | 69300 | NSY | 69300
LIV.NWD.1 | 1060 | 403.98 | 1183 | 450.78 | 1293 | 492.85 | 0.018196 | 0.13228 | 0.081488 | 0.46328 | 242 | 198 | 220 | LIV | 39800 | NWD | 69300
LIV.WTK.1 | 1495 | 569.84 | 1572 | 599.15 | 1645 | 626.83 | 0.0028326 | 0.021255 | 0.013001 | 0.074446 | 242 | 198 | 220 | LIV | 39800 | WTK | 39800
LTN.TWT.1 | 1822 | 694.33 | 1917 | 730.31 | 2006 | 764.34 | 0.00062975 | 0.0055215 | 0.0033924 | 0.016362 | 242 | 198 | 220 | LTN | 45600 | TWT
MAN.NMA.1 | 818 | 311.61 | 912 | 347.6 | 997 | 379.93 | 0.012271 | 0.087674 | 0.053003 | 0.28483 | 242 | 198 | 220 | MAN | 45600 | NMA | 69300
MAN.NMA.2 | 818 | 311.61 | 912 | 347.6 | 997 | 379.93 | 0.012275 | 0.087705 | 0.053022 | 0.28491 | 242 | 198 | 220 | MAN | 54600 | NMA | 69300
MAN.NMA.3 | 818 | 311.61 | 912 | 347.6 | 997 | 379.93 | 0.0123 | 0.085326 | 0.053174 | 0.2808 | 242 | 198 | 220 | MAN | 33800 | NMA | 69300
MDN.MPE.1 | 1200 | 228.63 | 1200 | 228.63 | 1200 | 228.63 | 0.010599 | 0.062488 | 0.046102 | 0.18072 | 121 | 99 | 110 | MDN | 43300 | MPE | 45600
MDN.MPE.2 | 1477 | 281.44 | 1561 | 297.5 | 1641 | 312.62 | 0.010416 | 0.062493 | 0.045919 | 0.18074 | 121 | 99 | 110 | MDN | 43300 | MPE | 69300
MGM.MST.1 | 709 | 135.1 | 746 | 142.14 | 781 | 148.79 | 0.045417 | 0.17946 | 0.11445 | 0.61983 | 121 | 99 | 110 | MGM | 43300 | MST | 43300
MGM.WDV.1 | 709 | 135.1 | 746 | 142.14 | 781 | 148.79 | 0.021113 | 0.085901 | 0.05347 | 0.28637 | 121 | 99 | 110 | MGM | 43300 | WDV | 54600
MKT.MNI.1 | 501 | 95.43 | 527 | 100.42 | 552 | 105.15 | 0.0079017 | 0.018931 | 0.014812 | 0.049133 | 121 | 99 | 110 | MKT |  | MNI | 54600
MKT.SFD.1 | 482 | 91.89 | 507 | 96.69 | 531 | 101.24 | 0.067971 | 0.15347 | 0.1248 | 0.43899 | 121 | 99 | 110 | MKT |  | SFD | 43300
MNG.OTA.1 | 1600 | 304.84 | 1600 | 304.84 | 1600 | 304.84 | 0.0010215 | 0.0078099 | 0.0055017 | 0.029137 | 121 | 99 | 110 | MNG | 69300 | OTA | 54600
MNG.OTA.2 | 1600 | 304.84 | 1600 | 304.84 | 1600 | 304.84 | 0.0010289 | 0.0078661 | 0.0055413 | 0.029394 | 121 | 99 | 110 | MNG | 69300 | OTA | 54600
MNG.ROS.1 | 501 | 95.43 | 527 | 100.42 | 552 | 105.15 | 0.016233 | 0.038155 | 0.030519 | 0.12715 | 121 | 99 | 110 | MNG | 69300 | ROS | 45600
MNG.ROS.2 | 501 | 95.43 | 527 | 100.42 | 552 | 105.15 | 0.016242 | 0.038225 | 0.030569 | 0.12747 | 121 | 99 | 110 | MNG | 69300 | ROS | 45600
MPE.MTO.1 | 292 | 55.68 | 326 | 62.16 | 357 | 67.99 | 0.070432 | 0.12453 | 0.11812 | 0.4373 | 121 | 99 | 110 | MPE | 69300 | MTO
MPE.MTO.2 | 292 | 55.68 | 326 | 62.16 | 357 | 67.99 | 0.070436 | 0.12453 | 0.11813 | 0.43732 | 121 | 99 | 110 | MPE | 43300 | MTO
MTM.PIE.2 | 333 | 63.36 | 371 | 70.73 | 406 | 77.36 | 0.013974 | 0.02927 | 0.024697 | 0.093636 | 121 | 99 | 110 | MTM | 45600 | PIE
MTN.WGN.1 | 345 | 65.81 | 386 | 73.46 | 422 | 80.34 | 0.03904 | 0.092374 | 0.073184 | 0.3035 | 121 | 99 | 110 | MTN |  | WGN | 45600
MTO.WEL.1 | 292 | 55.68 | 326 | 62.16 | 357 | 67.99 | 0.05084 | 0.09305 | 0.085285 | 0.30414 | 121 | 99 | 110 | MTO |  | WEL
MTO.WEL.2 | 292 | 55.68 | 326 | 62.16 | 357 | 67.99 | 0.050841 | 0.093051 | 0.085288 | 0.30415 | 121 | 99 | 110 | MTO |  | WEL
MTR.OKN.1 | 300 | 57.14 | 335 | 63.8 | 366 | 69.8 | 0.059679 | 0.14001 | 0.1077 | 0.43102 | 121 | 99 | 110 | MTR | 45600 | OKN | 54600
MTT.WGN.2 | 345 | 65.81 | 386 | 73.46 | 422 | 80.34 | 0.038973 | 0.092218 | 0.073059 | 0.30299 | 121 | 99 | 110 | MTT |  | WGN | 45600
NMA.TWI.1 | 1006 | 383.15 | 1121 | 427.34 | 1226 | 467.01 | 0.003069 | 0.022115 | 0.014165 | 0.073981 | 242 | 198 | 220 | NMA | 69300 | TWI | 54600
NMA.TWI.2 | 1006 | 383.15 | 1121 | 427.34 | 1226 | 467.01 | 0.0030688 | 0.022114 | 0.014164 | 0.073976 | 242 | 198 | 220 | NMA | 69300 | TWI | 54600
NSY.ROX.1 | 1600 | 609.53 | 1683 | 641.18 | 1761 | 671.11 | 0.0080244 | 0.060146 | 0.036834 | 0.20831 | 242 | 198 | 220 | NSY | 69300 | ROX | 69300
OHA.TWZ.1 | 911 | 347.16 | 958 | 365.15 | 1003 | 382.17 | 0.0011178 | 0.0067829 | 0.0035731 | 0.01971 | 242 | 198 | 220 | OHA | 45600 | TWZ | 54600
OHA.TWZ.2 | 911 | 347.16 | 958 | 365.15 | 1003 | 382.17 | 0.0011182 | 0.0067864 | 0.0035748 | 0.01972 | 242 | 198 | 220 | OHA | 45600 | TWZ | 54600
OHB.TWZ.3 | 1822 | 694.33 | 1917 | 730.31 | 2006 | 764.34 | 0.00025165 | 0.0021938 | 0.0013572 | 0.0058401 | 242 | 198 | 220 | OHB | 43300 | TWZ | 45600
OHC.TWZ.4 | 1822 | 694.33 | 1917 | 730.31 | 2006 | 764.34 | 0.00083223 | 0.0072479 | 0.0044839 | 0.020838 | 242 | 198 | 220 | OHC | 54600 | TWZ | 45600
OHK.WRK.1 | 874 | 333.13 | 908 | 346 | 940 | 358.32 | 0.0047506 | 0.022806 | 0.012656 | 0.052452 | 242 | 198 | 220 | OHK |  | WRK | 69300
OHW.OTA.1 | 1614 | 615.03 | 1689 | 643.71 | 1761 | 670.96 | 0.0066694 | 0.04323 | 0.028861 | 0.14172 | 242 | 198 | 220 | OHW |  | OTA | 69300
OHW.OTA.2 | 1614 | 615.03 | 1689 | 643.71 | 1761 | 670.96 | 0.0066899 | 0.043394 | 0.028993 | 0.14216 | 242 | 198 | 220 | OHW |  | OTA | 69300
OHW.WKM.1 | 1614 | 615.03 | 1689 | 643.71 | 1761 | 670.96 | 0.010873 | 0.070489 | 0.047062 | 0.23115 | 242 | 198 | 220 | OHW |  | WKM | 54600
OHW.WKM.2 | 1862 | 709.42 | 1958 | 746.18 | 2049 | 780.95 | 0.0037457 | 0.070306 | 0.040586 | 0.16809 | 242 | 198 | 220 | OHW | 54600 | WKM
OKE.OWH.1 | 298 | 56.74 | 332 | 63.33 | 364 | 69.28 | 0.012394 | 0.04556 | 0.028949 | 0.12288 | 121 | 99 | 110 | OKE |  | OWH | 43300
OKE.TMI.1 | 333 | 63.36 | 371 | 70.73 | 406 | 77.36 | 0.039347 | 0.087803 | 0.07125 | 0.28102 | 121 | 99 | 110 | OKE |  | TMI | 43300
OKE.TRK.1 | 333 | 63.36 | 371 | 70.73 | 406 | 77.36 | 0.031437 | 0.069963 | 0.056923 | 0.22359 | 121 | 99 | 110 | OKE |  | TRK | 43300
OKN.RTR.1 | 300 | 57.14 | 335 | 63.8 | 366 | 69.8 | 0.044094 | 0.10602 | 0.079558 | 0.31128 | 121 | 99 | 110 | OKN | 54600 | RTR
ONG.RTO.1 | 300 | 57.14 | 335 | 63.8 | 366 | 69.8 | 0.07694 | 0.18077 | 0.13884 | 0.55974 | 121 | 99 | 110 | ONG | 45600 | RTO
ONG.RTR.1 | 300 | 57.14 | 335 | 63.8 | 366 | 69.8 | 0.075434 | 0.17736 | 0.13613 | 0.54734 | 121 | 99 | 110 | ONG | 45600 | RTR
OPI.TIM.1 | 640 | 244.04 | 715 | 272.28 | 781 | 297.67 | 0.0043209 | 0.027352 | 0.014218 | 0.081781 | 242 | 198 | 220 | OPI |  | TIM | 39800
OPI.TIM.2 | 640 | 244.04 | 715 | 272.28 | 781 | 297.67 | 0.0043207 | 0.027351 | 0.014218 | 0.081778 | 242 | 198 | 220 | OPI |  | TIM | 39800
OPI.TWZ.1 | 1822 | 694.33 | 1917 | 730.31 | 2006 | 764.34 | 0.0052167 | 0.044607 | 0.02811 | 0.16324 | 242 | 198 | 220 | OPI |  | TWZ | 45600
OPI.TWZ.2 | 1822 | 694.33 | 1917 | 730.31 | 2006 | 764.34 | 0.0052167 | 0.044607 | 0.02811 | 0.16324 | 242 | 198 | 220 | OPI |  | TWZ | 69300
OTA.PAK.3 | 1600 | 609.68 | 1600 | 609.68 | 1600 | 609.68 | 0.00017438 | 0.0030843 | 0.0018264 | 0.010386 | 242 | 198 | 220 | OTA | 45600 | PAK
OTA.PAK.4 | 2991 | 1139.68 | 3145 | 1198.29 | 3150 | 1200.31 | 0.00016157 | 0.0028769 | 0.0016915 | 0.0096694 | 242 | 198 | 220 | OTA | 86600 | PAK
OTA.PEN.2 | 786 | 149.75 | 798 | 152.04 | 831 | 158.33 | 0.0057298 | 0.015179 | 0.017725 | 0.050735 | 121 | 99 | 110 | OTA | 54600 | PEN | 54600
OTA.PEN.5 | 1231 | 469.17 | 1262 | 480.9 | 1292 | 492.27 | 0.0013085 | 0.0080684 | 0.0042194 | 0.019533 | 242 | 198 | 220 | OTA | 86600 | PEN
OTA.PEN.6 | 1231 | 469.17 | 1262 | 480.9 | 1292 | 492.27 | 0.0013428 | 0.0083901 | 0.0044225 | 0.020413 | 242 | 198 | 220 | OTA | 69300 | PEN | 45600
OTA.ROS.1 | 415 | 79.07 | 440 | 83.83 | 458 | 87.26 | 0.0258 | 0.059538 | 0.050051 | 0.14952 | 121 | 99 | 110 | OTA | 54600 | ROS | 45600
OTA.ROS.2 | 415 | 79.07 | 440 | 83.83 | 458 | 87.26 | 0.025669 | 0.058783 | 0.049615 | 0.1477 | 121 | 99 | 110 | OTA | 50200 | ROS | 45600
OTA.SWN.1 | 2400 | 914.52 | 2400 | 914.52 | 2400 | 914.52 | 0.00041116 | 0.003599 | 0.0022351 | 0.011212 | 242 | 198 | 220 | OTA | 45600 | SWN | 43300
OTA.TAT.1 | 2991 | 1139.68 | 3145 | 1198.29 | 3150 | 1200.31 | 0.00037893 | 0.0067504 | 0.0039696 | 0.018607 | 242 | 198 | 220 | OTA | 69300 | TAT
OTA.TAT.2 | 1779 | 677.89 | 1806 | 688.18 | 1900 | 724 | 0.00039628 | 0.0068134 | 0.0040508 | 0.018773 | 242 | 198 | 220 | OTA | 69300 | TAT
PAK.PEN.3 | 2294 | 874.13 | 2294 | 874.13 | 2449 | 933.19 | 0.00027107 | 0.0038684 | 0.0013864 | 0.0011622 | 242 | 198 | 220 | PAK |  | PEN | 69300
PEN.REA.R862 | 1500 | 571.58 | 1500 | 571.58 | 1500 | 571.58 | 0.00010124 | 0.03719 |  |  | 242 | 198 | 220 | PEN | 14500
PEN.T34.G2 | 1258 | 479.36 | 1289 | 491.35 | 1320 | 502.97 | 3.3058e-06 | 2.1074e-05 | 1.095e-05 | 6.219e-05 | 242 | 198 | 220 | PEN | 69300 | T34
PEN.T34.G4 | 2400 | 914.52 | 2400 | 914.52 | 2400 | 914.52 | 3.719e-06 | 3.5744e-05 | 2.1488e-05 | 0.00013492 | 242 | 198 | 220 | PEN | 45600 | T34
RDF.TUI.1 | 300 | 57.15 | 335 | 63.81 | 366 | 69.81 | 0.147 | 0.33432 | 0.26532 | 1.086 | 121 | 99 | 110 | RDF | 45400 | TUI | 43300
RDF.TUI.2 | 300 | 57.15 | 335 | 63.81 | 366 | 69.81 | 0.14699 | 0.33432 | 0.26531 | 1.0859 | 121 | 99 | 110 | RDF | 45400 | TUI | 45600
RDF.WHI.1 | 1254 | 477.69 | 1399 | 532.98 | 1529 | 582.67 | 0.0016031 | 0.01373 | 0.0086403 | 0.051264 | 242 | 198 | 220 | RDF | 45600 | WHI | 54600
ROX.TMH.1 | 1011 | 385.42 | 1128 | 429.87 | 1233 | 469.78 | 0.0069959 | 0.06329 | 0.037912 | 0.23733 | 242 | 198 | 220 | ROX | 45600 | TMH | 69300
ROX.TMH.2 | 1011 | 385.42 | 1128 | 429.87 | 1233 | 469.78 | 0.0069955 | 0.063287 | 0.03791 | 0.23732 | 242 | 198 | 220 | ROX | 45600 | TMH | 69300
RPO.TNG.1 | 627 | 238.85 | 699 | 266.49 | 765 | 291.34 | 0.0080312 | 0.049084 | 0.025652 | 0.13878 | 242 | 198 | 220 | RPO | 54600 | TNG | 45600
RPO.WRK.1 | 955 | 363.85 | 999 | 380.78 | 1042 | 396.87 | 0.010283 | 0.06303 | 0.032842 | 0.18366 | 242 | 198 | 220 | RPO | 54600 | WRK | 69300
SBK.WPR.1 | 333 | 38.02 | 371 | 42.44 | 406 | 46.41 | 0.1451 | 0.31027 | 0.26278 | 1.0594 | 72.6 | 59.4 | 66 | SBK | 43300 | WPR | 43300
SDN.TMH.1 | 875 | 333.31 | 924 | 352.24 | 971 | 370.08 | 0.0011901 | 0.007112 | 0.0038012 | 0.020089 | 242 | 198 | 220 | SDN | 45600 | TMH | 69300
SFD.TMN.1 | 1231 | 469.17 | 1262 | 480.9 | 1292 | 492.27 | 0.015252 | 0.092322 | 0.048723 | 0.27678 | 242 | 198 | 220 | SFD | 45600 | TMN | 69300
STU.TIM.1 | 253 | 48.23 | 283 | 53.84 | 309 | 58.9 | 0.10158 | 0.16249 | 0.16117 | 0.5453 | 121 | 99 | 110 | STU | 45600 | TIM | 21700
THI.WKM.1 | 2600 | 990.73 | 2600 | 990.73 | 2600 | 990.73 | 0.0015775 | 0.021058 | 0.012079 | 0.060221 | 242 | 198 | 220 | THI | 125000 | WKM | 69300
THI.WRK.1 | 2600 | 990.73 | 2600 | 990.73 | 2600 | 990.73 | 0.00024711 | 0.0032919 | 0.0018926 | 0.0093595 | 242 | 198 | 220 | THI | 125000 | WRK | 69300
TKB.TWZ.1 | 1461 | 556.65 | 1546 | 589.22 | 1600 | 609.68 | 0.0023337 | 0.016031 | 0.010123 | 0.049384 | 242 | 198 | 220 | TKB | 45600 | TWZ | 45600
TKR.WIL.1 | 1477 | 281.44 | 1561 | 297.5 | 1641 | 312.62 | 0.0060479 | 0.038576 | 0.02726 | 0.11093 | 121 | 99 | 110 | TKR | 69300 | WIL | 43300
TKR.WIL.2 | 1477 | 281.44 | 1561 | 297.5 | 1641 | 312.62 | 0.0060545 | 0.038748 | 0.027321 | 0.11128 | 121 | 99 | 110 | TKR | 69300 | WIL | 43300
TKU.WKM.1 | 807 | 307.52 | 845 | 321.85 | 880 | 335.48 | 0.012483 | 0.060205 | 0.033254 | 0.16738 | 242 | 198 | 220 | TKU | 45600 | WKM | 54600
TKU.WKM.2 | 807 | 307.52 | 845 | 321.85 | 880 | 335.48 | 0.012551 | 0.060152 | 0.033438 | 0.16929 | 242 | 198 | 220 | TKU | 45600 | WKM | 54600
TMN.TWH.1 | 1231 | 469.17 | 1262 | 480.9 | 1292 | 492.27 | 0.020185 | 0.12082 | 0.064498 | 0.36797 | 242 | 198 | 220 | TMN | 69300 | TWH | 54600
WGN.WVY.1 | 805 | 153.41 | 836 | 159.36 | 866 | 165.05 | 0.038241 | 0.16007 | 0.09637 | 0.49878 | 121 | 99 | 110 | WGN | 45600 | WVY | 45600
WHI.WRK.1 | 1254 | 477.69 | 1399 | 532.98 | 1529 | 582.67 | 0.0079357 | 0.067843 | 0.042764 | 0.26182 | 242 | 198 | 220 | WHI | 45600 | WRK | 45600
WKM.WKM.AB.1 | 2694 | 1026.61 | 2797 | 1065.98 | 2896 | 1103.63 | 3.3264e-05 | 0.00043533 | 0.00025517 | 0.001149 | 242 | 198 | 220 | WKM |  | WKM | 69300
WKM.WKM.AB.2 | 2694 | 1026.61 | 2797 | 1065.98 | 2896 | 1103.63 | 3.3058e-05 | 0.00043202 | 0.0002531 | 0.0011403 | 242 | 198 | 220 | WKM |  | WKM | 69300
WKM.WRK.1 | 2500 | 952.63 | 2500 | 952.63 | 2500 | 952.63 | 0.0018475 | 0.024655 | 0.014149 | 0.070287 | 242 | 198 | 220 | WKM |  | WRK | 69300
WPR.WTT.2 | 870 | 331.51 | 870 | 331.51 | 870 | 331.51 | 2.0661e-05 | 0.00014091 | 6.7975e-05 | 0.0003376 | 242 | 198 | 220 | WPR | 55400 | WTT
WPR.WTT.3 | 870 | 331.51 | 870 | 331.51 | 870 | 331.51 | 2.7273e-05 | 0.00018657 | 8.8843e-05 | 0.00048368 | 242 | 198 | 220 | WPR | 55400 | WTT

## 3W Transformer
Branch | Overall 24 hour post contingency capacity rating | [11 empty] | Continuous capacity rating | [5 empty] | Resistive and Reactive Level of Positive Sequence Impedance | [5 empty] | Resistive and Reactive Level of Zero Sequence Impedance | [5 empty] | High voltage range that branch can operate over |  | Nominal HV Operating Voltage | Nominal MV Operating Voltage | Nominal LV Operating Voltage | Site | Fault Current
| HV |  |  |  | MV |  |  |  | LV |  |  |  | HV |  | MV |  | LV |  | HV |  | MV |  | LV |  | HV |  | MV |  | LV
| Summer |  | Winter |  | Summer |  | Winter |  | Summer |  | Winter | [7 empty] | Resistance | Reactance | Resistance | Reactance | Resistance | Reactance | Resistance | Reactance | Resistance | Reactance | Resistance | Reactance | Maximum | Minimum |  |  |  |  | HV | MV | LV
| Amps | MVA | Amps | MVA | Amps | MVA | Amps | MVA | Amps | MVA | Amps | MVA | Amps | MVA | Amps | MVA | Amps | MVA | PU (100MVA) | PU (100MVA) | PU (100MVA) | PU (100MVA) | PU (100MVA) | PU (100MVA) | PU (100MVA) | PU (100MVA) | PU (100MVA) | PU (100MVA) | PU (100MVA) | PU (100MVA) | kV | kV | kV | kV | kV |  | Amp/sec | Amp/sec | Amp/sec
ALB.TF.T5 | 525 | 200 | 548 | 208.9 | 1050 | 200 | 1096 | 208.9 | 3780 | 72.02 | 3780 | 72.02 | 394 | 150 | 787 | 150 | 3149 | 60 | 0.000405 | 0.073163 | 0.0008883 | -0.00537 | 0.0033617 | 0.10227 | 0 | 0.099726 | 0 | -0.040481 | 0 | 0.27286 | 242 | 198 | 220 | 110 | 11 | ALB | 45600 | 45000
BPE.TF.T2 | 563 | 214.7 | 588 | 224.2 | 936 | 178.35 | 936 | 178.35 | 3002 | 57.2 | 3139 | 59.8 | 394 | 150 | 787 | 150 | 2099 | 40 | 0.0005258 | 0.10354 | 0.0008008 | -0.0074342 | 0.0041492 | 0.11483 | 0 | 0.21847 | 0 | -0.12962 | 0 | 0.51541 | 242 | 198 | 220 | 110 | 11 | BPE | 32900 | 32900
BPE.TF.T3 | 563 | 214.7 | 589 | 224.3 | 936 | 178.34 | 936 | 178.34 | 3007 | 57.3 | 3139 | 59.8 | 394 | 150 | 787 | 150 | 2099 | 40 | 0.00051 | 0.10355 | 0.00081 | -0.0073983 | 0.004115 | 0.11557 | 0 | 0.21734 | 0 | -0.12867 | 0 | 0.51677 | 242 | 198 | 220 | 110 | 11 | BPE | 32900 | 32900
DOB.TF.T11 | 526 | 100.3 | 550 | 104.8 | 637 | 72.83 | 637 | 72.83 | 1753 | 33.4 | 1832 | 34.9 | 394 | 75 | 637 | 72.83 | 1312 | 25 | 0.0005533 | 0.14772 | 0.0019933 | -0.017 | 0.012007 | 0.3224 | 0 | 0.19666 | 0 | -0.081796 | 0 | 0.984 | 121 | 99 | 110 | 66 | 11 | DOB | 42100 | 42100
DOB.TF.T12 | 498 | 94.8 | 520 | 99 | 829 | 94.8 | 866 | 99 | 1659 | 31.6 | 1732 | 33 | 394 | 75 | 656 | 75 | 1312 | 25 | 0.002 | 0.1446 | 0.002 | -0.0114 | 0.015333 | 0.29007 | 0 | 0.085402 | 0 | 0.018621 | 0 | 0.25943 | 121 | 99 | 110 | 66 | 11 | DOB | 42100 | 27700
EDG.TF.T5 | 152 | 58 | 164 | 62.5 | 304 | 58 | 328 | 62.5 | 1827 | 34.8 | 1968 | 37.5 | 131 | 50.01 | 262 | 50.01 | 1575 | 30 | 5.39e-05 | 0.03782 | 0.003922 | 0.057465 | 0.011685 | 0.14201 | 5.39e-05 | 0.03782 | 0.003922 | 0.057465 | 0.011685 | 0.14201 | 242 | 198 | 220 | 110 | 11 | EDG | 45600 | 14700
GOR.TF.T11 | 564 | 215 | 589 | 224.6 | 1128 | 215 | 1179 | 224.6 | 3007 | 57.3 | 3144 | 59.9 | 394 | 150 | 787 | 150 | 2099 | 40 | 0.00051 | 0.10293 | 0.00081 | -0.0068442 | 0.00409 | 0.11504 | 0 | 0.21662 | 0 | -0.12656 | 0 | 0.51654 | 242 | 198 | 220 | 110 | 11 | GOR | 54600 | 54600
GOR.TF.T12 | 551 | 209.9 | 575 | 219.2 | 1102 | 209.9 | 1151 | 219.2 | 2939 | 56 | 3070 | 58.5 | 394 | 150 | 787 | 150 | 2099 | 40 | 0.00051 | 0.10303 | 0.00081 | -0.0069442 | 0.00409 | 0.11392 | 0 | 0.216 | 0 | -0.12752 | 0 | 0.51305 | 242 | 198 | 220 | 110 | 11 | GOR | 54600 | 54600
HAY.TF.T1 | 659 | 251.3 | 688 | 262.3 | 1221 | 232.7 | 1275 | 242.9 | 4886 | 93.1 | 5102 | 97.2 | 567 | 216 | 1050 | 200 | 4199 | 80 | 0.0001008 | -0.011035 | 0.0008195 | 0.066934 | 0.0034118 | 0.079276 | 0 | 0.011035 | 0 | 0.066939 | 0 | 0.079349 | 242 | 198 | 220 | 110 | 11 | HAY | 43300 | 43300
HAY.TF.T2 | 659 | 251.3 | 688 | 262.3 | 1221 | 232.7 | 1275 | 242.9 | 4886 | 93.1 | 5102 | 97.2 | 567 | 216 | 1050 | 200 | 4199 | 80 | 0.0001008 | -0.011035 | 0.0008195 | 0.066934 | 0.0034118 | 0.079276 | 0 | 0.011035 | 0 | 0.066939 | 0 | 0.079349 | 242 | 198 | 220 | 110 | 11 | HAY | 43300 | 43300
HAY.TF.T5 | 659 | 251.3 | 688 | 262.3 | 1221 | 232.7 | 1275 | 242.9 | 4886 | 93.1 | 5102 | 97.2 | 567 | 216 | 1050 | 200 | 4199 | 80 | 0.0001008 | -0.011035 | 0.0008195 | 0.066934 | 0.0034118 | 0.079276 | 0 | 0.011035 | 0 | 0.066939 | 0 | 0.079349 | 242 | 198 | 220 | 110 | 11 | HAY | 43300 | 43300
HEN.TF.T1 | 719 | 274 | 761 | 290 | 1438 | 274 | 1522 | 290 | 4157 | 79.2 | 4157 | 79.2 | 525 | 200.01 | 1050 | 200.01 | 3149 | 60 | 0.0003535 | 0.02907 | 0.0003801 | -0.0032389 | 0.0033637 | 0.071372 | 0.0003535 | 0.02907 | 0.0003801 | -0.0032389 | 0.0033637 | 0.071372 | 242 | 198 | 220 | 110 | 11 | HEN | 45600 | 69300
HEN.TF.T5 | 719 | 274 | 761 | 290 | 1438 | 274 | 1522 | 290 | 4157 | 79.2 | 4157 | 79.2 | 525 | 200.01 | 1050 | 200.01 | 3149 | 60 | 0.0002825 | 0.026274 | 0.0004425 | -0.000811 | 0.0033403 | 0.068753 | 0.0002825 | 0.026274 | 0.0004425 | -0.000811 | 0.0033403 | 0.068753 | 242 | 198 | 220 | 110 | 11 | HEN | 45600 | 69300
HWB.TF.T6 | 494 | 188.2 | 515 | 196.4 | 988 | 188.2 | 1031 | 196.4 | 2635 | 50.2 | 2750 | 52.4 | 394 | 150 | 787 | 150 | 2099 | 40 | 0.0015667 | 0.13191 | 0 | -0.032712 | 0.0044333 | 0.12396 | 0 | 0.30277 | 0 | -0.2128 | 0 | 0.53952 | 242 | 198 | 220 | 110 | 11 | HWB | 43300 | 19900
INV.TF.T1 | 315 | 120 | 315 | 120 | 598 | 113.85 | 598 | 113.85 | 1968 | 37.5 | 1968 | 37.5 | 210 | 80 | 420 | 80 | 1312 | 25 | 0.0008625 | 0.13494 | 0.0014875 | -0.011062 | 0.0093875 | 0.19769 | 0 | 0.11698 | 0 | -0.0023408 | 0 | 0.1824 | 242 | 198 | 220 | 110 | 11 | INV | 45600 | 43300
ISL.TF.T3 | 661 | 252 | 698 | 266 | 2204 | 252 | 2327 | 266 | 3160 | 60.21 | 3160 | 60.21 | 525 | 200.01 | 1750 | 200.01 | 3149 | 60 | 0.0007891 | 0.082765 | 0.000367 | -0.0046501 | 0.0024402 | 0.057178 | 0.0007891 | 0.082765 | 0.000367 | -0.0046501 | 0.017316 | 0.055856 | 242 | 198 | 220 | 66 | 11 | ISL | 54600 | 54600 | 90100
ISL.TF.T6 | 801 | 305.1 | 836 | 318.4 | 2595 | 296.7 | 2709 | 309.7 | 3737 | 71.2 | 3900 | 74.3 | 674 | 257 | 2187 | 250 | 3149 | 60 | 0.0008 | 0.076 | 0.00055 | -0.0045 | 0.00345 | 0.0515 | 0 | 0.076004 | 0 | 0.0045335 | 0 | 0.051615 | 242 | 198 | 220 | 66 | 11 | ISL | 43300 | 54600
ISL.TF.T7 | 661 | 252 | 698 | 266 | 2204 | 252 | 2327 | 266 | 3968 | 75.6 | 4188 | 79.8 | 525 | 200.01 | 1750 | 200.01 | 3149 | 60 | 0.000775 | 0.083221 | 0.00039 | -0.0047748 | 0.0013949 | 0.055222 | 0.000775 | 0.083221 | 0.00039 | -0.0047748 | 0.0013949 | 0.055222 | 242 | 198 | 220 | 66 | 11 | ISL | 54600 | 54600
KAW.TF.T12 | 772 | 294.2 | 806 | 307 | 1544 | 294.2 | 1611 | 307 | 3706 | 70.6 | 3868 | 73.7 | 656 | 250 | 1312 | 250 | 3149 | 60 | 0.0002123 | 0.044995 | 0.0004957 | -0.004055 | 0.0026043 | 0.063022 | 0 | 0.099163 | 0 | -0.06157 | 0 | 0.29732 | 242 | 198 | 220 | 110 | 11 | KAW | 45600 | 43300
KAW.TF.T14 | 723 | 275.5 | 754 | 287.4 | 1446 | 275.5 | 1508 | 287.4 | 3469 | 66.1 | 3622 | 69 | 656 | 250 | 1312 | 250 | 3149 | 60 | 0.0003267 | 0.065435 | 0.0004933 | -0.006115 | 0.0029733 | 0.088798 | 0 | 0.1356 | 0 | -0.059514 | 0 | 0.40159 | 242 | 198 | 220 | 110 | 11 | KAW | 69300 | 54600
KIK.TF.T1 | 164 | 62.5 | 176 | 67 | 328 | 62.5 | 352 | 67 | 462 | 8.8 | 462 | 8.8 | 131 | 50.01 | 262 | 50.01 | 462 | 8.8 | 0.0009498 | 0.028828 | 0.003096 | 0.095214 | 0.010885 | 0.09892 | 0.0009498 | 0.028828 | 0.003096 | 0.095214 | 0.013116 | 0.098342 | 239.8 | 198 | 220 | 110 | 11 | KIK | 45600 | 43300 | 26300
KIK.TF.T2 | 478 | 182.3 | 500 | 190.6 | 957 | 182.3 | 1000 | 190.6 | 2551 | 48.6 | 2666 | 50.8 | 394 | 150 | 787 | 150 | 2099 | 40 | 0.00016 | 0.069986 | 0.00106 | -0.0048392 | 0.005065 | 0.10556 | 0 | 0.13291 | 0 | -0.074707 | 0 | 0.43424 | 242 | 198 | 220 | 110 | 11 | KIK | 69300 | 54600
KMO.TF.T2 | 585 | 223 | 590 | 225 | 1170 | 223 | 1181 | 225 | 3123 | 59.5 | 3149 | 60 | 394 | 150 | 787 | 150 | 2099 | 40 | 0.00049 | 0.075753 | 0.0008233 | -0.00758 | 0.0036433 | 0.10958 | 0 | 0.063198 | 0 | -0.0002118 | 0 | 0.10178 | 242 | 198 | 220 | 110 | 11 | KMO | 54600 | 54600
KMO.TF.T4 | 568 | 216.6 | 590 | 225 | 1137 | 216.6 | 1181 | 225 | 3034 | 57.8 | 3149 | 60 | 394 | 150 | 787 | 150 | 2099 | 40 | 0.0005333 | 0.076 | 0.0008667 | -0.0073333 | 0.0036 | 0.10933 | 0 | 0.063216 | 0 | -0.0005519 | 0 | 0.10166 | 242 | 198 | 220 | 110 | 11 | KMO | 54600 | 54600
MDN.TF.T5 | 472 | 179.8 | 493 | 188 | 944 | 179.8 | 987 | 188 | 2500 | 47.63 | 2500 | 47.63 | 394 | 150 | 787 | 150 | 2099 | 40 | 0.0005658 | 0.070259 | 0.0006408 | -0.0047658 | 0.0044842 | 0.10574 | 0 | 0.13291 | 0 | -0.074707 | 0 | 0.43424 | 242 | 198 | 220 | 110 | 11 | MDN | 62700 | 43300 | 69300
MDN.TF.T6 | 474 | 180.8 | 496 | 189 | 949 | 180.8 | 992 | 189 | 2500 | 47.63 | 2500 | 47.63 | 394 | 150 | 787 | 150 | 2099 | 40 | 0.0001475 | 0.070539 | 0.0010725 | -0.0046858 | 0.0037525 | 0.10069 | 0 | 0.13537 | 0 | -0.076494 | 0 | 0.41814 | 242 | 198 | 220 | 110 | 11 | MDN | 62700 | 43300 | 69300
OTA.TF.T3 | 849 | 323.6 | 886 | 337.7 | 1698 | 323.6 | 1772 | 337.7 | 4755 | 90.6 | 4965 | 94.6 | 656 | 250 | 1312 | 250 | 3674 | 70 | 0.0003006 | 0.064186 | 0.0005434 | -0.0058423 | 0.0032709 | 0.095814 | 0 | 0.10197 | 0 | -0.053186 | 0 | 0.34778 | 242 | 198 | 220 | 110 | 11 | OTA | 54600 | 69300
OTA.TF.T4 | 824 | 314 | 860 | 327.7 | 1648 | 314 | 1720 | 327.7 | 3957 | 75.4 | 4131 | 78.7 | 656 | 250 | 1312 | 250 | 3149 | 60 | 0.0001083 | 0.065177 | 0.0005917 | -0.0070567 | 0.0027583 | 0.09009 | 0 | 0.14064 | 0 | -0.087866 | 0 | 0.44631 | 242 | 198 | 220 | 110 | 11 | OTA | 69300 | 69300
PEN.TF.T10 | 838 | 319.2 | 874 | 333.1 | 1664 | 317.01 | 1664 | 317.01 | 4020 | 76.6 | 4199 | 80 | 656 | 250 | 1312 | 250 | 3149 | 60 | 0.000221 | 0.06529 | 0.000471 | -0.0070937 | 0.002879 | 0.089327 | 0 | 0.14104 | 0 | -0.088257 | 0 | 0.44349 | 242 | 198 | 220 | 110 | 11 | PEN | 45600 | 43300
PEN.TF.T6 | 780 | 297.3 | 814 | 310.3 | 1560 | 297.3 | 1629 | 310.3 | 3748 | 71.4 | 3910 | 74.5 | 656 | 250 | 1312 | 250 | 3149 | 60 | 0.000271 | 0.063032 | 0.000621 | -0.0041517 | 0.0024123 | 0.088652 | 0 | 0.12818 | 0 | -0.077404 | 0 | 0.41693 | 242 | 198 | 220 | 110 | 11 | PEN | 54600 | 43300
RDF.TF.T5 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242 | 198 | 220 | 110 | 11 | RDF | 54600 | 125000
ROX.TF.T10 | 493 | 188 | 515 | 196.3 | 987 | 188 | 1030 | 196.3 | 2630 | 50.1 | 2745 | 52.3 | 394 | 150 | 787 | 150 | 2099 | 40 | 0.0004083 | 0.1072 | 0.0011583 | -0.0092 | 0.0054917 | 0.1424 | 0 | 0.21783 | 0 | -0.12865 | 0 | 0.60618 | 242 | 198 | 220 | 110 | 11 | ROX | 69300 | 54600
SFD.TF.T10 | 412 | 157.1 | 437 | 166.5 | 709 | 135 | 751 | 143 | 4251 | 81 | 4503 | 85.8 | 305 | 116.4 | 525 | 99.99 | 3149 | 60 | 0.0004778 | 0.02517 | 0.0015224 | 0.027765 | 0.0043782 | 0.079083 | 0.0004778 | 0.02517 | 0.0015224 | 0.027765 | 0.0043782 | 0.079083 | 242 | 198 | 220 | 110 | 11 | SFD |  | 54600
SFD.TF.T9 | 721 | 274.8 | 753 | 286.9 | 1310 | 249.56 | 1310 | 249.56 | 2887 | 55 | 3013 | 57.4 | 525 | 200 | 1050 | 200 | 2099 | 40 | 0.00025 | 0.062343 | 0.0006157 | -0.0044253 | 0.004275 | 0.072932 | 0 | 0.16476 | 6.5289e-05 | -0.11173 | 0 | 0.44583 | 242 | 198 | 220 | 110 | 11 | SFD | 69300 | 54600
STK.TF.T7 | 472 | 180 | 494 | 188.2 | 945 | 180 | 988 | 188.2 | 2519 | 48 | 2635 | 50.2 | 394 | 150 | 787 | 150 | 2099 | 40 | 9.08e-05 | 0.070101 | 0.0011158 | -0.0048742 | 0.0050342 | 0.1015 | 0 | 0.13291 | 0 | -0.074707 | 0 | 0.43424 | 239.8 | 198 | 220 | 110 | 11 | STK | 45600 | 43300
TIM.TF.T5 | 897 | 341.7 | 937 | 356.9 | 1666 | 317.33 | 1666 | 317.33 | 4304 | 82 | 4493 | 85.6 | 656 | 250 | 1312 | 250 | 3149 | 60 | 0.000213 | 0.044443 | 0.000463 | -0.004207 | 0.0024703 | 0.064524 | 0 | 0.098726 | 0 | -0.061575 | 0 | 0.30508 | 242 | 198 | 220 | 110 | 11 | TIM | 62700 | 43300
TIM.TF.T8 | 847 | 322.8 | 884 | 337 | 1664 | 317.02 | 1664 | 317.02 | 4068 | 77.5 | 4246 | 80.9 | 656 | 250 | 1312 | 250 | 3149 | 60 | 0.0001417 | 0.045994 | 0.0005583 | -0.0038897 | 0.0030417 | 0.06774 | 0 | 0.10124 | 0 | -0.062984 | 0 | 0.32011 | 242 | 198 | 220 | 110 | 11 | TIM | 69300 | 43300
TRK.TF.T2 | 528 | 201.2 | 551 | 210.1 | 1056 | 201.2 | 1103 | 210.1 | 630 | 12 | 630 | 12 | 394 | 150 | 787 | 150 | 630 | 12 | 0.0006167 | 0.1067 | 0.0009833 | -0.0067667 | 0.0055167 | 0.1065 | 0 | 0.1067 | 0 | 0.0068377 | 0 | 0.10664 | 242 | 198 | 220 | 110 | 11 | TRK | 54600 | 54600
TRK.TF.T3 | 528 | 201.2 | 551 | 210.1 | 1056 | 201.2 | 1103 | 210.1 | 2819 | 53.7 | 2939 | 56 | 394 | 150 | 787 | 150 | 2099 | 40 | 0.0006167 | 0.1067 | 0.0009833 | -0.0067667 | 0.0055167 | 0.1065 | 0 | 0.1067 | 0 | 0.0068377 | 0 | 0.10664 | 242 | 198 | 220 | 110 | 11 | TRK | 54600 | 43300
WIL.TF.T8 | 770 | 293.3 | 804 | 306.2 | 1539 | 293.3 | 1607 | 306.2 | 3695 | 70.4 | 3780 | 72.02 | 656 | 250 | 1312 | 250 | 3149 | 60 | 0.00026403 | 0.044213 | 0.0004703 | -0.0035153 | 0.002063 | 0.062032 | 3.9876e-05 | 0.087268 | 0 | -0.051799 | 0 | 0.28682 | 242 | 198 | 220 | 110 | 11 | WIL | 54600 | 43300
WTK.TF.T23 | 245 | 93.5 | 261 | 99.6 | 420 | 80 | 447 | 85.2 | 2519 | 48 | 2682 | 51.1 | 200 | 76.05 | 341 | 65.01 | 2047 | 39 | 0.000395 | 0.049177 | 0.0011401 | -0.0036392 | 0.0043754 | 0.069146 | 0.000395 | 0.049177 | 0.0011401 | -0.0036392 | 0.0043754 | 0.069146 | 242 | 198 | 220 | 110 | 11 | WTK | 39800 | 43300
WTK.TF.T24 | 245 | 93.5 | 261 | 99.6 | 420 | 80 | 447 | 85.2 | 2519 | 48 | 2682 | 51.1 | 200 | 76.05 | 341 | 65.01 | 2047 | 39 | 0.0006301 | 0.047532 | 0.0009101 | -0.0050283 | 0.0041254 | 0.069735 | 0.0006301 | 0.047532 | 0.0009101 | -0.0050283 | 0.0041254 | 0.069735 | 242 | 198 | 220 | 110 | 11 | WTK | 39800 | 43300

## 2W Transformer
Branch | Overall 24 hour post contingency capacity rating |  |  |  | Continuous capacity rating |  | Resistive and Reactive Level of Positive Sequence Impedance |  | Resistive and Reactive Level of Zero Sequence Impedance |  | High voltage range that branch can operate over |  | Nominal HV Operating Voltage | Nominal LV Operating Voltage | Site | Fault Current
| Summer |  | Winter |  |  |  | Resistance | Reactance | Resistance | Reactance | Maximum | Minimum |  |  |  | HV | LV
| Amps | MVA | Amps | MVA | Amps | MVA | PU (100MVA) | PU (100MVA) | PU (100MVA) | PU (100MVA) | kV | kV | kV | kV |  | Amp/sec | Amp/sec
HAM.TF.T6 | 1407 | 268 | 1469 | 279.8 | 1155 | 220 | 0.0021364 | 0.074091 | 0 | -0.049156 | 242 | 198 | 220 | 110 | HAM | 45600 | 43300
HAM.TF.T9 | 1304 | 248.5 | 1362 | 259.5 | 1050 | 200 | 0.0011112 | 0.073527 | 0.00034711 | 0.010334 | 242 | 198 | 220 | 110 | HAM | 43300 | 45600
OTA.TF.T5 | 1670 | 318.2 | 1745 | 332.4 | 1312 | 250 | 0.00068 | 0.05868 | 0 | 0.54318 | 242 | 198 | 220 | 110 | OTA | 54600 | 43300
RDF.TF.T4A | 514 | 98 | 546 | 104 | 446 | 85 | 0.00419 | 0.10091 | 0 | 0.101 | 242 | 198 | 220 | 110 | RDF
RDF.TF.T4B | 514 | 98 | 546 | 104 | 446 | 85 | 0.00419 | 0.10091 | 0 | 0.101 | 242 | 198 | 220 | 110 | RDF
WPR.TF.T12 | 925 | 105.7 | 967 | 110.6 | 700 | 80 | 0.0036 | 0.1567 | 0 | 0.15674 | 242 | 198 | 220 | 66 | WPR | 43300 | 43300
WPR.TF.T13 | 925 | 105.7 | 967 | 110.6 | 700 | 80 | 0.0036 | 0.1567 | 0 | 0.15674 | 242 | 198 | 220 | 66 | WPR | 43300 | 43300

## Tap Changers
Branch | Tap Changer | Tap Voltage Range (kV) |  | Number of Tapping Steps | Tapping step size as % of nominal operating voltage | On-Load/Off-Load | On-Load tapping capability | Auto selected | Normally set tap position | Off-Load normally set tap position
|  | Maximum | Minimum
ALB.TF.T5 | ALB-TF-T5-Tap Changer -- ONLOAD -- HV | 242 | 187 | 20 | 1.25 | ONLOAD | Automatic | No
BPE.TF.T2 | BPE-TF-T2-Tap Changer | 242 | 198 | 16 | 1.25 | ONLOAD | Manual |  | 8
BPE.TF.T3 | BPE-TF-T3-Tap Changer | 242 | 198 | 16 | 1.25 | ONLOAD | Manual |  | 8
DOB.TF.T11 | DOB-TF-T11-Tap Changer | 118.25 | 93.5 | 18 | 1.25 | ONLOAD | Manual |  | 6
DOB.TF.T12 | DOB-TF-T12-On Load Tap Changer | 118.25 | 93.5 | 18 | 1.25 | ONLOAD | Manual |  | 5
EDG.TF.T5 | EDG-TF-T5B-Tap Changer -- OFFLOAD -- HV | 220 | 198 | 4 | 2.5 | OFFLOAD |  |  |  | 2
EDG.TF.T5 | EDG-TF-T5R-Tap Changer -- OFFLOAD -- HV | 220 | 198 | 4 | 2.5 | OFFLOAD |  |  |  | 2
EDG.TF.T5 | EDG-TF-T5Y-Tap Changer -- OFFLOAD -- HV | 220 | 198 | 4 | 2.5 | OFFLOAD |  |  |  | 2
EDG.TF.T5 | EDG-TF-T5B-Tap Changer -- OFFLOAD -- LV | 11.55 | 10.45 | 2 | 5 | OFFLOAD |  |  |  | 2
EDG.TF.T5 | EDG-TF-T5R-Tap Changer -- OFFLOAD -- LV | 11.55 | 10.45 | 2 | 5 | OFFLOAD |  |  |  | 2
EDG.TF.T5 | EDG-TF-T5Y-Tap Changer -- OFFLOAD -- LV | 11.55 | 10.45 | 2 | 5 | OFFLOAD |  |  |  | 2
GOR.TF.T11 | GOR-TF-T11-Tap Changer | 242 | 198 | 16 | 1.25 | ONLOAD | Manual |  | 5
GOR.TF.T12 | GOR-TF-T12-Tap Changer | 242 | 198 | 16 | 1.25 | ONLOAD | Manual |  | 5
HAM.TF.T6 | HAM-TF-T6-Tap Changer -- ONLOAD -- HV | 242 | 198 | 16 | 1.25 | ONLOAD | Manual |  | 9
HAM.TF.T9 | HAM-TF-T9-Tap Changer -- ONLOAD -- HV | 242 | 198 | 16 | 1.25 | ONLOAD | Manual |  | 9
HAY.TF.T1 | HAY-TF-T1-Tap Changer -- ONLOAD -- HV | 242 | 187 | 20 | 1.25 | ONLOAD | Automatic | No
HAY.TF.T1 | HAY-TF-T1-Tap Changer -- OFFLOAD -- LV | 11.55 | 10.45 | 4 | 2.5 | OFFLOAD |  |  |  | 4
HAY.TF.T2 | HAY-TF-T2-Tap Changer -- ONLOAD -- HV | 242 | 187 | 20 | 1.25 | ONLOAD | Automatic | No
HAY.TF.T2 | HAY-TF-T2-Tap Changer -- OFFLOAD -- LV | 11.55 | 10.45 | 4 | 2.5 | OFFLOAD |  |  |  | 4
HAY.TF.T5 | HAY-TF-T5-Tap Changer -- ONLOAD -- HV | 242 | 187 | 20 | 1.25 | ONLOAD | Automatic | No
HAY.TF.T5 | HAY-TF-T5-Tap Changer -- OFFLOAD -- LV | 11.55 | 10.45 | 4 | 2.5 | OFFLOAD |  |  |  | 4
HEN.TF.T1 | HEN-TF-T1B-Tap Changer -- ONLOAD -- HV | 231 | 198 | 12 | 1.25 | ONLOAD | Manual |  | 6
HEN.TF.T1 | HEN-TF-T1Y-Tap Changer -- ONLOAD -- HV | 231 | 198 | 12 | 1.25 | ONLOAD | Manual |  | 6
HEN.TF.T1 | HEN-TF-T1B-Tap Changer -- OFFLOAD -- LV | 11.55 | 10.45 | 4 | 2.5 | OFFLOAD |  |  |  | 5
HEN.TF.T1 | HEN-TF-T1Y-Tap Changer -- OFFLOAD -- LV | 11.73 | 10.27 | 4 | 3.33 | OFFLOAD |  |  |  | 5
HEN.TF.T5 | HEN-TF-T5B-Tap Changer -- ONLOAD -- HV | 231 | 198 | 12 | 1.25 | ONLOAD | Manual |  | 6
HEN.TF.T5 | HEN-TF-T5R-Tap Changer -- ONLOAD -- HV | 231 | 198 | 12 | 1.25 | ONLOAD | Manual |  | 6
HEN.TF.T5 | HEN-TF-T5Y-Tap Changer -- ONLOAD -- HV | 231 | 198 | 12 | 1.25 | ONLOAD | Manual |  | 6
HEN.TF.T5 | HEN-TF-T5B-Tap Changer -- OFFLOAD -- LV | 11.55 | 10.45 | 4 | 2.5 | OFFLOAD |  |  |  | 5
HEN.TF.T5 | HEN-TF-T5R-Tap Changer -- OFFLOAD -- LV | 11.55 | 10.45 | 4 | 2.5 | OFFLOAD |  |  |  | 5
HEN.TF.T5 | HEN-TF-T5Y-Tap Changer -- OFFLOAD -- LV | 11.55 | 10.45 | 4 | 2.5 | OFFLOAD |  |  |  | 5
HWB.TF.T6 | HWB-TF-T6-Tap Changer | 242 | 198 | 17 | 1.25 | ONLOAD | Manual |  | 6
INV.TF.T1 | INV-TF-T1-Tap Changer | 242 | 198 | 16 | 1.25 | ONLOAD | Manual |  | 7
ISL.TF.T3 | ISL-TF-T3B-Tap Changer -- ONLOAD -- HV | 231 | 187 | 16 | 1.25 | ONLOAD | Manual |  | 5
ISL.TF.T3 | ISL-TF-T3R-Tap Changer -- ONLOAD -- HV | 231 | 187 | 16 | 1.25 | ONLOAD | Manual |  | 5
ISL.TF.T3 | ISL-TF-T3B-Tap Changer -- OFFLOAD -- LV | 11.48 | 10.45 | 4 | 2.37 | OFFLOAD |  |  |  | 4
ISL.TF.T3 | ISL-TF-T3R-Tap Changer -- OFFLOAD -- LV | 11.48 | 10.45 | 4 | 2.37 | OFFLOAD |  |  |  | 4
ISL.TF.T6 | ISL-TF-T6-Tap Changer -- ONLOAD -- HV | 240.02 | 194.26 | 16 | 1.3 | ONLOAD | Manual |  | 5
ISL.TF.T6 | ISL-TF-T6-Tap Changer -- OFFLOAD -- LV | 11.55 | 10.45 | 4 | 2.5 | OFFLOAD |  |  |  | 3
ISL.TF.T7 | ISL-TF-T7B-Tap Changer -- ONLOAD -- HV | 231 | 187 | 16 | 1.25 | ONLOAD | Manual |  | 5
ISL.TF.T7 | ISL-TF-T7R-Tap Changer -- ONLOAD -- HV | 231 | 187 | 16 | 1.25 | ONLOAD | Manual |  | 5
ISL.TF.T7 | ISL-TF-T7Y-Tap Changer -- ONLOAD -- HV | 231 | 187 | 16 | 1.25 | ONLOAD | Manual |  | 5
ISL.TF.T7 | ISL-TF-T7B-Tap Changer -- OFFLOAD -- LV | 11.48 | 10.45 | 4 | 2.37 | OFFLOAD |  |  |  | 4
ISL.TF.T7 | ISL-TF-T7R-Tap Changer -- OFFLOAD -- LV | 11.48 | 10.45 | 4 | 2.37 | OFFLOAD |  |  |  | 3
ISL.TF.T7 | ISL-TF-T7Y-Tap Changer -- OFFLOAD -- LV | 11.48 | 10.45 | 4 | 2.37 | OFFLOAD |  |  |  | 3
KAW.TF.T12 | KAW-TF-T12-Tap Changer | 242 | 198 | 16 | 1.25 | ONLOAD | Manual |  | 8
KAW.TF.T14 | KAW-TF-T14-Tap Changer | 242 | 187 | 20 | 1.25 | ONLOAD | Manual |  | 10
KIK.TF.T1 | KIK-TF-T1B-Tap Changer -- OFFLOAD -- HV | 220 | 198 | 4 | 2.5 | OFFLOAD |  |  |  | 1
KIK.TF.T1 | KIK-TF-T1R-Tap Changer -- OFFLOAD -- HV | 220 | 198 | 4 | 2.5 | OFFLOAD |  |  |  | 1
KIK.TF.T1 | KIK-TF-T1Y-Tap Changer -- OFFLOAD -- HV | 220 | 198 | 4 | 2.5 | OFFLOAD |  |  |  | 1
KIK.TF.T1 | KIK-TF-T1B-Tap Changer -- OFFLOAD -- LV | 11.55 | 10.45 | 2 | 5 | OFFLOAD |  |  |  | 3
KIK.TF.T1 | KIK-TF-T1R-Tap Changer -- OFFLOAD -- LV | 11.55 | 10.45 | 2 | 5 | OFFLOAD |  |  |  | 3
KIK.TF.T1 | KIK-TF-T1Y-Tap Changer -- OFFLOAD -- LV | 11.55 | 10.45 | 2 | 5 | OFFLOAD |  |  |  | 3
KIK.TF.T2 | KIK-TF-T2-Tap Changer | 242 | 198 | 16 | 1.25 | ONLOAD | Manual |  | 8
KIK.TF.T2 | KIK-TF-T2-Tap Changer -- OFFLOAD -- LV | 11.55 | 10.45 | 5 | 2.5 | OFFLOAD |  |  |  | 3
KMO.TF.T2 | KMO-TF-T2-Tap Changer | 242 | 198 | 16 | 1.25 | ONLOAD | Manual |  | 7
KMO.TF.T4 | KMO-TF-T4-Tap Changer | 242 | 198 | 16 | 1.25 | ONLOAD | Manual |  | 7
MDN.TF.T5 | MDN-TF-T5-Tap Changer -- ONLOAD -- HV | 242 | 198 | 17 | 1.25 | ONLOAD | Manual |  | 7
MDN.TF.T5 | MDN-TF-T5-Tap Changer -- OFFLOAD -- LV | 11.55 | 10.45 | 5 | 2.5 | OFFLOAD |  |  |  | 3
MDN.TF.T6 | MDN-TF-T6-Tap Changer-ONLOAD-HV | 242 | 198 | 17 | 1.25 | ONLOAD | Manual |  | 7
MDN.TF.T6 | MDN-TF-T6-Tap Changer -- OFFLOAD -- LV | 11.55 | 10.45 | 5 | 2.5 | OFFLOAD |  |  |  | 3
OTA.TF.T3 | OTA-TF-T3-Tap Changer -- ONLOAD -- HV | 242 | 198 | 16 | 1.25 | ONLOAD | Manual |  | 8
OTA.TF.T3 | OTA-TF-T3-Tap Changer -- OFFLOAD -- LV | 11.55 | 10.45 | 4 | 2.5 | OFFLOAD |  |  |  | 3
OTA.TF.T4 | OTA-TF-T4-Tap Changer-Onload-HV | 242 | 198 | 16 | 1.25 | ONLOAD | Manual |  | 8
OTA.TF.T5 | OTA-TF-T5-Tap Changer -- ONLOAD -- HV | 242 | 198 | 16 | 1.25 | ONLOAD | Manual |  | 8
PEN.TF.T10 | PEN-TF-T10-Tap Changer-Onload-HV | 242 | 198 | 16 | 1.25 | ONLOAD | Manual |  | 6
PEN.TF.T6 | PEN-TF-T6-Tap Changer | 242 | 187 | 20 | 1.25 | ONLOAD | Manual |  | 9
RDF.TF.T4A | RDF-TF-T4-Tap Changer -- ONLOAD -- HV | 231 | 187 | 16 | 1.25 | ONLOAD | Manual |  | 6
RDF.TF.T4B | RDF-TF-T3-Tap Changer -- ONLOAD -- HV | 231 | 187 | 16 | 1.25 | ONLOAD | Manual |  | 6
RDF.TF.T5 | RDF-TF-T5-Tap Changer | 242 | 198 | 17 | 1.25 | ONLOAD | Manual |  | 7
ROX.TF.T10 | ROX-TF-T10-Tap Changer | 242 | 198 | 16 | 1.25 | ONLOAD | Manual |  | 7
SFD.TF.T10 | SFD-TF-T10B-Tap Changer -- ONLOAD -- HV | 231 | 198 | 12 | 1.25 | ONLOAD | Manual |  | 5
SFD.TF.T10 | SFD-TF-T10R-Tap Changer -- ONLOAD -- HV | 231 | 198 | 12 | 1.25 | ONLOAD | Manual |  | 5
SFD.TF.T10 | SFD-TF-T10Y-Tap Changer -- ONLOAD -- HV | 231 | 198 | 12 | 1.25 | ONLOAD | Manual |  | 5
SFD.TF.T10 | SFD-TF-T10B-Tap Changer -- OFFLOAD -- LV | 11.55 | 10.45 | 2 | 5 | OFFLOAD |  |  |  | 2
SFD.TF.T10 | SFD-TF-T10R-Tap Changer -- OFFLOAD -- LV | 11.55 | 10.45 | 2 | 5 | OFFLOAD |  |  |  | 2
SFD.TF.T10 | SFD-TF-T10Y-Tap Changer -- OFFLOAD -- LV | 11.55 | 10.45 | 2 | 5 | OFFLOAD |  |  |  | 2
SFD.TF.T9 | SFD-TF-T9-Tap Changer-Onload-HV | 242 | 198 | 16 | 1.25 | ONLOAD | Manual |  | 6
STK.TF.T7 | STK-TF-T7-Tap Changer | 242 | 198 | 17 | 1.25 | ONLOAD | Manual |  | 9
STK.TF.T7 | STK-TF-T7-Tap Changer -- OFFLOAD -- LV | 11.55 | 10.45 | 5 | 2.5 | OFFLOAD |  |  |  | 5
TIM.TF.T5 | TIM-TF-T5-Tap Changer | 242 | 198 | 16 | 1.25 | ONLOAD | Manual |  | 7
TIM.TF.T8 | TIM-TF-T8-Tap Changer | 242 | 198 | 17 | 1.25 | ONLOAD | Manual |  | 7
TRK.TF.T2 | TRK-TF-T2-Tap Changer | 242 | 198 | 16 | 1.25 | ONLOAD | Manual |  | 9
TRK.TF.T3 | TRK-TF-T3-Tap Changer | 242 | 198 | 16 | 1.25 | ONLOAD | Manual |  | 9
WIL.TF.T8 | WIL-TF-T8-Tap Changer -- ONLOAD -- HV | 242 | 187 | 20 | 1.25 | ONLOAD | Manual |  | 11
WPR.TF.T12 | WPR-TF-T12-Tap Changer - T12 | 236.5 | 187 | 18 | 1.25 | ONLOAD | Automatic | No
WPR.TF.T13 | WPR-TF-T13-Tap Changer - T13 | 236.5 | 187 | 18 | 1.25 | ONLOAD | Automatic | No
WTK.TF.T23 | WTK-TF-T23B-Tap Changer -- OFFLOAD -- HV | 220 | 198 | 4 | 2.5 | OFFLOAD |  |  |  | 2
WTK.TF.T23 | WTK-TF-T23R-Tap Changer -- OFFLOAD -- HV | 220 | 198 | 4 | 2.5 | OFFLOAD |  |  |  | 2
WTK.TF.T23 | WTK-TF-T23Y-Tap Changer -- OFFLOAD -- HV | 220 | 198 | 4 | 2.5 | OFFLOAD |  |  |  | 2
WTK.TF.T23 | WTK-TF-T23B-Tap Changer -- OFFLOAD -- LV | 11.55 | 10.45 | 2 | 5 | OFFLOAD |  |  |  | 2
WTK.TF.T23 | WTK-TF-T23R-Tap Changer -- OFFLOAD -- LV | 11.55 | 10.45 | 2 | 5 | OFFLOAD |  |  |  | 2
WTK.TF.T23 | WTK-TF-T23Y-Tap Changer -- OFFLOAD -- LV | 11.55 | 10.45 | 2 | 5 | OFFLOAD |  |  |  | 2
WTK.TF.T24 | WTK-TF-T24B-Tap Changer -- OFFLOAD -- HV | 220 | 198 | 4 | 2.5 | OFFLOAD |  |  |  | 2
WTK.TF.T24 | WTK-TF-T24R-Tap Changer -- OFFLOAD -- HV | 220 | 198 | 4 | 2.5 | OFFLOAD |  |  |  | 2
WTK.TF.T24 | WTK-TF-T24Y-Tap Changer -- OFFLOAD -- HV | 220 | 198 | 4 | 2.5 | OFFLOAD |  |  |  | 2
WTK.TF.T24 | WTK-TF-T24B-Tap Changer -- OFFLOAD -- LV | 11.55 | 10.45 | 2 | 5 | OFFLOAD |  |  |  | 2
WTK.TF.T24 | WTK-TF-T24R-Tap Changer -- OFFLOAD -- LV | 11.55 | 10.45 | 2 | 5 | OFFLOAD |  |  |  | 2
WTK.TF.T24 | WTK-TF-T24Y-Tap Changer -- OFFLOAD -- LV | 11.55 | 10.45 | 2 | 5 | OFFLOAD |  |  |  | 2