## Sign-off (hidden)
Tab |  | Team responsible | Prepared by | Initials | Date | Reviewed by/inputs provided by | Initials | Date | Approved by | Initials | Date | Check
Tab 1 | Summary of Normalisation events | Performance/Regulatory | Raghu Krishnaswamy | RK | 2023-08-21 | Joel Cook | JC |  | Julian Morton |  |  | Incomplete
Tab 2 | AP3 | Grid Operations | Raghu Krishnaswamy | RK | 2023-08-21 | Shaneel Singh | SS | 2023-08-30 | Julian Morton |  |  | Incomplete
Tab 3 | AP4 | Grid Operations | Raghu Krishnaswamy | RK | 2023-08-21 | Shaneel Singh | SS | 2023-08-30 | Julian Morton |  |  | Incomplete
Tab 4 | AP5 | Operations Planning/Sytem Planning | Lexmen Selvaraj | LS | 2023-08-25 | Pravin Jannoo | PJ | 2023-08-25 | Julian Morton |  |  | Incomplete
Tab 5 | Summary of Periodic Reporting | Grid Compliance | Raghu Krishnaswamy | RK | 2023-08-21 | Ben Denton | BD | 2023-09-07 | Julian Morton |  |  | Incomplete
Tab 6 | Summary of Periodic Reporting | Grid Compliance | Raghu Krishnaswamy | RK | 2023-08-21 | Ben Denton | BD | 2023-09-07 | Julian Morton |  |  | Incomplete
Tab 7 | GP-M | Performance | Raghu Krishnaswamy | RK | 2023-08-21 | Monina Sta Romana | MSR | 2023-08-30 | Julian Morton |  |  | Incomplete
Tab 8 | AP1 if Outside Collar | Performance | Raghu Krishnaswamy | RK | 2023-08-21 | Monina Sta Romana | MSR | 2023-09-04 | Julian Morton |  |  | Incomplete
Tab 9 | AP2 if Outside Collar | Performance | Raghu Krishnaswamy | RK | 2023-08-21 | Carmen Yip and Joel Cook | CY | 2023-09-08 | Julian Morton |  |  | Incomplete
Tab 10 | Non compliant Asset Health Measures | Performance | Raghu Krishnaswamy | RK | 2023-08-21 | Blaine Morch/Sahed Hossain | SH | 2023-08-31 | Julian Morton |  |  | Incomplete
Incomplete
Incomplete
Incomplete
Incomplete
Incomplete
Incomplete
Incomplete
Incomplete
Incomplete
Incomplete
Incomplete
Incomplete
Incomplete

## Cover
Regulatory disclosure of information to accompany the Annual Compliance Statement as required by
Part 5 of the Transpower Individual Price-Quality Path Determination 2020 ("IPP")
for the period
1 July 2024 to 30 June 2025
Published: 24 October 2025

## Contents
Workbook contents
This workbook contains the disclosure of information to accompany our Annual Compliance Statement (ACS) as required by our Individual Price Quality Path Determination (IPP) in additional to disclosure under the Annual Compliance Statement (ACS) .
Information accompanying The Annual Compliance Statement (Transpower IPP determination 2020, Part 5, clause 25) | Workbook location | IPP reference
Summary of Normalisation events | Tab 1 | Transpower IPP determination 2020, Part 5, clause 20 (plus any exceptional events)
AP3 | Tab 2 | Transpower IPP determination 2020, Part 5, clause 25.1.1
AP4 | Tab 3 | Transpower IPP determination 2020, Part 5, clause 25.1.2
AP5 | Tab 4 | Transpower IPP determination 2020, Part 5, clause 25.1.3
Summary of Periodic Reporting | Tab 5 | Transpower IPP determination 2020, Part 5, clause 28.1
Summary of Periodic Reporting | Tab 6 | Transpower IPP determination 2020, Part 5, clause 28.2
GP-M | Tab 7 | Transpower IPP determination 2020, Part 5, clauses 28.3 and 28.4
AP1 if Outside Collar | Tab 8 | Transpower IPP determination 2020, Part 5, clause 28.5
AP2 if Outside Collar | Tab 9 | Transpower IPP determination 2020, Part 5, clause 28.6
Non compliant Asset Health Measures | Tab 10 | Transpower IPP determination 2020, Part 5, clause 28.7

## 1
Normalisation events
Transpower IPP determination 2020, Part 5, clause 20.4
| Events | Description
| Tekapo-Timaru circuit outage | On 30 September 2024, the TKA-TIM 1 circuit tripped, when two conductors were cut by the rotor and boom on a weed-spraying helicopter. This resulted in a loss of supply at the Albury and Tekapo grid exit points (GXPs) The Commerce Commission approved our normalisation application.
Commission-decision-on-Transpower27s-normalisation-application-Tekapo-Timaru-30-January-2025.pdf

## 2
Asset performance measure AP3
Transpower IPP determination 2020, Part 5, clause 25.1.1
25.1.1 for asset performance measure AP3, which measures the extent to which Transpower meets planned return to service times for planned outages of the HVAC assets set out in Schedule G, those assets in Schedule G that are returned to service two or more hours after Transpower’s planned return to service time, including:
(a) when this has occurred;
(b) the known or estimated impact on affected parties, if applicable; and
(c) the steps Transpower took to inform affected parties and the market;
| Outage Block | Removed Asset | Removed Circuit Section (if applicable) | Outage Start Date | Outage End Date | Planned Finish before Release | the known or estimated impact on affected parties, if applicable | the steps Transpower took to inform affected parties and the market
| ISL_WPR_CUL_KIK_2 | ISL-WPR-CUL-KIK-2 |  | 2025-05-26 06:44 | 2025-05-31 13:40 | 2025-05-29 18:30 | Increased time on reduced Security of Grid | Market notificed via Change-to-offer
| ISL_T3 | ISL-TF-T3 |  | 2025-01-27 06:48 | 2025-02-05 19:04 | 2025-02-01 08:30 | Increased time on reduced Security of Grid | Market notificed via Change-to-offer
| HAY_T1 | HAY-TF-T1 |  | 2025-01-14 06:18 | 2025-01-23 10:55 | 2025-01-21 18:00 | Increased time on reduced Security of Grid | Market notified via Change-to-offer
| THI_WRK_1 | THI-WRK-1 |  | 2025-01-14 09:22 | 2025-01-17 20:05 | 2025-01-16 18:30 | Increased time on reduced Security of Grid | Market notified via Change-to-offer
| ISL_T3 | ISL-TF-T3 |  | 2024-08-19 08:16 | 2024-08-21 21:07 | 2024-08-21 17:00 | Increased time on reduced Security of Grid | Market notified via Change-to-offer
| HAM_KPO_2 | HAM-KPO-2 |  | 2024-07-14 07:39 | 2024-07-14 15:10 | 2024-07-14 13:00 | Increased time on reduced Security of Grid | Market notified via Change-to-offer
| Outages count | [5 empty] | Outages percentage
| 6 out of 136 Planned Outages | [5 empty] | 4.41%

## 3
Asset performance measure AP4
Transpower IPP determination 2020, Part 5, clause 25.1.2
for asset performance measure AP4, which measures the extent to which Transpower communicates delays to affected parties of planned outage return to service times of the HVAC assets set out in Schedule G, the percentage of outages that Transpower gives 1.5 hours or less notice to the market in the event assets are going to be returned to service later than:
(a) the original planned return to service time; or
(b) the extended return to service time;
13.24%
Outages count
18 out of 136 Planned Outages

## 4
Asset performance measure AP5
Transpower IPP determination 2020, Part 5, clause 25.1.3
25.1.3 for asset performance measure AP5, which measures the extent that Transpower has placed customers on a reduced level of supply security due to an outage, with that reduced level being N-security of supply, the occasions that Transpower has placed customers on N-security of supply, including:
(a) when this has occurred;
(b) how much notice Transpower provided to the customers before it occurred;
(c) how long the customers were reduced to N-security of supply; and
(d) the points of service affected by the reduced N-security of supply.
Notes: Actual duration for Multi Day Daily (MDD) Outages will be calculated based on Actual times out of service. Actual Start date reported below is earliest of the Outage start date time and Actual End Date is Latest Outage end date time. Outages carried out in real time has "No Notification".
| Outage Block | Actual Outage Start Date | Actual Outage End Date | Planned Start Date/Time | Is MDD | Customers affected | notice Transpower provided to the customers before it occurred (in days) | Actual Duration customers were reduced to N-security of supply (in hours) | points of service affected by the reduced N-security of supply
| BRB_T3 | 2024-07-01 07:32 | 2024-07-03 15:36 | 2024-07-01 07:30 | No | Northpower | 109.9 | 56.06 | BRB0331
| TMK_TIM_1_TMK_T1 | 2024-07-01 07:38 | 2024-07-08 16:16 | 2024-07-01 07:30 | No | Alpine Energy | 516.8403 | 176.65 | TMK0331
| HKK_KUM_1 | 2024-07-02 07:35 | 2024-07-05 14:06 | 2024-07-02 07:30 | No | Westpower | No Notification | 78.51 | HKK0661
| GYM_KUM_1 | 2024-07-02 07:36 | 2024-07-05 14:06 | 2024-07-02 07:30 | No | Westpower | No Notification | 78.51 | GYM0661
| OWH_T1 | 2024-07-02 07:37 | 2024-07-03 17:37 | 2024-07-02 07:30 | No | Unison Networks | 89 | 34.01 | OWH0111
| TMI_T1 | 2024-07-03 09:20 | 2024-07-03 12:15 | 2024-07-03 09:00 | No | Powerco | No Notification | 2.91 | TMI0331
| TMI_T2 | 2024-07-03 12:36 | 2024-07-03 14:45 | 2024-07-03 12:30 | No | Powerco | No Notification | 2.16 | TMI0331
| TMU_T1 | 2024-07-04 08:40 | 2024-07-05 11:05 | 2024-07-04 08:30 | No | Waipa Networks | 7 | 26.41 | TMU0111, TMU0112
| MST_T3 | 2024-07-05 08:37 | 2024-07-05 14:06 | 2024-07-05 08:30 | No | Powerco | No Notification | 5.48 | MST0331
| ROT_T5 | 2024-07-05 08:55 | 2024-07-05 16:11 | 2024-07-05 08:30 | No | Unison Network | 107 | 7.27 | ROT0331
| CUL_T23 | 2024-07-05 09:08 | 2024-07-05 13:26 | 2024-07-05 09:00 | No | Mainpower New Zealand | No Notification | 4.3 | CUL0331
| HOR_T5 | 2024-07-08 06:38 | 2024-07-12 15:50 | 2024-07-08 06:30 | No | Orion New Zealand | 41.7 | 105.19 | HOR0331
| EDN_T2 | 2024-07-08 07:35 | 2024-07-10 14:43 | 2024-07-08 07:30 | No | PowerNet | 41.8 | 55.14 | EDN0331
| ATU_RFN_IGH_1 | 2024-07-09 06:36 | 2024-07-12 15:47 | 2024-07-09 06:30 | No | Westpower | 42.7 | 81.17 | RFN1101, RFN1102
| OWH_CB_112 | 2024-07-09 07:31 | 2024-07-12 11:50 | 2024-07-09 07:30 | No | Unison Network | 25.7 | 76.32 | OWH0111
| DRY_GLN_1 | 2024-07-09 07:32 | 2024-07-11 17:07 | 2024-07-09 07:30 | No | NZ Steel, Counties Power | 41.8 | 57.59 | GLN0331, GLN0332, GLN0333
| KAW_T5 | 2024-07-09 07:44 | 2024-07-12 11:21 | 2024-07-09 07:30 | No | Horizon Energy | 46.7 | 75.63 | KAW0111
| LTN_T3 | 2024-07-09 07:47 | 2024-07-09 16:16 | 2024-07-09 07:30 | No | Powerco | 4.6 | 8.47 | LTN0331
| WIR_T1 | 2024-07-11 07:04 | 2024-07-13 13:53 | 2024-07-11 07:00 | No | Vector | 49.7 | 54.83 | WIR0331
| LTN_T2 | 2024-07-11 07:13 | 2024-07-11 15:07 | 2024-07-11 07:00 | No | Powerco | 6.6 | 7.9 | LTN0331
| HAM_T5 | 2024-07-12 10:18 | 2024-07-12 14:37 | 2024-07-12 10:00 | No | WEL Networks | 7 | 4.32 | HAM0331
| CBG_T3 | 2024-07-14 07:40 | 2024-07-14 15:09 | 2024-07-14 07:30 | No | Waipa Networks | 478 | 7.49 | CBG0111
| HAM_PAO_WHU_1 | 2024-07-14 07:44 | 2024-07-14 15:02 | 2024-07-14 07:30 | No | Powerco | 478 | 7.32 | PAO1101, WHU0331, WKO0331, KPU0661
| HAM_T1 | 2024-07-14 07:48 | 2024-07-14 14:56 | 2024-07-14 07:30 | No | WEL Networks | 478 | 7.13 | HAM0111
| ARI_HTI_ONG_1 | 2024-07-14 09:37 | 2024-07-14 18:54 | 2024-07-14 09:30 | No | Waipa Networks | 478.1 | 9.28 | TMU0111, TMU0112
| HKK_OTI_2 | 2024-07-15 06:37 | 2024-07-19 16:05 | 2024-07-15 06:30 | No | Westpower | 19.7 | 105.46 | HKK0661
| EDN_INV_1 | 2024-07-15 07:45 | 2024-07-18 16:22 | 2024-07-15 07:30 | No | Daiken , PowerNet | 26.7 | 80.61 | BDE0111, BDE0112, EDN0331
| MTO_T1 | 2024-07-15 21:00 | 2024-07-17 16:52 | 2024-07-15 21:00 | No | Northpower | No Notification | 43.86 | MTO0331
| KMO_MTM_TGA_2 | 2024-07-16 07:33 | 2024-07-16 13:14 | 2024-07-16 07:30 | No | Powerco | 75.9 | 5.67 | MTM0331, TGA0111, TGA0331
| HWB_SDN_1 | 2024-07-17 07:55 | 2024-07-19 15:12 | 2024-07-17 07:30 | No | Aurora Energy | 11.6 | 55.28 | SDN0331
| WRD_T7 | 2024-07-17 08:11 | 2024-07-18 15:16 | 2024-07-17 08:00 | No | Vector | 90.8 | 31.08 | WRD0331
| CBG_T4 | 2024-07-17 10:40 | 2024-07-17 13:38 | 2024-07-17 10:40 | No | Waipa Networks | No Notification | 2.96 | CBG0111
| CYD_CML_TWZ_2 | 2024-07-18 11:41 | 2024-07-18 16:16 | 2024-07-18 11:30 | No | Aurora Energy, PowerNet | 5.9 | 4.57 | CML0331, FKN0331, FKN0332
| HKK_OTI_2 | 2024-07-22 06:44 | 2024-07-26 16:38 | 2024-07-22 06:30 | No | Westpower | 32.8 | 105.9 | HKK0661
| HOR_T8 | 2024-07-22 06:47 | 2024-07-26 15:48 | 2024-07-22 06:30 | No | Orion New Zealand | 33.6 | 105.03 | HOR0331
| GLN_T4 | 2024-07-22 07:18 | 2024-07-22 13:14 | 2024-07-22 07:00 | No | NZ Steel | 41.7 | 5.93 | GLN0331, GLN0332
| BAL_GOR_1 | 2024-07-22 08:36 | 2024-07-24 15:44 | 2024-07-22 08:30 | No | PowerNet | 33.7 | 55.14 | BAL0331
| GLN_T5 | 2024-07-23 07:21 | 2024-07-23 13:44 | 2024-07-23 07:00 | No | NZ Steel | 41.9 | 6.39 | GLN0331, GLN0332
| BWK_HWB_1 | 2024-07-25 08:32 | 2024-07-26 14:07 | 2024-07-25 08:30 | No | PowerNet | No Notification | 29.58 | BAL0331
| CBG_T3 | 2024-07-27 08:17 | 2024-07-27 15:22 | 2024-07-27 08:00 | No | Waipa Networks | 491 | 7.08 | CBG0111
| HAM_PAO_WHU_1 | 2024-07-27 08:25 | 2024-07-27 15:12 | 2024-07-27 08:00 | No | Powerco | 491 | 6.78 | PAO1101, WHU0331, WKO0331, KPU0661
| HAM_T1 | 2024-07-27 08:37 | 2024-07-27 15:03 | 2024-07-27 08:30 | No | WEL Networks | 491 | 6.44 | HAM0111
| MGM_T2 | 2024-07-29 07:10 | 2024-07-31 16:10 | 2024-07-29 07:00 | No | Powerco | 52.9 | 57.01 | MGM0331
| BAL_T2 | 2024-07-29 07:32 | 2024-08-24 08:42 | 2024-08-01 | No | PowerNet | 40.6 | 625.15 | BAL0331
| MNG_T1 | 2024-07-29 09:04 | 2024-08-04 12:22 | 2024-08-01 | No | Vector | 189 | 147.3 | MNG0331
| WRD_T7 | 2024-07-30 08:46 | 2024-07-30 15:19 | 2024-07-30 08:30 | No | Vector | 33 | 6.55 | WRD0331
| HAY_WIL_LTN_1 | 2024-07-31 06:42 | 2024-07-31 18:53 | 2024-07-31 06:30 | No | Wellington Electricity | 35.8 | 12.18 | WIL0331
| TIM_T8 | 2024-08-01 07:05 | 2024-08-01 17:07 | 2024-08-01 07:00 | No | Alpine Energy | 48.6 | 10.02 | TIM0111, TMK0331
| COL_OTI_2 | 2024-08-01 07:05 | 2024-08-01 13:05 | 2024-08-01 07:00 | No | Westpower | 2.8 | 5.99 | GYM0661, HKK0661
| MGM_T3 | 2024-08-01 07:35 | 2024-08-01 12:51 | 2024-08-01 07:30 | No | Powerco | 56 | 5.27 | MGM0331
| NMA_T1 | 2024-08-01 09:14 | 2024-08-01 14:37 | 2024-08-01 09:00 | No | PowerNet | No Notification | 5.37 | NMA0331
| TNG_T12 | 2024-08-01 09:34 | 2024-08-01 14:15 | 2024-08-01 09:30 | No | Winstone Pulp | 80 | 4.68 | TNG0111
| WIR_T1 | 2024-08-01 10:04 | 2024-08-01 10:36 | 2024-08-01 10:00 | No | Vector | No Notification | 0.54 | WIR0331
| PEN_220BS_A | 2024-08-01 10:12 | 2024-08-01 11:50 | 2024-08-01 10:00 | No | Vector, Southpark | 134.8 | 1.63 | PEN0221, PEN0331, PEN0332
| WIR_T2 | 2024-08-01 11:04 | 2024-08-01 11:41 | 2024-08-01 11:00 | No | Vector | No Notification | 0.62 | WIR0331
| HKK_OTI_2 | 2024-08-05 06:56 | 2024-08-09 16:43 | 2024-08-05 06:30 | No | Westpower | No Notification | 105.79 | GYM0661
| WDV_DVK_WPW_1 | 2024-08-05 07:09 | 2024-08-09 14:31 | 2024-08-05 07:00 | No | Scanpower, Centralines | 40.8 | 103.37 | DVK0111, WPW0331
| EDN_T1 | 2024-08-05 07:34 | 2024-08-09 10:50 | 2024-08-05 07:30 | No | PowerNet | 45.8 | 99.27 | EDN0331
| HUI_T5 | 2024-08-05 08:10 | 2024-08-09 16:24 | 2024-08-05 08:00 | No | Powerco | 27 | 104.23 | HUI0331
| KWA_WIL_1 | 2024-08-05 09:08 | 2024-08-05 14:12 | 2024-08-05 09:00 | No | Wellington Electricity | 21 | 5.08 | KWA0111
| RDF_T3 | 2024-08-06 07:02 | 2024-08-08 12:34 | 2024-08-06 07:00 | No | Unison Network, Eastlands Networks | 82.9 | 53.53 | RDF0331, WTU0331, FHL0331,TUI1101
| KOE_MPE_1 | 2024-08-06 08:36 | 2024-08-06 13:20 | 2024-08-06 08:30 | No | Top Energy | 41.9 | 4.73 | KOE1101
| KWA_WIL_1 | 2024-08-06 09:05 | 2024-08-06 16:46 | 2024-08-06 09:00 | No | Wellington Electricity | No Notification | 7.69 | KWA0111
| OPK_T4 | 2024-08-07 08:15 | 2024-08-08 18:47 | 2024-08-07 08:00 | Yes | Powerco | 55.8 | 19.63 | OPK0331
| KOE_MPE_2 | 2024-08-07 08:36 | 2024-08-07 14:12 | 2024-08-07 08:30 | No | Top Energy | 42.9 | 5.6 | KOE1101
| BRY_T7 | 2024-08-07 09:02 | 2024-08-07 16:11 | 2024-08-07 09:00 | No | Orion New Zealand | 1.9 | 7.15 | BRY0661, BRY0662, BRY0663
| OAM_BPT_WTK_1 | 2024-08-08 08:18 | 2024-08-08 15:42 | 2024-08-08 08:00 | No | Network Waitaki | 12.8 | 7.4 | OAM0331
| KWA_WIL_1 | 2024-08-08 09:08 | 2024-08-08 13:54 | 2024-08-08 09:00 | No | Wellington Electricity | 24 | 4.76 | KWA0111
| OWH_CB_112 | 2024-08-09 08:03 | 2024-08-09 16:21 | 2024-08-09 08:00 | No | Unison Networks | 29.7 | 8.29 | OWH0111
| KAW_OHK_1 | 2024-08-09 08:08 | 2024-08-09 16:19 | 2024-08-09 08:00 | No | Horizon Energy | 29.7 | 8.19 | KAW0111
| SDN_TMH_1 | 2024-08-09 08:54 | 2024-08-09 15:55 | 2024-08-09 08:30 | No | Aurora Energy | No Notification | 7.02 | SDN0331
| HKK_OTI_2 | 2024-08-12 06:53 | 2024-08-16 16:43 | 2024-08-12 06:30 | No | Westpower | 48.9 | 105.83 | GYM0661
| WDV_DVK_WPW_2 | 2024-08-12 07:16 | 2024-08-16 14:12 | 2024-08-12 07:00 | No | Scanpower, Centralines | 39.8 | 102.93 | DVK0111, WPW0331
| IGH_ROB_1 | 2024-08-12 07:34 | 2024-08-16 11:02 | 2024-08-12 07:30 | No | Buller Electricity | 48.9 | 99.46 | ROB0111, ROB0331
| EDN_T2 | 2024-08-12 07:40 | 2024-08-15 16:26 | 2024-08-12 07:30 | No | PowerNet | 51.7 | 80.77 | EDN0331
| KIK_DIS_43 | 2024-08-13 00:17 | 2024-08-21 15:02 | 2024-08-13 | No | Network Tasman | No Notification | 206.76 | KIK0111
| KIN_TRK_1 | 2024-08-13 07:42 | 2024-08-13 14:19 | 2024-08-13 07:30 | No | Vector | 5.8 | 6.62 | LFD1101
| MNI_11BS_K | 2024-08-13 07:44 | 2024-08-14 16:16 | 2024-08-13 07:30 | No | Methanex | 40.8 | 32.53 | MNI0111, MNI0112
| STU_TIM_1 | 2024-08-13 08:34 | 2024-08-14 18:07 | 2024-08-13 08:30 | No | Alpine Energy | 47.9 | 33.54 | STU0111
| UHT_T1 | 2024-08-13 11:27 | 2024-08-14 15:32 | 2024-08-13 11:26 | No | Wellington Electricity | No Notification | 28.09 | UHT0331
| STU_67_76_T5 | 2024-08-14 07:54 | 2024-08-14 17:22 | 2024-08-14 07:30 | No | Alpine Energy | 274.7 | 9.46 | STU0111
| SVL_T1 | 2024-08-14 07:54 | 2024-08-15 18:14 | 2024-08-14 07:30 | No | Vector | 74.7 | 34.32 | SVL0331
| OAM_BPT_WTK_1 | 2024-08-15 14:51 | 2024-08-15 17:49 | 2024-08-15 14:50 | No | Network Waitaki | No Notification | 2.96 | OAM0331
| WIL_T3 | 2024-08-17 08:12 | 2024-08-17 10:50 | 2024-08-17 08:00 | No | Wellington Electricity | 32.7 | 2.63 | WIL0331
| WIL_T5 | 2024-08-17 11:03 | 2024-08-17 12:06 | 2024-08-17 11:00 | No | Wellington Electricity | 32.9 | 1.05 | WIL0331
| KAW_T2 | 2024-08-19 07:12 | 2024-08-27 08:20 | 2024-08-19 07:00 | No | Horizon Energy | 41.8 | 193.13 | KAW0111
| GYM_KUM_1 | 2024-08-19 08:19 | 2024-08-22 10:18 | 2024-08-19 08:00 | No | Westpower | 20.7 | 73.99 | GYM0661
| MNI_11BS_L | 2024-08-20 07:39 | 2024-08-22 14:10 | 2024-08-20 07:30 | No | Methanex | 35.9 | 54.52 | MNI0111, MNI0112
| KMO_TMI_1 | 2024-08-20 08:01 | 2024-08-20 16:02 | 2024-08-20 08:00 | No | Powerco | 25.7 | 8.01 | TMI0331
| NMA_T2 | 2024-08-20 08:43 | 2024-08-22 11:25 | 2024-08-20 08:30 | No | PowerNet | 48.9 | 50.69 | NMA0331
| LIV_NSY_1 | 2024-08-20 08:55 | 2024-08-23 12:56 | 2024-08-20 08:30 | No | PowerNet | 54.9 | 76.01 | NSY0331
| HUI_T5 | 2024-08-21 08:05 | 2024-08-21 17:11 | 2024-08-21 08:00 | No | Powerco | 7.6 | 9.09 | HUI0331
| STU_TIM_1 | 2024-08-21 09:19 | 2024-08-21 17:44 | 2024-08-21 09:00 | No | Alpine Energy | No Notification | 8.41 | STU0111
| KPU_T3 | 2024-08-21 10:08 | 2024-08-22 15:52 | 2024-08-21 10:00 | Yes | Powerco | 48.9 | 14.22 | KPU0661
| DOB_GYM_1 | 2024-08-23 06:35 | 2024-08-23 11:33 | 2024-08-23 06:30 | No | Westpower | 10.9 | 4.97 | GYM0661
| HUI_T6 | 2024-08-23 08:05 | 2024-08-23 14:20 | 2024-08-23 08:00 | No | Powerco | 9.6 | 6.25 | HUI0331
| PAO_CB_212 | 2024-08-23 08:15 | 2024-08-23 17:05 | 2024-08-23 08:00 | No | Powerco | No Notification | 8.84 | PAO1101
| HKK_OTI_2 | 2024-08-26 06:41 | 2024-08-26 17:10 | 2024-08-26 06:30 | No | Westpower | 52.7 | 10.49 | HKK0661
| IGH_ROB_1 | 2024-08-26 07:32 | 2024-08-28 11:17 | 2024-08-26 07:30 | No | Buller Electricity | 52.7 | 51.76 | ROB0111, ROB0331
| BRB_T2 | 2024-08-26 07:39 | 2024-09-20 18:04 | 2024-09-01 | No | Northpower | 165.9 | 610.42 | BRB0331
| NMA_T1 | 2024-08-26 08:05 | 2024-08-31 09:43 | 2024-08-26 08:00 | No | PowerNet | 104.8 | 121.63 | NMA0331
| DRY_GLN_1 | 2024-08-26 12:16 | 2024-08-26 16:41 | 2024-08-26 12:00 | No | NZ Steel, Counties Power | No Notification | 4.42 | GLN0331, GLN0332, GLN0333
| HKK_KUM_1 | 2024-08-27 06:50 | 2024-08-27 17:48 | 2024-08-27 06:30 | No | Westpower | 53.7 | 10.96 | HKK0661
| EDG_OWH_2 | 2024-08-27 07:32 | 2024-08-27 12:39 | 2024-08-27 07:30 | No | Unison Networks | 42.8 | 5.12 | OWH0111
| MLG_T4 | 2024-08-27 07:35 | 2024-08-27 14:06 | 2024-08-27 07:30 | No | Wellington Electricity | 18.6 | 6.52 | MLG0331
| MTO_T1 | 2024-08-27 08:36 | 2024-08-27 16:10 | 2024-08-27 08:30 | No | Northpower | 20.9 | 7.56 | MTO0331
| WEL_T2 | 2024-08-27 08:36 | 2024-08-27 16:10 | 2024-08-27 08:30 | No | Vector | 20.9 | 7.57 | WEL0331
| HKK_OTI_2 | 2024-08-28 06:35 | 2024-08-28 17:07 | 2024-08-28 06:30 | No | Westpower | 54.7 | 10.54 | HKK0661
| WIR_T1 | 2024-08-28 07:03 | 2024-08-28 15:13 | 2024-08-28 07:00 | No | Vector | 105 | 8.16 | WIR0331
| EDG_OWH_2 | 2024-08-28 07:32 | 2024-08-29 15:08 | 2024-08-28 07:30 | No | Unison Networks | 42.7 | 31.61 | OWH0111
| PAO_CB_232 | 2024-08-28 08:13 | 2024-08-28 16:17 | 2024-08-28 08:00 | No | Powerco | No Notification | 8.07 | PAO1101
| WEL_T1 | 2024-08-28 08:35 | 2024-08-29 11:33 | 2024-08-28 08:30 | Yes | Vector | 21.9 | 10.46 | WEL0331
| MTO_T2 | 2024-08-28 08:38 | 2024-08-28 16:08 | 2024-08-28 08:30 | No | Northpower | 21.9 | 7.5 | MTO0331
| OAM_STU_BPD_WTK_2 | 2024-08-28 09:51 | 2024-08-28 11:49 | 2024-08-28 09:50 | No | Network Waitaki, Alpine Energy | No Notification | 1.97 | OAM0331, STU0111
| STU_DIS_76 | 2024-08-28 10:05 | 2024-09-02 15:53 | 2024-08-28 10:04 | No | Alpine Energy | No Notification | 125.81 | STU0111
| STU_CB_62 | 2024-08-28 12:01 | 2024-09-02 15:53 | 2024-09-01 | No | Alpine Energy | No Notification | 123.87 | STU0111
| HKK_KUM_1 | 2024-08-29 06:47 | 2024-08-29 09:15 | 2024-08-29 06:30 | No | Westpower | 55.7 | 2.47 | HKK0661
| FHL_CB_2188 | 2024-08-29 07:59 | 2024-08-29 12:48 | 2024-08-29 07:30 | No | Unison Networks | 34.8 | 4.83 | FHL0331
| OAM_BPT_WTK_1 | 2024-08-29 10:09 | 2024-08-29 14:18 | 2024-08-29 10:00 | No | Network Waitaki | 2 | 4.15 | OAM0331
| TIM_T5 | 2024-08-31 07:06 | 2024-09-02 17:03 | 2024-09-01 | No | Alpine Energy | 291.7 | 57.95 | TIM0111, TMK0331
| COL_OTI_2 | 2024-09-02 06:40 | 2024-09-13 09:50 | 2024-09-02 06:30 | No | Westpower | 55.8 | 267.17 | GYM0661, HKK0661
| GLN_220BS_A | 2024-09-02 07:07 | 2024-09-02 11:34 | 2024-09-02 07:00 | No | NZ Steel, Counties Power | 48.8 | 4.44 | GLN0331, GLN0332, GLN0333
| KAW_T5 | 2024-09-02 07:13 | 2024-09-02 15:39 | 2024-09-02 07:00 | No | Horizon Energy | 101.6 | 8.425 | KAW0111
| CYD_T7 | 2024-09-02 08:19 | 2024-09-20 16:57 | 2024-09-02 08:00 | No | Aurora Energy | 54.9 | 440.64 | CYD0331
| OAM_STU_BPD_WTK_2 | 2024-09-02 10:21 | 2024-09-02 15:47 | 2024-09-02 10:00 | No | Network Waitaki, Alpine Energy | 5.8 | 5.44 | OAM0331, STU0111
| GLN_220BS_B | 2024-09-02 12:03 | 2024-09-02 16:13 | 2024-09-02 12:00 | No | NZ Steel, Counties Power | 49 | 4.17 | GLN0331, GLN0332, GLN0333
| MHO_T3 | 2024-09-03 07:05 | 2024-09-06 12:09 | 2024-09-03 07:00 | No | Electra | 61.7 | 77.07 | MHO0331
| DRY_GLN_2 | 2024-09-03 07:07 | 2024-09-03 14:43 | 2024-09-03 07:00 | No | NZ Steel, Counties Power | 49.8 | 7.6 | GLN0331, GLN0332, GLN0333
| OWH_TMI_TRK_1 | 2024-09-03 07:31 | 2024-09-03 15:36 | 2024-09-03 07:30 | No | Unison Networks, Powerco | 63.7 | 8.08 | OWH0111, TMI0331
| WEL_T2 | 2024-09-03 08:17 | 2024-09-04 10:20 | 2024-09-03 08:30 | Yes | Vector | 19.8 | 8.88 | WEL0331
| GLN_220BS_A | 2024-09-04 07:11 | 2024-09-04 11:37 | 2024-09-04 07:00 | No | NZ Steel, Counties Power | 50.7 | 4.43 | GLN0331, GLN0332, GLN0333
| GLN_220BS_B | 2024-09-04 12:05 | 2024-09-04 15:39 | 2024-09-04 12:00 | No | NZ Steel, Counties Power | 50.9 | 3.58 | GLN0331, GLN0332, GLN0333
| DRY_GLN_1 | 2024-09-05 07:06 | 2024-09-05 15:06 | 2024-09-05 07:00 | No | NZ Steel, Counties Power | 41.9 | 7.99 | GLN0331, GLN0332, GLN0333
| SDN_T1 | 2024-09-05 09:14 | 2024-09-05 15:13 | 2024-09-05 09:00 | No | Aurora Energy | No Notification | 5.98 | SDN0331
| GLN_220BS_A | 2024-09-06 07:18 | 2024-09-06 11:34 | 2024-09-06 07:00 | No | NZ Steel, Counties Power | 38.9 | 4.27 | GLN0331, GLN0332, GLN0333
| GLN_220BS_B | 2024-09-06 12:03 | 2024-09-06 15:04 | 2024-09-06 12:00 | No | NZ Steel, Counties Power | 39.1 | 3.01 | GLN0331, GLN0332, GLN0333
| TMU_T2 | 2024-09-07 08:08 | 2024-09-07 17:43 | 2024-09-07 08:00 | No | Waipa Networks | 4.7 | 9.59 | TMU0111, TMU0112
| RDF_TUI_1 | 2024-09-09 06:06 | 2024-09-11 15:36 | 2024-09-09 06:00 | No | Unison Network, Eastlands Networks | 55.9 | 57.49 | RDF0331, FHL0331,TUI1101
| GLN_220BS_A | 2024-09-09 07:16 | 2024-09-09 14:35 | 2024-09-09 07:00 | No | NZ Steel, Counties Power | 41.7 | 7.32 | GLN0331, GLN0332, GLN0333
| HLY_T21 | 2024-09-09 07:24 | 2024-09-10 18:49 | 2024-09-09 07:00 | No | WEL Networks | 89.7 | 35.42 | HLY0331, HLY0332
| GLN_220BS_B | 2024-09-10 07:14 | 2024-09-10 13:06 | 2024-09-10 07:00 | No | NZ Steel, Counties Power | 41.9 | 5.87 | GLN0331, GLN0332, GLN0333
| INV_T5 | 2024-09-11 07:35 | 2024-09-13 15:41 | 2024-09-11 07:30 | No | PowerNet | No Notification | 56.1 | INV0331
| OTA_T13 | 2024-09-11 07:49 | 2024-09-11 14:46 | 2024-09-11 07:30 | No | Vector | 152.9 | 6.96 | OTA0221
| HPI_MDN_1 | 2024-09-14 02:17 | 2024-09-14 06:33 | 2024-09-14 02:15 | No | Northpower, Top Energy | No Notification | 4.26 | BRB0331, MPE1101, KOE1101, MTO0331
| ASB_TIM_TWZ_1 | 2024-09-14 07:35 | 2024-09-15 17:34 | 2024-09-14 07:30 | No | Alpine Energy | 305.7 | 33.97 | TIM0111
| HPI_MDN_1 | 2024-09-15 00:31 | 2024-09-15 06:39 | 2024-09-15 00:30 | No | Northpower, Top Energy | No Notification | 6.13 | BRB0331, MPE1101, KOE1101, MTO0331
| HPI_MDN_1 | 2024-09-16 00:01 | 2024-09-16 05:43 | 2024-09-16 | No | Northpower, Top Energy | No Notification | 5.7 | BRB0331, MPE1101, KOE1101, MTO0331
| WPW_T2 | 2024-09-16 07:24 | 2024-09-20 15:04 | 2024-09-16 07:00 | No | Centralines | 26.7 | 103.67 | WPW0331
| WDV_DVK_WPW_1 | 2024-09-16 07:26 | 2024-09-20 15:02 | 2024-09-16 07:00 | No | Scanpower, Centralines | 26.7 | 103.61 | DVK0111, WPW0331
| IGH_ROB_2 | 2024-09-16 07:32 | 2024-09-17 14:37 | 2024-09-16 07:30 | No | Buller Electricity | 26.9 | 31.1 | ROB0111, ROB0331
| GOR_T3 | 2024-09-16 07:45 | 2024-09-20 15:20 | 2024-09-16 07:30 | No | PowerNet | 26.9 | 103.59 | GOR0331
| GYM_KUM_1 | 2024-09-16 07:55 | 2024-09-20 09:28 | 2024-09-16 07:30 | No | Westpower | 18.8 | 97.535 | GYM0661
| BAL_BWK_1 | 2024-09-16 08:32 | 2024-09-18 15:02 | 2024-09-16 08:30 | No | PowerNet | 88.8 | 54.49 | BAL0331
| LTN_T3 | 2024-09-17 08:03 | 2024-09-17 12:25 | 2024-09-17 08:00 | No | Powerco | No Notification | 4.35 | LTN0331
| KPU_T4 | 2024-09-17 10:27 | 2024-09-17 14:51 | 2024-09-17 10:00 | No | Powerco | 91 | 4.39 | KPU0661
| MPE_CB_252 | 2024-09-17 15:43 | 2024-09-17 20:01 | 2024-09-17 15:40 | No | Northpower, Top Energy | No Notification | 4.3 | BRB0331, KOE1101, MTO0331
| KAW_T5 | 2024-09-18 12:51 | 2024-09-23 15:16 | 2024-09-18 12:30 | No | Horizon Energy | 117.8 | 122.41 | KAW0111
| KPU_WKO_1 | 2024-09-19 07:42 | 2024-09-19 16:05 | 2024-09-19 07:30 | No | Powerco | 92.9 | 8.37 | KPU0661
| WPW_214_267 | 2024-09-19 08:38 | 2024-09-19 14:36 | 2024-09-19 08:00 | No | Centralines | 29.8 | 5.96 | WPW0331
| CML_T8 | 2024-09-20 07:38 | 2024-09-27 16:10 | 2024-09-20 07:30 | No | Aurora Energy, PowerNet | 206.7 | 176.54 | CML0331, FKN0331, FKN0332
| WTU_T4 | 2024-09-21 07:35 | 2024-09-21 17:13 | 2024-09-21 07:30 | No | Unison Network | 249 | 9.63 | WTU0331
| ASB_TIM_TWZ_1 | 2024-09-21 13:05 | 2024-09-21 16:17 | 2024-09-21 13:00 | No | Alpine Energy | 78.9 | 3.21 | TIM0111
| HPI_MDN_1 | 2024-09-22 01:33 | 2024-09-22 06:03 | 2024-09-22 01:30 | No | Northpower, Top Energy | No Notification | 4.5 | BRB0331, MPE1101, KOE1101, MTO0331
| WTU_T3 | 2024-09-22 07:32 | 2024-09-22 14:42 | 2024-09-22 07:30 | No | Unison Network | 250 | 7.17 | WTU0331
| HPI_MDN_1 | 2024-09-23 00:17 | 2024-09-23 05:06 | 2024-09-23 00:15 | No | Northpower, Top Energy | No Notification | 4.82 | BRB0331, MPE1101, KOE1101, MTO0331
| ASB_BRY_1 | 2024-09-23 06:44 | 2024-09-27 17:49 | 2024-09-23 06:30 | No | Orion New Zealand | 62.8 | 107.07 | BRY0661, BRY0662, BRY0663
| ASB_337_364_386_407 | 2024-09-23 06:54 | 2024-09-27 17:43 | 2024-09-23 06:30 | No | Electricity Ashburton | 62.8 | 106.81 | ASB0331
| WDV_DVK_WPW_2 | 2024-09-23 07:08 | 2024-09-27 14:07 | 2024-09-23 07:00 | No | Scanpower, Centralines | 33.7 | 102.98 | DVK0111, WPW0331
| WPW_T1 | 2024-09-23 07:09 | 2024-09-27 14:07 | 2024-09-23 07:00 | No | Centralines | 33.7 | 102.97 | WPW0331
| BRB_T2 | 2024-09-23 07:47 | 2024-09-25 15:55 | 2024-09-23 07:30 | No | Northpower | 53.9 | 56.13 | BRB0331
| CYD_T8 | 2024-09-23 08:10 | 2024-10-03 10:52 | 2024-10-01 | No | Aurora Energy | 33.8 | 242.7083 | CYD0331
| KMO_MTM_1 | 2024-09-23 08:23 | 2024-09-23 16:33 | 2024-09-23 08:00 | No | Powerco | 129.8 | 8.16 | MTM0331
| HPI_MDN_1 | 2024-09-24 00:02 | 2024-09-24 05:31 | 2024-09-24 | No | Northpower, Top Energy | No Notification | 5.5 | BRB0331, MPE1101, KOE1101, MTO0331
| KIN_TRK_2 | 2024-09-24 07:10 | 2024-09-26 17:02 | 2024-09-24 07:00 | No | Vector | 70 | 57.86 | LFD1101
| DRY_GLN_1 | 2024-09-24 07:35 | 2024-09-27 14:38 | 2024-09-24 07:30 | No | NZ Steel, Counties Power | 33.9 | 79.04 | GLN0331, GLN0332, GLN0333
| HAM_PAO_WHU_1 | 2024-09-24 07:36 | 2024-09-27 15:35 | 2024-09-24 07:30 | No | Powerco | 42 | 79.98 | PAO1101, WHU0331, WKO0331, KPU0661
| TMI_T1 | 2024-09-24 07:41 | 2024-09-24 16:51 | 2024-09-24 07:30 | No | Powerco | 40 | 9.17 | TMI0331
| HPI_MDN_1 | 2024-09-25 00:03 | 2024-09-25 05:34 | 2024-09-25 | No | Northpower, Top Energy | No Notification | 5.51 | BRB0331, MPE1101, KOE1101, MTO0331
| HPI_MDN_1 | 2024-09-26 01:06 | 2024-09-26 05:33 | 2024-09-26 01:00 | No | Northpower, Top Energy | No Notification | 4.45 | BRB0331, MPE1101, KOE1101, MTO0331
| STU_TIM_1 | 2024-09-27 07:33 | 2024-09-27 16:06 | 2024-09-27 07:30 | No | Alpine Energy | 318.7 | 8.54 | STU0111
| COL_OTI_2 | 2024-09-30 06:32 | 2024-10-04 15:03 | 2024-10-01 | No | Westpower | 39.8 | 104.51 | GYM0661, HKK0661
| MDN_MPE_2 | 2024-09-30 07:36 | 2024-10-05 16:25 | 2024-10-01 | No | Northpower, Top Energy | 30.8 | 128.82 | MPE1101, KOE1101
| DRY_GLN_2 | 2024-09-30 07:40 | 2024-10-04 16:35 | 2024-09-30 07:30 | No | NZ Steel, Counties Power | 39.9 | 104.93 | GLN0331, GLN0332, GLN0333
| TKR_T1 | 2024-09-30 07:48 | 2024-11-05 09:34 | 2024-11-01 | No | Wellington Electricity | 109.8 | 865.77 | TKR0331
| BRB_T3 | 2024-09-30 08:06 | 2024-10-25 13:55 | 2024-10-01 | No | Northpower | 200.9 | 605.83 | BRB0331
| HTI_T1 | 2024-10-01 06:02 | 2024-10-01 06:14 | 2024-10-01 06:00 | No | The Lines Company | No Notification | 0.2 | HTI0331
| MPE_CB_252 | 2024-10-01 06:10 | 2024-10-05 11:52 | 2024-10-01 | Yes | Northpower, Top Energy | 26.9 | 63.5 | BRB0331, KOE1101, MTO0331
| STU_DIS_76 | 2024-10-01 07:06 | 2024-10-06 18:41 | 2024-10-01 07:00 | No | Alpine Energy | No Notification | 131.58 | STU0111
| HAM_117_157 | 2024-10-01 07:52 | 2024-10-01 18:41 | 2024-10-01 07:30 | No | WEL Networks, Waipa Networks, Powerco | 70.8 | 10.83 | HAM0111, CBG0111, TMU0111, TMU0112, WHU0331, WKO0331, KPU0661, PAO1101
| OPK_T4 | 2024-10-01 08:35 | 2024-10-01 16:52 | 2024-10-01 08:30 | No | Powerco | 25.9 | 8.29 | OPK0331
| HTI_T1 | 2024-10-01 20:03 | 2024-10-01 20:11 | 2024-10-01 20:00 | No | The Lines Company | No Notification | 0.14 | HTI0331
| EDG_OWH_2 | 2024-10-03 02:51 | 2024-10-03 08:10 | 2024-10-03 02:51 | No | Unison Networks | No Notification | 5.31 | OWH0111
| BPE_PRM_HAY_2 | 2024-10-03 08:38 | 2024-10-03 17:17 | 2024-10-03 08:30 | No | Electra | No Notification | 8.66 | PRM0331
| OWH_CB_112 | 2024-10-04 07:26 | 2024-10-11 13:43 | 2024-10-04 07:00 | No | Unison Networks | 38.7 | 174.28 | OWH0111
| KAI_T1 | 2024-10-06 06:37 | 2024-10-12 09:11 | 2024-10-06 06:30 | No | Mainpower New Zealand | 92.7 | 146.58 | KAI0111
| COL_OTI_2 | 2024-10-07 06:33 | 2024-10-11 12:18 | 2024-10-07 06:30 | No | Westpower | 39.8 | 101.75 | GYM0661, HKK0661
| HAM_PAO_WHU_2 | 2024-10-07 07:06 | 2024-10-09 18:03 | 2024-10-07 07:00 | No | Powerco | 46.9 | 58.96 | PAO1101, WHU0331, WKO0331, KPU0661
| DRY_GLN_1 | 2024-10-07 07:43 | 2024-10-11 14:34 | 2024-10-07 07:30 | No | NZ Steel, Counties Power | 46.9 | 102.85 | GLN0331, GLN0332, GLN0333
| CYD_T7 | 2024-10-07 07:47 | 2024-10-07 17:23 | 2024-10-07 07:30 | No | Aurora Energy | 76.7 | 9.6 | CYD0331
| SFD_T9 | 2024-10-07 20:26 | 2024-10-08 12:20 | 2024-10-07 20:25 | No | Powerco, Beach Energy | No Notification | 15.9 | SFD0331, OPK0331, HWA0331, HWA0332
| ALB_SVL_2 | 2024-10-08 07:09 | 2024-10-11 17:10 | 2024-10-08 07:00 | No | Vector | 47.8 | 82.03 | SVL0331
| CYD_CML_TWZ_2 | 2024-10-08 07:41 | 2024-10-10 10:15 | 2024-10-08 07:30 | No | Aurora Energy, PowerNet | 35.9 | 50.57 | CML0331, FKN0331, FKN0332
| HAY_MLG_1 | 2024-10-08 07:43 | 2024-10-09 15:42 | 2024-10-08 07:30 | No | Wellington Electricity | 40.6 | 31.98 | MLG0111, MLG0331
| CYD_FDR_2052 | 2024-10-09 09:17 | 2024-10-09 11:11 | 2024-10-09 08:30 | No | Aurora Energy | No Notification | 1.9 | CYD0331
| MPE_CB_252 | 2024-10-10 07:03 | 2024-10-11 22:48 | 2024-10-10 07:00 | Yes | Northpower, Top Energy | 36.9 | 32.87 | BRB0331, KOE1101, MTO0331
| MDN_MPE_2 | 2024-10-10 07:12 | 2024-10-12 15:47 | 2024-10-10 07:00 | No | Northpower, Top Energy | 40.8 | 56.58 | MPE1101, KOE1101
| FHL_T2 | 2024-10-10 07:51 | 2024-10-10 18:28 | 2024-10-10 07:30 | No | Unison Networks | 42.9 | 10.62 | FHL0331
| FHL_64_107 | 2024-10-11 07:58 | 2024-10-11 14:53 | 2024-10-11 07:30 | No | Unison Networks | 43.9 | 6.91 | FHL0331
| BAL_GOR_1 | 2024-10-11 08:04 | 2024-10-11 15:12 | 2024-10-11 08:00 | No | PowerNet | 108.8 | 7.14 | BAL0331
| TMN_CB_1552 | 2024-10-11 19:12 | 2024-10-14 07:43 | 2024-10-11 19:11 | No | KiwiRail | No Notification | 60.51 | TMN0551
| MPE_CB_252 | 2024-10-12 07:04 | 2024-10-12 13:47 | 2024-10-12 07:00 | No | Northpower, Top Energy | 38.9 | 6.73 | BRB0331, KOE1101, MTO0331
| BRY_ISL_1 | 2024-10-14 06:48 | 2024-10-18 09:24 | 2024-10-14 06:30 | No | Orion New Zealand | 45.8 | 98.6 | BRY0661, BRY0662, BRY0663
| OWH_CB_112 | 2024-10-14 07:01 | 2024-10-19 07:17 | 2024-10-14 07:00 | No | Unison Networks | 45.8 | 120.26 | OWH0111
| BPE_T15 | 2024-10-14 07:04 | 2024-10-14 18:07 | 2024-10-14 07:00 | No | KiwiRail | 40.9 | 11.06 | BPE0551
| ALB_SVL_1 | 2024-10-14 07:11 | 2024-10-18 16:13 | 2024-10-14 07:00 | No | Vector | 51.8 | 105.05 | SVL0331
| HAM_OHW_1 | 2024-10-14 07:19 | 2024-10-18 10:41 | 2024-10-14 07:00 | No | WEL Networks, Waipa Networks, Powerco | 53.8 | 99.37 | HAM0111, CBG0111, TMU0111, TMU0112, WHU0331, WKO0331, KPU0661, PAO1101
| DRY_GLN_2 | 2024-10-14 07:36 | 2024-10-16 16:26 | 2024-10-14 07:30 | No | NZ Steel, Counties Power | 53.9 | 56.83 | GLN0331, GLN0332, GLN0333
| HEN_T3 | 2024-10-14 07:42 | 2024-10-16 16:43 | 2024-10-14 07:30 | No | Vector | 41.9 | 57.02 | HEN0339
| HAY_MLG_2 | 2024-10-14 07:49 | 2024-10-16 11:07 | 2024-10-14 07:30 | No | Wellington Electricity | 46.6 | 51.3 | MLG0111, MLG0331
| MPE_CB_252 | 2024-10-14 08:03 | 2024-10-14 23:01 | 2024-10-14 08:00 | No | Northpower, Top Energy | 6 | 14.97 | BRB0331, KOE1101, MTO0331
| MDN_T5 | 2024-10-14 08:13 | 2024-10-19 18:47 | 2024-10-14 08:00 | No | Northpower, Top Energy | 44.8 | 130.56 | MPE1101, KOE1101
| MPE_CB_252 | 2024-10-15 06:08 | 2024-10-15 22:04 | 2024-10-15 06:00 | No | Northpower, Top Energy | 41.8 | 15.93 | BRB0331, KOE1101, MTO0331
| BPE_T16 | 2024-10-15 07:07 | 2024-10-15 14:42 | 2024-10-15 07:00 | No | KiwiRail | 41.9 | 7.6 | BPE0551
| CYD_CML_TWZ_1 | 2024-10-15 07:45 | 2024-10-18 12:10 | 2024-10-15 07:30 | No | Aurora Energy, PowerNet | 40.9 | 76.43 | CML0331, FKN0331, FKN0332
| MPE_CB_252 | 2024-10-16 06:36 | 2024-10-18 19:39 | 2024-10-16 06:30 | Yes | Northpower, Top Energy | 8 | 46.01 | BRB0331, KOE1101, MTO0331
| HAY_CB_2772 | 2024-10-16 07:10 | 2024-10-18 13:44 | 2024-10-16 07:00 | No | Wellington Electricity | 40.7 | 54.56 | HAY0111
| LTN_T2 | 2024-10-16 07:36 | 2024-10-18 16:53 | 2024-10-16 07:30 | No | Powerco | 40.7 | 57.3 | LTN0331
| TIM_T6 | 2024-10-16 07:42 | 2024-10-16 13:53 | 2024-10-16 07:30 | No | Alpine Energy | 337.7 | 6.17 | TIM0111
| INV_T5 | 2024-10-17 07:39 | 2024-10-18 14:06 | 2024-10-17 07:30 | No | PowerNet | 42.7 | 30.45 | INV0331
| CST_T4 | 2024-10-17 12:11 | 2024-10-17 19:14 | 2024-10-17 12:00 | No | Powerco | 20.9 | 7.05 | CST0331
| RPO_WRK_1 | 2024-10-18 18:07 | 2024-10-19 16:05 | 2024-10-18 18:00 | No | Winstone Pulp, KiwiRail | No Notification | 21.97 | TNG0111, TNG0551
| HTI_TMU_1 | 2024-10-19 06:31 | 2024-10-19 16:32 | 2024-10-19 06:30 | No | Waipa Networks | No Notification | 10.02 | TMU0111, TMU0112
| CST_T2 | 2024-10-19 14:06 | 2024-10-19 21:43 | 2024-10-19 15:00 | No | Powerco | No Notification | 7.61 | CST0331
| TNG_220BS_B | 2024-10-21 06:33 | 2024-10-21 07:01 | 2024-10-21 06:30 | No | Winstone Pulp, KiwiRail | No Notification | 0.46 | TNG0111, TNG0551
| ASY_WPR_1 | 2024-10-21 07:37 | 2024-10-25 14:33 | 2024-10-21 07:30 | No | Mainpower New Zealand | 34.9 | 102.92 | ASY0111
| HPI_MDN_1 | 2024-10-21 07:40 | 2024-10-25 16:33 | 2024-10-21 07:30 | No | Northpower, Top Energy | 42 | 104.88 | BRB0331, MPE1101, KOE1101, MTO0331
| BPE_TNG_1 | 2024-10-21 07:44 | 2024-10-25 14:45 | 2024-10-21 07:30 | No | Winstone Pulp, KiwiRail | 39.7 | 103.03 | TNG0111, TNG0551
| TNG_T2 | 2024-10-21 07:44 | 2024-10-21 18:15 | 2024-10-21 07:30 | No | KiwiRail | 39.8 | 10.52 | TNG0555
| HWA_T2 | 2024-10-21 08:03 | 2024-10-31 16:20 | 2024-10-21 08:00 | No | Powerco, Beach Energy | 87.9 | 248.27 | HWA0331, HWA0332
| HKK_KUM_1 | 2024-10-22 06:58 | 2024-10-22 17:20 | 2024-10-22 06:30 | No | Westpower | 49.8 | 10.36 | HKK0661
| WHI_WRK_1 | 2024-10-22 07:02 | 2024-10-22 17:09 | 2024-10-22 07:00 | No | Unison Network, Eastlands Networks, Panpac | No Notification | 10.12 | RDF0331, WTU0331, FHL0331,TUI1101, WHI0111, WHI0112
| OAM_BPT_WTK_1 | 2024-10-22 10:16 | 2024-10-22 12:16 | 2024-10-22 10:00 | No | Network Waitaki | No Notification | 2 | OAM0331
| ROT_T2 | 2024-10-22 12:44 | 2024-10-22 19:26 | 2024-10-22 12:44 | No | Unison Network | No Notification | 6.69 | ROT0331
| HKK_OTI_2 | 2024-10-23 06:35 | 2024-10-23 16:34 | 2024-10-23 06:30 | No | Westpower | 50.8 | 9.98 | HKK0661
| PNI_TKR_1 | 2024-10-23 07:35 | 2024-10-23 16:02 | 2024-10-23 07:30 | No | Wellington Electricity | 41.7 | 8.45 | PNI0331
| TNG_T3 | 2024-10-23 07:42 | 2024-10-23 16:27 | 2024-10-23 07:30 | No | KiwiRail | 41.8 | 8.75 | TNG0555
| TNG_T12 | 2024-10-23 17:38 | 2024-10-24 19:22 | 2024-10-23 17:30 | No | Winstone Pulp | 15.1 | 25.73 | TNG0111
| HKK_KUM_1 | 2024-10-24 06:48 | 2024-10-24 14:45 | 2024-10-24 06:30 | No | Westpower | 51.8 | 7.95 | HKK0661
| PNI_T2 | 2024-10-24 07:36 | 2024-10-24 17:10 | 2024-10-24 07:30 | No | Wellington Electricity | 35.8 | 9.57 | PNI0331
| HEN_T2 | 2024-10-24 15:53 | 2024-10-24 19:33 | 2024-10-24 15:52 | No | Vector | No Notification | 3.67 | HEN0338
| HTI_TMU_1 | 2024-10-25 07:34 | 2024-10-25 16:08 | 2024-10-25 07:30 | No | Waipa Networks | 1.6 | 8.57 | TMU0111, TMU0112
| WPW_T1 | 2024-10-25 12:10 | 2024-10-25 13:40 | 2024-10-25 12:00 | No | Centralines | No Notification | 1.49 | WPW0331
| WDV_DVK_WPW_2 | 2024-10-25 12:11 | 2024-10-25 13:38 | 2024-10-25 12:00 | No | Scanpower, Centralines | No Notification | 1.45 | DVK0111, WPW0331
| COL_OTI_2 | 2024-10-26 09:29 | 2024-10-29 15:02 | 2024-10-26 09:28 | No | Westpower | No Notification | 77.55 | GYM0661, HKK0661
| STK_T6 | 2024-10-29 06:39 | 2024-11-01 11:20 | 2024-11-01 | No | Network Tasman | 41.9 | 76.67 | STK0331
| BPE_PRM_HAY_1 | 2024-10-29 07:36 | 2024-11-01 17:06 | 2024-10-29 07:30 | No | Electra | 40.8 | 81.5 | PRM0331
| KOE_MPE_2 | 2024-10-29 07:36 | 2024-11-01 15:16 | 2024-11-01 | No | Top Energy | 42.8 | 79.66 | KOE1101
| RPO_TNG_1 | 2024-10-29 07:39 | 2024-11-01 19:11 | 2024-11-01 | No | Winstone Pulp, KiwiRail | 33.7 | 83.53 | TNG0111, TNG0551
| HAM_T7 | 2024-10-30 07:06 | 2024-11-01 17:37 | 2024-11-01 | No | KiwiRail | 43.8 | 58.51 | HAM0551, HAM0552
| RDF_WTU_2 | 2024-10-30 07:14 | 2024-11-21 16:08 | 2024-10-30 07:00 | No | Unison Network | 139.8 | 536.9 | WTU0331
| WTU_T3 | 2024-10-30 07:14 | 2024-11-22 10:11 | 2024-11-01 | No | Unison Network | 139.8 | 554.94 | WTU0331
| TWH_T2 | 2024-10-30 08:11 | 2024-11-01 16:11 | 2024-11-01 | No | WEL Networks | 70 | 55.99 | TWH0331
| WEL_T2 | 2024-10-31 07:04 | 2024-10-31 07:17 | 2024-10-31 07:00 | No | Vector | No Notification | 0.21 | WEL0331
| HEN_WEL_1 | 2024-10-31 07:11 | 2024-10-31 17:45 | 2024-10-31 07:00 | No | Northpower | 49.6 | 10.57 | MTO0331
| HEN_MPE_2 | 2024-10-31 07:32 | 2024-10-31 07:44 | 2024-10-31 07:30 | No | Vector, Northpower | No Notification | 0.19 | WEL0331, MTO0331
| DOB_GYM_1 | 2024-10-31 07:39 | 2024-11-01 16:15 | 2024-11-01 | No | Westpower | 36.9 | 32.59 | GYM0661
| TNG_T2 | 2024-10-31 07:47 | 2024-10-31 16:16 | 2024-10-31 07:30 | No | KiwiRail | 37.7 | 8.49 | TNG0555
| HEN_MPE_2 | 2024-10-31 17:46 | 2024-10-31 17:56 | 2024-10-31 17:30 | No | Vector, Northpower | No Notification | 0.16 | WEL0331, MTO0331
| TGA_T4 | 2024-11-01 06:59 | 2024-11-01 10:34 | 2024-11-01 | Yes | Powerco | 46.7 | 3.5822 | TGA0331
| HWA_T1 | 2024-11-01 08:05 | 2024-11-04 07:53 | 2024-11-01 08:00 | No | Powerco, Beach Energy | 6.6 | 71.8 | HWA0331, HWA0332
| STK_T3 | 2024-11-04 06:52 | 2024-11-07 10:45 | 2024-11-04 06:30 | No | Network Tasman | 34.9 | 75.88 | STK0661
| WIR_T2 | 2024-11-04 07:04 | 2024-11-06 14:13 | 2024-11-04 07:00 | No | Vector | 157.8 | 55.14 | WIR0331
| EDG_KAW_3 | 2024-11-04 07:15 | 2024-11-16 10:38 | 2024-11-04 07:00 | No | Unison Networks | 68.7 | 291.3811 | OWH0111
| HWB_SDN_1 | 2024-11-04 07:34 | 2024-11-08 12:12 | 2024-11-04 07:30 | No | Aurora Energy | 35 | 100.63 | SDN0331
| RDF_TUI_2 | 2024-11-04 07:36 | 2024-11-08 13:32 | 2024-11-04 07:30 | No | Unison Network, Eastlands Networks | 80.7 | 101.94 | RDF0331, FHL0331,TUI1101
| BRB_HPI_1 | 2024-11-04 07:53 | 2024-11-23 15:15 | 2024-11-04 07:30 | No | Northpower, Top Energy | 53.6 | 463.37 | BRB0331, MPE1101, KOE1101
| HWA_T1 | 2024-11-04 08:02 | 2024-11-04 17:02 | 2024-11-04 08:00 | No | Powerco, Beach Energy | 3.9 | 9 | HWA0331, HWA0332
| HWA_CB_2648 | 2024-11-04 08:15 | 2025-03-14 14:22 | 2025-03-01 | No | Powerco, Beach Energy | 160.8 | 3126.12 | HWA0331, HWA0332
| BPE_PRM_HAY_1 | 2024-11-04 08:49 | 2024-11-08 16:11 | 2024-11-04 08:30 | No | Electra | 39.8 | 103.35 | PRM0331
| HWA_T1 | 2024-11-04 17:30 | 2024-11-08 13:50 | 2024-11-04 17:30 | No | Powerco, Beach Energy | 161.2 | 92.34 | HWA0331, HWA0332
| RDF_WHI_1 | 2024-11-05 07:16 | 2024-11-05 07:24 | 2024-11-05 07:00 | No | Unison Network, Eastlands Networks, Panpac | No Notification | 0.15 | RDF0331, WTU0331, TUI1101, FHL0331, WHI0111, WHI0112
| WHI_547_587 | 2024-11-05 07:51 | 2024-11-05 17:25 | 2024-11-05 07:30 | No | Panpac, Unison Network | 40.7 | 9.56 | WHI0111, WHI0112, RDF0331
| HAY_T11 | 2024-11-05 07:56 | 2024-11-07 15:41 | 2024-11-05 07:30 | No | Wellington Electricity | 40.8 | 55.74 | HAY0111, HAY0331
| MHO_T3 | 2024-11-05 10:03 | 2024-11-05 13:19 | 2024-11-05 10:00 | No | Electra | No Notification | 3.28 | MHO0331
| RDF_WHI_1 | 2024-11-05 17:15 | 2024-11-05 17:28 | 2024-11-05 17:00 | No | Unison Network, Eastlands Networks, Panpac | No Notification | 0.21 | RDF0331, WTU0331, TUI1101, FHL0331, WHI0111, WHI0112
| TNG_T2 | 2024-11-06 00:47 | 2024-11-06 02:55 | 2024-11-06 00:46 | No | KiwiRail | No Notification | 2.14 | TNG0555
| WIL_T3 | 2024-11-06 07:21 | 2024-11-15 07:08 | 2024-11-06 07:00 | No | Wellington Electricity | 160 | 216.54 | WIL0331
| HAM_T1 | 2024-11-06 07:34 | 2024-11-08 16:36 | 2024-11-06 07:30 | No | WEL Networks | 36.9 | 57.04 | HAM0111
| HWB_T3 | 2024-11-06 07:42 | 2024-11-08 12:18 | 2024-11-06 07:30 | No | Aurora Energy, PowerNet | 100 | 52.6 | HWB0331, HWB0332
| SFD_T9 | 2024-11-07 18:06 | 2024-11-08 10:35 | 2024-11-07 18:05 | No | Powerco, Beach Energy | No Notification | 16.48 | SFD0331, OPK0331, HWA0331, HWA0332
| BPE_MTR_1 | 2024-11-08 06:18 | 2024-11-08 10:43 | 2024-11-08 06:00 | No | Electra | No Notification | 4.42 | MHO0331
| MGM_CB_172 | 2024-11-08 06:31 | 2024-11-08 13:41 | 2024-11-08 06:30 | No | Powerco | 16.7 | 7.17 | MGM0331
| BPE_WDV_1 | 2024-11-08 06:39 | 2024-11-08 13:34 | 2024-11-08 06:30 | No | Scanpower, Centralines | 48.6 | 6.91 | DVK0111, WPW0331, WDV0111
| OWH_TMI_TRK_1 | 2024-11-08 07:32 | 2024-11-15 08:43 | 2024-11-08 07:30 | No | Unison Networks, Powerco | 72.8 | 169.19 | OWH0111, TMI0331
| KIN_TRK_2 | 2024-11-10 07:41 | 2024-11-10 13:15 | 2024-11-10 07:30 | No | Vector | 5.9 | 5.56 | LFD1101
| TAK_T8 | 2024-11-11 07:01 | 2024-11-15 15:38 | 2024-11-11 07:00 | No | Vector | 61.6 | 104.62 | TAK0331
| WGN_WVY_1 | 2024-11-11 07:05 | 2024-11-15 17:22 | 2024-11-11 07:00 | No | Powerco, Beach Energy | 40.7 | 106.28 | HWA0331, HWA0332
| HAM_T1 | 2024-11-11 07:35 | 2024-11-12 18:06 | 2024-11-11 07:30 | No | WEL Networks | 41.9 | 34.52 | HAM0111
| ALB_SVL_2 | 2024-11-11 07:38 | 2024-11-15 16:14 | 2024-11-11 07:30 | No | Vector | 41.9 | 104.6 | SVL0331
| HWB_T5 | 2024-11-11 07:38 | 2024-11-15 13:53 | 2024-11-11 07:30 | No | Aurora Energy, PowerNet | 139.8 | 102.25 | HWB0331, HWB0332
| KWA_WIL_1 | 2024-11-11 08:15 | 2024-11-13 13:50 | 2024-11-11 08:00 | No | Wellington Electricity | 118.9 | 53.59 | KWA0111
| ASY_T3 | 2024-11-11 09:13 | 2024-11-14 12:19 | 2024-11-11 09:00 | No | Mainpower New Zealand | 47.9 | 75.1 | ASY0111
| MGM_CB_172 | 2024-11-12 06:34 | 2024-11-12 15:27 | 2024-11-12 06:30 | No | Powerco | 13.6 | 8.89 | MGM0331
| HAY_WIL_LTN_2 | 2024-11-12 06:34 | 2024-11-19 15:33 | 2024-11-12 06:30 | No | Wellington Electricity | 88.6 | 105 | WIL0331
| BPE_WDV_2 | 2024-11-12 06:41 | 2024-11-12 15:26 | 2024-11-12 06:30 | No | Scanpower, Centralines | 41.7 | 8.74 | DVK0111, WPW0331, WDV0111
| STK_T10 | 2024-11-12 06:43 | 2024-11-14 16:28 | 2024-11-12 06:30 | No | Network Tasman | 59.7 | 57.74 | STK0331
| MTN_T1 | 2024-11-12 08:05 | 2024-11-12 14:07 | 2024-11-12 08:00 | No | Powerco | 53.8 | 6.02 | MTN0331
| WHU_T3 | 2024-11-12 12:41 | 2024-11-15 16:36 | 2024-11-12 12:30 | No | Powerco | 29 | 75.91 | WHU0331
| WHU_WKO_1 | 2024-11-12 12:42 | 2024-11-15 16:31 | 2024-11-12 12:30 | No | Powerco | 29 | 75.82 | WKO0331, KPU0661
| HRP_RDF_1 | 2024-11-13 07:32 | 2024-11-13 17:11 | 2024-11-13 07:30 | No | Unison Network, Eastlands Networks, Panpac | 125.8 | 9.65 | RDF0331, WTU0331, FHL0331,TUI1101, WHI0111, WHI0112
| DOB_GYM_1 | 2024-11-13 07:38 | 2024-11-13 15:40 | 2024-11-13 07:30 | No | Westpower | 125.8 | 8.03 | GYM0661
| MTN_T2 | 2024-11-13 09:31 | 2024-11-13 12:34 | 2024-11-13 09:30 | No | Powerco | 54.8 | 3.05 | MTN0331
| TNG_T2 | 2024-11-14 00:16 | 2024-11-14 01:17 | 2024-11-14 00:15 | No | KiwiRail | No Notification | 1.03 | TNG0555
| OWH_CB_112 | 2024-11-15 09:00 | 2024-11-16 10:42 | 2024-11-15 09:00 | No | Unison Networks | 79.8 | 25.7 | OWH0111
| PRM_T2 | 2024-11-16 07:01 | 2024-11-16 13:19 | 2024-11-16 07:00 | No | Electra | No Notification | 6.3 | PRM0331
| HTI_TMU_1 | 2024-11-17 08:36 | 2024-11-22 16:40 | 2024-11-17 08:30 | No | Waipa Networks | 3 | 128.07 | TMU0111, TMU0112
| HTI_T1 | 2024-11-18 06:02 | 2024-11-18 06:10 | 2024-11-18 06:00 | No | The Lines Company | No Notification | 0.13 | HTI0331
| ISL_T1 | 2024-11-18 06:40 | 2024-11-21 17:21 | 2024-11-18 06:30 | No | Orion New Zealand | 101.8 | 82.68 | ISL0331
| DRY_BOB_HLY_1 | 2024-11-18 07:05 | 2024-11-26 14:22 | 2024-11-18 07:00 | No | NZ Steel, Counties Power | 47 | 199.27 | GLN0331, GLN0332, GLN0333
| RPO_TNG_1 | 2024-11-18 07:35 | 2024-11-22 14:28 | 2024-11-18 07:30 | No | Winstone Pulp, KiwiRail | 44.8 | 102.89 | TNG0111, TNG0551
| WIL_T5 | 2024-11-18 07:36 | 2024-11-22 14:53 | 2024-11-18 07:30 | No | Wellington Electricity | 38.9 | 70 | WIL0331
| WIR_T2 | 2024-11-19 07:01 | 2024-11-22 17:37 | 2024-11-19 07:00 | No | Vector | 46 | 82.6 | WIR0331
| EDG_OWH_2 | 2024-11-19 07:33 | 2024-11-22 15:32 | 2024-11-19 07:30 | No | Unison Networks | 46 | 79.99 | OWH0111
| WHU_124_134_127 | 2024-11-19 07:47 | 2024-11-21 11:26 | 2024-11-19 07:30 | No | Powerco | 35.8 | 51.65 | WHU0331, WKO0331, KPU0661
| HLY_T21 | 2024-11-20 07:03 | 2024-11-22 09:53 | 2024-11-20 07:00 | No | WEL Networks | 47 | 50.83 | HLY0331, HLY0332
| DOB_GYM_1 | 2024-11-21 13:36 | 2024-11-21 14:47 | 2024-11-21 13:35 | No | Westpower | No Notification | 1.18 | GYM0661
| STK_FDR_92 | 2024-11-22 08:10 | 2024-11-22 14:37 | 2024-11-22 08:00 | No | Network Tasman | 3.8 | 6.45 | STK0661
| HTI_T1 | 2024-11-22 17:03 | 2024-11-22 17:14 | 2024-11-22 17:00 | No | The Lines Company | No Notification | 0.18 | HTI0331
| KAW_OHK_1 | 2024-11-23 08:07 | 2024-11-23 17:14 | 2024-11-23 08:00 | No | Norse Skog | 3.7 | 9.11 | KAW0111
| BDE_GOR_1 | 2024-11-23 08:07 | 2024-11-23 12:44 | 2024-11-23 08:00 | No | Daiken , PowerNet | 1.7 | 4.61 | BDE0111, BDE0112, EDN0331
| BAL_GOR_1 | 2024-11-23 08:07 | 2024-11-23 12:44 | 2024-11-23 08:00 | No | PowerNet | 1.7 | 4.61 | BAL0331
| TNG_T2 | 2024-11-24 08:03 | 2024-11-24 15:18 | 2024-11-24 08:00 | No | KiwiRail | 5.8 | 7.25 | TNG0555
| BDE_GOR_1 | 2024-11-24 08:14 | 2024-11-24 12:19 | 2024-11-24 08:00 | No | Daiken , PowerNet | 2.7 | 4.09 | BDE0111, BDE0112, EDN0331
| BAL_GOR_1 | 2024-11-24 08:14 | 2024-11-24 12:18 | 2024-11-24 08:00 | No | PowerNet | 2.7 | 4.07 | BAL0331
| HTI_T1 | 2024-11-25 06:06 | 2024-11-25 06:15 | 2024-11-25 06:00 | No | The Lines Company | No Notification | 0.15 | HTI0331
| GYM_KUM_1 | 2024-11-25 06:32 | 2024-11-29 15:16 | 2024-11-25 06:30 | No | Westpower | No Notification | 104.73 | GYM0661
| KIK_MCH_1 | 2024-11-25 06:36 | 2024-11-29 15:13 | 2024-11-25 06:30 | No | Westpower, Buller Electricity | 67.8 | 104.62 | DOB0331, RFN1101, RFN1102, ORO0111, ORO0331
| BLN_STK_1 | 2024-11-25 06:47 | 2024-11-29 13:35 | 2024-11-25 06:30 | No | Marlborough Lines | 139.7 | 102.8 | BLN0331
| STK_T7 | 2024-11-25 06:47 | 2024-11-29 13:35 | 2024-11-25 06:30 | No | Network Tasman, Marlborough Lines | 139.7 | 102.79 | STK0661, BLN0331
| ASB_BRY_1 | 2024-11-25 06:52 | 2024-11-29 16:40 | 2024-11-25 06:30 | No | Orion New Zealand | 67.9 | 105.79 | BRY0661, BRY0662, BRY0663
| WHU_WKO_2 | 2024-11-25 06:53 | 2024-11-27 10:44 | 2024-11-25 06:30 | No | Powerco | 41.7 | 51.85 | WKO0331, KPU0661
| RDF_WTU_1 | 2024-11-25 07:18 | 2024-12-17 11:08 | 2024-11-25 07:00 | No | Unison Network | 165.8 | 531.83 | WTU0331
| WTU_T4 | 2024-11-25 07:18 | 2024-12-18 07:08 | 2024-12-01 | No | Unison Network | 165.8 | 551.83 | WTU0331
| HPI_MDN_1 | 2024-11-25 07:41 | 2024-12-11 17:02 | 2024-12-01 | No | Northpower, Top Energy | 74.6 | 393.35 | BRB0331, MPE1101, KOE1101, MTO0331
| BPE_MHO_2 | 2024-11-25 07:44 | 2024-11-27 17:39 | 2024-11-25 07:30 | No | Electra | 129 | 57.92 | MHO0331
| KPO_TMU_1 | 2024-11-25 07:44 | 2024-11-29 15:17 | 2024-11-25 07:30 | No | Waipa Networks | 62.7 | 103.55 | TMU0111, TMU0112
| WDV_T1 | 2024-11-25 07:52 | 2024-12-04 14:16 | 2024-12-01 | No | Scanpower | 39 | 222.4 | WDV0111
| TGA_T4 | 2024-11-26 07:07 | 2024-11-26 07:33 | 2024-11-26 07:00 | No | Powerco | No Notification | 0.43 | TGA0331
| TGA_T1 | 2024-11-26 07:13 | 2024-11-27 12:26 | 2024-11-26 07:00 | No | Powerco | 68.8 | 29.22 | TGA0111
| HLY_T22 | 2024-11-27 07:02 | 2024-11-29 10:18 | 2024-11-27 07:00 | No | WEL Networks | 42 | 51.26 | HLY0331, HLY0332
| BPE_TWC_LTN_1 | 2024-11-27 08:23 | 2024-11-27 10:43 | 2024-11-27 08:00 | No | Powerco | 14.6 | 2.34 | LTN0331
| TGA_T4 | 2024-11-27 12:02 | 2024-11-27 12:18 | 2024-11-27 12:00 | No | Powerco | No Notification | 0.28 | TGA0331
| BPE_MHO_2 | 2024-11-28 07:22 | 2024-11-28 16:48 | 2024-11-28 07:00 | No | Electra | No Notification | 9.42 | MHO0331
| OWH_CB_112 | 2024-11-28 08:13 | 2024-12-05 08:32 | 2024-12-01 | No | Unison Networks | 70.8 | 168.31 | OWH0111
| EDG_KAW_3 | 2024-11-28 08:21 | 2024-12-05 08:26 | 2024-11-28 08:00 | No | Unison Networks | 91.9 | 168.08 | OWH0111
| BDE_T1 | 2024-11-29 10:08 | 2024-11-29 14:14 | 2024-11-29 10:00 | No | Daiken | No Notification | 4.11 | BDE0111, BDE0112
| HTI_T1 | 2024-11-29 18:02 | 2024-11-29 18:19 | 2024-11-29 18:00 | No | The Lines Company | No Notification | 0.28 | HTI0331
| CUL_T22 | 2024-12-02 06:37 | 2024-12-02 15:48 | 2024-12-02 06:30 | No | Mainpower New Zealand | No Notification | 9.19 | CUL0331
| BOB_214_227_267 | 2024-12-02 07:20 | 2024-12-06 16:40 | 2024-12-02 07:00 | No | Counties Power | 41.9 | 105.33 | BOB0331
| KAW_T11 | 2024-12-02 07:31 | 2024-12-06 14:33 | 2024-12-02 07:30 | No | Norse Skog | 23.9 | 103.02 | KAW0111
| HAM_WKM_1 | 2024-12-02 08:44 | 2024-12-06 17:20 | 2024-12-02 08:30 | No | WEL Networks, Waipa Networks, Powerco | 62 | 104.6 | HAM0111, CBG0111, TMU0111, TMU0112, WHU0331, WKO0331, KPU0661, PAO1101
| CBG_KPO_2 | 2024-12-03 06:13 | 2024-12-10 15:41 | 2024-12-03 06:00 | No | Waipa Networks | 112.6 | 177.48 | CBG0111
| GYM_KUM_1 | 2024-12-03 06:33 | 2024-12-05 13:24 | 2024-12-03 06:30 | No | Westpower | 61.9 | 54.85 | GYM0661
| HAY_CB_2892 | 2024-12-04 05:07 | 2024-12-04 06:29 | 2024-12-04 05:00 | No | Wellington Electricity | 7.5 | 1.37 | HAY0111
| MGM_CB_172 | 2024-12-04 05:10 | 2024-12-10 13:42 | 2024-12-04 05:00 | No | Powerco | 7.5 | 152.53 | MGM0331
| HAY_T11 | 2024-12-04 06:35 | 2024-12-04 15:58 | 2024-12-04 06:30 | No | Wellington Electricity | 29.7 | 9.37 | HAY0111, HAY0331
| HAY_CB_2892 | 2024-12-04 16:01 | 2024-12-06 06:29 | 2024-12-04 16:00 | No | Wellington Electricity | 8 | 38.46 | HAY0111
| HAY_MLG_2 | 2024-12-05 06:38 | 2024-12-05 14:51 | 2024-12-05 06:30 | No | Wellington Electricity | 30.7 | 8.22 | MLG0111, MLG0331
| COL_OTI_2 | 2024-12-05 13:34 | 2024-12-06 19:36 | 2024-12-05 13:30 | No | Westpower | No Notification | 30.03 | GYM0661, HKK0661
| HAY_T11 | 2024-12-06 06:37 | 2024-12-07 21:07 | 2024-12-06 06:30 | No | Wellington Electricity | 31.7 | 38.49 | HAY0111, HAY0331
| OWH_CB_112 | 2024-12-07 07:31 | 2024-12-10 18:02 | 2024-12-07 07:30 | No | Unison Networks | 66.9 | 82.53 | OWH0111
| HAY_CB_2892 | 2024-12-07 21:00 | 2024-12-08 06:13 | 2024-12-07 21:00 | No | Wellington Electricity | No Notification | 9.21 | HAY0111
| HAY_T11 | 2024-12-08 06:42 | 2024-12-08 15:26 | 2024-12-08 06:30 | No | Wellington Electricity | 33.7 | 8.74 | HAY0111, HAY0331
| KOE_MPE_1 | 2024-12-08 07:39 | 2024-12-08 17:49 | 2024-12-08 07:30 | No | Top Energy | 67 | 10.18 | KOE1101
| HEN_MPE_1 | 2024-12-08 07:46 | 2024-12-08 17:47 | 2024-12-08 07:30 | No | Vector, Northpower | 67 | 10.02 | WEL0331, MTO0331
| HAY_CB_2892 | 2024-12-08 15:33 | 2024-12-09 16:45 | 2024-12-08 15:30 | No | Wellington Electricity | 9 | 25.2 | HAY0111
| HAY_MLG_2 | 2024-12-09 06:48 | 2024-12-09 16:20 | 2024-12-09 06:30 | No | Wellington Electricity | 34.7 | 9.54 | MLG0111, MLG0331
| HAY_UHT_2 | 2024-12-09 06:48 | 2024-12-10 13:32 | 2024-12-09 06:30 | No | Wellington Electricity, Powerco | 34.7 | 30.72 | UHT0331, MST0331, GYT0331
| TWH_T1 | 2024-12-09 07:40 | 2024-12-19 07:41 | 2024-12-09 07:30 | No | WEL Networks | 69.8 | 240.02 | TWH0331
| TNG_T2 | 2024-12-09 07:43 | 2024-12-09 16:48 | 2024-12-09 07:30 | No | KiwiRail | 209.7 | 9.08 | TNG0555
| KOE_MPE_2 | 2024-12-09 07:48 | 2024-12-10 16:35 | 2024-12-09 07:30 | No | Top Energy | 68.8 | 32.79 | KOE1101
| BRB_T2 | 2024-12-10 07:10 | 2024-12-10 13:35 | 2024-12-10 07:00 | No | Northpower | 21.7 | 6.43 | BRB0331
| RPO_WRK_1 | 2024-12-10 08:26 | 2024-12-13 16:50 | 2024-12-10 08:00 | No | Winstone Pulp, KiwiRail | 39.7 | 80.4 | TNG0111, TNG0551
| WRK_T30 | 2024-12-11 07:31 | 2024-12-12 15:21 | 2024-12-11 07:30 | No | Unison Network | 40.7 | 10.27 | WRK0331
| WHI_WRK_1 | 2024-12-11 07:34 | 2024-12-12 14:35 | 2024-12-11 07:30 | No | Unison Network, Eastlands Networks, Panpac | 40.6 | 31.02 | RDF0331, WTU0331, FHL0331,TUI1101, WHI0111, WHI0112
| MGM_CB_172 | 2024-12-11 07:39 | 2024-12-12 14:09 | 2024-12-11 07:30 | No | Powerco | 19.6 | 30.5 | MGM0331
| TGA_T2 | 2024-12-11 07:40 | 2024-12-13 16:15 | 2024-12-11 07:30 | No | Powerco | 39.9 | 56.58 | TGA0111
| HAY_UHT_1 | 2024-12-11 07:45 | 2024-12-12 14:09 | 2024-12-11 07:30 | No | Wellington Electricity, Powerco | 153.8 | 30.4 | UHT0331, MST0331, GYT0331
| KPU_WKO_1 | 2024-12-11 09:20 | 2024-12-11 15:17 | 2024-12-11 09:00 | No | Powerco | 92.9 | 5.95 | KPU0661
| MPE_CB_252 | 2024-12-12 06:02 | 2024-12-12 21:36 | 2024-12-12 06:00 | No | Northpower, Top Energy | 180.7 | 15.56 | BRB0331, KOE1101, MTO0331
| TMI_CB_3222 | 2024-12-12 07:10 | 2024-12-12 15:34 | 2024-12-12 07:10 | No | Powerco | No Notification | 8.4 | TMI0331
| INV_T3 | 2024-12-12 07:48 | 2024-12-12 15:45 | 2024-12-12 07:30 | No | PowerNet | 9.7 | 7.94 | INV0331
| MPE_CB_252 | 2024-12-13 06:03 | 2024-12-13 21:33 | 2024-12-13 06:00 | No | Northpower, Top Energy | 181.7 | 15.49 | BRB0331, KOE1101, MTO0331
| MPE_CB_252 | 2024-12-14 06:06 | 2024-12-14 07:29 | 2024-12-14 06:00 | No | Northpower, Top Energy | 182.7 | 1.38 | BRB0331, KOE1101, MTO0331
| KOE_MPE_2 | 2024-12-14 07:23 | 2024-12-15 16:36 | 2024-12-14 07:30 | Yes | Top Energy | 73.8 | 18.84 | KOE1101
| MPE_CB_252 | 2024-12-15 06:04 | 2024-12-15 07:25 | 2024-12-15 06:00 | No | Northpower, Top Energy | No Notification | 1.34 | BRB0331, KOE1101, MTO0331
| BPE_T9 | 2024-12-16 06:54 | 2024-12-17 17:52 | 2024-12-16 06:30 | No | Powerco | 87.6 | 34.96 | BPE0331
| RPO_TNG_1 | 2024-12-16 07:07 | 2024-12-20 14:42 | 2024-12-16 07:00 | No | Winstone Pulp, KiwiRail | 90.8 | 103.59 | TNG0111, TNG0551
| HAM_T7 | 2024-12-16 07:09 | 2024-12-16 16:16 | 2024-12-16 07:00 | No | KiwiRail | 23.7 | 9.12 | HAM0551, HAM0552
| RDF_TUI_1 | 2024-12-16 07:09 | 2024-12-18 16:39 | 2024-12-16 07:00 | No | Unison Network, Eastlands Networks | 87.7 | 57.49 | RDF0331, FHL0331,TUI1101
| KOE_MPE_1 | 2024-12-16 07:33 | 2024-12-17 16:50 | 2024-12-16 07:30 | No | Top Energy | 75 | 33.27 | KOE1101
| MPE_CB_252 | 2024-12-16 07:35 | 2024-12-16 21:31 | 2024-12-16 07:30 | No | Northpower, Top Energy | 75 | 13.94 | BRB0331, KOE1101, MTO0331
| HAY_WIL_LTN_1 | 2024-12-16 07:57 | 2024-12-19 16:10 | 2024-12-16 07:30 | No | Powerco | 24.8 | 80.2 | LTN0331
| MPE_CB_252 | 2024-12-17 06:02 | 2024-12-20 13:06 | 2024-12-17 06:00 | Yes | Northpower, Top Energy | 42.7 | 53.64 | BRB0331, KOE1101, MTO0331
| WGN_T2 | 2024-12-17 08:06 | 2024-12-17 12:10 | 2024-12-17 08:00 | No | Powerco | 130.7 | 4.06 | WGN0331
| CML_CB_1042 | 2024-12-17 09:54 | 2024-12-19 10:21 | 2024-12-17 18:00 | No | Aurora Energy | 84.7 | 48.46 | CML0331
| CML_T5 | 2024-12-17 09:54 | 2024-12-17 17:45 | 2024-12-17 09:30 | No | Aurora Energy, PowerNet | 84.7 | 7.85 | CML0331, FKN0331, FKN0332
| KAW_T5 | 2024-12-18 07:45 | 2024-12-18 21:48 | 2024-12-18 07:30 | No | Horizon Energy | 6.7 | 14.05 | KAW0111
| BRY_T5 | 2024-12-19 07:34 | 2024-12-19 12:20 | 2024-12-19 07:30 | No | Orion New Zealand | 19.9 | 4.76 | BRY0661, BRY0662, BRY0663
| MGM_WDV_1 | 2024-12-20 07:06 | 2024-12-20 10:06 | 2024-12-20 07:00 | No | Powerco | No Notification | 2.99 | MGM0331
| RDF_T4 | 2024-12-21 16:24 | 2024-12-21 16:43 | 2024-12-21 16:24 | No | Unison Network, Eastlands Networks | No Notification | 0.3 | RDF0331, WTU0331, FHL0331,TUI1101
| RPO_WRK_1 | 2024-12-24 09:06 | 2024-12-24 13:12 | 2024-12-24 09:00 | No | Winstone Pulp, KiwiRail | No Notification | 4.11 | TNG0111, TNG0551
| MTN_T2 | 2025-01-07 05:31 | 2025-01-07 13:11 | 2025-01-07 05:31 | No | Powerco | No Notification | 7.66 | MTN0331
| HEN_WEL_1 | 2025-01-08 07:15 | 2025-01-09 15:54 | 2025-01-08 07:00 | No | Northpower | 118.6 | 32.66 | MTO0331
| UHT_T1 | 2025-01-12 06:50 | 2025-01-12 11:17 | 2025-01-12 06:49 | No | Wellington Electricity | No Notification | 4.46 | UHT0331
| HTI_TMU_1 | 2025-01-13 07:05 | 2025-01-15 15:12 | 2025-01-13 07:00 | No | Waipa Networks | 30.7 | 56.13 | TMU0111, TMU0112
| EDG_OWH_2 | 2025-01-13 07:11 | 2025-01-17 14:04 | 2025-01-13 07:00 | No | Unison Networks | 41 | 102.875 | OWH0111
| CPK_T3 | 2025-01-13 07:13 | 2025-01-13 16:38 | 2025-01-13 07:00 | No | Wellington Electricity | 173.9 | 9.4 | CPK0331
| KAW_T5 | 2025-01-13 07:19 | 2025-01-24 09:52 | 2025-01-13 07:00 | No | Horizon Energy | 187.7 | 266.55 | KAW0111
| BRB_HPI_1 | 2025-01-13 07:33 | 2025-01-17 15:03 | 2025-01-13 07:30 | No | Northpower, Top Energy | 40.9 | 103.51 | BRB0331, MPE1101, KOE1101
| MPE_CB_252 | 2025-01-13 07:35 | 2025-01-13 21:40 | 2025-01-13 07:30 | No | Northpower, Top Energy | 40.9 | 14.08 | BRB0331, KOE1101, MTO0331
| TKR_T2 | 2025-01-13 07:40 | 2025-02-19 12:02 | 2025-02-01 | No | Wellington Electricity | 214.8 | 892.37 | TKR0331
| RPO_TNG_1 | 2025-01-13 10:07 | 2025-01-13 13:11 | 2025-01-13 10:00 | No | Winstone Pulp, KiwiRail | 40.8 | 3.07 | TNG0111, TNG0551
| MPE_CB_252 | 2025-01-14 05:59 | 2025-01-16 21:47 | 2025-01-14 06:00 | Yes | Northpower, Top Energy | 41.8 | 47.01 | BRB0331, KOE1101, MTO0331
| BPE_MTN_WGN_1 | 2025-01-14 06:38 | 2025-01-15 16:18 | 2025-01-14 06:30 | No | Powerco | 115.9 | 33.66 | MTN0331
| CPK_T4 | 2025-01-14 07:21 | 2025-01-14 15:25 | 2025-01-14 07:00 | No | Wellington Electricity | 174.9 | 8.07 | CPK0331
| WHI_T2 | 2025-01-14 07:56 | 2025-01-16 10:45 | 2025-01-14 07:30 | No | Panpac | 116 | 50.83 | WHI0111, WHI0112
| WRK_T29 | 2025-01-14 09:23 | 2025-01-17 19:58 | 2025-01-14 09:00 | No | Unison Network | 42 | 82.59 | WRK0331
| MTN_T2 | 2025-01-16 06:37 | 2025-01-17 14:41 | 2025-01-16 06:30 | No | Powerco | 117.9 | 32.07 | MTN0331
| HAM_PAO_WHU_1 | 2025-01-16 08:13 | 2025-01-17 17:50 | 2025-01-16 08:00 | No | Powerco | 104.8 | 33.63 | PAO1101, WHU0331, WKO0331, KPU0661
| ROT_11BS_B | 2025-01-16 08:48 | 2025-01-16 16:56 | 2025-01-16 07:30 | No | Unison Network | 156.7 | 8.14 | ROT0111
| MPE_CB_252 | 2025-01-17 06:02 | 2025-01-17 15:07 | 2025-01-17 06:00 | No | Northpower, Top Energy | 44.8 | 9.08 | BRB0331, KOE1101, MTO0331
| TIM_T5 | 2025-01-18 06:43 | 2025-01-18 12:38 | 2025-01-18 06:30 | No | Alpine Energy | 25.7 | 5.93 | TIM0111, TMK0331
| CPK_T11 | 2025-01-18 08:12 | 2025-01-19 12:55 | 2025-01-18 08:00 | No | Wellington Electricity | 154.8 | 28.72 | CPK0111, CPK0331
| TIM_T8 | 2025-01-19 06:36 | 2025-01-19 13:40 | 2025-01-19 06:30 | No | Alpine Energy | 26.7 | 7.05 | TIM0111, TMK0331
| KPO_CB_252 | 2025-01-20 06:04 | 2025-01-25 09:52 | 2025-01-20 06:00 | No | Waipa Networks | No Notification | 123.8 | CBG0111
| DOB_T2 | 2025-01-20 06:42 | 2025-01-24 17:15 | 2025-01-20 06:30 | No | Westpower | 47.6 | 106.54 | DOB0331
| KMO_TMI_1 | 2025-01-20 07:03 | 2025-01-22 20:33 | 2025-01-20 07:00 | No | Powerco | 47.7 | 61.5 | TMI0331
| KMO_TRK_2 | 2025-01-20 07:06 | 2025-01-22 20:32 | 2025-01-20 07:00 | No | Powerco | 47.7 | 61.43 | MTM0331, TGA0111, TGA0331
| GLN_220BS_A | 2025-01-20 07:17 | 2025-01-20 11:40 | 2025-01-20 07:00 | No | NZ Steel, Counties Power | 41.9 | 4.37 | GLN0331, GLN0332, GLN0333
| EDG_OWH_2 | 2025-01-20 07:35 | 2025-01-24 18:01 | 2025-01-20 07:30 | No | Unison Networks | 41 | 106.44 | OWH0111
| ROT_T4 | 2025-01-20 07:40 | 2025-01-24 13:14 | 2025-01-20 07:30 | No | Unison Network | 160.8 | 101.57 | ROT0111
| MPE_CB_252 | 2025-01-20 07:42 | 2025-01-20 16:21 | 2025-01-20 07:30 | No | Northpower, Top Energy | 41.8 | 8.64 | BRB0331, KOE1101, MTO0331
| BRB_MDN_1 | 2025-01-20 07:48 | 2025-01-20 16:15 | 2025-01-20 07:30 | No | Northpower, Top Energy | 41.8 | 8.45 | BRB0331, MPE1101, KOE1101, MTO0331
| ASY_T5 | 2025-01-20 09:18 | 2025-01-23 12:10 | 2025-01-20 09:00 | No | Mainpower New Zealand | 117.9 | 74.85 | ASY0111
| HAM_T7 | 2025-01-20 10:04 | 2025-01-24 17:12 | 2025-01-20 10:00 | No | KiwiRail | 122.9 | 103.14 | HAM0551, HAM0552
| HAM_T5 | 2025-01-20 10:13 | 2025-01-24 17:25 | 2025-01-20 10:00 | No | WEL Networks | 41.9 | 103.21 | HAM0331
| GLN_220BS_B | 2025-01-20 12:04 | 2025-01-20 15:12 | 2025-01-20 12:00 | No | NZ Steel, Counties Power | 42.1 | 3.13 | GLN0331, GLN0332, GLN0333
| BRY_T7 | 2025-01-21 06:37 | 2025-01-24 15:23 | 2025-01-21 06:30 | No | Orion New Zealand | 41.7 | 80.77 | BRY0661, BRY0662, BRY0663
| DRY_GLN_2 | 2025-01-21 07:23 | 2025-01-21 15:03 | 2025-01-21 07:00 | No | NZ Steel, Counties Power | 42 | 7.66 | GLN0331, GLN0332, GLN0333
| EDG_T7 | 2025-01-21 07:36 | 2025-01-24 16:24 | 2025-01-21 07:30 | No | Horizon Energy | 96 | 80.8 | EDG0331
| WHI_T2 | 2025-01-21 07:39 | 2025-01-23 11:27 | 2025-01-21 07:30 | No | Panpac | 123 | 51.8 | WHI0111, WHI0112
| KWA_WIL_1 | 2025-01-21 07:40 | 2025-01-24 13:11 | 2025-01-21 07:30 | No | Wellington Electricity | 38.7 | 77.52 | KWA0111
| TKR_107_137 | 2025-01-21 07:44 | 2025-01-21 14:23 | 2025-01-21 07:30 | No | Wellington Electricity | 32.7 | 6.66 | PNI0331, TKR0331
| BPE_TNG_1 | 2025-01-21 08:08 | 2025-01-24 15:31 | 2025-01-21 08:00 | No | Winstone Pulp, KiwiRail | 145.9 | 79.39 | TNG0111, TNG0551
| GLN_220BS_A | 2025-01-22 07:20 | 2025-01-24 16:17 | 2025-01-22 07:00 | No | NZ Steel, Counties Power | 42.7 | 56.94 | GLN0331, GLN0332, GLN0333
| MPE_CB_252 | 2025-01-22 07:33 | 2025-01-22 21:43 | 2025-01-22 07:30 | Yes | Northpower, Top Energy | No Notification | 14.16 | BRB0331, KOE1101, MTO0331
| BRB_MDN_1 | 2025-01-22 07:38 | 2025-01-24 14:35 | 2025-01-22 07:30 | No | Northpower, Top Energy | No Notification | 54.96 | BRB0331, MPE1101, KOE1101, MTO0331
| WGN_T1 | 2025-01-22 07:41 | 2025-01-24 15:12 | 2025-01-22 07:30 | No | Powerco | 39.7 | 55.5 | WGN0331
| MPE_CB_252 | 2025-01-23 06:01 | 2025-01-23 21:13 | 2025-01-23 06:00 | No | Northpower, Top Energy | No Notification | 15.19 | BRB0331, KOE1101, MTO0331
| MPE_CB_252 | 2025-01-24 06:04 | 2025-01-24 14:42 | 2025-01-24 06:00 | No | Northpower, Top Energy | No Notification | 8.65 | BRB0331, KOE1101, MTO0331
| ASB_BRY_1 | 2025-01-27 06:36 | 2025-01-29 08:33 | 2025-01-27 06:30 | No | Orion New Zealand | 41.8 | 49.94 | BRY0661, BRY0662, BRY0663
| BPE_MHO_1 | 2025-01-27 07:33 | 2025-02-01 14:03 | 2025-02-01 | No | Electra | 40.7 | 126.51 | MHO0331
| MHO_T3 | 2025-01-27 07:33 | 2025-02-01 14:06 | 2025-01-27 07:30 | No | Electra | 40.7 | 126.55 | MHO0331
| HWB_TMH_1 | 2025-01-27 07:48 | 2025-01-31 15:40 | 2025-01-27 07:30 | No | Aurora Energy, PowerNet | 41.8 | 103.87 | HWB0331, HWB0332
| HEN_MPE_1 | 2025-01-28 07:08 | 2025-01-30 17:11 | 2025-01-28 07:00 | No | Vector, Northpower | 94.8 | 58.06 | WEL0331, MTO0331
| GLN_220BS_A | 2025-01-28 07:20 | 2025-01-28 14:05 | 2025-01-28 07:00 | No | NZ Steel, Counties Power | 41.9 | 6.75 | GLN0331, GLN0332, GLN0333
| EDG_T7 | 2025-01-28 07:47 | 2025-02-01 19:16 | 2025-02-01 | No | Horizon Energy | No Notification | 107.48 | EDG0331
| GLN_220BS_B | 2025-01-29 07:14 | 2025-01-29 13:34 | 2025-01-29 07:00 | No | NZ Steel, Counties Power | 42 | 6.34 | GLN0331, GLN0332, GLN0333
| WRK_T30 | 2025-01-29 07:14 | 2025-01-30 16:24 | 2025-01-29 07:00 | No | Unison Network | 42.7 | 33.15 | WRK0331
| HWA_T2 | 2025-01-29 08:09 | 2025-01-29 19:03 | 2025-01-29 08:00 | No | Powerco, Beach Energy | 14.6 | 10.9 | HWA0331, HWA0332
| FKN_CB_2808 | 2025-01-30 08:24 | 2025-01-30 17:08 | 2025-01-30 08:00 | No | Aurora Energy, PowerNet | 50.7 | 8.74 | FKN0331, FKN0332
| HEN_MPE_2 | 2025-01-31 07:09 | 2025-02-03 17:45 | 2025-02-01 | No | Vector, Northpower | 97.8 | 82.59 | WEL0331, MTO0331
| ROT_TRK_2 | 2025-01-31 08:39 | 2025-02-01 18:25 | 2025-01-31 08:30 | No | Unison Network | 98 | 33.77 | ROT0111, ROT0331
| INV_T5 | 2025-01-31 09:10 | 2025-01-31 14:51 | 2025-01-31 09:00 | No | PowerNet | No Notification | 5.68 | INV0331
| ROT_T2 | 2025-02-01 08:54 | 2025-02-01 18:57 | 2025-02-01 08:30 | No | Unison Network | No Notification | 10.05 | ROT0331
| OWH_CB_112 | 2025-02-03 07:04 | 2025-02-05 14:26 | 2025-02-03 07:00 | No | Unison Networks, Powerco | 66.9 | 55.37 | OWH0111, TMI0331
| BRY_ISL_1 | 2025-02-03 07:07 | 2025-02-08 16:36 | 2025-02-03 07:00 | No | Orion New Zealand | 202.8 | 129.48 | BRY0661, BRY0662, BRY0663
| GLN_T4 | 2025-02-03 07:35 | 2025-02-10 05:15 | 2025-02-03 07:30 | No | NZ Steel | 444.9 | 165.66 | GLN0331, GLN0332
| MTM_T1 | 2025-02-03 07:43 | 2025-02-04 16:22 | 2025-02-03 12:00 | No | Powerco | 116.9 | 32.65 | MTM0331
| KMO_MTM_TGA_2 | 2025-02-03 07:49 | 2025-02-03 11:41 | 2025-02-03 07:30 | No | Powerco | 52.8 | 3.86 | MTM0331, TGA0111, TGA0331
| SDN_T1 | 2025-02-03 08:19 | 2025-02-07 17:53 | 2025-02-03 08:00 | No | Aurora Energy | 23.8 | 105.58 | SDN0331
| KPO_TMU_1 | 2025-02-04 06:37 | 2025-02-04 13:22 | 2025-02-04 06:30 | No | Waipa Networks | No Notification | 6.75 | TMU0111, TMU0112
| FKN_T4 | 2025-02-05 07:41 | 2025-02-14 15:13 | 2025-02-05 07:30 | No | Aurora Energy, PowerNet | 154.7 | 223.53 | FKN0331, FKN0332
| KOE_MPE_2 | 2025-02-07 07:27 | 2025-02-07 16:33 | 2025-02-07 07:00 | No | Top Energy | 79.6 | 9.1 | KOE1101
| SDN_TMH_1 | 2025-02-08 08:24 | 2025-02-08 17:52 | 2025-02-08 08:00 | No | Aurora Energy | No Notification | 9.45 | SDN0331
| IGH_ROB_2 | 2025-02-10 06:32 | 2025-02-14 15:38 | 2025-02-10 06:30 | No | Buller Electricity | 27.7 | 105.1 | ROB0111, ROB0331
| GYM_KUM_1 | 2025-02-10 06:32 | 2025-02-10 14:46 | 2025-02-10 06:30 | No | Westpower | No Notification | 8.22 | GYM0661
| KIK_STK_3 | 2025-02-10 06:34 | 2025-02-10 14:42 | 2025-02-10 06:30 | No | Network Tasman, Marlborough Lines | No Notification | 8.13 | STK0661, BLN0331
| HEN_MPE_1 | 2025-02-10 07:10 | 2025-02-15 15:47 | 2025-02-10 07:00 | No | Vector, Northpower | 59.7 | 128.62 | WEL0331, MTO0331
| KWA_WIL_2 | 2025-02-10 07:16 | 2025-02-14 15:01 | 2025-02-10 07:00 | No | Wellington Electricity | 31.8 | 103.76 | KWA0111
| DRY_BOB_HLY_1 | 2025-02-10 07:24 | 2025-02-11 16:05 | 2025-02-10 07:00 | No | NZ Steel, Counties Power | 146 | 32.69 | GLN0331, GLN0332, GLN0333
| HAM_WKM_1 | 2025-02-10 07:24 | 2025-02-10 16:43 | 2025-02-10 07:00 | No | WEL Networks, Waipa Networks, Powerco | 81.9 | 9.32 | HAM0111, CBG0111, TMU0111, TMU0112, WHU0331, WKO0331, KPU0661, PAO1101
| HWB_T5 | 2025-02-10 07:32 | 2025-02-14 12:20 | 2025-02-10 07:30 | No | Aurora Energy, PowerNet | 27.7 | 100.79 | HWB0331, HWB0332
| ROT_T3 | 2025-02-10 07:39 | 2025-02-14 13:37 | 2025-02-10 07:30 | No | Unison Network | 181.8 | 101.96 | ROT0111
| WDV_DVK_WPW_2 | 2025-02-10 07:48 | 2025-02-14 16:31 | 2025-02-10 07:30 | No | Scanpower, Centralines | 31.8 | 104.73 | DVK0111, WPW0331
| WPW_T1 | 2025-02-10 07:48 | 2025-02-14 16:33 | 2025-02-10 07:30 | No | Centralines | 31.8 | 104.76 | WPW0331
| BAL_GOR_1 | 2025-02-10 08:35 | 2025-02-14 15:39 | 2025-02-10 08:30 | No | PowerNet | 27.7 | 103.07 | BAL0331
| ASY_T5 | 2025-02-10 09:07 | 2025-02-20 14:09 | 2025-02-10 09:00 | No | Mainpower New Zealand | 80.9 | 245.03 | ASY0111
| KIK_STK_3 | 2025-02-11 06:36 | 2025-02-13 17:29 | 2025-02-11 06:30 | No | Network Tasman, Marlborough Lines | No Notification | 58.88 | STK0661, BLN0331
| OWH_TMI_TRK_1 | 2025-02-11 07:35 | 2025-02-14 15:33 | 2025-02-11 07:30 | No | Unison Networks, Powerco | 60 | 79.98 | OWH0111, TMI0331
| CML_T8 | 2025-02-11 07:43 | 2025-02-11 17:13 | 2025-02-11 07:30 | No | Aurora Energy, PowerNet | 129.9 | 9.5 | CML0331, FKN0331, FKN0332
| HAM_WKM_1 | 2025-02-12 07:55 | 2025-02-15 07:09 | 2025-02-12 07:30 | No | WEL Networks, Waipa Networks, Powerco | No Notification | 71.24 | HAM0111, CBG0111, TMU0111, TMU0112, WHU0331, WKO0331, KPU0661, PAO1101
| DRY_GLN_1 | 2025-02-13 07:15 | 2025-02-13 14:41 | 2025-02-13 07:00 | No | NZ Steel, Counties Power | 8 | 7.44 | GLN0331, GLN0332, GLN0333
| GYM_KUM_1 | 2025-02-14 06:38 | 2025-02-14 17:26 | 2025-02-14 06:30 | No | Westpower | No Notification | 10.79 | GYM0661
| GLN_220BS_A | 2025-02-14 07:21 | 2025-02-14 11:36 | 2025-02-14 07:00 | No | NZ Steel, Counties Power | 9 | 4.24 | GLN0331, GLN0332, GLN0333
| GLN_220BS_B | 2025-02-14 11:52 | 2025-02-14 14:03 | 2025-02-14 11:49 | No | NZ Steel, Counties Power | 9.2 | 2.19 | GLN0331, GLN0332, GLN0333
| GYM_KUM_1 | 2025-02-15 06:34 | 2025-02-16 13:38 | 2025-02-15 06:30 | No | Westpower | No Notification | 31.07 | GYM0661
| GLN_220BS_B | 2025-02-15 08:50 | 2025-02-15 11:06 | 2025-02-15 08:30 | No | NZ Steel, Counties Power | 10 | 2.265 | GLN0331, GLN0332, GLN0333
| DOB_RFN_IGH_2 | 2025-02-17 06:36 | 2025-03-07 13:56 | 2025-03-01 | No | Westpower | 83.8 | 439.34 | DOB0331, GYM0661, HKK0661, RFN1101, RFN1102
| RDF_T4 | 2025-02-17 07:04 | 2025-02-17 12:46 | 2025-02-17 07:00 | No | Unison Network, Eastlands Networks | 17.8 | 5.71 | RDF0331, WTU0331, FHL0331,TUI1101
| OWH_CB_112 | 2025-02-17 07:09 | 2025-02-23 07:40 | 2025-02-17 07:00 | No | Unison Networks, Powerco | 172.9 | 144.5 | OWH0111, TMI0331
| KAW_T14 | 2025-02-17 07:17 | 2025-02-20 20:26 | 2025-02-17 07:00 | No | Norse Skog | 124.8 | 85.14 | KAW0111
| WDV_DVK_WPW_1 | 2025-02-17 07:37 | 2025-02-20 18:26 | 2025-02-17 07:30 | No | Scanpower, Centralines | 37.8 | 82.81 | DVK0111, WPW0331
| WPW_T2 | 2025-02-17 07:37 | 2025-02-20 18:26 | 2025-02-17 07:30 | No | Centralines | 37.8 | 82.8 | WPW0331
| HWB_SDN_1 | 2025-02-17 07:39 | 2025-02-21 13:21 | 2025-02-17 07:30 | No | Aurora Energy | 33.6 | 101.7 | SDN0331
| MPE_CB_252 | 2025-02-17 07:53 | 2025-02-20 21:44 | 2025-02-18 06:00 | Yes | Northpower, Top Energy | 66.8 | 47.16 | BRB0331, KOE1101, MTO0331
| MPE_CB_252 | 2025-02-17 08:02 | 2025-02-17 21:36 | 2025-02-17 08:00 | No | Northpower, Top Energy | 65.9 | 13.56 | BRB0331, KOE1101, MTO0331
| BRB_HPI_1 | 2025-02-17 08:15 | 2025-02-21 17:43 | 2025-02-17 08:00 | No | Northpower, Top Energy | 65.9 | 105.47 | BRB0331, MPE1101, KOE1101
| BAL_GOR_1 | 2025-02-17 08:41 | 2025-02-21 15:13 | 2025-02-17 08:30 | No | PowerNet | 33.6 | 102.54 | BAL0331
| HUI_T5 | 2025-02-17 09:05 | 2025-02-17 14:19 | 2025-02-17 09:00 | No | Powerco | 89.8 | 5.235 | HUI0331
| CBG_KPO_1 | 2025-02-18 07:30 | 2025-02-21 15:56 | 2025-02-18 07:00 | No | Waipa Networks | 28.8 | 80.44 | CBG0111
| WHI_WRK_1 | 2025-02-18 07:33 | 2025-02-21 17:10 | 2025-02-18 07:30 | No | Unison Network, Eastlands Networks, Panpac | 10.8 | 81.62 | RDF0331, WTU0331, FHL0331,TUI1101, WHI0111, WHI0112
| TKR_107_137 | 2025-02-18 07:44 | 2025-02-18 15:48 | 2025-02-18 07:30 | No | Wellington Electricity | 60.7 | 8.07 | PNI0331, TKR0331
| WDV_T2 | 2025-02-18 07:50 | 2025-02-24 16:14 | 2025-02-18 07:30 | No | Scanpower | 258.9 | 152.39 | WDV0111
| HAM_T5 | 2025-02-18 09:42 | 2025-02-20 18:13 | 2025-02-18 09:30 | No | WEL Networks | 74.9 | 56.51 | HAM0331
| MPE_CB_252 | 2025-02-21 06:03 | 2025-02-21 17:43 | 2025-02-21 06:00 | No | Northpower, Top Energy | 69.8 | 11.66 | BRB0331, KOE1101, MTO0331
| GYM_KUM_1 | 2025-02-22 16:17 | 2025-02-22 19:37 | 2025-02-22 16:00 | No | Westpower | No Notification | 3.33 | GYM0661
| IGH_ROB_2 | 2025-02-24 06:41 | 2025-02-28 12:19 | 2025-02-24 06:30 | No | Buller Electricity | 39.7 | 101.63 | ROB0111, ROB0331
| HEN_MPE_2 | 2025-02-24 07:04 | 2025-03-01 17:03 | 2025-03-01 | No | Vector, Northpower | 40.7 | 129.98 | WEL0331, MTO0331
| KMO_MTM_TGA_2 | 2025-02-24 07:05 | 2025-02-28 16:24 | 2025-02-24 07:00 | No | Powerco | 40.7 | 105.32 | MTM0331, TGA0111, TGA0331
| TGA_T4 | 2025-02-24 07:05 | 2025-02-28 16:58 | 2025-02-24 07:00 | No | Powerco | 40.7 | 105.89 | TGA0331
| BRY_ISL_1 | 2025-02-24 07:07 | 2025-02-24 17:43 | 2025-02-24 07:00 | No | Orion New Zealand | 223.8 | 10.6 | BRY0661, BRY0662, BRY0663
| HWA_T1 | 2025-02-24 08:05 | 2025-03-13 17:47 | 2025-02-24 08:00 | No | Powerco, Beach Energy | 213.9 | 417.69 | HWA0331, HWA0332
| ASY_T3 | 2025-02-24 09:11 | 2025-03-06 14:52 | 2025-03-01 | No | Mainpower New Zealand | 94.9 | 245.68 | ASY0111
| BAL_GOR_1 | 2025-02-24 16:16 | 2025-02-24 23:33 | 2025-02-24 16:10 | No | PowerNet | No Notification | 7.28 | BAL0331
| BAL_GOR_1 | 2025-02-25 06:23 | 2025-02-25 20:39 | 2025-02-25 06:20 | No | PowerNet | No Notification | 14.26 | BAL0331
| HLY_T21 | 2025-02-25 07:02 | 2025-02-25 18:45 | 2025-02-25 07:00 | No | WEL Networks | No Notification | 11.71 | HLY0331, HLY0332
| TMI_T1 | 2025-02-25 07:34 | 2025-02-26 11:16 | 2025-02-25 07:30 | No | Powerco | 39.9 | 27.7 | TMI0331
| TMU_T2 | 2025-02-25 07:34 | 2025-02-25 16:08 | 2025-02-25 07:30 | No | Waipa Networks | 81.8 | 8.57 | TMU0111, TMU0112
| MGM_CB_172 | 2025-02-25 07:35 | 2025-02-25 16:57 | 2025-02-25 07:30 | No | Powerco | 19.7 | 9.38 | MGM0331
| BPE_WDV_1 | 2025-02-25 08:03 | 2025-02-25 16:54 | 2025-02-25 08:00 | No | Scanpower, Centralines | 41.6 | 8.85 | DVK0111, WPW0331, WDV0111
| KPU_WKO_1 | 2025-02-25 08:04 | 2025-02-26 16:37 | 2025-02-25 08:00 | No | Powerco | 39.9 | 32.55 | KPU0661
| HTI_TMU_1 | 2025-02-25 11:05 | 2025-02-26 13:35 | 2025-02-25 16:30 | No | Waipa Networks | No Notification | 26.505 | TMU0111, TMU0112
| DRY_BOB_HLY_1 | 2025-02-25 12:06 | 2025-02-25 18:41 | 2025-02-25 12:00 | No | NZ Steel, Counties Power | No Notification | 6.58 | GLN0331, GLN0332, GLN0333
| BAL_GOR_1 | 2025-02-27 07:04 | 2025-02-27 10:07 | 2025-02-27 07:00 | No | PowerNet | No Notification | 3.05 | BAL0331
| KPU_367_VT10 | 2025-02-27 07:33 | 2025-02-28 16:46 | 2025-02-27 07:30 | No | Powerco | 41.9 | 33.21 | KPU0661
| DOB_T1 | 2025-03-03 06:47 | 2025-03-07 14:21 | 2025-03-03 06:30 | No | Westpower | 97.8 | 103.57 | DOB0331
| BPE_PRM_HAY_2 | 2025-03-03 07:15 | 2025-03-07 15:06 | 2025-03-03 07:00 | No | Electra | 38.7 | 103.86 | PRM0331
| DRY_TAK_OTA_1 | 2025-03-03 07:15 | 2025-03-06 16:33 | 2025-03-03 07:00 | No | Vector | 42 | 81.31 | TAK0331
| HWB_SDN_1 | 2025-03-03 07:36 | 2025-03-05 10:02 | 2025-03-03 07:30 | No | Aurora Energy | 177.7 | 50.44 | SDN0331
| ALB_SVL_1 | 2025-03-03 07:40 | 2025-03-07 11:39 | 2025-03-03 07:30 | No | Vector | 41.9 | 99.98 | SVL0331
| KPU_WKO_2 | 2025-03-03 07:48 | 2025-03-23 18:43 | 2025-03-03 07:30 | No | Powerco | 185.8 | 490.91 | KPU0661
| TNG_T11 | 2025-03-03 07:56 | 2025-03-07 14:49 | 2025-03-03 07:30 | No | Winstone Pulp | No Notification | 102.89 | TNG0111
| KOE_MPE_2 | 2025-03-03 08:03 | 2025-03-07 14:45 | 2025-03-03 08:00 | No | Top Energy | 41.9 | 102.7 | KOE1101
| MHO_T3 | 2025-03-03 08:03 | 2025-03-07 15:49 | 2025-03-03 08:00 | No | Electra | 38.7 | 103.76 | MHO0331
| BWK_HWB_1 | 2025-03-03 08:36 | 2025-03-07 09:04 | 2025-03-03 08:30 | No | PowerNet | 41.7 | 96.47 | BAL0331
| HUI_T6 | 2025-03-06 08:03 | 2025-03-13 12:14 | 2025-03-06 08:00 | No | Powerco | No Notification | 172.17 | HUI0331
| EDN_T2 | 2025-03-06 11:34 | 2025-03-06 11:43 | 2025-03-06 11:30 | No | PowerNet | No Notification | 0.15 | EDN0331
| KPO_TMU_1 | 2025-03-07 08:04 | 2025-03-07 14:33 | 2025-03-07 08:00 | No | Waipa Networks | 1 | 6.49 | TMU0111, TMU0112
| CST_CB_2188 | 2025-03-07 12:21 | 2025-03-07 16:24 | 2025-03-07 12:00 | No | Powerco | No Notification | 4.04 | CST0331
| TNG_T12 | 2025-03-07 15:04 | 2025-03-08 15:25 | 2025-03-07 15:00 | No | Winstone Pulp | No Notification | 24.34 | TNG0111
| BPE_PRM_HAY_1 | 2025-03-07 20:02 | 2025-03-07 21:34 | 2025-03-07 20:00 | No | Electra | No Notification | 1.53 | PRM0331
| CST_CB_2188 | 2025-03-09 16:17 | 2025-03-09 20:17 | 2025-03-09 16:15 | No | Powerco | No Notification | 4 | CST0331
| COL_OTI_2 | 2025-03-10 06:32 | 2025-03-14 15:05 | 2025-03-10 06:30 | No | Westpower | 44.7 | 104.55 | GYM0661, HKK0661
| RDF_WHI_1 | 2025-03-10 06:44 | 2025-03-10 15:50 | 2025-03-10 06:30 | No | Unison Network, Eastlands Networks, Panpac | 110.7 | 9.09 | RDF0331, WTU0331, TUI1101, FHL0331, WHI0111, WHI0112
| OWH_CB_112 | 2025-03-10 07:02 | 2025-03-15 15:56 | 2025-03-10 07:00 | No | Unison Networks, Powerco | 25.7 | 128.9 | OWH0111, TMI0331
| HEN_MPE_1 | 2025-03-10 07:05 | 2025-03-15 16:38 | 2025-03-10 07:00 | No | Vector, Northpower | 40.9 | 129.56 | WEL0331, MTO0331
| BPE_PRM_HAY_2 | 2025-03-10 07:11 | 2025-03-14 13:38 | 2025-03-10 07:00 | No | Electra | 39.9 | 102.44 | PRM0331
| RDF_WTU_2 | 2025-03-10 07:26 | 2025-03-18 10:36 | 2025-03-10 07:00 | No | Unison Network | 164.6 | 195.17 | WTU0331
| BPE_MHO_2 | 2025-03-10 07:35 | 2025-03-14 15:43 | 2025-03-10 07:30 | No | Electra | 39.6 | 104.14 | MHO0331
| MGM_MST_1 | 2025-03-10 07:39 | 2025-03-14 16:23 | 2025-03-10 07:30 | No | Powerco | 39.6 | 104.73 | MGM0331
| PNI_TKR_2 | 2025-03-10 07:40 | 2025-03-10 16:15 | 2025-03-10 07:30 | No | Wellington Electricity | 282.9 | 8.59 | PNI0331
| MST_GYT_UHT_1 | 2025-03-10 07:42 | 2025-03-14 16:24 | 2025-03-10 07:30 | No | Powerco | 39.6 | 104.7 | GYT0331
| BAL_GOR_1 | 2025-03-10 08:33 | 2025-03-14 15:38 | 2025-03-10 08:30 | No | PowerNet | No Notification | 103.08 | BAL0331
| KMO_TMI_1 | 2025-03-11 07:04 | 2025-03-14 16:23 | 2025-03-11 07:00 | No | Powerco | 97.8 | 81.33 | TMI0331
| KMO_TRK_2 | 2025-03-11 07:06 | 2025-03-14 16:21 | 2025-03-11 07:00 | No | Powerco | 119.7 | 81.25 | MTM0331, TGA0111, TGA0331
| RDF_WHI_1 | 2025-03-11 07:30 | 2025-03-12 16:13 | 2025-03-11 07:30 | Yes | Unison Network, Eastlands Networks, Panpac | 54 | 18.19 | RDF0331, WTU0331, TUI1101, FHL0331, WHI0111, WHI0112
| OPK_SFD_1 | 2025-03-11 07:37 | 2025-03-28 19:11 | 2025-03-11 07:30 | No | Powerco | 27.9 | 419.56 | OPK0331
| EDG_T7 | 2025-03-11 07:43 | 2025-03-11 16:50 | 2025-03-11 07:30 | No | Horizon Energy | 97.8 | 9.13 | EDG0331
| CST_CB_2188 | 2025-03-11 10:07 | 2025-03-12 09:11 | 2025-03-11 10:00 | No | Powerco | No Notification | 23.07 | CST0331
| WHU_WKO_1 | 2025-03-12 07:40 | 2025-03-15 14:43 | 2025-03-12 07:30 | No | Powerco | 27.8 | 79.05 | WKO0331, KPU0661
| HEP_T1 | 2025-03-12 09:47 | 2025-03-12 16:21 | 2025-03-12 09:30 | No | Vector | 42.8 | 6.57 | HEP0331
| TMK_TIM_2_TMK_T2 | 2025-03-12 10:04 | 2025-03-12 13:45 | 2025-03-12 10:00 | No | Alpine Energy | 11.9 | 3.68 | TMK0331
| HUI_837_864_894 | 2025-03-12 19:50 | 2025-03-12 21:24 | 2025-03-12 19:30 | No | Powerco | No Notification | 1.57 | HUI0331
| PEN_220BS_C | 2025-03-14 07:12 | 2025-03-15 14:18 | 2025-03-14 07:00 | No | Vector, Southpark | 175.8 | 31.1 | PEN0221, PEN0331, PEN0332
| TRK_CB_142 | 2025-03-14 16:42 | 2025-03-18 17:32 | 2025-03-14 16:40 | No | Powerco | No Notification | 96.83 | TMI0331
| SFD_T10 | 2025-03-15 07:03 | 2025-03-23 07:21 | 2025-03-15 07:00 | No | Powerco, Beach Energy | 94.7 | 192.29 | SFD0331, OPK0331, HWA0331, HWA0332
| TNG_CB_1572 | 2025-03-16 02:35 | 2025-03-16 14:32 | 2025-03-16 02:34 | No | KiwiRail | No Notification | 11.95 | TNG0555
| WHU_WKO_2 | 2025-03-16 07:33 | 2025-03-17 15:42 | 2025-03-16 07:30 | No | Powerco | 31.8 | 32.16 | WKO0331, KPU0661
| KPO_TMU_1 | 2025-03-16 10:07 | 2025-03-16 13:37 | 2025-03-16 10:00 | No | Waipa Networks | No Notification | 3.5 | TMU0111, TMU0112
| DOB_GYM_1 | 2025-03-17 06:44 | 2025-03-17 17:52 | 2025-03-17 06:30 | No | Westpower | 33.9 | 11.14 | GYM0661
| ATU_RFN_IGH_1 | 2025-03-17 06:45 | 2025-04-04 15:22 | 2025-04-01 | No | Westpower | 40.8 | 440.62 | RFN1101, RFN1102
| HEN_MPE_2 | 2025-03-17 07:09 | 2025-03-22 13:40 | 2025-03-17 07:00 | No | Vector, Northpower | 40.8 | 126.52 | WEL0331, MTO0331
| BPE_TWC_LTN_1 | 2025-03-17 07:34 | 2025-03-21 09:40 | 2025-03-17 07:30 | No | Powerco | 102.8 | 98.11 | LTN0331
| BRY_T5 | 2025-03-17 07:35 | 2025-03-25 16:19 | 2025-03-17 07:30 | No | Orion New Zealand | 62.9 | 200.73 | BRY0661, BRY0662, BRY0663
| HAM_T4 | 2025-03-17 07:42 | 2025-03-18 14:58 | 2025-03-17 07:30 | No | WEL Networks | 11.8 | 31.27 | HAM0331
| MST_T3 | 2025-03-17 10:32 | 2025-03-23 17:27 | 2025-03-17 10:30 | No | Powerco | 34.1 | 150.92 | MST0331
| MST_GYT_UHT_2 | 2025-03-17 10:44 | 2025-03-19 15:12 | 2025-03-17 10:30 | No | Powerco | 34.1 | 52.47 | GYT0331
| TNG_T2 | 2025-03-18 07:33 | 2025-03-20 18:33 | 2025-03-18 07:30 | No | KiwiRail | 26.7 | 59.01 | TNG0555
| HTI_T2 | 2025-03-18 09:06 | 2025-03-18 13:21 | 2025-03-18 09:00 | No | The Lines Company | 18.7 | 4.25 | HTI0331
| OWH_CB_112 | 2025-03-19 07:34 | 2025-03-21 12:46 | 2025-03-19 07:30 | No | Unison Networks, Powerco | 18.7 | 53.2 | OWH0111, TMI0331
| TAK_T5 | 2025-03-19 07:40 | 2025-03-19 12:13 | 2025-03-19 07:30 | No | Vector | 300 | 4.54 | TAK0331
| TRK_T3 | 2025-03-19 07:41 | 2025-03-21 12:44 | 2025-03-19 07:30 | No | Unison Network, Vector | 216.7 | 53.04 | ROT0111, LFD1101
| KMO_TRK_1 | 2025-03-19 07:42 | 2025-03-21 12:40 | 2025-03-19 07:30 | No | Powerco | 216.7 | 52.96 | MTM0331, TGA0111, TGA0331
| HAM_T5 | 2025-03-19 07:45 | 2025-03-20 14:35 | 2025-03-19 07:30 | No | WEL Networks | 27 | 30.84 | HAM0331
| CYD_T8 | 2025-03-19 10:15 | 2025-03-19 13:45 | 2025-03-19 10:00 | No | Aurora Energy | 43.8 | 3.51 | CYD0331
| TAK_T8 | 2025-03-20 07:33 | 2025-03-20 12:45 | 2025-03-20 07:30 | No | Vector | 300 | 5.2 | TAK0331
| RDF_WTU_2 | 2025-03-20 13:57 | 2025-03-20 20:04 | 2025-03-20 13:56 | No | Unison Network | No Notification | 6.12 | WTU0331
| WRK_T29 | 2025-03-22 09:35 | 2025-03-22 11:55 | 2025-03-22 09:30 | No | Unison Network | 122 | 2.33 | WRK0331
| BPE_PRM_HAY_1 | 2025-03-23 18:11 | 2025-03-23 18:15 | 2025-03-23 18:00 | No | Electra | 11 | 0.08 | PRM0331
| CUL_T23 | 2025-03-24 07:01 | 2025-03-28 18:48 | 2025-03-24 07:00 | No | Mainpower New Zealand | 37.8 | 107.79 | CUL0331
| DRY_GLN_1 | 2025-03-24 07:05 | 2025-03-28 14:32 | 2025-03-24 07:00 | No | NZ Steel, Counties Power | 41.7 | 103.44 | GLN0331, GLN0332, GLN0333
| RDF_WTU_1 | 2025-03-24 07:18 | 2025-04-01 11:33 | 2025-03-24 07:00 | No | Unison Network | 178.6 | 196.25 | WTU0331
| TNG_T3 | 2025-03-24 07:47 | 2025-03-25 17:14 | 2025-03-24 07:30 | No | KiwiRail | 26.8 | 33.44 | TNG0555
| LTN_T2 | 2025-03-24 07:53 | 2025-03-24 16:12 | 2025-03-24 07:30 | No | Powerco | 23.8 | 8.31 | LTN0331
| MPE_CB_252 | 2025-03-24 08:05 | 2025-03-24 21:32 | 2025-03-24 08:00 | No | Northpower, Top Energy | 41.8 | 13.45 | BRB0331, KOE1101, MTO0331
| SDN_TMH_1 | 2025-03-24 08:08 | 2025-03-28 17:39 | 2025-03-24 08:00 | No | Aurora Energy | 251.8 | 105.51 | SDN0331
| EDN_INV_1 | 2025-03-24 08:36 | 2025-03-28 16:50 | 2025-03-24 08:30 | No | Daiken , PowerNet | 41.7 | 104.23 | BDE0111, BDE0112, EDN0331
| WHI_T2 | 2025-03-24 10:17 | 2025-05-04 14:17 | 2025-05-01 | No | Panpac | 252 | 988.0053 | WHI0111, WHI0112
| MPE_CB_252 | 2025-03-25 05:53 | 2025-03-27 21:40 | 2025-03-25 06:00 | Yes | Northpower, Top Energy | 42.7 | 38 | BRB0331, KOE1101, MTO0331
| CML_FKN_1 | 2025-03-25 07:44 | 2025-03-27 17:08 | 2025-03-25 07:30 | No | Aurora Energy, PowerNet | 104.9 | 57.4 | FKN0331, FKN0332
| KWA_WIL_1 | 2025-03-25 08:21 | 2025-03-27 12:19 | 2025-03-25 08:00 | No | Wellington Electricity | 36 | 51.96 | KWA0111
| TWZ_T18 | 2025-03-26 07:35 | 2025-03-28 16:45 | 2025-03-26 07:30 | No | Alpine Energy, Meridian Energy, Network Waitaki | 28.8 | 57.16 | TWZ0331, TWZ0332, TWZ0333
| CYD_FDR_2052 | 2025-03-26 08:00 | 2025-03-26 16:02 | 2025-03-26 08:00 | No | Aurora Energy | No Notification | 8.03 | CYD0331
| MPE_CB_252 | 2025-03-28 06:06 | 2025-03-28 17:42 | 2025-03-28 06:00 | No | Northpower, Top Energy | 45.7 | 11.6 | BRB0331, KOE1101, MTO0331
| HAY_WIL_LTN_1 | 2025-03-31 06:36 | 2025-04-04 12:39 | 2025-03-31 06:30 | No | Powerco | 165.6 | 102.06 | LTN0331
| DRY_GLN_2 | 2025-03-31 07:03 | 2025-04-04 13:21 | 2025-03-31 07:00 | No | NZ Steel, Counties Power | 44.9 | 102.3 | GLN0331, GLN0332, GLN0333
| SFD_TMN_1 | 2025-03-31 07:10 | 2025-04-04 17:03 | 2025-03-31 07:00 | No | KiwiRail, WEL Networks | 255.6 | 105.88 | TMN0551, TWH0331
| KPI_OPK_2 | 2025-03-31 07:16 | 2025-04-17 17:27 | 2025-03-31 07:00 | No | Powerco | 33.7 | 418.1814 | OPK0331
| HAM_T2 | 2025-03-31 07:21 | 2025-04-04 12:20 | 2025-03-31 07:00 | No | WEL Networks | 41.9 | 100.98 | HAM0111
| DRY_TAK_OTA_2 | 2025-03-31 07:40 | 2025-04-05 16:03 | 2025-03-31 07:30 | No | Vector | 101.9 | 128.39 | TAK0331
| CYD_T7 | 2025-03-31 07:43 | 2025-04-02 14:44 | 2025-04-01 | No | Aurora Energy | 34.7 | 55.02 | CYD0331
| HTI_TMU_1 | 2025-03-31 08:12 | 2025-04-02 15:46 | 2025-03-31 08:00 | No | Waipa Networks | 115.7 | 55.56 | TMU0111, TMU0112
| SDN_TMH_1 | 2025-03-31 08:23 | 2025-04-03 12:08 | 2025-04-01 | No | Aurora Energy | 258.8 | 75.75 | SDN0331
| WRD_T7 | 2025-03-31 08:37 | 2025-03-31 15:38 | 2025-03-31 08:30 | No | Vector | 23.8 | 7 | WRD0331
| BDE_GOR_1 | 2025-03-31 08:42 | 2025-03-31 15:48 | 2025-03-31 08:30 | No | Daiken , PowerNet | 35 | 7.1 | BDE0111, BDE0112, EDN0331
| HLY_T21 | 2025-04-01 07:08 | 2025-04-01 15:39 | 2025-04-01 07:00 | No | WEL Networks | 7 | 8.52 | HLY0331, HLY0332
| OWH_TMI_TRK_1 | 2025-04-01 08:05 | 2025-04-04 09:49 | 2025-04-01 08:00 | No | Unison Networks, Powerco | 131 | 73.74 | OWH0111, TMI0331
| ASY_WPR_1 | 2025-04-01 08:25 | 2025-04-05 11:20 | 2025-04-01 08:00 | No | Mainpower New Zealand | 39.8 | 98.91 | ASY0111
| BDE_EDN_1 | 2025-04-01 08:42 | 2025-04-03 17:35 | 2025-04-01 08:30 | No | Daiken , PowerNet | 36 | 56.88 | BDE0111, BDE0112, EDN0331
| TMK_TIM_1_TMK_T1 | 2025-04-02 07:46 | 2025-04-06 17:21 | 2025-04-02 07:30 | No | Alpine Energy | 35.8 | 105.5756 | TMK0331
| ASB_TIM_TWZ_1 | 2025-04-02 07:51 | 2025-04-06 17:11 | 2025-04-02 07:30 | No | Alpine Energy | 63.7 | 105.3189 | TIM0111
| ASB_347_296 | 2025-04-02 07:57 | 2025-04-06 17:10 | 2025-04-02 07:30 | No | Electricity Ashburton | 7.9 | 105.2233 | ASB0331
| HWA_SFD_1 | 2025-04-02 08:40 | 2025-04-02 19:29 | 2025-04-02 08:30 | No | Powerco, Beach Energy | 190.9 | 10.81 | HWA0331, HWA0332
| SFD_T6 | 2025-04-02 08:40 | 2025-04-02 19:29 | 2025-04-02 08:30 | No | Powerco | 33.9 | 10.81 | SFD0331
| RPO_TNG_1 | 2025-04-02 14:38 | 2025-04-02 15:37 | 2025-04-02 14:30 | No | Winstone Pulp, KiwiRail | 120 | 0.99 | TNG0111, TNG0551
| HWA_SFD_1 | 2025-04-02 19:31 | 2025-04-03 18:40 | 2025-04-02 19:30 | No | Powerco, Beach Energy | 15.3 | 23.16 | HWA0331, HWA0332
| HTI_87_97_127 | 2025-04-03 07:39 | 2025-04-04 12:57 | 2025-04-03 07:30 | No | The Lines Company, Waipa Networks | 118.7 | 29.3 | HTI0331, TMU0111, TMU0112
| RDF_T4 | 2025-04-03 08:26 | 2025-04-03 16:14 | 2025-04-03 08:00 | No | Unison Network, Eastlands Networks | 13.8 | 7.8 | RDF0331, WTU0331, FHL0331,TUI1101
| DOB_GYM_1 | 2025-04-04 06:46 | 2025-04-04 15:22 | 2025-04-04 06:30 | No | Westpower | 51.9 | 8.61 | GYM0661
| DOB_T2 | 2025-04-04 06:46 | 2025-04-04 15:22 | 2025-04-04 06:30 | No | Westpower | 51.9 | 8.61 | DOB0331
| MGM_CB_172 | 2025-04-04 07:07 | 2025-04-06 18:56 | 2025-04-04 07:00 | No | Powerco | 14.6 | 59.8128 | MGM0331
| HAY_CB_2892 | 2025-04-04 07:09 | 2025-04-06 18:24 | 2025-04-04 07:00 | No | Wellington Electricity | No Notification | 59.2564 | HAY0111
| HAY_UHT_2 | 2025-04-04 07:11 | 2025-04-06 18:26 | 2025-04-04 07:00 | No | Wellington Electricity, Powerco | 30.9 | 59.2481 | UHT0331, MST0331, GYT0331
| HAY_MLG_2 | 2025-04-04 07:16 | 2025-04-06 18:26 | 2025-04-04 07:00 | No | Wellington Electricity | 30.9 | 59.1669 | MLG0111, MLG0331
| ISL_T2 | 2025-04-07 06:40 | 2025-04-07 17:40 | 2025-04-07 06:30 | No | Orion New Zealand | 69.8 | 11 | ISL0331
| HUI_T6 | 2025-04-07 07:09 | 2025-04-11 12:42 | 2025-04-07 07:00 | No | Powerco | 38.7 | 101.55 | HUI0331
| HAM_OHW_1 | 2025-04-07 07:12 | 2025-04-09 21:05 | 2025-04-07 07:00 | No | WEL Networks, Waipa Networks, Powerco | 42 | 61.87 | HAM0111, CBG0111, TMU0111, TMU0112, WHU0331, WKO0331, KPU0661, PAO1101
| TKR_WIL_2 | 2025-04-07 07:14 | 2025-04-09 07:19 | 2025-04-07 07:00 | No | Wellington Electricity | 310.9 | 48.08 | TKR0331
| BPE_MTN_WGN_1 | 2025-04-07 07:19 | 2025-04-12 16:36 | 2025-04-07 07:00 | No | Powerco | 178.9 | 129.29 | MTN0331
| WGN_T2 | 2025-04-07 07:19 | 2025-04-12 16:39 | 2025-04-07 07:00 | No | Powerco | 55.6 | 129.33 | WGN0331
| HEN_T2 | 2025-04-07 07:36 | 2025-04-11 13:32 | 2025-04-07 07:30 | No | Vector | 42 | 101.94 | HEN0338
| TMU_T1 | 2025-04-07 07:47 | 2025-04-11 13:40 | 2025-04-07 07:30 | No | Waipa Networks | 42 | 101.88 | TMU0111, TMU0112
| HLY_T21 | 2025-04-07 07:52 | 2025-04-08 07:29 | 2025-04-07 07:30 | No | WEL Networks | 18.8 | 23.61 | HLY0331, HLY0332
| BAL_BWK_1 | 2025-04-07 08:36 | 2025-04-11 15:08 | 2025-04-07 08:30 | No | PowerNet | 58.8 | 102.53 | BAL0331
| HKK_OTI_2 | 2025-04-07 23:14 | 2025-04-08 00:11 | 2025-04-07 23:12 | No | Westpower | No Notification | 0.95 | HKK0661
| PRM_T2 | 2025-04-08 06:42 | 2025-04-15 13:07 | 2025-04-08 06:30 | No | Electra | No Notification | 174.4 | PRM0331
| PNI_TKR_1 | 2025-04-08 07:20 | 2025-04-11 17:10 | 2025-04-08 07:00 | No | Wellington Electricity | 314.6 | 81.83 | PNI0331
| HLY_T21 | 2025-04-08 07:31 | 2025-04-09 14:17 | 2025-04-08 07:30 | No | WEL Networks | 39.8 | 30.77 | HLY0331, HLY0332
| BRB_MDN_1 | 2025-04-08 07:37 | 2025-04-09 13:28 | 2025-04-08 07:30 | No | Northpower, Top Energy | 43 | 29.84 | BRB0331, MPE1101, KOE1101, MTO0331
| EDG_OWH_2 | 2025-04-08 08:02 | 2025-04-11 09:40 | 2025-04-08 08:00 | No | Unison Networks | 45.7 | 73.63 | OWH0111
| STK_FDR_92 | 2025-04-08 08:12 | 2025-04-09 14:31 | 2025-04-08 08:00 | No | Network Tasman | 11.9 | 30.32 | STK0661
| STU_77_66_T6 | 2025-04-09 04:38 | 2025-04-09 14:44 | 2025-04-09 04:38 | No | Alpine Energy | No Notification | 10.1 | STU0111
| RDF_WTU_2 | 2025-04-09 15:49 | 2025-04-09 18:14 | 2025-04-09 15:30 | No | Unison Network | 5 | 2.41 | WTU0331
| HLY_T22 | 2025-04-10 07:02 | 2025-04-11 15:09 | 2025-04-10 07:00 | No | WEL Networks | 41.8 | 32.11 | HLY0331, HLY0332
| HAM_KPO_2 | 2025-04-10 07:34 | 2025-04-11 16:13 | 2025-04-10 07:30 | No | Waipa Networks | 41.9 | 32.65 | CBG0111
| HAY_TKR_1 | 2025-04-11 07:16 | 2025-04-11 17:09 | 2025-04-11 07:00 | No | Wellington Electricity | 16.8 | 9.89 | TKR0331
| HAY_MLG_2 | 2025-04-11 08:14 | 2025-04-11 11:46 | 2025-04-11 08:00 | No | Wellington Electricity | 281.9 | 3.53 | MLG0111, MLG0331
| EDN_INV_1 | 2025-04-11 08:41 | 2025-04-11 14:41 | 2025-04-11 08:30 | No | Daiken , PowerNet | No Notification | 6 | BDE0111, BDE0112, EDN0331
| SBK_47_204 | 2025-04-14 06:54 | 2025-04-17 14:19 | 2025-04-14 06:30 | No | Mainpower New Zealand | 59.7 | 79.41 | SBK0331, SBK0661
| DRY_GLN_1 | 2025-04-14 07:03 | 2025-04-16 10:12 | 2025-04-14 07:00 | No | NZ Steel, Counties Power | 41.8 | 51.16 | GLN0331, GLN0332, GLN0333
| HLY_T21 | 2025-04-14 07:12 | 2025-04-17 09:48 | 2025-04-14 07:00 | No | WEL Networks | 13.7 | 74.61 | HLY0331, HLY0332
| BPE_MTN_WGN_2 | 2025-04-14 07:13 | 2025-04-16 13:06 | 2025-04-14 07:00 | No | Powerco | 205.9 | 53.88 | MTN0331
| PNI_TKR_2 | 2025-04-14 07:13 | 2025-04-16 16:03 | 2025-04-14 07:00 | No | Wellington Electricity | 40.6 | 56.84 | PNI0331
| TWH_T1 | 2025-04-14 07:24 | 2025-04-15 14:14 | 2025-04-14 07:00 | No | WEL Networks | 45.8 | 30.84 | TWH0331
| LIV_WTK_1 | 2025-04-14 07:40 | 2025-04-17 12:56 | 2025-04-14 07:30 | No | Network Waitaki | 296.7 | 77.27 | OAM0331
| MDN_MPE_1 | 2025-04-14 07:52 | 2025-04-16 08:39 | 2025-04-14 07:30 | No | Northpower, Top Energy | 75 | 48.79 | MPE1101, KOE1101
| SDN_T2 | 2025-04-14 08:17 | 2025-04-17 19:43 | 2025-04-14 08:00 | No | Aurora Energy | 40.7 | 83.43 | SDN0331
| KAI_SBK_2 | 2025-04-14 09:17 | 2025-04-14 15:05 | 2025-04-14 09:00 | No | Mainpower New Zealand | 59.8 | 5.8 | KAI0111
| ASY_SBK_1 | 2025-04-14 09:22 | 2025-04-14 15:05 | 2025-04-14 09:00 | No | Mainpower New Zealand | 59.8 | 5.72 | ASY0111
| HKK_KUM_1 | 2025-04-14 10:15 | 2025-04-14 16:24 | 2025-04-14 10:00 | No | Westpower | 40.7 | 6.14 | HKK0661
| HKK_OTI_2 | 2025-04-15 07:11 | 2025-04-15 16:37 | 2025-04-15 07:00 | No | Westpower | 41.6 | 9.43 | HKK0661
| LIV_NSY_1 | 2025-04-15 07:51 | 2025-04-16 18:21 | 2025-04-15 07:30 | No | PowerNet | 39.7 | 34.5 | NSY0331
| ASY_SBK_1 | 2025-04-15 09:15 | 2025-04-15 15:07 | 2025-04-15 09:00 | No | Mainpower New Zealand | 32.9 | 5.87 | ASY0111
| KAI_SBK_2 | 2025-04-15 09:15 | 2025-04-15 15:07 | 2025-04-15 09:00 | No | Mainpower New Zealand | 32.9 | 5.87 | KAI0111
| PEN_220BS_A | 2025-04-16 06:14 | 2025-04-17 15:41 | 2025-04-16 06:00 | No | Vector, Southpark | 272.9 | 33.45 | PEN0221, PEN0331, PEN0332
| HKK_KUM_1 | 2025-04-16 07:19 | 2025-04-16 16:16 | 2025-04-16 07:00 | No | Westpower | 42.6 | 8.95 | HKK0661
| TRK_407_437_567 | 2025-04-16 07:48 | 2025-04-17 09:41 | 2025-04-16 07:30 | No | Vector, Unison Network | 155.7 | 25.87 | LFD1101, ROT0111
| TWH_T2 | 2025-04-16 07:50 | 2025-04-17 11:17 | 2025-04-16 07:30 | No | WEL Networks | 47.8 | 27.45 | TWH0331
| HAY_WIL_LTN_2 | 2025-04-17 07:03 | 2025-04-17 13:52 | 2025-04-17 07:00 | No | Wellington Electricity | 182.6 | 6.81 | WIL0331
| HLY_TWH_1 | 2025-04-17 11:19 | 2025-04-17 14:15 | 2025-04-17 11:18 | No | KiwiRail, WEL Networks | No Notification | 2.94 | TMN0551, TWH0331
| HWA_WVY_1 | 2025-04-17 11:24 | 2025-04-17 14:23 | 2025-04-17 11:23 | No | Powerco, Beach Energy | No Notification | 2.99 | HWA0331, HWA0332
| HLY_T21 | 2025-04-17 12:06 | 2025-04-17 19:59 | 2025-04-17 12:00 | No | WEL Networks | No Notification | 7.88 | HLY0331, HLY0332
| MPE_CB_252 | 2025-04-18 22:16 | 2025-04-19 03:18 | 2025-04-18 22:08 | No | Northpower, Top Energy | No Notification | 5.03 | BRB0331, KOE1101, MTO0331
| KMO_TMI_1 | 2025-04-22 07:32 | 2025-04-25 10:50 | 2025-04-22 07:30 | No | Powerco | 45.8 | 75.31 | TMI0331
| TRK_567_607_627 | 2025-04-22 07:52 | 2025-04-25 10:38 | 2025-04-22 07:30 | No | Powerco | 161.7 | 74.76 | MTM0331, TGA0111
| OPK_SFD_1 | 2025-04-22 08:44 | 2025-04-22 14:04 | 2025-04-22 08:30 | No | Powerco | 7.7 | 5.34 | OPK0331
| OAM_STU_BPD_WTK_2 | 2025-04-26 09:05 | 2025-04-26 10:16 | 2025-04-26 09:05 | No | Network Waitaki, Alpine Energy | No Notification | 1.19 | OAM0331, STU0111
| HAY_WIL_LTN_1 | 2025-04-28 06:34 | 2025-05-06 15:44 | 2025-05-01 | No | Powerco | 193.6 | 201.16 | LTN0331
| UHT_T1 | 2025-04-28 07:05 | 2025-04-28 07:45 | 2025-04-28 07:00 | No | Wellington Electricity | 20.6 | 0.68 | UHT0331
| HWA_T2 | 2025-04-28 07:06 | 2025-05-08 19:13 | 2025-05-01 | No | Powerco, Beach Energy | 276.8 | 252.12 | HWA0331, HWA0332
| HEN_T2 | 2025-04-28 07:07 | 2025-05-03 11:22 | 2025-04-28 07:00 | No | Vector | 495.8 | 124.27 | HEN0338
| HEN_414_447_487 | 2025-04-28 07:17 | 2025-05-03 11:11 | 2025-05-01 | No | Vector | 495.8 | 123.9 | HEN0334
| WGN_T2 | 2025-04-28 07:21 | 2025-05-02 14:50 | 2025-05-01 | No | Powerco | 76.6 | 103.48 | WGN0331
| WGN_77_94 | 2025-04-28 07:28 | 2025-05-02 14:42 | 2025-05-01 | No | Powerco | 76.6 | 103.24 | MTN0331, WGN0331
| HEN_MPE_1 | 2025-04-28 07:42 | 2025-05-03 12:36 | 2025-05-01 | No | Vector, Northpower | 88 | 124.91 | WEL0331, MTO0331
| GFD_HAY_2 | 2025-04-28 07:44 | 2025-04-30 13:37 | 2025-04-28 07:30 | No | Wellington Electricity | 18.9 | 53.88 | GFD0331
| TMN_TWH_1 | 2025-04-28 07:46 | 2025-05-02 17:16 | 2025-05-01 | No | KiwiRail, WEL Networks | 72.8 | 105.49 | TMN0551, TWH0331
| TMN_T8 | 2025-04-28 07:47 | 2025-05-02 17:08 | 2025-04-28 07:30 | No | KiwiRail | 26.9 | 105.35 | TMN0551
| TWH_T1 | 2025-04-28 07:50 | 2025-05-02 17:14 | 2025-05-01 | No | WEL Networks | 41.9 | 105.4 | TWH0331
| DRY_GLN_2 | 2025-04-28 07:56 | 2025-05-02 16:05 | 2025-05-01 | No | NZ Steel, Counties Power | 285 | 104.14 | GLN0331, GLN0332, GLN0333
| UHT_T2 | 2025-04-28 08:52 | 2025-04-29 16:04 | 2025-04-28 08:30 | No | Wellington Electricity | 46.8 | 31.19 | UHT0331
| TWZ_T18 | 2025-04-29 07:32 | 2025-05-01 17:04 | 2025-05-01 | No | Alpine Energy, Meridian Energy, Network Waitaki | 287.8 | 57.53 | TWZ0331, TWZ0332, TWZ0333
| CST_T2 | 2025-04-29 07:35 | 2025-04-30 16:05 | 2025-04-29 07:30 | No | Powerco | 27.9 | 32.5 | CST0331
| ROT_T5 | 2025-04-30 07:24 | 2025-04-30 09:28 | 2025-04-30 07:00 | No | Unison Network | 13.6 | 2.06 | ROT0331
| UHT_T1 | 2025-04-30 07:38 | 2025-05-01 12:03 | 2025-04-30 07:30 | No | Wellington Electricity | 48.8 | 28.42 | UHT0331
| STU_DIS_76 | 2025-04-30 21:14 | 2025-05-07 11:55 | 2025-05-01 | No | Alpine Energy | No Notification | 158.69 | STU0111
| CST_T4 | 2025-05-01 07:33 | 2025-05-02 14:25 | 2025-05-01 07:30 | No | Powerco | 8 | 30.88 | CST0331
| ROT_TRK_2 | 2025-05-01 09:04 | 2025-05-01 17:47 | 2025-05-01 09:00 | No | Unison Network | No Notification | 8.72 | ROT0111, ROT0331
| GFD_HAY_2 | 2025-05-01 19:34 | 2025-05-01 21:11 | 2025-05-01 19:33 | No | Wellington Electricity | No Notification | 1.62 | GFD0331
| OWH_TMI_TRK_1 | 2025-05-03 07:07 | 2025-05-03 17:12 | 2025-05-03 07:00 | No | Unison Networks, Powerco | 15.6 | 10.08 | OWH0111, TMI0331
| GLN_220BS_A | 2025-05-05 07:02 | 2025-05-05 11:37 | 2025-05-05 07:00 | No | NZ Steel, Counties Power | 42 | 4.6 | GLN0331, GLN0332, GLN0333
| HOR_KBY_ISL_2 | 2025-05-05 07:08 | 2025-05-10 16:24 | 2025-05-05 07:00 | No | Orion New Zealand | 12.9 | 129.27 | KBY0661, KBY0662
| HEN_MPE_2 | 2025-05-05 07:16 | 2025-05-08 10:34 | 2025-05-05 07:00 | No | Vector, Northpower | 41.7 | 75.31 | WEL0331, MTO0331
| WGN_77_94 | 2025-05-05 07:25 | 2025-05-08 13:42 | 2025-05-05 07:00 | No | Powerco | 56 | 78.28 | MTN0331, WGN0331
| RDF_WTU_1 | 2025-05-05 07:28 | 2025-05-09 14:16 | 2025-05-05 07:00 | No | Unison Network | 54.8 | 102.79 | WTU0331
| KOE_MPE_1 | 2025-05-05 07:36 | 2025-05-09 17:24 | 2025-05-05 07:30 | No | Top Energy | 41.8 | 105.79 | KOE1101
| GOR_CB_2158 | 2025-05-05 07:40 | 2025-05-05 15:10 | 2025-05-05 07:30 | No | PowerNet | 39.7 | 7.51 | GOR0331
| MTN_1084_1094_1107 | 2025-05-05 07:41 | 2025-05-05 17:16 | 2025-05-05 07:30 | No | Powerco | 26.7 | 9.58 | MTN0331
| EDG_OWH_2 | 2025-05-05 07:42 | 2025-05-14 13:43 | 2025-05-05 07:30 | No | Unison Networks | 102.8 | 222.03 | OWH0111
| CML_FKN_1 | 2025-05-05 07:49 | 2025-05-13 16:52 | 2025-05-05 07:30 | No | Aurora Energy, PowerNet | 39.8 | 201.04 | FKN0331, FKN0332
| ROT_T5 | 2025-05-05 07:51 | 2025-05-26 17:44 | 2025-05-05 07:30 | No | Unison Network | 39.8 | 513.87 | ROT0331
| TWH_T2 | 2025-05-05 08:05 | 2025-05-08 16:42 | 2025-05-05 08:00 | No | WEL Networks | 150.9 | 80.61 | TWH0331
| HLY_TWH_1 | 2025-05-05 08:07 | 2025-05-06 18:10 | 2025-05-05 08:00 | No | KiwiRail, WEL Networks | 150.9 | 34.05 | TMN0551, TWH0331
| GLN_220BS_B | 2025-05-05 12:04 | 2025-05-05 15:46 | 2025-05-05 12:00 | No | NZ Steel, Counties Power | 42.2 | 3.7 | GLN0331, GLN0332, GLN0333
| DRY_GLN_2 | 2025-05-06 07:13 | 2025-05-06 15:33 | 2025-05-06 07:00 | No | NZ Steel, Counties Power | 42 | 8.34 | GLN0331, GLN0332, GLN0333
| GOR_T3 | 2025-05-06 07:44 | 2025-05-07 14:16 | 2025-05-06 07:30 | No | PowerNet | 40.7 | 30.53 | GOR0331
| GFD_T6 | 2025-05-06 08:19 | 2025-05-08 13:14 | 2025-05-06 08:00 | No | Wellington Electricity | 19.7 | 52.92 | GFD0331
| DOB_RFN_IGH_2 | 2025-05-06 09:20 | 2025-05-09 11:56 | 2025-05-06 09:00 | No | Westpower | 41 | 74.59 | DOB0331, GYM0661, HKK0661, RFN1101, RFN1102
| GLN_220BS_A | 2025-05-07 07:12 | 2025-05-07 11:34 | 2025-05-07 07:00 | No | NZ Steel, Counties Power | 41.8 | 4.37 | GLN0331, GLN0332, GLN0333
| BPE_TNG_1 | 2025-05-07 08:14 | 2025-05-09 12:40 | 2025-05-07 08:00 | No | Winstone Pulp, KiwiRail | 96.8 | 52.43 | TNG0111, TNG0551
| TIM_T8 | 2025-05-07 09:48 | 2025-05-11 14:44 | 2025-05-07 09:30 | No | Alpine Energy | 34.7 | 100.94 | TIM0111, TMK0331
| GLN_220BS_B | 2025-05-07 12:04 | 2025-05-07 15:04 | 2025-05-07 12:00 | No | NZ Steel, Counties Power | 42.1 | 3 | GLN0331, GLN0332, GLN0333
| DRY_GLN_1 | 2025-05-08 07:15 | 2025-05-08 15:37 | 2025-05-08 07:00 | No | NZ Steel, Counties Power | 41.9 | 8.36 | GLN0331, GLN0332, GLN0333
| OAM_T1 | 2025-05-08 09:12 | 2025-05-16 15:58 | 2025-05-08 09:00 | No | Network Waitaki | 23.7 | 198.78 | OAM0331
| GLN_220BS_A | 2025-05-09 07:22 | 2025-05-09 11:37 | 2025-05-09 07:00 | No | NZ Steel, Counties Power | 42.1 | 4.25 | GLN0331, GLN0332, GLN0333
| GLN_220BS_B | 2025-05-09 12:07 | 2025-05-09 15:45 | 2025-05-09 12:00 | No | NZ Steel, Counties Power | 42.3 | 3.64 | GLN0331, GLN0332, GLN0333
| GYM_KUM_1 | 2025-05-12 06:33 | 2025-05-12 21:22 | 2025-05-12 06:30 | No | Westpower | 31.7 | 14.82 | DOB0331, GYM0661
| GLN_220BS_A | 2025-05-12 07:15 | 2025-05-12 14:05 | 2025-05-12 07:00 | No | NZ Steel, Counties Power | 42.1 | 6.82 | GLN0331, GLN0332, GLN0333
| LFD_DIS_56 | 2025-05-12 07:31 | 2025-05-14 17:41 | 2025-05-12 07:30 | No | Vector | 74.8 | 58.16 | LFD1101
| MTN_T1 | 2025-05-12 07:33 | 2025-05-15 16:04 | 2025-05-12 07:30 | Yes | Powerco | 33.7 | 34.64 | MTN0331
| MST_GYT_UHT_1 | 2025-05-12 07:35 | 2025-05-16 16:06 | 2025-05-12 07:30 | No | Powerco | 79.7 | 104.53 | GYT0331
| WIL_T3 | 2025-05-12 07:44 | 2025-05-13 15:45 | 2025-05-12 07:30 | No | Wellington Electricity | 33.7 | 32 | WIL0331
| SVL_T2 | 2025-05-12 07:47 | 2025-05-17 06:15 | 2025-05-12 07:30 | No | Vector | 202.9 | 118.47 | SVL0331
| HAM_T4 | 2025-05-12 09:23 | 2025-05-12 15:45 | 2025-05-12 09:00 | No | WEL Networks | 220.9 | 6.35 | HAM0331
| GYM_KUM_1 | 2025-05-13 06:39 | 2025-05-13 21:40 | 2025-05-13 06:30 | No | Westpower | No Notification | 15.01 | DOB0331, GYM0661
| WHI_WRK_1 | 2025-05-13 07:06 | 2025-05-22 17:01 | 2025-05-13 07:00 | No | Unison Network, Eastlands Networks, Panpac | 160.6 | 225.92 | RDF0331, WTU0331, FHL0331,TUI1101, WHI0111, WHI0112
| GLN_220BS_B | 2025-05-13 07:12 | 2025-05-13 13:48 | 2025-05-13 07:00 | No | NZ Steel, Counties Power | 41.9 | 6.6 | GLN0331, GLN0332, GLN0333
| WRD_T7 | 2025-05-13 07:33 | 2025-05-14 17:52 | 2025-05-13 07:30 | No | Vector | 90.9 | 34.32 | WRD0331
| ROT_TRK_1 | 2025-05-13 08:18 | 2025-05-13 18:36 | 2025-05-13 08:00 | No | Unison Network | 47.8 | 10.3 | ROT0111, ROT0331
| GYM_KUM_1 | 2025-05-14 06:42 | 2025-05-14 20:02 | 2025-05-14 06:30 | No | Westpower | No Notification | 13.32 | DOB0331, GYM0661
| WIL_T5 | 2025-05-14 07:43 | 2025-05-15 13:50 | 2025-05-14 07:30 | No | Wellington Electricity | 35.7 | 30.11 | WIL0331
| ROT_T4 | 2025-05-14 08:05 | 2025-05-14 18:57 | 2025-05-14 08:00 | No | Unison Network | No Notification | 10.87 | ROT0111
| GYM_KUM_1 | 2025-05-15 06:05 | 2025-05-15 21:23 | 2025-05-15 06:00 | No | Westpower | No Notification | 15.3 | DOB0331, GYM0661
| LFD_DIS_76 | 2025-05-15 07:43 | 2025-05-17 15:31 | 2025-05-15 07:30 | No | Vector | 77.8 | 55.8 | LFD1101
| MGM_MST_1 | 2025-05-15 11:25 | 2025-05-16 08:05 | 2025-05-15 11:24 | No | Powerco | No Notification | 20.66 | MGM0331
| GYM_KUM_1 | 2025-05-16 06:07 | 2025-05-16 11:36 | 2025-05-16 06:00 | No | Westpower | No Notification | 5.48 | DOB0331, GYM0661
| HAM_OHW_1 | 2025-05-17 07:45 | 2025-05-17 15:05 | 2025-05-17 07:30 | No | WEL Networks, Waipa Networks, Powerco | 30.7 | 7.34 | HAM0111, CBG0111, TMU0111, TMU0112, WHU0331, WKO0331, KPU0661, PAO1101
| DRY_TAK_OTA_2 | 2025-05-19 07:02 | 2025-05-20 17:41 | 2025-05-19 07:00 | No | Vector | 41.9 | 34.64 | TAK0331
| TGA_T4 | 2025-05-19 07:33 | 2025-05-19 19:09 | 2025-05-19 07:30 | No | Powerco | 47 | 11.6 | TGA0331
| MST_GYT_UHT_2 | 2025-05-19 07:35 | 2025-05-23 14:03 | 2025-05-19 07:30 | No | Powerco | 86.7 | 102.47 | GYT0331
| CML_FKN_2 | 2025-05-19 07:37 | 2025-05-23 18:32 | 2025-05-19 07:30 | No | Aurora Energy, PowerNet | 59 | 106.91 | FKN0331, FKN0332
| STU_TIM_1 | 2025-05-19 07:51 | 2025-05-23 14:25 | 2025-05-19 07:30 | No | Alpine Energy | 44.8 | 102.56 | STU0111
| WKO_504_514_547 | 2025-05-19 08:18 | 2025-05-22 15:30 | 2025-05-19 08:00 | No | Powerco | 107.9 | 79.2 | WKO0331, KPU0661
| NSY_T1 | 2025-05-19 09:41 | 2025-05-19 10:46 | 2025-05-19 09:30 | No | PowerNet | 39.9 | 1.09 | NSY0331
| PRM_T1 | 2025-05-20 06:46 | 2025-05-27 12:18 | 2025-05-20 06:30 | No | Electra | 17.6 | 173.53 | PRM0331
| WTU_33BS_K | 2025-05-20 07:11 | 2025-05-23 15:13 | 2025-05-20 07:00 | No | Unison Network | 74.8 | 80.04 | WTU0331
| CUL_T23 | 2025-05-20 07:15 | 2025-05-20 16:51 | 2025-05-20 07:00 | No | Mainpower New Zealand | 4.5 | 9.59 | CUL0331
| DRY_TAK_OTA_1 | 2025-05-21 07:14 | 2025-05-22 17:38 | 2025-05-21 07:00 | No | Vector | 42 | 34.4 | TAK0331
| HWA_WVY_1 | 2025-05-21 08:21 | 2025-05-21 16:50 | 2025-05-21 08:00 | No | Powerco, Beach Energy | 7.6 | 8.49 | HWA0331, HWA0332
| CUL_T22 | 2025-05-26 06:44 | 2025-05-31 13:40 | 2025-05-26 06:30 | No | Mainpower New Zealand | 41.6 | 126.94 | CUL0331
| GFD_HAY_1 | 2025-05-26 07:44 | 2025-05-27 14:52 | 2025-05-26 07:30 | No | Wellington Electricity | 47.7 | 31.14 | GFD0331
| WTK_T23 | 2025-05-26 09:06 | 2025-05-30 11:26 | 2025-05-26 08:30 | No | Network Waitaki, Alpine Energy | 41.7 | 98.33 | OAM0331, STU0111
| TGA_11BS_B | 2025-05-26 09:11 | 2025-05-29 20:43 | 2025-05-26 08:30 | No | Powerco | 101.8 | 83.52 | TGA0111
| STU_CB_62 | 2025-05-26 09:21 | 2025-06-06 12:18 | 2025-06-01 | No | Alpine Energy | No Notification | 266.95 | STU0111
| HRP_RDF_1 | 2025-05-27 07:03 | 2025-06-05 13:33 | 2025-06-01 | No | Unison Network, Eastlands Networks, Panpac | 174.6 | 222.49 | RDF0331, WTU0331, FHL0331,TUI1101, WHI0111, WHI0112
| GOR_T2 | 2025-05-27 07:32 | 2025-05-27 14:11 | 2025-05-27 07:30 | No | PowerNet | 39.8 | 6.65 | GOR0331
| ROT_T3 | 2025-05-27 07:35 | 2025-05-29 18:45 | 2025-05-27 07:30 | No | Unison Network | 45.9 | 59.17 | ROT0111
| HAM_PAO_WHU_2 | 2025-05-27 07:39 | 2025-05-29 18:44 | 2025-05-27 07:30 | No | Powerco | 185.8 | 59.08 | PAO1101, WHU0331, WKO0331, KPU0661
| MPE_CB_252 | 2025-05-27 07:45 | 2025-05-27 22:31 | 2025-05-27 07:30 | No | Northpower, Top Energy | 87.8 | 14.765 | BRB0331, KOE1101, MTO0331
| HPI_MDN_1 | 2025-05-27 07:52 | 2025-05-28 15:05 | 2025-05-27 07:30 | No | Northpower, Top Energy | 91.7 | 31.21 | BRB0331, MPE1101, KOE1101, MTO0331
| HAM_127_224 | 2025-05-27 12:29 | 2025-05-28 17:35 | 2025-05-27 12:00 | No | WEL Networks, Waipa Networks, Powerco | 42.3 | 29.1 | HAM0111, CBG0111, TMU0111, TMU0112,
| MPE_CB_252 | 2025-05-28 06:03 | 2025-05-28 15:16 | 2025-05-28 06:00 | No | Northpower, Top Energy | 88.8 | 9.22 | BRB0331, KOE1101, MTO0331
| HAY_WIL_LTN_1 | 2025-05-28 06:34 | 2025-05-30 12:34 | 2025-05-28 06:30 | No | Powerco | 22 | 53.99 | LTN0331
| EDN_INV_1 | 2025-05-28 07:39 | 2025-05-30 15:15 | 2025-05-28 07:30 | No | Daiken , PowerNet | 40.8 | 55.6 | BDE0111, BDE0112, EDN0331
| HOR_KBY_ISL_1 | 2025-05-28 07:40 | 2025-07-04 13:07 | 2025-05-28 07:30 | No | Orion New Zealand | 186.9 | 893.45 | KBY0661, KBY0662
| GFD_HAY_2 | 2025-05-28 07:46 | 2025-05-29 09:48 | 2025-05-28 07:30 | No | Wellington Electricity | 49.7 | 26.03 | GFD0331
| KPO_TMU_1 | 2025-05-29 07:41 | 2025-05-30 13:02 | 2025-05-29 07:30 | No | Waipa Networks | 69.8 | 29.35 | TMU0111, TMU0112
| ALB_WRD_GXP_TIE | 2025-05-30 08:32 | 2025-05-31 08:56 | 2025-05-30 08:30 | No | Vector | No Notification | 24.41 | WRD0331
| KOE_MPE_1 | 2025-05-31 11:02 | 2025-05-31 14:37 | 2025-05-31 11:00 | No | Top Energy | 8.9 | 3.57 | KOE1101
| LFD_DIS_56 | 2025-06-03 07:07 | 2025-06-05 14:20 | 2025-06-03 07:00 | No | Vector | 20.9 | 55.22 | LFD1101
| CBG_T3 | 2025-06-03 07:34 | 2025-06-04 15:39 | 2025-06-03 07:30 | No | Waipa Networks | 136.9 | 32.08 | CBG0111
| ROT_T2 | 2025-06-03 07:35 | 2025-06-27 13:22 | 2025-06-03 07:30 | No | Unison Network | 59.8 | 581.7772 | ROT0331
| TMK_TIM_2_TMK_T2 | 2025-06-03 07:36 | 2025-06-03 16:22 | 2025-06-03 07:30 | No | Alpine Energy | 34.7 | 8.775 | TMK0331
| HAM_T8 | 2025-06-03 07:41 | 2025-06-03 16:15 | 2025-06-03 07:30 | No | KiwiRail | 48.9 | 8.56 | HAM0551, HAM0552
| TMU_T1 | 2025-06-03 07:45 | 2025-06-04 16:17 | 2025-06-03 07:30 | No | Waipa Networks | 27.7 | 32.52 | TMU0111, TMU0112
| HAM_PAO_WHU_1 | 2025-06-03 07:51 | 2025-06-05 17:23 | 2025-06-03 07:30 | No | Powerco | 66.7 | 57.54 | PAO1101, WHU0331, WKO0331, KPU0661
| HWA_T1 | 2025-06-03 08:03 | 2025-06-05 15:34 | 2025-06-03 08:00 | No | Powerco, Beach Energy | 312.9 | 55.51 | HWA0331, HWA0332
| EDN_T2 | 2025-06-03 08:04 | 2025-06-04 09:23 | 2025-06-03 08:00 | No | PowerNet | 49.7 | 25.31 | EDN0331
| DRY_GLN_2 | 2025-06-03 08:16 | 2025-06-06 16:12 | 2025-06-03 08:00 | No | NZ Steel, Counties Power | 83.9 | 79.94 | GLN0331, GLN0332, GLN0333
| CBG_T4 | 2025-06-05 07:34 | 2025-06-06 13:13 | 2025-06-05 07:30 | No | Waipa Networks | 138.9 | 29.65 | CBG0111
| TMU_T2 | 2025-06-05 08:06 | 2025-06-06 15:08 | 2025-06-05 08:00 | No | Waipa Networks | 138.9 | 31.03 | TMU0111, TMU0112
| BRB_T3 | 2025-06-05 08:09 | 2025-06-05 12:48 | 2025-06-05 08:00 | No | Northpower | 6 | 4.66 | BRB0331
| HEN_MPE_1 | 2025-06-05 09:46 | 2025-06-05 14:03 | 2025-06-05 09:30 | No | Vector, Northpower | 28.8 | 4.27 | WEL0331, MTO0331
| GYM_KUM_1 | 2025-06-06 08:12 | 2025-06-06 11:26 | 2025-06-06 08:00 | No | Westpower | No Notification | 3.23 | GYM0661
| OAM_STU_BPD_WTK_2 | 2025-06-06 09:40 | 2025-06-06 12:28 | 2025-06-06 09:30 | No | Network Waitaki, Alpine Energy | 76.9 | 2.8 | OAM0331, STU0111
| DVK_T1 | 2025-06-09 07:33 | 2025-06-11 11:52 | 2025-06-09 07:30 | No | Scanpower | 54.7 | 52.32 | DVK0111
| BRB_T2 | 2025-06-09 07:33 | 2025-06-13 17:36 | 2025-06-09 07:30 | No | Northpower | 229.7 | 106.04 | BRB0331
| WIR_T1 | 2025-06-09 08:27 | 2025-06-17 16:21 | 2025-06-09 08:00 | No | Vector | 128.7 | 199.91 | WIR0331
| LFD_DIS_76 | 2025-06-10 07:14 | 2025-06-12 15:07 | 2025-06-10 07:00 | No | Vector | 3.8 | 55.89 | LFD1101
| UHT_T1 | 2025-06-10 07:36 | 2025-06-12 12:34 | 2025-06-10 07:30 | No | Wellington Electricity | 382.6 | 52.96 | UHT0331
| BAL_T1 | 2025-06-10 07:52 | 2025-06-12 18:15 | 2025-06-10 07:30 | No | PowerNet | 40.7 | 58.39 | BAL0331
| WDV_T1 | 2025-06-10 09:25 | 2025-06-11 08:52 | 2025-06-10 09:00 | No | Scanpower | 39.7 | 23.45 | WDV0111
| KMO_MTM_TGA_2 | 2025-06-11 07:03 | 2025-06-13 14:42 | 2025-06-11 07:00 | No | Powerco | 43.9 | 55.64 | MTM0331, TGA0111, TGA0331
| KMO_TMI_1 | 2025-06-11 07:10 | 2025-06-13 14:41 | 2025-06-11 07:00 | No | Powerco | 43.9 | 55.52 | TMI0331
| IGH_ROB_1 | 2025-06-11 10:52 | 2025-06-11 15:26 | 2025-06-11 10:45 | No | Buller Electricity | No Notification | 4.57 | ROB0111, ROB0331
| DVK_T2 | 2025-06-11 12:22 | 2025-06-13 10:52 | 2025-06-11 12:00 | No | Scanpower | 56.9 | 46.51 | DVK0111
| WRK_T29 | 2025-06-14 08:09 | 2025-06-14 17:14 | 2025-06-14 08:00 | No | Unison Network | 37.9 | 9.085 | WRK0331
| CYD_T8 | 2025-06-14 10:17 | 2025-06-14 14:26 | 2025-06-14 10:00 | No | Aurora Energy | No Notification | 4.15 | CYD0331
| KOE_MPE_1 | 2025-06-15 10:15 | 2025-06-15 12:16 | 2025-06-15 10:00 | No | Top Energy | 23.8 | 2.01 | KOE1101
| MPE_CB_252 | 2025-06-16 06:29 | 2025-06-26 10:49 | 2025-06-17 06:00 | Yes | Northpower, Top Energy | 193.8 | 96.4 | BRB0331, KOE1101, MTO0331
| PNI_TKR_1 | 2025-06-16 07:35 | 2025-06-17 13:36 | 2025-06-16 07:30 | No | Wellington Electricity | 26.8 | 30.02 | PNI0331
| TMK_TIM_2_TMK_T2 | 2025-06-16 07:35 | 2025-06-26 16:36 | 2025-06-16 07:30 | No | Alpine Energy | 52.9 | 249.01 | TMK0331
| MPE_CB_252 | 2025-06-16 07:36 | 2025-06-16 21:43 | 2025-06-16 07:30 | No | Northpower, Top Energy | 296.7 | 14.12 | BRB0331, KOE1101, MTO0331
| OWH_TMI_TRK_1 | 2025-06-16 07:36 | 2025-06-26 11:26 | 2025-06-16 07:30 | No | Unison Networks, Powerco | 144.8 | 243.83 | OWH0111, TMI0331
| HPI_MDN_1 | 2025-06-16 07:38 | 2025-06-27 10:35 | 2025-06-16 07:30 | No | Northpower, Top Energy | 296.7 | 266.96 | BRB0331, MPE1101, KOE1101, MTO0331
| BAL_T2 | 2025-06-16 07:42 | 2025-06-19 15:43 | 2025-06-16 07:30 | No | PowerNet | 41.9 | 80.02 | BAL0331
| MGM_CB_172 | 2025-06-17 06:00 | 2025-06-18 15:20 | 2025-06-17 08:00 | Yes | Powerco | 7.7 | 7.25 | MGM0331
| BDE_EDN_1 | 2025-06-17 07:42 | 2025-06-18 14:50 | 2025-06-17 07:30 | No | Daiken , PowerNet | 42.9 | 31.13 | BDE0111, BDE0112, EDN0331
| ROT_TRK_2 | 2025-06-17 08:25 | 2025-06-19 17:36 | 2025-06-17 08:00 | No | Unison Network | 73.8 | 57.17 | ROT0111, ROT0331
| PNI_TKR_2 | 2025-06-18 07:33 | 2025-06-19 08:04 | 2025-06-18 07:30 | No | Wellington Electricity | 28.8 | 24.51 | PNI0331
| SFD_T9 | 2025-06-18 10:01 | 2025-06-18 15:01 | 2025-06-18 10:00 | No | Powerco, Beach Energy | 41.9 | 4.99 | SFD0331, OPK0331, HWA0331, HWA0332
| HOR_T5 | 2025-06-23 07:07 | 2025-07-21 14:41 | 2025-06-23 07:00 | No | Orion New Zealand | 394.9 | 679.57 | HOR0331
| SDN_T1 | 2025-06-23 07:40 | 2025-06-27 19:16 | 2025-06-23 07:30 | No | Aurora Energy | 44.7 | 107.61 | SDN0331
| MGM_T2 | 2025-06-24 07:10 | 2025-06-25 14:07 | 2025-06-24 07:00 | No | Powerco | 27.9 | 30.96 | MGM0331
| OPK_SFD_1 | 2025-06-24 08:16 | 2025-06-25 18:52 | 2025-06-24 08:00 | No | Powerco | 52.9 | 34.61 | OPK0331
| UHT_T2 | 2025-06-24 08:34 | 2025-06-26 11:33 | 2025-06-24 08:30 | No | Wellington Electricity | 396.7 | 50.98 | UHT0331
| MGM_T3 | 2025-06-26 07:02 | 2025-06-27 14:39 | 2025-06-26 07:00 | No | Powerco | 29.9 | 31.61 | MGM0331
| KAW_T5 | 2025-06-26 07:02 | 2025-06-26 15:10 | 2025-06-26 07:00 | No | Horizon Energy | 30.9 | 8.12 | KAW0111
| MPE_CB_252 | 2025-06-27 06:04 | 2025-06-27 10:39 | 2025-06-27 06:00 | No | Northpower, Top Energy | 203.8 | 4.58 | BRB0331, KOE1101, MTO0331
| MNI_T3 | 2025-06-30 08:06 | 2025-06-30 17:10 | 2025-06-30 08:00 | No | Methanex | 26.7 | 9.08 | MNI0111, MNI0112
| KAW_T2 | 2025-06-30 13:39 | 2025-06-30 16:49 | 2025-06-30 13:30 | No | Horizon Energy | 35.2 | 3.17 | KAW0111

## 5
Summary of all reports publicly disclosed under clause 26.1 for the disclosure year
Transpower IPP determination 2020, Part 5, clause 28.1
28.1 Transpower must publicly disclose at the same time as its annual compliance statement a summary of all reports publicly disclosed under clause 26.1 for the disclosure year.
26.1 Subject to clause 27, for each unplanned interruption during a disclosure year which lasts 12 hours or more, Transpower must publicly disclose within 42 working days of the unplanned interruption:
26.1.1 the cause of the unplanned interruption; | 26.1.1 the cause of the unplanned interruption;
26.1.2 the start date and time of the unplanned interruption; | 26.1.2 the start date and time of the unplanned interruption;
26.1.3 the end date and time of the unplanned interruption; | 26.1.3 the end date and time of the unplanned interruption;
26.1.4 the megawatts affected by the unplanned interruption; | 26.1.4 the megawatts affected by the unplanned interruption;
26.1.5 the grid exit point(s) and grid injection point(s) affected by the unplanned interruption; | 26.1.5 the grid exit point(s) and grid injection point(s) affected by the unplanned interruption;
26.1.6 actions Transpower took to minimise the effect of the unplanned interruption; and | 26.1.6 actions Transpower took to minimise the effect of the unplanned interruption; and
26.1.7 a description of steps that Transpower proposes to take to mitigate the risk of future unplanned interruptions of this type. | 26.1.7 a description of steps that Transpower proposes to take to mitigate the risk of future unplanned interruptions of this type.
| Event | Published report link below
| South Canterbury Loss of Supply – 30 September–1 October 2024 | Albury and Tekapo interruption report (published November 2024)

## 6
Summary of all reports publicly disclosed under clause 26.2 for the disclosure year
Transpower IPP determination 2020, Part 5, clause 28.2
28.2 Transpower must publicly disclose at the same time as its annual compliance statement a summary of all reports publicly disclosed under clause 26.2 for the disclosure year.
26.2 Subject to clause 27, for each unplanned interruption during a disclosure year over one system minute, Transpower must publicly disclose within 42 working days of the unplanned interruption:
26.2.1 the cause of the unplanned interruption;
26.2.2 the start date and time of the unplanned interruption;
26.2.3 the end date and time of the unplanned interruption;
26.2.4 the megawatts affected by the unplanned interruption;
26.2.5 the grid exit point(s) and grid injection point(s) affected by the unplanned interruption;
26.2.6 actions Transpower took to minimise the effect of the unplanned interruption; and
26.2.7 a description of steps that Transpower proposes to take to mitigate the risk of future unplanned interruptions of this type
| Event | Published report link below
| South Canterbury Loss of Supply – 30 September–1 October 2024 | Albury and Tekapo interruption report (published November 2024)
| Hawkes Bay Loss of Supply – 21 December 2024 | Hawkes Bay interruption report (published February 2025)

## 7
Grid performance Measure GP-M
Transpower IPP determination 2020, Part 5, clause 28.3
28.3 Transpower must publicly disclose at the same time as its annual compliance statement, for measure of grid performance GP-M, which measures reliability through the number of momentary interruptions, the number of momentary interruptions for the disclosure year;
The number of momentary interruptions for the disclosure year
28
GP-M Details
Transpower IPP determination 2020, Part 5, clause 28.4
28.4 Transpower must publicly disclose at the same time as its annual compliance statement:
28.4.1 the cause of each momentary interruption, which may include ‘unknown causes’, for the disclosure year;
28.4.2 the date and time of each momentary interruption for the disclosure year;
28.4.3 the grid exit point(s) and grid injection point(s) affected by each momentary interruption for the disclosure year;
| Site | Point of Service (GXP/GIP) | RCP3 Category | Start Date Time | Cause | Comment
| Waiotahe | WAI011S1 | N Material | 2025-06-11 01:06 | Environmental - Suspected Lightning (NO damage but SDTF, FALLS, or SCADA/relay evidence) | EDG-WAI-2 trip & A/R, probably caused by a lightning strike. Momentary LOS to Horizon Energy.
| Arthurs Pass | APS011S1 | N Material | 2025-06-02 19:18 | Miscellaneous - Cause Not Found | COL-OTI-1 trip & A/R, Rph-E fault, cause unknown. Momentary LOS at CLH and APS. No circuit patrol.
| Castle Hill | CLH011S1 | N Material | 2025-06-02 19:18 | Miscellaneous - Cause Not Found | COL-OTI-1 trip & A/R, Rph-E fault, cause unknown. Momentary LOS at CLH and APS. No circuit patrol.
| Murchison | MCH011S1 | N Material | 2025-04-23 14:17 | Miscellaneous - Cause Not Found | IGH-KIK-1 trip & A/R YPh-E fault, momentary LOS at MCH to Network Tasman of 3MW.
| Wellsford | WEL033S1 | N-1 Material | 2025-04-18 21:50 | Environmental - Suspected Lightning (NO damage but SDTF, FALLS, or SCADA/relay evidence) | HEN-MPE-1&2 trip & A/R. Momentary LOS at WEL.
| Studholme | STU011S1 | N-1 Material | 2025-02-19 20:29 | Environmental - Suspected Lightning (NO damage but SDTF, FALLS, or SCADA/relay evidence) | STU-TIM-1 trip & TIM82 A/R, lightning near twr 153. Momentary LOS to STU.
| Murchison | MCH011S1 | N Material | 2025-01-20 10:25 | Miscellaneous - Cause Not Found | IGH-KIK-1 trip & A/R YPh-E fault, momentary LOS at MCH to Network Tasman of 2MW.
| Arthurs Pass | APS011S1 | N Material | 2025-01-02 03:00 | Miscellaneous - Cause Not Found | COL-OTI-1 trip & A/R, Rph-E fault, cause unknown, momentary LOS at CLH and APS. No circuit patrol.
| Castle Hill | CLH011S1 | N Material | 2025-01-02 03:00 | Miscellaneous - Cause Not Found | COL-OTI-1 trip & A/R, Rph-E fault, cause unknown, momentary LOS at CLH and APS. No circuit patrol.
| Arthurs Pass | APS011S1 | N Material | 2025-01-01 23:34 | Miscellaneous - Cause Not Found | COL-OTI-1 trip & A/R, Rph-E fault, cause unknown, momentary LOS at CLH and APS. No circuit patrol.
| Castle Hill | CLH011S1 | N Material | 2025-01-01 23:34 | Miscellaneous - Cause Not Found | COL-OTI-1 trip & A/R, Rph-E fault, cause unknown, momentary LOS at CLH and APS. No circuit patrol.
| Murchison | MCH011S1 | N Material | 2024-12-21 16:47 | Miscellaneous - Cause Not Found | IGH-KIK-1 trip & A/R RPh-E fault, momentary LOS at MCH to Network Tasman.
| Reefton | RFN110S1 | N-1 Material | 2024-12-16 00:30 | Environmental - Suspected Lightning (NO damage but SDTF, FALLS, or SCADA/relay evidence) | ATU-RFN-IGH-1 tripped & A/R, yellow phase to earth fault, probably caused by a lightning strike. Circuit was not patrolled. Momentary LOS at RFN to Westpower.
| Arthurs Pass | APS011S1 | N Material | 2024-12-12 22:31 | Miscellaneous - Cause Not Found | COL-OTI-1 trip & A/R, Rph-E fault, cause unknown, momentary LOS at CLH and APS. No circuit patrol.
| Castle Hill | CLH011S1 | N Material | 2024-12-12 22:31 | Miscellaneous - Cause Not Found | COL-OTI-1 trip & A/R, Rph-E fault, cause unknown, momentary LOS at CLH and APS. No circuit patrol
| Murchison | MCH011S1 | N Material | 2024-11-06 00:20 | Miscellaneous - Cause Not Found | IGH-KIK-1 trip & A/R RPh-E fault, momentary LOS at MCH to Network Tasman.
| Arthurs Pass | APS011S1 | N Material | 2024-10-26 09:10 | Environmental - Snow or Ice | COL-OTI 1 tripped & A/R at OTI & COL, only COL272 tripped again, caused by snow or ice loading of Rph & Yph conductors which clashed. Momentary LOS at APS to Orion.
| Castle Hill | CLH011S1 | N Material | 2024-10-26 09:10 | Environmental - Snow or Ice | COL-OTI 1 tripped & A/R at COL & OTI, only COL272 tripped again, caused by snow or ice loading of Rph & Yph conductors which clashed. Momentary LOS at CLH to Orion.
| National Park | NPK033S1 | N Material | 2024-10-20 06:25 | Miscellaneous - Cause Not Found | OKN-NPK-ONG-1 trip & A/R, for a yellow phase to earth fault, cause unknown. NPK-TF-T1 trip & A/R. There was a momentary interruption of supply to The Lines Company Ltd at NPK. The circuit was not patrolled.
| Black Point | BPT110S1 | N Material | 2024-10-10 06:13 | Miscellaneous - Cause Not Found | OAM-BPT-WTK-1 trip, Yph-E fault, cause unknown, no circuit patrol, momentary LOS at BPT.
| National Park | NPK033S1 | N Material | 2024-09-22 16:54 | Environmental - Suspected Lightning (NO damage but SDTF, FALLS, or SCADA/relay evidence) | OKN-NPK-ONG-1 trip & A/R, for a yellow to blue phase to earth fault, probably caused by a lightning strike. NPK-TF-T1 trip & A/R. There was a momentary interruption of supply to The Lines Company Ltd at NPK. The circuit was not patrolled.
| National Park | NPK033S1 | N Material | 2024-09-01 01:16 | Environmental - Suspected Lightning (NO damage but SDTF, FALLS, or SCADA/relay evidence) | OKN-NPK-ONG-1 trip & A/R, for a yellow phase to earth fault, probably caused by a lightning strike. NPK-TF-T1 trip & A/R. There was a momentary interruption of supply to The Lines Company Ltd at NPK. The circuit was not patrolled.
| Studholme | STU011S1 | N-1 Material | 2024-08-28 09:42 | Environmental - Birds or Bird Streamers | OAM-STU-BPD-WTK2 tripped. Cause unknown. Momentary ITC at STU to Alpine Energy (as STU DS76, on STU-TIM-1, is normally open but auto switched if drop in STU VT6 voltage).
| Greytown | GYT033S1 | N-1 Material | 2024-08-19 16:14 | Environmental - Suspected Lightning (NO damage but SDTF, FALLS, or SCADA/relay evidence) | MST-GYT-UHT1&2 tripped, cct 1 A/R, momentary LOS at GYT to Powerco.
| Arthurs Pass | APS011S1 | N Material | 2024-08-18 16:14 | Environmental - Snow or Ice | COL-OTI-1 trip & A/R, YPh-BPh momentary LOS at APS and CLH to ORN, caused by a build up of snow or ice on conductors that clashed when ice or snow fell off.
| Castle Hill | CLH011S1 | N Material | 2024-08-18 16:14 | Environmental - Snow or Ice | COL-OTI-1 trip & A/R, YPh-BPh, momentary LOS at APS and CLH, caused by a build up of snow or ice on conductors that clashed when ice or snow fell off.
| Murchison | MCH011S1 | N Material | 2024-08-01 11:14 | Miscellaneous - Cause Not Found | IGH-KIK-1 trip & A/R RPh-E fault, momentary LOS at MCH to Network Tasman.
| Waiotahe | WAI011S1 | N Material | 2024-07-21 23:27 | Environmental - Lightning in area (No physical evidence or SDTF, FALLS, SCADA/relay data | EDG-WAI-2 trip & A/R, probably caused by a lightning strike, momentary LOS to Horizon Energy.
Explanation of any general trends in momentary interruptions
28.4.4 an explanation of any general trends in momentary interruptions.
Most of the momentary interruptions causes were not found. Out of the causes that could be identified, most are due to environmental factors. The number of momentary interruptions for 2024/25 disclosure year is close to the average for the last 5 years (2020/21 - 2024/25) which is 28.

## 8
Asset performance measure AP1 if outside of the collar value
Transpower IPP determination 2020, Part 5, clause 28.5
28.5 Where asset performance measure AP1, as calculated in accordance with clause 19.3.3, is outside of the collar value specified in Table 4.2, Transpower must publicly disclose at the same time as its annual compliance statement:
28.5.1 reasons, including whether the reasons are unknown, for asset performance measure AP1 going outside of the collar, and including any significant impact on the market (for example, the effect on market price or grid congestion);
28.5.2 actions Transpower has taken to minimise the effect of the events described in clause 28.5.1; and
28.5.3 a description of steps that Transpower proposes to take to mitigate the risk of going outside of the collar in the future
Additional Planned work primarily caused AP1 to be outside the collar value. Pole 2 refurbishment project (referred to as Project K) required more work than we originally planned. This additional planned work was not anticipated when we submitted our RCP3 proposal. Tab 2 of the Annual Compliance Statement workbook shows Transpower's performance against the quality standards.
| Events | Reasons for AP1 going below the collar | Transpower's actions to minimise the effect of the events
| Pole 2 refurbishment project (referred to as Project K) February-March 2025 | The collar was breached by 0.26%. the allowance for project K was 0.7%, which equates to 6 additional days of Pole 2 outage to undertake project works. In 2025, 14 days of Pole 2 outage were rquired above the regular 4 day Pole 2 and 2 day Bipole shutdown. This had an impact of 1.43% on the AP1 availability, so the reason for breaching can be attributed to project K exceeding the allowance. | Transpower is undertaking the Pole 2 midlife refurbishments as a one-off project through RCP3 to ensure continued high availability of the aging Pole 2. At the time of setting the RCP3 AP1 target, detailed planning for the outage requirements of the various projects associated with the Pole 2 mid-life refurbishment had not been completed.

## 9
Asset performance measure AP2 if outside of the collar value
Transpower IPP determination 2020, Part 5, clause 28.6
28.6 Where asset performance measure AP2, as calculated in accordance with clause 19.3.4, is outside of the collar value specified in Table 4.2, Transpower must publicly disclose at the same time as its annual compliance statement:
28.6.1 the events that caused asset performance measure AP2 to go below the collar;
28.6.2 reasons, including whether the reasons are unknown, for asset performance measure AP2 going below the collar;
28.6.3 actions Transpower has taken to minimise the effect of the events described in clause 28.6.1; and
28.6.4 a description of steps that Transpower proposes to take to mitigate the risk of going below the collar in the future
The planned outages that primarily caused AP2 to be outside the collar value: Outages associated with the PAK-WKM-2 cable joint replacement work. Details are described in the table below. We consider this outage meet our definition of an exceptional event and have informed Commerce Commission accordingly. Tab 2 of the Annual Compliance Statement workbook shows Transpower's performance against the quality standards (including the exceptional events). Tab 2(a) of the Annual Compliance Statement workbook shows Transpower's performance against the quality standards (excluding the exceptional events).
| Events | Reasons for AP2 going below the collar | Transpower's actions to minimise the effect of the events
| PAK-WKM-2 cable joint replacement work: 8498 hours, corresponding to1.37% AP2 Unavailability | "The event involves excavating joint bays and replacing 45 cable joints on the ""B"" cable circuit (PAK-WKM-2) commenced in 23/24 following the completion of replacement of six joints on the ""A"" cable circuit (PAK-WKM-1). To allow for this we need to extend each joint bay (up to 30 metres long) for replacement of cable joints on the ""B"" cable. For efficiency, we have work at multiple bays happening at once utilising two specialist local Civil Engineering subcontractors. Prior to the outage, a bypass was established utilising an overhead line deviation near the Ohinewai substation to negate the full outage impact. Two cable joints failed in the last couple of years on the ""B"" cable circuit between Brownhill and Pakuranga substations. This led us to investigate the condition of joints elsewhere on the circuit, and the condition of joints on the adjacent ""A"" circuit. We found that the ""A"" circuit joints were in the condition we expected, but there were potential future issues with the ""B"" circuit. The cables support security of supply for Auckland and Northland and ensure peak demand can be met. Replacing these joints now returns this important cable to its intended condition, so it can operate effectively for its expected remaining 30–40-year asset life." Two cable joints failed in the last couple of years on the "B" cable circuit between Brownhill and Pakuranga substations. This led us to investigate the condition of joints elsewhere on the circuit, and the condition of joints on the adjacent "A" circuit. We found that the "A" circuit joints were in the condition we expected, but there were potential future issues with the "B" circuit. The cables support security of supply for Auckland and Northland and ensure peak demand can be met. Replacing these joints now returns this important cable to its intended condition, so it can operate effectively for its expected remaining 30–40-year asset life. | Transpower identified the need to address failure risks while recognised the impact from this event. A bypass was put in to minimise (negate) the affect the outage of the listed assets. Despite the link being re-established with the bypass, the specifications of the IPP require us to continue to report the hours when the PAK-WKM cable is out of service. During the replacement process, Transpower and its Service Provider undertook the replacement work by balancing the speed of replacement and resourcing requirement in line with Good Electricity Industry Practice.
To mitigate the risk of going below the AP2 collar in the future, we have established an AP2 governance and management approach. This framework provides for oversight and key decision making in relation to AP2.

## 10
If not complied with the asset health measure AH quality standard for an asset health measure asset class
Transpower IPP determination 2020, Part 5, clause 28.7
28.7 Where Transpower has not complied with the asset health measure AH quality standard for an asset health measure asset class, as specified in clause 21.2, it must publicly disclose at the same time as its annual compliance statement:
28.7.1 reasons for not meeting the quality standard, and supporting evidence for those reasons; and
28.7.2 steps that have been put in place by Transpower to prevent future noncompliance with the quality standard.
Not Applicable as Asset Health has complied with Quality Standard
| Asset class | Reasons | Steps
Not Applicable for Disclosure Year 2024/25